## Description
Ventilation Increase Impacts Calculator
Background
Industry-standard recommendations are to increase outside air flow and reduce (re-)circulation of air within buildings, in order to reduce SARS-CoV-2 concentration. This ventilation calculator was developed to help building operators assess the impact of these recommendations on their HVAC systems. The tool has been derived from an existing building retuning energy savings calculator created by CUNY’s Building Performance Lab to support Load Management efforts. It enables the user to calculate the heating load (in kBTU/hr) and cooling loads (in Tons) needed to satisfy discharge air setpoints when more outside air is used in a building. Loads are calculated over a range of outside air temperatures, outside air enthalpies and outside air fractions.
How it works
This calculator requires a series of inputs that can be found from equipment schedules, BAS data, sequences of operation, and operators’ discretion.
Input tab
For general use: Input the time of day when HVAC operation starts and ends. Also input CFM in the supply duct, space area, ceiling height, and fuel type used for heating.
For the heating season: Input the unit’s expected return air temperature (RAT), discharge air temperature setpoint (DATSP) and heating efficiency.
For the cooling season: Input the unit’s expected return air temperature (RAT), discharge air temperature setpoint (DATSP) and cooling efficiency.
For air flush use: Input Filter MERV rating
Outputs tabs
Ventilation Scenarios tab: | Shows achivable air exchange rates for different weather scenarios based on system's capacity
Average Heating Load vs OAT tab: | Shows the average load for heating outside air at specific temperatures and outside air fraction (outside air changes per hour).
Average Cooling Load vs OAT tab: | Shows the average load for cooling outside air at specific temperatures and outside air fraction (outside air changes per hour).
Average Cooling Load vs Enthalpy tab: | Shows the average cooling load for cooling outside air at specific enthalpies and outside air fraction (outside air changes per hour).
Energy Consumption tab: | Shows two graphs: Annualized cooling energy consumption, energy cost, and CO2 Equivalent GHG emissions for specific outside air fractions plus annualized heating energy consumption and CO2 equivalent GHG emissions for specific outside air fractions (outside air changes per hour).
Air Flush tab: | Shows aerosol removal time for different outside air fractions (outside air changes per hour) and removal efficiencies.
CO2 Risk Assessment: | Shows the amount required to reach the user defined CO2 critical threshold for different ventilation and weather scenarios.
Other tabs: The last three tabs have values for calculations (Cooling Season calculations; Heating Season calculations; Dropdown Contents + Conversion); no user inputs required.
ASHRAE, “Building Readiness” ASHRAE Website, https://www.ashrae.org/technical-resources/building-readiness#increasedvent

## Inputs
Ventilation Increase Impacts Calculator
Inputs | [8 empty] | Description
| Sun | Mon | Tue | Wed | Thu | Fri | Sat | Heating Season | 10/1 to 5/31
HVAC Operation Starts | 06:00:00.000 | 06:00:00.000 | 06:00:00.000 | 06:00:00.000 | 06:00:00.000 | 06:00:00.000 | 06:00:00.000 | Cooling Season | 6/1 to 9/30
HVAC Operation Ends | 19:00:00.00000000002558025 | 19:00:00.00000000002558025 | 19:00:00.00000000002558025 | 19:00:00.00000000002558025 | 19:00:00.00000000002558025 | 19:00:00.00000000002558025 | 19:00:00.00000000002558025
User Input Variables
General
CFM in the supply duct | 35000
Space Area (ft2) | 100000
Ceiling Height (ft) | 10
Pick your heating fuel type | Natural Gas
Heating Season
RAT | 72
DATSP | 80
Heating Capacity (kBTU/hr) | 1000
Heating efficiency | 0.75
Cooling Season
RAT | 74
DATSP | 55
Cooling Capacity (Tons) | 120
Cooling efficiency | 0.75
Filter Efficiency (MERV)
MERV | 8
Chiller Efficiency Guideline (kW/ton)
High | 0.6
Medium | 0.75
Low | 0.9
RTU Enery Efficiency Ratio (EER)
High | 12
Medium | 8
Low | 5
Directions & Notes
Fill out the yellow boxes with values from your systems.
In some boxes, an arrow will appear to the right side. Click it to expand the dropdown list.
Please be sure that your outside air damper position is sufficient to at least meet ASHRAE's 62.1 minimum ventilation requirement (https://ashrae.iwrapper.com/ViewOnline/Standard_62.1-2019).
For cooling efficiency, please input chiller efficiency (kW/ton) if you have a chiller system or the Energy Efficiency Ratio (ERR) if you have a DX unit. Efficiency tables are provided for reference.
Cooling or heating capacity for air units connected to a central plant can be found from the HVAC schedule or unit nameplate. They may need to be converted to the specific units for this calculator. If the cooling capacity units are MBTUH, divide the value by 12 to conver units to Tons.
To use the charts in the "Average Heating Load vs OAT", "Average Cooling Load vs OAT and "Average Cooling Load vs Enthalpy" sheets: First find the expected outside air temperature. Then select an outside air fraction. Ensure that the corresponding load is below the units maximum load (within the green zone). if not, decrease the outside air fraction until the load is below the maximum (within the green zone).
Assumptions & Definitions
1. DA RH is 75%.
2. RA RH is 50%.
3. During cooling season, Economizing occurs when in cooling mode and when the OAT is between 55°F and 65°F.
4. Total CFM is assumed to remain constant. Outdoor CFM varies as a function of Outdoor Air Fraction.
5. OA damper leakage, when closed, is negligible.
6. Outdoor Air Changes per Hour are calculated as Outdoor Air Fraction x CFM x 60 / Space Volume.
7. Room Outdoor air CFM is assumed to be 0.12 CFM/ft2 based on ASHRAE 62.1
8. RAT: Return Air Temperature; DASTP: Discharge Air Temperature Setpoint.
9. Perfect mixing of air is assumed for air flush calculations. Filtration aerosol removal rate is considered.
10. Aerosol removal time required might be longer than shown as this is an approximation for ideal ventilation configurations.
11. OAD is assumed to be equivalent to OAF. The amount of outside air actually brought in to the unit may differ based on unit construction, sensor placement and sensor accuracy.
12. The Chiller and Boiler plant is assumed to meet the max load of all the air units.
Useful Links
Author:
Default value: 72
Author:
Default value: 0.75
Author:
Default value: 74
Author:
Refer to the chiller efficiency guildeline table
Note on B15: Author: Default value: 72
Note on B18: Author: Default value: 0.75
Note on B20: Author: Default value: 74
Note on B23: Author: Refer to the chiller efficiency guildeline table

## Ventilation Scenarios
Ventilation Increase Impacts Calculator
Operation Scenarios |  |  | Description
Inputs
Air Exchange Rate (OAF)
| Freezing (<32F) | 0.84 (40%)
| Cold (33F-52F) | 1.05 (50%)
| Mild (53F-67F) | 2.1 (100%)
| Warm (68F-82F) | 0.84 (40%)
| Hot (>83F) | 0.63 (30%)
Notes
Air Exchange Rate for different weather scenarios could be used to perform risk assesments in AIRC (https://research.qut.edu.au/ilaqh/projects/expiratory-aerosols-and-infection-spread/).
The term found in AIRC as Air Exchange Rate is equivalent to Outside Air Changes per Hours.
Useful Links

## Average Heating Load vs OAT
Ventilation Increase Impacts Calculator
Average Heating Load for different Outside Air Temperatures | [12 empty] | Description
| Heating Load (kBTU) |  | Outside Air Fraction (Outside Air Changes per Hour) | [9 empty] | Inputs
|  |  | 10% (0.21) | 20% (0.42) | 30% (0.63) | 40% (0.84) | 50% (1.05) | 60% (1.26) | 70% (1.47) | 80% (1.68) | 90% (1.89) | 100% (2.1)
| Outside Air Temperature (F) | 25 | 473.4332 | 644.4664 | 815.4996 | 986.5328 | 1157.5659 | 1328.5991 | 1499.6323 | 1670.6655 | 1841.6987 | 2012.7319
|  | 30 | 459.2459 | 616.0918 | 772.9377 | 929.7836 | 1086.6295 | 1243.4754 | 1400.3213 | 1557.1672 | 1714.0131 | 1870.859
|  | 35 | 441.5665 | 580.7329 | 719.8994 | 859.0658 | 998.2323 | 1137.3988 | 1276.5652 | 1415.7317 | 1554.8981 | 1694.0646
|  | 40 | 423.5193 | 544.6386 | 665.7579 | 786.8772 | 907.9964 | 1029.1157 | 1150.235 | 1271.3543 | 1392.4736 | 1513.5929
|  | 45 | 404.4238 | 506.4476 | 608.4714 | 710.4952 | 812.5189 | 914.5427 | 1016.5665 | 1118.5903 | 1220.6141 | 1322.6379
|  | 50 | 385.6933 | 468.9866 | 552.2799 | 635.5732 | 718.8665 | 802.1598 | 885.4531 | 968.7464 | 1052.0397 | 1135.333
Green shaded area highlights achievable operating conditions based your system's capacity
Useful Links

## Average Cooling Load vs OAT
Ventilation Increase Impacts Calculator
Average Cooling Load for different Outside Air Temperatures | [12 empty] | Description
| Cooling Load (Tons) |  | Outside Air Fraction (Outside Air Changes per Hour) | [9 empty] | Inputs
|  |  | 10% (0.21) | 20% (0.42) | 30% (0.63) | 40% (0.84) | 50% (1.05) | 60% (1.26) | 70% (1.47) | 80% (1.68) | 90% (1.89) | 100% (2.1)
| Outside Air Temperature (F) | 65 | 78.9525 | 78.3153 | 77.6781 | 77.0408 | 76.4036 | 75.7664 | 75.1292 | 74.492 | 73.8548 | 73.2175
|  | 70 | 90.7738 | 92.3423 | 93.9107 | 95.4792 | 97.0477 | 98.6162 | 100.1847 | 101.7531 | 103.3216 | 104.8901
|  | 75 | 93.112 | 97.0187 | 100.9253 | 104.832 | 108.7387 | 112.6453 | 116.552 | 120.4587 | 124.3654 | 128.272
|  | 80 | 96.026 | 102.8467 | 109.6674 | 116.4881 | 123.3089 | 130.1296 | 136.9503 | 143.771 | 150.5917 | 157.4124
|  | 85 | 97.7332 | 106.261 | 114.7888 | 123.3167 | 131.8445 | 140.3724 | 148.9002 | 157.4281 | 165.9559 | 174.4838
|  | 90 | 99.0497 | 108.894 | 118.7384 | 128.5827 | 138.4271 | 148.2714 | 158.1158 | 167.9601 | 177.8045 | 187.6488
Green shaded area highlights achievable operating conditions based your system's capacity
Useful Links

## Average CoolingLoad vs Enthalpy
Ventilation Increase Impacts Calculator
Average Cooling Load for different Outside Air Enthalpy | [12 empty] | Description
|  |  | Outside Air Fraction (Outside Air Changes per Hour) | [9 empty] | Inputs
|  |  | 10% (0.21) | 20% (0.42) | 30% (0.63) | 40% (0.84) | 50% (1.05) | 60% (1.26) | 70% (1.47) | 80% (1.68) | 90% (1.89) | 100% (2.1)
| Enthalpy (BTU/lb) | 24 | 52.0669 | 51.9449 | 51.823 | 51.701 | 51.579 | 51.4571 | 51.3351 | 51.2132 | 51.0912 | 50.9692
|  | 26 | 80.9672 | 79.9449 | 78.9226 | 77.9003 | 76.878 | 75.8557 | 74.8334 | 73.8111 | 72.7887 | 71.7664
|  | 28 | 89.7644 | 90.3316 | 90.8988 | 91.4661 | 92.0333 | 92.6005 | 93.1678 | 93.735 | 94.3022 | 94.8695
|  | 30 | 92.3648 | 95.5243 | 98.6838 | 101.8432 | 105.0027 | 108.1622 | 111.3217 | 114.4812 | 117.6406 | 120.8001
|  | 32 | 94.9332 | 100.6612 | 106.3891 | 112.117 | 117.8449 | 123.5728 | 129.3007 | 135.0287 | 140.7566 | 146.4845
|  | 34 | 97.1931 | 105.1808 | 113.1685 | 121.1563 | 129.144 | 137.1318 | 145.1195 | 153.1073 | 161.095 | 169.0828
|  | 36 | 99.4502 | 109.695 | 119.9398 | 130.1847 | 140.4295 | 150.6744 | 160.9192 | 171.164 | 181.4089 | 191.6537
Green shaded area highlights achievable operating conditions based your system's capacity
Useful Links

## Energy Consumption
Ventilation Increase Impacts Calculator
Energy Consumption |  |  |  |  | Description
Inputs
| OAF (OACH) | Electricity (kWh) | GHG Emissions | Cost*
| 10% (0.21) | 109838.7372 | 47.1293 | 15487.2619
| 20% (0.42) | 115065.6773 | 49.372 | 16224.2605
| 30% (0.63) | 120292.6173 | 51.6148 | 16961.259
| 40% (0.84) | 125519.5573 | 53.8576 | 17698.2576
| 50% (1.05) | 130746.4974 | 56.1003 | 18435.2561
| 60% (1.26) | 135973.4374 | 58.3431 | 19172.2547
| 70% (1.47) | 141200.3774 | 60.5859 | 19909.2532
| 80% (1.68) | 146427.3175 | 62.8286 | 20646.2518
| 90% (1.89) | 151654.2575 | 65.0714 | 21383.2503
| 100% (2.1) | 156881.1976 | 67.3141 | 22120.2489
| OAF (OACH) | Natural Gas (therms) | GHG Emissions | Cost*
| 10% (0.21) | 16561.98 | 88.08 | 12620.23
| 20% (0.42) | 20386.88 | 108.42 | 15534.8
| 30% (0.63) | 24211.77 | 128.76 | 18449.37
| 40% (0.84) | 28036.67 | 149.1 | 21363.94
| 50% (1.05) | 31861.56 | 169.45 | 24278.51
| 60% (1.26) | 35686.46 | 189.79 | 27193.08
| 70% (1.47) | 39511.36 | 210.13 | 30107.65
| 80% (1.68) | 43336.25 | 230.47 | 33022.22
| 90% (1.89) | 47161.15 | 250.81 | 35936.8
| 100% (2.1) | 50986.05 | 271.16 | 38851.37
Energy Cost Rates per Fuel Type (Modify rates as needed)
| Fuel Type | Price
| Electricity ($/kWh) | 0.141
| Fuel Oil (#2) ($/Gallon) | 1.9009
| Fuel Oil (#4) ($/Gallon) | 1.7059
| Fuel Oil (#6) ($/Gallon) | 1.5996
| Natural Gas ($/therms) | 0.762
| Steam ($/mlbs) | 27.97
Annualized Energy Consumption, GHG, and Cost during Heating Season
Annualized Energy Consumption, GHG, and Cost during Cooling Season
Useful Links

## Air Flush
Ventilation Increase Impacts Calculator
Air Flush Duration |  |  |  | Description
Inputs
Filtration Removal Rate from MERV 8 (1/hr) | 0.4075
OAF (OACH) | Time (mins) required for removal of 90% efficiency | Time (mins) required for removal of 99% efficiency | Time (mins) required for removal of 99.9% efficiency
10% (0.21) | 140.9494 | 281.8989 | 422.8483
20% (0.42) | 125.0725 | 250.145 | 375.2176
30% (0.63) | 112.4103 | 224.8207 | 337.231
40% (0.84) | 102.0763 | 204.1525 | 306.2288
50% (1.05) | 93.4823 | 186.9645 | 280.4468
60% (1.26) | 86.223 | 172.446 | 258.669
70% (1.47) | 80.0099 | 160.0198 | 240.0297
80% (1.68) | 74.632 | 149.2641 | 223.8961
90% (1.89) | 69.9316 | 139.8632 | 209.7948
100% (2.1) | 65.7881 | 131.5763 | 197.3644
Useful Links

## CO2 Risk Assesment
Ventilation Increase Impacts Calculator
CO2 Risk Assesment
User Input Variables |  | CO2 buildup time (hours) |  | Outside Air Fraction (Outside Air Changes per Hour)
General |  |  |  | 10% (1.63) | 20% (3.26) | 30% (4.89) | 40% (6.52) | 50% (8.15) | 60% (9.78) | 70% (11.41) | 80% (13.04) | 90% (14.67) | 100% (16.3)
Space Area (ft2) | 1000 | Outside Air Temperature (F) | 25 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
Ceiling Height (ft) | 8 |  | 30 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
CO2 Critical Threshold | 1000 |  | 35 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
Number of People | 20 |  | 40 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
|  |  | 45 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
|  |  | 50 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
Green shaded area highlights achievable operating conditions based your system's capacity
|  | CO2 buildup time (hours) |  | Outside Air Fraction (Outside Air Changes per Hour)
|  |  |  | 10% (1.63) | 20% (3.26) | 30% (4.89) | 40% (6.52) | 50% (8.15) | 60% (9.78) | 70% (11.41) | 80% (13.04) | 90% (14.67) | 100% (16.3)
|  | Outside Air Temperature (F) | 65 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
|  |  | 70 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
|  |  | 75 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
|  |  | 80 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
|  |  | 85 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
|  |  | 90 | <0.5 | 0.5 | 0.5 | 1 | >12 | >12 | >12 | >12 | >12 | >12
Green shaded area highlights achievable operating conditions based your system's capacity
Assumptions & Definitions
1. Room outdoor air CFM is assumed to be 0.12 CFM/ft2 based on ASHRAE 62.1.
2. Perfect mixing of air is assumed.
3. CO2 buildup time might be longer than shown as this is an approximation for ideal ventilation configurations and infiltration is not considered.
4. Outdoor air CO2 concentration is assumed to be 420 ppm.
5. CO2 emission rate per person is assumed to be 0.0225 m3/h based on ASHRAE 62.1 Figure D-2.
6. Supply air CO2 concentration is calculated based on the outside air fraction for each ventilation scenario.
Directions & Notes
Fill out the yellow boxes with values from a specific room.
Data from "Inputs" tab is used to determine achivable operating conditions.
The values represent the amount of time for CO2 concentration to reach the critical threshold for different ventilation scenarios.
The green shaded area denotes the weather and ventilation scenarios where the system is able to meet the cooling and heating loads.

## Cooling Season calculations
User input is not required in this sheet.
These data are used for calculations.
[13 empty] | 10% OAF | [11 empty] | 20% OAF | [11 empty] | 30% OAF | [11 empty] | 40% OAF | [11 empty] | 50% OAF | [11 empty] | 60% OAF | [11 empty] | 70% OAF | [11 empty] | 80% OAF | [11 empty] | 90% OAF | [11 empty] | 100% OAF
Date & Time | Time | Day | OAT | OA RH | W_A (lower number) | W_B (higher number) | W_B - W_A | For interpolation | OAT sorted | Half | OAT sorted NEW | W, OA | OAD | MAT (eq. 40) | dT (eq. 41) | Qs dot (eq. 31) | Qs (eq. 42) | Qs, edited | W_ MA (eq. 37) | dW | QL dot (eq. 33) | QL (eq. 38) | QL, edited | Qtotal | OAD | MAT (eq. 40) | dT (eq. 41) | Qs dot (eq. 31) | Qs (eq. 42) | Qs, edited | W_ MA (eq. 37) | dW | QL dot (eq. 33) | QL (eq. 38) | QL, edited | Qtotal | OAD | MAT (eq. 40) | dT (eq. 41) | Qs dot (eq. 31) | Qs (eq. 42) | Qs, edited | W_ MA (eq. 37) | dW | QL dot (eq. 33) | QL (eq. 38) | QL, edited | Qtotal | OAD | MAT (eq. 40) | dT (eq. 41) | Qs dot (eq. 31) | Qs (eq. 42) | Qs, edited | W_ MA (eq. 37) | dW | QL dot (eq. 33) | QL (eq. 38) | QL, edited | Qtotal | OAD | MAT (eq. 40) | dT (eq. 41) | Qs dot (eq. 31) | Qs (eq. 42) | Qs, edited | W_ MA (eq. 37) | dW | QL dot (eq. 33) | QL (eq. 38) | QL, edited | Qtotal | OAD | MAT (eq. 40) | dT (eq. 41) | Qs dot (eq. 31) | Qs (eq. 42) | Qs, edited | W_ MA (eq. 37) | dW | QL dot (eq. 33) | QL (eq. 38) | QL, edited | Qtotal | OAD | MAT (eq. 40) | dT (eq. 41) | Qs dot (eq. 31) | Qs (eq. 42) | Qs, edited | W_ MA (eq. 37) | dW | QL dot (eq. 33) | QL (eq. 38) | QL, edited | Qtotal | OAD | MAT (eq. 40) | dT (eq. 41) | Qs dot (eq. 31) | Qs (eq. 42) | Qs, edited | W_ MA (eq. 37) | dW | QL dot (eq. 33) | QL (eq. 38) | QL, edited | Qtotal | OAD | MAT (eq. 40) | dT (eq. 41) | Qs dot (eq. 31) | Qs (eq. 42) | Qs, edited | W_ MA (eq. 37) | dW | QL dot (eq. 33) | QL (eq. 38) | QL, edited | Qtotal | OAD | MAT (eq. 40) | dT (eq. 41) | Qs dot (eq. 31) | Qs (eq. 42) | Qs, edited | W_ MA (eq. 37) | dW | QL dot (eq. 33) | QL (eq. 38) | QL, edited | Qtotal | OAT Bins | RH Bins | Enthalpy | Entalphy bins | RH new | Maximum OACH | Schedule
5/31/20XX 12:00:00 AM | 0 | 5 | 65.9 | 72.5 | 66.3121 | 75.9577 | 9.6456 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | MHS |  | M_heat | 665
6/1/20XX 1:00:00 AM | 0.041667 | 5 | 64.9 | 73.8 | 63.9732 | 73.2731 | 9.2999 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | MCS |  | M_cool | 342 |  |  | Measure 5
6/1/20XX 2:00:00 AM | 0.083333 | 5 | 64.2 | 74.8 | 62.3806 | 71.4454 | 9.0649 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | MOS | 0.25 | M_post | 1007 |  |  | W_RA | 62.6216
6/1/20XX 3:00:00 AM | 0.125 | 5 | 64.2 | 73.2 | 62.3806 | 71.4454 | 9.0649 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | MOE | 0.79167 |  |  |  |  | W_DA | 47.8206
6/1/20XX 4:00:00 AM | 0.16667 | 5 | 63 | 75.7 | 59.7337 | 68.4087 | 8.6749 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | User Input Variables (Cooling Season)
6/1/20XX 5:00:00 AM | 0.20833 | 5 | 63.1 | 76.2 | 59.9503 | 68.6572 | 8.7068 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | TUHS |  | T_heat | 665 | CFM in the Supply Duct | 35000
6/1/20XX 6:00:00 AM | 0.25 | 5 | 64.4 | 73.1 | 62.8319 | 71.9634 | 9.1314 | 70 | 64.4 |  | 64.4 | 65.6627 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 65.6627 | 17.842 | 424640.3882 | 35.3867 | 35.3867 | 64.9967 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 65.6627 | 17.842 | 424640.3882 | 35.3867 | 35.3867 | 64.9967 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 65.6627 | 17.842 | 424640.3882 | 35.3867 | 35.3867 | 64.9967 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 65.6627 | 17.842 | 424640.3882 | 35.3867 | 35.3867 | 64.9967 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 65.6627 | 17.842 | 424640.3882 | 35.3867 | 35.3867 | 64.9967 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 65.6627 | 17.842 | 424640.3882 | 35.3867 | 35.3867 | 64.9967 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 65.6627 | 17.842 | 424640.3882 | 35.3867 | 35.3867 | 64.9967 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 65.6627 | 17.842 | 424640.3882 | 35.3867 | 35.3867 | 64.9967 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 65.6627 | 17.842 | 424640.3882 | 35.3867 | 35.3867 | 64.9967 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 65.6627 | 17.842 | 424640.3882 | 35.3867 | 35.3867 | 64.9967 | 65 | 75 | 25.687 | 26 | 73.1 |  | TUCS |  | T_cool | 342 | OAD Position in % | 10
6/1/20XX 7:00:00 AM | 0.29167 | 5 | 65.8 | 70.7 | 66.0748 | 75.6853 | 9.6105 | 70 | 65.8 |  | 65.8 | 66.7475 | 0.1 | 73.18 | 18.18 | 687204 | 57.267 | 57.267 | 63.0342 | 15.2136 | 362083.3918 | 30.1736 | 30.1736 | 87.4406 | 0.2 | 72.36 | 17.36 | 656208 | 54.684 | 54.684 | 63.4468 | 15.6262 | 371902.9836 | 30.9919 | 30.9919 | 85.6759 | 0.3 | 71.54 | 16.54 | 625212 | 52.101 | 52.101 | 63.8594 | 16.0388 | 381722.5755 | 31.8102 | 31.8102 | 83.9112 | 0.4 | 70.72 | 15.72 | 594216 | 49.518 | 49.518 | 64.272 | 16.4514 | 391542.1673 | 32.6285 | 32.6285 | 82.1465 | 0.5 | 69.9 | 14.9 | 563220 | 46.935 | 46.935 | 64.6846 | 16.8639 | 401361.7591 | 33.4468 | 33.4468 | 80.3818 | 0.6 | 69.08 | 14.08 | 532224 | 44.352 | 44.352 | 65.0972 | 17.2765 | 411181.3509 | 34.2651 | 34.2651 | 78.6171 | 0.7 | 68.26 | 13.26 | 501228 | 41.769 | 41.769 | 65.5097 | 17.6891 | 421000.9427 | 35.0834 | 35.0834 | 76.8524 | 0.8 | 67.44 | 12.44 | 470232 | 39.186 | 39.186 | 65.9223 | 18.1017 | 430820.5345 | 35.9017 | 35.9017 | 75.0877 | 0.9 | 66.62 | 11.62 | 439236 | 36.603 | 36.603 | 66.3349 | 18.5143 | 440640.1264 | 36.72 | 36.72 | 73.323 | 1 | 65.8 | 10.8 | 408240 | 34.02 | 34.02 | 66.7475 | 18.9269 | 450459.7182 | 37.5383 | 37.5383 | 71.5583 | 65 | 70 | 26.198 | 26 | 70.7 |  | TUOS | 0.25 | T_post | 1007 |  | 20
6/1/20XX 8:00:00 AM | 0.33333 | 5 | 67.5 | 69.1 | 60.054 | 70.2137 | 10.1597 | 60 | 67.5 |  | 67.5 | 69.2994 | 0.1 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 63.2894 | 15.4688 | 368156.7914 | 30.6797 | 30.6797 | 88.4822 | 0.2 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 63.9572 | 16.1365 | 384049.7828 | 32.0041 | 32.0041 | 87.7591 | 0.3 | 72.05 | 17.05 | 644490 | 53.7075 | 53.7075 | 64.625 | 16.8043 | 399942.7742 | 33.3286 | 33.3286 | 87.0361 | 0.4 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 65.2927 | 17.4721 | 415835.7656 | 34.653 | 34.653 | 86.313 | 0.5 | 70.75 | 15.75 | 595350 | 49.6125 | 49.6125 | 65.9605 | 18.1399 | 431728.757 | 35.9774 | 35.9774 | 85.5899 | 0.6 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 66.6283 | 18.8076 | 447621.7484 | 37.3018 | 37.3018 | 84.8668 | 0.7 | 69.45 | 14.45 | 546210 | 45.5175 | 45.5175 | 67.296 | 19.4754 | 463514.7398 | 38.6262 | 38.6262 | 84.1437 | 0.8 | 68.8 | 13.8 | 521640 | 43.47 | 43.47 | 67.9638 | 20.1432 | 479407.7312 | 39.9506 | 39.9506 | 83.4206 | 0.9 | 68.15 | 13.15 | 497070 | 41.4225 | 41.4225 | 68.6316 | 20.811 | 495300.7226 | 41.2751 | 41.2751 | 82.6976 | 1 | 67.5 | 12.5 | 472500 | 39.375 | 39.375 | 69.2994 | 21.4787 | 511193.714 | 42.5995 | 42.5995 | 81.9745 | 65 | 70 | 27.0113 | 28 | 69.1 |  | TUOE | 0.79167 |  |  |  | 30
6/1/20XX 9:00:00 AM | 0.375 | 5 | 69.4 | 64.5 | 64.2269 | 75.1104 | 10.8835 | 60 | 69.4 |  | 69.4 | 69.1245 | 0.1 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 63.2719 | 15.4513 | 367740.6541 | 30.6451 | 30.6451 | 89.0461 | 0.2 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 63.9222 | 16.1016 | 383217.5082 | 31.9348 | 31.9348 | 88.8868 | 0.3 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 64.5725 | 16.7519 | 398694.3623 | 33.2245 | 33.2245 | 88.7275 | 0.4 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 65.2228 | 17.4022 | 414171.2164 | 34.5143 | 34.5143 | 88.5683 | 0.5 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 65.8731 | 18.0524 | 429648.0705 | 35.804 | 35.804 | 88.409 | 0.6 | 71.24 | 16.24 | 613872 | 51.156 | 51.156 | 66.5234 | 18.7027 | 445124.9246 | 37.0937 | 37.0937 | 88.2497 | 0.7 | 70.78 | 15.78 | 596484 | 49.707 | 49.707 | 67.1736 | 19.353 | 460601.7787 | 38.3835 | 38.3835 | 88.0905 | 0.8 | 70.32 | 15.32 | 579096 | 48.258 | 48.258 | 67.8239 | 20.0033 | 476078.6327 | 39.6732 | 39.6732 | 87.9312 | 0.9 | 69.86 | 14.86 | 561708 | 46.809 | 46.809 | 68.4742 | 20.6536 | 491555.4868 | 40.963 | 40.963 | 87.772 | 1 | 69.4 | 14.4 | 544320 | 45.36 | 45.36 | 69.1245 | 21.3039 | 507032.3409 | 42.2527 | 42.2527 | 87.6127 | 70 | 65 | 27.4484 | 28 | 64.5 | [6 empty] | 40
6/1/20XX 10:00:00 AM | 0.41667 | 5 | 71.6 | 60.7 | 69.3749 | 81.1522 | 11.7773 | 60 | 71.6 |  | 71.6 | 70.1993 | 0.1 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 63.3794 | 15.5588 | 370298.6912 | 30.8582 | 30.8582 | 89.9522 | 0.2 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 64.1372 | 16.3165 | 388333.5823 | 32.3611 | 32.3611 | 90.6991 | 0.3 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 64.8949 | 17.0743 | 406368.4735 | 33.864 | 33.864 | 91.446 | 0.4 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 65.6527 | 17.8321 | 424403.3647 | 35.3669 | 35.3669 | 92.1929 | 0.5 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 66.4105 | 18.5898 | 442438.2558 | 36.8699 | 36.8699 | 92.9399 | 0.6 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 67.1682 | 19.3476 | 460473.147 | 38.3728 | 38.3728 | 93.6868 | 0.7 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 67.926 | 20.1054 | 478508.0381 | 39.8757 | 39.8757 | 94.4337 | 0.8 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 68.6838 | 20.8631 | 496542.9293 | 41.3786 | 41.3786 | 95.1806 | 0.9 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 69.4415 | 21.6209 | 514577.8205 | 42.8815 | 42.8815 | 95.9275 | 1 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 70.1993 | 22.3787 | 532612.7116 | 44.3844 | 44.3844 | 96.6744 | 70 | 60 | 28.154 | 28 | 60.7 |  | WHS |  | W_heat | 665 |  | 50
6/1/20XX 11:00:00 AM | 0.45833 | 5 | 74.3 | 55.9 | 63.2706 | 76.1783 | 12.9077 | 50 | 74.3 |  | 74.3 | 70.8861 | 0.1 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 63.4481 | 15.6275 | 371933.3493 | 30.9944 | 30.9944 | 90.9389 | 0.2 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 64.2745 | 16.4539 | 391602.8985 | 32.6336 | 32.6336 | 92.6726 | 0.3 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 65.101 | 17.2804 | 411272.4478 | 34.2727 | 34.2727 | 94.4062 | 0.4 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.9274 | 18.1068 | 430941.9971 | 35.9118 | 35.9118 | 96.1398 | 0.5 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 66.7539 | 18.9333 | 450611.5463 | 37.551 | 37.551 | 97.8735 | 0.6 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 67.5803 | 19.7597 | 470281.0956 | 39.1901 | 39.1901 | 99.6071 | 0.7 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 68.4068 | 20.5862 | 489950.6449 | 40.8292 | 40.8292 | 101.3407 | 0.8 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 69.2332 | 21.4126 | 509620.1941 | 42.4683 | 42.4683 | 103.0743 | 0.9 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 70.0597 | 22.2391 | 529289.7434 | 44.1075 | 44.1075 | 104.808 | 1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 70.8861 | 23.0655 | 548959.2927 | 45.7466 | 45.7466 | 106.5416 | 75 | 55 | 28.9215 | 28 | 55.9 |  | WCS |  | W_cool | 323 |  | 60
6/1/20XX 12:00:00 PM | 0.5 | 5 | 76.7 | 52.7 | 68.6709 | 82.6964 | 14.0254 | 50 | 76.7 |  | 76.7 | 72.4578 | 0.1 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 63.6052 | 15.7846 | 375673.8773 | 31.3062 | 31.3062 | 92.0067 | 0.2 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 64.5889 | 16.7682 | 399083.9545 | 33.257 | 33.257 | 94.808 | 0.3 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 65.5725 | 17.7519 | 422494.0318 | 35.2078 | 35.2078 | 97.6093 | 0.4 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 66.5561 | 18.7355 | 445904.109 | 37.1587 | 37.1587 | 100.4107 | 0.5 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 67.5397 | 19.7191 | 469314.1863 | 39.1095 | 39.1095 | 103.212 | 0.6 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 68.5233 | 20.7027 | 492724.2635 | 41.0604 | 41.0604 | 106.0134 | 0.7 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 69.5069 | 21.6863 | 516134.3408 | 43.0112 | 43.0112 | 108.8147 | 0.8 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 70.4906 | 22.6699 | 539544.418 | 44.962 | 44.962 | 111.616 | 0.9 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 71.4742 | 23.6536 | 562954.4953 | 46.9129 | 46.9129 | 114.4174 | 1 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 72.4578 | 24.6372 | 586364.5725 | 48.8637 | 48.8637 | 117.2187 | 75 | 55 | 29.7544 | 30 | 52.7 |  | WOS | 0.25 | W_post | 988 |  | 70
6/1/20XX 1:00:00 PM | 0.54167 | 5 | 76.7 | 51.8 | 68.6709 | 82.6964 | 14.0254 | 50 | 76.7 |  | 76.7 | 71.1955 | 0.1 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 63.479 | 15.6584 | 372669.6265 | 31.0558 | 31.0558 | 91.7563 | 0.2 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 64.3364 | 16.5158 | 393075.453 | 32.7563 | 32.7563 | 94.3073 | 0.3 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 65.1938 | 17.3732 | 413481.2794 | 34.4568 | 34.4568 | 96.8583 | 0.4 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 66.0512 | 18.2306 | 433887.1059 | 36.1573 | 36.1573 | 99.4093 | 0.5 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 66.9086 | 19.0879 | 454292.9324 | 37.8577 | 37.8577 | 101.9602 | 0.6 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 67.766 | 19.9453 | 474698.7589 | 39.5582 | 39.5582 | 104.5112 | 0.7 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 68.6233 | 20.8027 | 495104.5853 | 41.2587 | 41.2587 | 107.0622 | 0.8 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 69.4807 | 21.6601 | 515510.4118 | 42.9592 | 42.9592 | 109.6132 | 0.9 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 70.3381 | 22.5175 | 535916.2383 | 44.6597 | 44.6597 | 112.1642 | 1 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 71.1955 | 23.3749 | 556322.0648 | 46.3602 | 46.3602 | 114.7152 | 75 | 50 | 29.5567 | 30 | 51.8 |  | WOE | 0.79167 |  |  |  | 80
6/1/20XX 2:00:00 PM | 0.58333 | 5 | 76.5 | 52.5 | 68.2065 | 82.1358 | 13.9292 | 50 | 76.5 |  | 76.5 | 71.6888 | 0.1 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 63.5284 | 15.7077 | 373843.7533 | 31.1536 | 31.1536 | 91.7911 | 0.2 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 64.4351 | 16.6144 | 395423.7066 | 32.952 | 32.952 | 94.377 | 0.3 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 65.3418 | 17.5212 | 417003.6599 | 34.7503 | 34.7503 | 96.9628 | 0.4 | 75 | 20 | 756000 | 63 | 63 | 66.2485 | 18.4279 | 438583.6132 | 36.5486 | 36.5486 | 99.5486 | 0.5 | 75.25 | 20.25 | 765450 | 63.7875 | 63.7875 | 67.1552 | 19.3346 | 460163.5665 | 38.347 | 38.347 | 102.1345 | 0.6 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 68.062 | 20.2413 | 481743.5198 | 40.1453 | 40.1453 | 104.7203 | 0.7 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 68.9687 | 21.148 | 503323.473 | 41.9436 | 41.9436 | 107.3061 | 0.8 | 76 | 21 | 793800 | 66.15 | 66.15 | 69.8754 | 22.0548 | 524903.4263 | 43.742 | 43.742 | 109.892 | 0.9 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 70.7821 | 22.9615 | 546483.3796 | 45.5403 | 45.5403 | 112.4778 | 1 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 71.6888 | 23.8682 | 568063.3329 | 47.3386 | 47.3386 | 115.0636 | 75 | 50 | 29.585 | 30 | 52.5 | [6 empty] | 90
6/1/20XX 3:00:00 PM | 0.625 | 5 | 75.5 | 53.8 | 65.924 | 79.3806 | 13.4566 | 50 | 75.5 |  | 75.5 | 71.0375 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 63.4632 | 15.6426 | 372293.6324 | 31.0245 | 31.0245 | 91.347 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 64.3048 | 16.4842 | 392323.4648 | 32.6936 | 32.6936 | 93.4886 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 65.1464 | 17.3258 | 412353.2972 | 34.3628 | 34.3628 | 95.6303 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 65.988 | 18.1674 | 432383.1297 | 36.0319 | 36.0319 | 97.7719 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 66.8296 | 19.0089 | 452412.9621 | 37.7011 | 37.7011 | 99.9136 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 67.6712 | 19.8505 | 472442.7945 | 39.3702 | 39.3702 | 102.0552 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 68.5128 | 20.6921 | 492472.6269 | 41.0394 | 41.0394 | 104.1969 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 69.3543 | 21.5337 | 512502.4593 | 42.7085 | 42.7085 | 106.3385 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 70.1959 | 22.3753 | 532532.2917 | 44.3777 | 44.3777 | 108.4802 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 71.0375 | 23.2169 | 552562.1242 | 46.0468 | 46.0468 | 110.6218 | 75 | 55 | 29.2386 | 30 | 53.8 |  | THHS |  | TH_heat | 665 |  | 100
6/1/20XX 4:00:00 PM | 0.66667 | 5 | 75.3 | 55.1 | 65.4753 | 78.8391 | 13.3637 | 50 | 75.3 |  | 75.3 | 72.2909 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 63.5886 | 15.7679 | 375276.5533 | 31.273 | 31.273 | 91.5325 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 64.5555 | 16.7348 | 398289.3066 | 33.1908 | 33.1908 | 93.8598 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 65.5224 | 17.7018 | 421302.0598 | 35.1085 | 35.1085 | 96.187 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 66.4893 | 18.6687 | 444314.8131 | 37.0262 | 37.0262 | 98.5142 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 67.4562 | 19.6356 | 467327.5664 | 38.944 | 38.944 | 100.8415 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 68.4232 | 20.6025 | 490340.3197 | 40.8617 | 40.8617 | 103.1687 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 69.3901 | 21.5695 | 513353.073 | 42.7794 | 42.7794 | 105.4959 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 70.357 | 22.5364 | 536365.8262 | 44.6972 | 44.6972 | 107.8232 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 71.3239 | 23.5033 | 559378.5795 | 46.6149 | 46.6149 | 110.1504 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 72.2909 | 24.4702 | 582391.3328 | 48.5326 | 48.5326 | 112.4776 | 75 | 55 | 29.3858 | 30 | 55.1 |  | THCS |  | TH_cool | 323 | RAT (if available) | 74
6/1/20XX 5:00:00 PM | 0.70833 | 5 | 74.4 | 56.3 | 63.4882 | 76.4409 | 12.9527 | 50 | 74.4 |  | 74.4 | 71.6484 | 0.1 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 63.5243 | 15.7037 | 373747.5007 | 31.1456 | 31.1456 | 91.1216 | 0.2 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 64.427 | 16.6064 | 395231.2014 | 32.9359 | 32.9359 | 93.0379 | 0.3 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.3297 | 17.509 | 416714.9022 | 34.7262 | 34.7262 | 94.9542 | 0.4 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 66.2323 | 18.4117 | 438198.6029 | 36.5166 | 36.5166 | 96.8706 | 0.5 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 67.135 | 19.3144 | 459682.3036 | 38.3069 | 38.3069 | 98.7869 | 0.6 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 68.0377 | 20.2171 | 481166.0043 | 40.0972 | 40.0972 | 100.7032 | 0.7 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 68.9404 | 21.1197 | 502649.705 | 41.8875 | 41.8875 | 102.6195 | 0.8 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 69.843 | 22.0224 | 524133.4057 | 43.6778 | 43.6778 | 104.5358 | 0.9 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 70.7457 | 22.9251 | 545617.1065 | 45.4681 | 45.4681 | 106.4521 | 1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 71.6484 | 23.8278 | 567100.8072 | 47.2584 | 47.2584 | 108.3684 | 75 | 55 | 29.0652 | 30 | 56.3 |  | THOS | 0.25 | TH_post | 988 | DATSP (if available) | 55
6/1/20XX 6:00:00 PM | 0.75 | 5 | 73.2 | 59.1 | 60.9187 | 73.3404 | 12.4216 | 50 | 73.2 |  | 73.2 | 72.2224 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 63.5817 | 15.7611 | 375113.6556 | 31.2595 | 31.2595 | 90.8575 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 64.5418 | 16.7212 | 397963.5112 | 33.1636 | 33.1636 | 92.5096 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 65.5019 | 17.6812 | 420813.3668 | 35.0678 | 35.0678 | 94.1618 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 66.4619 | 18.6413 | 443663.2224 | 36.9719 | 36.9719 | 95.8139 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 67.422 | 19.6014 | 466513.078 | 38.8761 | 38.8761 | 97.4661 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 68.3821 | 20.5615 | 489362.9336 | 40.7802 | 40.7802 | 99.1182 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 69.3422 | 21.5215 | 512212.7893 | 42.6844 | 42.6844 | 100.7704 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 70.3023 | 22.4816 | 535062.6449 | 44.5886 | 44.5886 | 102.4226 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 71.2623 | 23.4417 | 557912.5005 | 46.4927 | 46.4927 | 104.0747 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 72.2224 | 24.4018 | 580762.3561 | 48.3969 | 48.3969 | 105.7269 | 75 | 60 | 28.8615 | 28 | 59.1 |  | THOE | 0.79167 |  |  | Chiller efficiency | 0.75
6/1/20XX 7:00:00 PM | 0.79167 | 5 | 71.5 | 61.3 | 69.1333 | 80.8687 | 11.7354 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/1/20XX 8:00:00 PM | 0.83333 | 5 | 70.2 | 64.5 | 66.0589 | 77.2604 | 11.2015 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | FHS |  | F_heat | 646
6/1/20XX 9:00:00 PM | 0.875 | 5 | 70.1 | 63.9 | 65.8275 | 76.9888 | 11.1613 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | FCS |  | F_cool | 342
6/1/20XX 10:00:00 PM | 0.91667 | 5 | 69.5 | 64.4 | 64.4535 | 75.3763 | 10.9228 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | FOS | 0.25 | F_post | 988
6/1/20XX 11:00:00 PM | 0.95833 |  | 69 | 64.1 | 63.3278 | 74.0553 | 10.7275 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | FOE | 0.79167
6/1/20XX 12:00:00 AM | 0 | 6 | 68 | 67.1 | 61.1282 | 71.4742 | 10.346 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/2/20XX 1:00:00 AM | 0.041667 | 6 | 66.8 | 69.3 | 58.5784 | 68.4823 | 9.9039 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | SAHS |  | SA_heat | 665
6/2/20XX 2:00:00 AM | 0.083333 | 6 | 66.1 | 70.1 | 66.7889 | 76.5051 | 9.7162 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | SACS |  | SA_cool | 323
6/2/20XX 3:00:00 AM | 0.125 | 6 | 65.4 | 70.8 | 65.1332 | 74.6045 | 9.4713 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | SAOS | 0.25 | SA_post | 988
6/2/20XX 4:00:00 AM | 0.16667 | 6 | 64.6 | 71.8 | 63.2862 | 72.4847 | 9.1985 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | SAOE | 0.79167
6/2/20XX 5:00:00 AM | 0.20833 | 6 | 63.8 | 74.7 | 61.4867 | 70.4198 | 8.9331 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/2/20XX 6:00:00 AM | 0.25 | 6 | 64.8 | 73.6 | 63.7435 | 73.0095 | 9.266 | 70 | 64.8 |  | 64.8 | 67.0792 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 67.0792 | 19.2586 | 458354.7702 | 38.1962 | 38.1962 | 69.0662 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 67.0792 | 19.2586 | 458354.7702 | 38.1962 | 38.1962 | 69.0662 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 67.0792 | 19.2586 | 458354.7702 | 38.1962 | 38.1962 | 69.0662 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 67.0792 | 19.2586 | 458354.7702 | 38.1962 | 38.1962 | 69.0662 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 67.0792 | 19.2586 | 458354.7702 | 38.1962 | 38.1962 | 69.0662 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 67.0792 | 19.2586 | 458354.7702 | 38.1962 | 38.1962 | 69.0662 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 67.0792 | 19.2586 | 458354.7702 | 38.1962 | 38.1962 | 69.0662 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 67.0792 | 19.2586 | 458354.7702 | 38.1962 | 38.1962 | 69.0662 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 67.0792 | 19.2586 | 458354.7702 | 38.1962 | 38.1962 | 69.0662 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 67.0792 | 19.2586 | 458354.7702 | 38.1962 | 38.1962 | 69.0662 | 65 | 75 | 26.0054 | 26 | 73.6 |  | SHS |  | S_heat | 646
6/2/20XX 7:00:00 AM | 0.29167 | 6 | 66.2 | 70.1 | 67.0285 | 76.7802 | 9.7517 | 70 | 66.2 |  | 66.2 | 67.126 | 0.1 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 63.0721 | 15.2514 | 362984.3035 | 30.2487 | 30.2487 | 87.6417 | 0.2 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 63.5225 | 15.7019 | 373704.8071 | 31.1421 | 31.1421 | 86.0781 | 0.3 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 63.973 | 16.1523 | 384425.3106 | 32.0354 | 32.0354 | 84.5144 | 0.4 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 64.4234 | 16.6028 | 395145.8142 | 32.9288 | 32.9288 | 82.9508 | 0.5 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 64.8738 | 17.0532 | 405866.3177 | 33.8222 | 33.8222 | 81.3872 | 0.6 | 69.32 | 14.32 | 541296 | 45.108 | 45.108 | 65.3243 | 17.5036 | 416586.8212 | 34.7156 | 34.7156 | 79.8236 | 0.7 | 68.54 | 13.54 | 511812 | 42.651 | 42.651 | 65.7747 | 17.9541 | 427307.3248 | 35.6089 | 35.6089 | 78.2599 | 0.8 | 67.76 | 12.76 | 482328 | 40.194 | 40.194 | 66.2252 | 18.4045 | 438027.8283 | 36.5023 | 36.5023 | 76.6963 | 0.9 | 66.98 | 11.98 | 452844 | 37.737 | 37.737 | 66.6756 | 18.855 | 448748.3319 | 37.3957 | 37.3957 | 75.1327 | 1 | 66.2 | 11.2 | 423360 | 35.28 | 35.28 | 67.126 | 19.3054 | 459468.8354 | 38.2891 | 38.2891 | 73.5691 | 65 | 70 | 26.3547 | 26 | 70.1 |  | SCS |  | S_cool | 323
6/2/20XX 8:00:00 AM | 0.33333 | 6 | 67.6 | 66.7 | 60.2675 | 70.4642 | 10.1967 | 60 | 67.6 |  | 67.6 | 67.0993 | 0.1 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 63.0694 | 15.2488 | 362920.7022 | 30.2434 | 30.2434 | 88.0774 | 0.2 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 63.5172 | 15.6965 | 373577.6043 | 31.1315 | 31.1315 | 86.9495 | 0.3 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 63.9649 | 16.1443 | 384234.5065 | 32.0195 | 32.0195 | 85.8215 | 0.4 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 64.4127 | 16.5921 | 394891.4086 | 32.9076 | 32.9076 | 84.6936 | 0.5 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 64.8605 | 17.0398 | 405548.3108 | 33.7957 | 33.7957 | 83.5657 | 0.6 | 70.16 | 15.16 | 573048 | 47.754 | 47.754 | 65.3082 | 17.4876 | 416205.2129 | 34.6838 | 34.6838 | 82.4378 | 0.7 | 69.52 | 14.52 | 548856 | 45.738 | 45.738 | 65.756 | 17.9354 | 426862.1151 | 35.5718 | 35.5718 | 81.3098 | 0.8 | 68.88 | 13.88 | 524664 | 43.722 | 43.722 | 66.2038 | 18.3832 | 437519.0172 | 36.4599 | 36.4599 | 80.1819 | 0.9 | 68.24 | 13.24 | 500472 | 41.706 | 41.706 | 66.6516 | 18.8309 | 448175.9194 | 37.348 | 37.348 | 79.054 | 1 | 67.6 | 12.6 | 476280 | 39.69 | 39.69 | 67.0993 | 19.2787 | 458832.8215 | 38.2361 | 38.2361 | 77.9261 | 70 | 65 | 26.6925 | 26 | 66.7 |  | SOS | 0.25 | S_post
6/2/20XX 9:00:00 AM | 0.375 | 6 | 69.5 | 63.4 | 64.4535 | 75.3763 | 10.9228 | 60 | 69.5 |  | 69.5 | 68.1672 | 0.1 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 63.1762 | 15.3556 | 365462.3207 | 30.4552 | 30.4552 | 88.8877 | 0.2 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 63.7308 | 15.9101 | 378660.8415 | 31.5551 | 31.5551 | 88.5701 | 0.3 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 64.2853 | 16.4647 | 391859.3622 | 32.6549 | 32.6549 | 88.2524 | 0.4 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 64.8399 | 17.0192 | 405057.883 | 33.7548 | 33.7548 | 87.9348 | 0.5 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 65.3944 | 17.5738 | 418256.4037 | 34.8547 | 34.8547 | 87.6172 | 0.6 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 65.949 | 18.1284 | 431454.9244 | 35.9546 | 35.9546 | 87.2996 | 0.7 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 66.5036 | 18.6829 | 444653.4452 | 37.0545 | 37.0545 | 86.982 | 0.8 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 67.0581 | 19.2375 | 457851.9659 | 38.1543 | 38.1543 | 86.6643 | 0.9 | 69.95 | 14.95 | 565110 | 47.0925 | 47.0925 | 67.6127 | 19.792 | 471050.4867 | 39.2542 | 39.2542 | 86.3467 | 1 | 69.5 | 14.5 | 548100 | 45.675 | 45.675 | 68.1672 | 20.3466 | 484249.0074 | 40.3541 | 40.3541 | 86.0291 | 70 | 65 | 27.3233 | 28 | 63.4 |  | SOE | 0.79167
6/2/20XX 10:00:00 AM | 0.41667 | 6 | 72.4 | 57.3 | 59.2556 | 71.3339 | 12.0782 | 50 | 72.4 |  | 72.4 | 68.0727 | 0.1 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 63.1667 | 15.3461 | 365237.4203 | 30.4365 | 30.4365 | 89.7825 | 0.2 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 63.7119 | 15.8912 | 378211.0405 | 31.5176 | 31.5176 | 90.3596 | 0.3 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 64.257 | 16.4363 | 391184.6608 | 32.5987 | 32.5987 | 90.9367 | 0.4 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 64.8021 | 16.9814 | 404158.281 | 33.6799 | 33.6799 | 91.5139 | 0.5 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 65.3472 | 17.5266 | 417131.9013 | 34.761 | 34.761 | 92.091 | 0.6 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 65.8923 | 18.0717 | 430105.5216 | 35.8421 | 35.8421 | 92.6681 | 0.7 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 66.4374 | 18.6168 | 443079.1418 | 36.9233 | 36.9233 | 93.2453 | 0.8 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 66.9825 | 19.1619 | 456052.7621 | 38.0044 | 38.0044 | 93.8224 | 0.9 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 67.5276 | 19.707 | 469026.3824 | 39.0855 | 39.0855 | 94.3995 | 1 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 68.0727 | 20.2521 | 482000.0026 | 40.1667 | 40.1667 | 94.9767 | 70 | 55 | 28.0171 | 28 | 57.3
6/2/20XX 11:00:00 AM | 0.45833 | 6 | 74.7 | 52.8 | 64.1448 | 77.2333 | 13.0885 | 50 | 74.7 |  | 74.7 | 67.8096 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 63.1404 | 15.3198 | 364611.1428 | 30.3843 | 30.3843 | 90.4548 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 63.6592 | 15.8386 | 376958.4856 | 31.4132 | 31.4132 | 91.7042 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 64.178 | 16.3574 | 389305.8284 | 32.4422 | 32.4422 | 92.9537 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 64.6968 | 16.8762 | 401653.1712 | 33.4711 | 33.4711 | 94.2031 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 65.2156 | 17.395 | 414000.514 | 34.5 | 34.5 | 95.4525 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 65.7344 | 17.9138 | 426347.8568 | 35.529 | 35.529 | 96.702 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 66.2532 | 18.4326 | 438695.1997 | 36.5579 | 36.5579 | 97.9514 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 66.772 | 18.9514 | 451042.5425 | 37.5869 | 37.5869 | 99.2009 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 67.2908 | 19.4702 | 463389.8853 | 38.6158 | 38.6158 | 100.4503 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 67.8096 | 19.989 | 475737.2281 | 39.6448 | 39.6448 | 101.6998 | 75 | 55 | 28.5379 | 28 | 52.8 |  | Hours_post BRT |  | 5966
6/2/20XX 12:00:00 PM | 0.5 | 6 | 76.4 | 50.4 | 67.9753 | 81.8567 | 13.8813 | 50 | 76.4 |  | 76.4 | 68.5306 | 0.1 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 63.2125 | 15.3919 | 366327.0901 | 30.5273 | 30.5273 | 91.1333 | 0.2 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 63.8034 | 15.9828 | 380390.3802 | 31.6992 | 31.6992 | 93.0612 | 0.3 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 64.3943 | 16.5737 | 394453.6703 | 32.8711 | 32.8711 | 94.9891 | 0.4 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 64.9852 | 17.1646 | 408516.9604 | 34.0431 | 34.0431 | 96.9171 | 0.5 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 65.5761 | 17.7555 | 422580.2505 | 35.215 | 35.215 | 98.845 | 0.6 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 66.167 | 18.3464 | 436643.5406 | 36.387 | 36.387 | 100.773 | 0.7 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 66.7579 | 18.9373 | 450706.8307 | 37.5589 | 37.5589 | 102.7009 | 0.8 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 67.3488 | 19.5282 | 464770.1208 | 38.7308 | 38.7308 | 104.6288 | 0.9 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 67.9397 | 20.1191 | 478833.4109 | 39.9028 | 39.9028 | 106.5568 | 1 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 68.5306 | 20.7099 | 492896.701 | 41.0747 | 41.0747 | 108.4847 | 75 | 50 | 29.0661 | 30 | 50.4
6/2/20XX 1:00:00 PM | 0.54167 | 6 | 76.3 | 50.2 | 67.7448 | 81.5784 | 13.8336 | 50 | 76.3 |  | 76.3 | 68.0214 | 0.1 | 74.23 | 19.23 | 726894 | 60.5745 | 60.5745 | 63.1616 | 15.341 | 365115.3641 | 30.4263 | 30.4263 | 91.0008 | 0.2 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 63.7016 | 15.881 | 377966.9283 | 31.4972 | 31.4972 | 92.7962 | 0.3 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 64.2416 | 16.4209 | 390818.4924 | 32.5682 | 32.5682 | 94.5917 | 0.4 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 64.7816 | 16.9609 | 403670.0565 | 33.6392 | 33.6392 | 96.3872 | 0.5 | 75.15 | 20.15 | 761670 | 63.4725 | 63.4725 | 65.3215 | 17.5009 | 416521.6207 | 34.7101 | 34.7101 | 98.1826 | 0.6 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 65.8615 | 18.0409 | 429373.1848 | 35.7811 | 35.7811 | 99.9781 | 0.7 | 75.61 | 20.61 | 779058 | 64.9215 | 64.9215 | 66.4015 | 18.5809 | 442224.7489 | 36.8521 | 36.8521 | 101.7736 | 0.8 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 66.9415 | 19.1209 | 455076.313 | 37.923 | 37.923 | 103.569 | 0.9 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 67.4815 | 19.6608 | 467927.8772 | 38.994 | 38.994 | 105.3645 | 1 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 68.0214 | 20.2008 | 480779.4413 | 40.065 | 40.065 | 107.16 | 75 | 50 | 28.9619 | 28 | 50.2
6/2/20XX 2:00:00 PM | 0.58333 | 6 | 75.7 | 51.8 | 66.3753 | 79.9253 | 13.55 | 50 | 75.7 |  | 75.7 | 68.8143 | 0.1 | 74.17 | 19.17 | 724626 | 60.3855 | 60.3855 | 63.2409 | 15.4203 | 367002.3304 | 30.5835 | 30.5835 | 90.969 | 0.2 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 63.8602 | 16.0395 | 381740.8609 | 31.8117 | 31.8117 | 92.7327 | 0.3 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 64.4794 | 16.6588 | 396479.3913 | 33.0399 | 33.0399 | 94.4964 | 0.4 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 65.0987 | 17.2781 | 411217.9217 | 34.2682 | 34.2682 | 96.2602 | 0.5 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 65.718 | 17.8973 | 425956.4521 | 35.4964 | 35.4964 | 98.0239 | 0.6 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 66.3372 | 18.5166 | 440694.9826 | 36.7246 | 36.7246 | 99.7876 | 0.7 | 75.19 | 20.19 | 763182 | 63.5985 | 63.5985 | 66.9565 | 19.1359 | 455433.513 | 37.9528 | 37.9528 | 101.5513 | 0.8 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 67.5758 | 19.7551 | 470172.0434 | 39.181 | 39.181 | 103.315 | 0.9 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 68.195 | 20.3744 | 484910.5739 | 40.4092 | 40.4092 | 105.0787 | 1 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 68.8143 | 20.9937 | 499649.1043 | 41.6374 | 41.6374 | 106.8424 | 75 | 50 | 28.9395 | 28 | 51.8
6/2/20XX 3:00:00 PM | 0.625 | 6 | 75.3 | 52 | 65.4753 | 78.8391 | 13.3637 | 50 | 75.3 |  | 75.3 | 68.1481 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 63.1743 | 15.3536 | 365416.7846 | 30.4514 | 30.4514 | 90.7109 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 63.7269 | 15.9063 | 378569.7693 | 31.5475 | 31.5475 | 92.2165 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 64.2796 | 16.4589 | 391722.7539 | 32.6436 | 32.6436 | 93.7221 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 64.8322 | 17.0116 | 404875.7385 | 33.7396 | 33.7396 | 95.2276 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 65.3849 | 17.5642 | 418028.7232 | 34.8357 | 34.8357 | 96.7332 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 65.9375 | 18.1169 | 431181.7078 | 35.9318 | 35.9318 | 98.2388 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 66.4902 | 18.6695 | 444334.6924 | 37.0279 | 37.0279 | 99.7444 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 67.0428 | 19.2222 | 457487.6771 | 38.124 | 38.124 | 101.25 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 67.5955 | 19.7748 | 470640.6617 | 39.2201 | 39.2201 | 102.7556 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 68.1481 | 20.3275 | 483793.6464 | 40.3161 | 40.3161 | 104.2611 | 75 | 50 | 28.7374 | 28 | 52
6/2/20XX 4:00:00 PM | 0.66667 | 6 | 73.5 | 57.4 | 61.5526 | 74.1052 | 12.5526 | 50 | 73.5 |  | 73.5 | 70.8415 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 63.4436 | 15.623 | 371827.1644 | 30.9856 | 30.9856 | 90.6781 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.2656 | 16.445 | 391390.5288 | 32.6159 | 32.6159 | 92.1509 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 65.0876 | 17.267 | 410953.8932 | 34.2462 | 34.2462 | 93.6237 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 65.9096 | 18.089 | 430517.2576 | 35.8764 | 35.8764 | 95.0964 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 66.7316 | 18.911 | 450080.622 | 37.5067 | 37.5067 | 96.5692 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 67.5536 | 19.7329 | 469643.9864 | 39.137 | 39.137 | 98.042 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 68.3756 | 20.5549 | 489207.3508 | 40.7673 | 40.7673 | 99.5148 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 69.1976 | 21.3769 | 508770.7152 | 42.3976 | 42.3976 | 100.9876 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 70.0195 | 22.1989 | 528334.0796 | 44.0278 | 44.0278 | 102.4603 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 70.8415 | 23.0209 | 547897.444 | 45.6581 | 45.6581 | 103.9331 | 75 | 55 | 28.7189 | 28 | 57.4
6/2/20XX 5:00:00 PM | 0.70833 | 6 | 73.7 | 55 | 61.9783 | 74.6189 | 12.6406 | 50 | 73.7 |  | 73.7 | 68.2986 | 0.1 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 63.1893 | 15.3687 | 365775.0238 | 30.4813 | 30.4813 | 90.2368 | 0.2 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 63.757 | 15.9364 | 379286.2477 | 31.6072 | 31.6072 | 91.2682 | 0.3 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 64.3247 | 16.5041 | 392797.4715 | 32.7331 | 32.7331 | 92.2996 | 0.4 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 64.8924 | 17.0718 | 406308.6954 | 33.8591 | 33.8591 | 93.3311 | 0.5 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 65.4601 | 17.6395 | 419819.9192 | 34.985 | 34.985 | 94.3625 | 0.6 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 66.0278 | 18.2072 | 433331.1431 | 36.1109 | 36.1109 | 95.3939 | 0.7 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 66.5955 | 18.7749 | 446842.3669 | 37.2369 | 37.2369 | 96.4254 | 0.8 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 67.1632 | 19.3426 | 460353.5907 | 38.3628 | 38.3628 | 97.4568 | 0.9 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 67.7309 | 19.9103 | 473864.8146 | 39.4887 | 39.4887 | 98.4882 | 1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 68.2986 | 20.478 | 487376.0384 | 40.6147 | 40.6147 | 99.5197 | 75 | 55 | 28.3701 | 28 | 55
6/2/20XX 6:00:00 PM | 0.75 | 6 | 72.4 | 56.6 | 59.2556 | 71.3339 | 12.0782 | 50 | 72.4 |  | 72.4 | 67.2273 | 0.1 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 63.0822 | 15.2616 | 363225.1859 | 30.2688 | 30.2688 | 89.6148 | 0.2 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 63.5428 | 15.7221 | 374186.5718 | 31.1822 | 31.1822 | 90.0242 | 0.3 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 64.0033 | 16.1827 | 385147.9578 | 32.0957 | 32.0957 | 90.4337 | 0.4 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 64.4639 | 16.6432 | 396109.3437 | 33.0091 | 33.0091 | 90.8431 | 0.5 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 64.9244 | 17.1038 | 407070.7296 | 33.9226 | 33.9226 | 91.2526 | 0.6 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 65.385 | 17.5644 | 418032.1155 | 34.836 | 34.836 | 91.662 | 0.7 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 65.8456 | 18.0249 | 428993.5014 | 35.7495 | 35.7495 | 92.0715 | 0.8 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 66.3061 | 18.4855 | 439954.8873 | 36.6629 | 36.6629 | 92.4809 | 0.9 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 66.7667 | 18.9461 | 450916.2733 | 37.5764 | 37.5764 | 92.8904 | 1 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 67.2273 | 19.4066 | 461877.6592 | 38.4898 | 38.4898 | 93.2998 | 70 | 55 | 27.885 | 28 | 56.6
6/2/20XX 7:00:00 PM | 0.79167 | 6 | 71.2 | 58.1 | 56.8343 | 68.413 | 11.5787 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/2/20XX 8:00:00 PM | 0.83333 | 6 | 69.8 | 60.9 | 65.1373 | 76.1788 | 11.0415 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/2/20XX 9:00:00 PM | 0.875 | 6 | 68.8 | 63.3 | 62.8824 | 73.5326 | 10.6502 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/2/20XX 10:00:00 PM | 0.91667 | 6 | 67.1 | 67.6 | 59.2068 | 69.2196 | 10.0128 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/2/20XX 11:00:00 PM | 0.95833 | 6 | 65.2 | 70.7 | 64.667 | 74.0694 | 9.4024 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/2/20XX 12:00:00 AM | 0 | 7 | 64.4 | 72 | 62.8319 | 71.9634 | 9.1314 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/3/20XX 1:00:00 AM | 0.041667 | 7 | 63.3 | 72.5 | 60.3857 | 69.1566 | 8.7709 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/3/20XX 2:00:00 AM | 0.083333 | 7 | 63.2 | 72.6 | 60.1677 | 68.9065 | 8.7388 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/3/20XX 3:00:00 AM | 0.125 | 7 | 62.8 | 73.9 | 59.3027 | 67.9142 | 8.6115 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/3/20XX 4:00:00 AM | 0.16667 | 7 | 62.2 | 74.1 | 58.0265 | 66.4504 | 8.4239 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/3/20XX 5:00:00 AM | 0.20833 | 7 | 62 | 75.5 | 57.6068 | 65.969 | 8.3623 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/3/20XX 6:00:00 AM | 0.25 | 7 | 62.5 | 75.1 | 58.6614 | 67.1787 | 8.5172 | 70 | 62.5 |  | 62.5 | 63.0052 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 63.0052 | 15.1846 | 361393.0949 | 30.1161 | 30.1161 | 53.7411 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 63.0052 | 15.1846 | 361393.0949 | 30.1161 | 30.1161 | 53.7411 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 63.0052 | 15.1846 | 361393.0949 | 30.1161 | 30.1161 | 53.7411 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 63.0052 | 15.1846 | 361393.0949 | 30.1161 | 30.1161 | 53.7411 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 63.0052 | 15.1846 | 361393.0949 | 30.1161 | 30.1161 | 53.7411 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 63.0052 | 15.1846 | 361393.0949 | 30.1161 | 30.1161 | 53.7411 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 63.0052 | 15.1846 | 361393.0949 | 30.1161 | 30.1161 | 53.7411 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 63.0052 | 15.1846 | 361393.0949 | 30.1161 | 30.1161 | 53.7411 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 63.0052 | 15.1846 | 361393.0949 | 30.1161 | 30.1161 | 53.7411 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 63.0052 | 15.1846 | 361393.0949 | 30.1161 | 30.1161 | 53.7411 | 60 | 75 | 24.8094 | 24 | 75.1
6/3/20XX 7:00:00 AM | 0.29167 | 7 | 63 | 73.2 | 59.7337 | 68.4087 | 8.6749 | 70 | 63 |  | 63 | 62.5097 | 1 | 63 | 8 | 302400 | 25.2 | 25.2 | 62.5097 | 14.6891 | 349600.3956 | 29.1334 | 29.1334 | 54.3334 | 1 | 63 | 8 | 302400 | 25.2 | 25.2 | 62.5097 | 14.6891 | 349600.3956 | 29.1334 | 29.1334 | 54.3334 | 1 | 63 | 8 | 302400 | 25.2 | 25.2 | 62.5097 | 14.6891 | 349600.3956 | 29.1334 | 29.1334 | 54.3334 | 1 | 63 | 8 | 302400 | 25.2 | 25.2 | 62.5097 | 14.6891 | 349600.3956 | 29.1334 | 29.1334 | 54.3334 | 1 | 63 | 8 | 302400 | 25.2 | 25.2 | 62.5097 | 14.6891 | 349600.3956 | 29.1334 | 29.1334 | 54.3334 | 1 | 63 | 8 | 302400 | 25.2 | 25.2 | 62.5097 | 14.6891 | 349600.3956 | 29.1334 | 29.1334 | 54.3334 | 1 | 63 | 8 | 302400 | 25.2 | 25.2 | 62.5097 | 14.6891 | 349600.3956 | 29.1334 | 29.1334 | 54.3334 | 1 | 63 | 8 | 302400 | 25.2 | 25.2 | 62.5097 | 14.6891 | 349600.3956 | 29.1334 | 29.1334 | 54.3334 | 1 | 63 | 8 | 302400 | 25.2 | 25.2 | 62.5097 | 14.6891 | 349600.3956 | 29.1334 | 29.1334 | 54.3334 | 1 | 63 | 8 | 302400 | 25.2 | 25.2 | 62.5097 | 14.6891 | 349600.3956 | 29.1334 | 29.1334 | 54.3334 | 65 | 75 | 24.8542 | 24 | 73.2
6/3/20XX 8:00:00 AM | 0.33333 | 7 | 64.1 | 72.7 | 62.156 | 71.1877 | 9.0317 | 70 | 64.1 |  | 64.1 | 64.5946 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 64.5946 | 16.7739 | 399219.8152 | 33.2683 | 33.2683 | 61.9333 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 64.5946 | 16.7739 | 399219.8152 | 33.2683 | 33.2683 | 61.9333 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 64.5946 | 16.7739 | 399219.8152 | 33.2683 | 33.2683 | 61.9333 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 64.5946 | 16.7739 | 399219.8152 | 33.2683 | 33.2683 | 61.9333 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 64.5946 | 16.7739 | 399219.8152 | 33.2683 | 33.2683 | 61.9333 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 64.5946 | 16.7739 | 399219.8152 | 33.2683 | 33.2683 | 61.9333 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 64.5946 | 16.7739 | 399219.8152 | 33.2683 | 33.2683 | 61.9333 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 64.5946 | 16.7739 | 399219.8152 | 33.2683 | 33.2683 | 61.9333 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 64.5946 | 16.7739 | 399219.8152 | 33.2683 | 33.2683 | 61.9333 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 64.5946 | 16.7739 | 399219.8152 | 33.2683 | 33.2683 | 61.9333 | 65 | 75 | 25.4474 | 26 | 72.7
6/3/20XX 9:00:00 AM | 0.375 | 7 | 66.1 | 68.2 | 57.1351 | 66.7889 | 9.6538 | 60 | 66.1 |  | 66.1 | 65.0513 | 0.1 | 73.21 | 18.21 | 688338 | 57.3615 | 57.3615 | 62.8646 | 15.044 | 358046.2951 | 29.8372 | 29.8372 | 87.1987 | 0.2 | 72.42 | 17.42 | 658476 | 54.873 | 54.873 | 63.1076 | 15.2869 | 363828.7903 | 30.3191 | 30.3191 | 85.1921 | 0.3 | 71.63 | 16.63 | 628614 | 52.3845 | 52.3845 | 63.3505 | 15.5299 | 369611.2854 | 30.8009 | 30.8009 | 83.1854 | 0.4 | 70.84 | 15.84 | 598752 | 49.896 | 49.896 | 63.5935 | 15.7728 | 375393.7806 | 31.2828 | 31.2828 | 81.1788 | 0.5 | 70.05 | 15.05 | 568890 | 47.4075 | 47.4075 | 63.8364 | 16.0158 | 381176.2757 | 31.7647 | 31.7647 | 79.1722 | 0.6 | 69.26 | 14.26 | 539028 | 44.919 | 44.919 | 64.0794 | 16.2588 | 386958.7709 | 32.2466 | 32.2466 | 77.1656 | 0.7 | 68.47 | 13.47 | 509166 | 42.4305 | 42.4305 | 64.3224 | 16.5017 | 392741.266 | 32.7284 | 32.7284 | 75.1589 | 0.8 | 67.68 | 12.68 | 479304 | 39.942 | 39.942 | 64.5653 | 16.7447 | 398523.7611 | 33.2103 | 33.2103 | 73.1523 | 0.9 | 66.89 | 11.89 | 449442 | 37.4535 | 37.4535 | 64.8083 | 16.9877 | 404306.2563 | 33.6922 | 33.6922 | 71.1457 | 1 | 66.1 | 11.1 | 419580 | 34.965 | 34.965 | 65.0513 | 17.2306 | 410088.7514 | 34.1741 | 34.1741 | 69.1391 | 65 | 70 | 26.0068 | 26 | 68.2
6/3/20XX 10:00:00 AM | 0.41667 | 7 | 68.9 | 64.4 | 63.1047 | 73.7935 | 10.6888 | 60 | 68.9 |  | 68.9 | 67.8078 | 0.1 | 73.49 | 18.49 | 698922 | 58.2435 | 58.2435 | 63.1402 | 15.3196 | 364606.8454 | 30.3839 | 30.3839 | 88.6274 | 0.2 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 63.6589 | 15.8382 | 376949.8908 | 31.4125 | 31.4125 | 88.0495 | 0.3 | 72.47 | 17.47 | 660366 | 55.0305 | 55.0305 | 64.1775 | 16.3568 | 389292.9361 | 32.4411 | 32.4411 | 87.4716 | 0.4 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 64.6961 | 16.8755 | 401635.9815 | 33.4697 | 33.4697 | 86.8937 | 0.5 | 71.45 | 16.45 | 621810 | 51.8175 | 51.8175 | 65.2147 | 17.3941 | 413979.0269 | 34.4983 | 34.4983 | 86.3158 | 0.6 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 65.7333 | 17.9127 | 426322.0723 | 35.5268 | 35.5268 | 85.7378 | 0.7 | 70.43 | 15.43 | 583254 | 48.6045 | 48.6045 | 66.2519 | 18.4313 | 438665.1177 | 36.5554 | 36.5554 | 85.1599 | 0.8 | 69.92 | 14.92 | 563976 | 46.998 | 46.998 | 66.7706 | 18.9499 | 451008.163 | 37.584 | 37.584 | 84.582 | 0.9 | 69.41 | 14.41 | 544698 | 45.3915 | 45.3915 | 67.2892 | 19.4685 | 463351.2084 | 38.6126 | 38.6126 | 84.0041 | 1 | 68.9 | 13.9 | 525420 | 43.785 | 43.785 | 67.8078 | 19.9872 | 475694.2538 | 39.6412 | 39.6412 | 83.4262 | 70 | 65 | 27.1206 | 28 | 64.4
6/3/20XX 11:00:00 AM | 0.45833 | 7 | 71.2 | 59.5 | 56.8343 | 68.413 | 11.5787 | 50 | 71.2 |  | 71.2 | 67.8341 | 0.1 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 63.1429 | 15.3222 | 364669.4591 | 30.3891 | 30.3891 | 89.3571 | 0.2 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 63.6641 | 15.8435 | 377075.1181 | 31.4229 | 31.4229 | 89.5089 | 0.3 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 64.1854 | 16.3647 | 389480.7772 | 32.4567 | 32.4567 | 89.6607 | 0.4 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 64.7066 | 16.886 | 401886.4362 | 33.4905 | 33.4905 | 89.8125 | 0.5 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 65.2279 | 17.4072 | 414292.0953 | 34.5243 | 34.5243 | 89.9643 | 0.6 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 65.7491 | 17.9285 | 426697.7544 | 35.5581 | 35.5581 | 90.1161 | 0.7 | 72.04 | 17.04 | 644112 | 53.676 | 53.676 | 66.2704 | 18.4497 | 439103.4134 | 36.592 | 36.592 | 90.268 | 0.8 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 66.7916 | 18.971 | 451509.0725 | 37.6258 | 37.6258 | 90.4198 | 0.9 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 67.3128 | 19.4922 | 463914.7315 | 38.6596 | 38.6596 | 90.5716 | 1 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 67.8341 | 20.0135 | 476320.3906 | 39.6934 | 39.6934 | 90.7234 | 70 | 60 | 27.6866 | 28 | 59.5
6/3/20XX 12:00:00 PM | 0.5 | 7 | 72.3 | 55.8 | 59.0505 | 71.0864 | 12.0359 | 50 | 72.3 |  | 72.3 | 66.0313 | 0.1 | 73.83 | 18.83 | 711774 | 59.3145 | 59.3145 | 62.9626 | 15.142 | 360378.8679 | 30.0316 | 30.0316 | 89.3461 | 0.2 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 63.3036 | 15.4829 | 368493.9359 | 30.7078 | 30.7078 | 89.4868 | 0.3 | 73.49 | 18.49 | 698922 | 58.2435 | 58.2435 | 63.6445 | 15.8239 | 376609.0038 | 31.3841 | 31.3841 | 89.6276 | 0.4 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 63.9855 | 16.1649 | 384724.0718 | 32.0603 | 32.0603 | 89.7683 | 0.5 | 73.15 | 18.15 | 686070 | 57.1725 | 57.1725 | 64.3265 | 16.5058 | 392839.1397 | 32.7366 | 32.7366 | 89.9091 | 0.6 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 64.6674 | 16.8468 | 400954.2077 | 33.4129 | 33.4129 | 90.0499 | 0.7 | 72.81 | 17.81 | 673218 | 56.1015 | 56.1015 | 65.0084 | 17.1878 | 409069.2756 | 34.0891 | 34.0891 | 90.1906 | 0.8 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 65.3494 | 17.5288 | 417184.3436 | 34.7654 | 34.7654 | 90.3314 | 0.9 | 72.47 | 17.47 | 660366 | 55.0305 | 55.0305 | 65.6904 | 17.8697 | 425299.4115 | 35.4416 | 35.4416 | 90.4721 | 1 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 66.0313 | 18.2107 | 433414.4794 | 36.1179 | 36.1179 | 90.6129 | 70 | 55 | 27.6736 | 28 | 55.8
6/3/20XX 1:00:00 PM | 0.54167 | 7 | 73 | 51.6 | 60.4992 | 72.8342 | 12.335 | 50 | 73 |  | 73 | 62.4728 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 62.6068 | 14.7861 | 351909.6615 | 29.3258 | 29.3258 | 88.8608 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 62.5919 | 14.7712 | 351555.5231 | 29.2963 | 29.2963 | 88.5163 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 62.577 | 14.7564 | 351201.3846 | 29.2668 | 29.2668 | 88.1718 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 62.5621 | 14.7415 | 350847.2461 | 29.2373 | 29.2373 | 87.8273 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 62.5472 | 14.7266 | 350493.1077 | 29.2078 | 29.2078 | 87.4828 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 62.5324 | 14.7117 | 350138.9692 | 29.1782 | 29.1782 | 87.1382 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 62.5175 | 14.6968 | 349784.8307 | 29.1487 | 29.1487 | 86.7937 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 62.5026 | 14.682 | 349430.6922 | 29.1192 | 29.1192 | 86.4492 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 62.4877 | 14.6671 | 349076.5538 | 29.0897 | 29.0897 | 86.1047 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 62.4728 | 14.6522 | 348722.4153 | 29.0602 | 29.0602 | 85.7602 | 75 | 50 | 27.2881 | 28 | 51.6
6/3/20XX 2:00:00 PM | 0.58333 | 7 | 71.8 | 54 | 58.0341 | 69.8602 | 11.8262 | 50 | 71.8 |  | 71.8 | 62.7645 | 0.1 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 62.6359 | 14.8153 | 352603.8906 | 29.3837 | 29.3837 | 88.5407 | 0.2 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 62.6502 | 14.8296 | 352943.9813 | 29.412 | 29.412 | 87.876 | 0.3 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 62.6645 | 14.8439 | 353284.0719 | 29.4403 | 29.4403 | 87.2113 | 0.4 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 62.6788 | 14.8582 | 353624.1625 | 29.4687 | 29.4687 | 86.5467 | 0.5 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 62.6931 | 14.8724 | 353964.2532 | 29.497 | 29.497 | 85.882 | 0.6 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 62.7074 | 14.8867 | 354304.3438 | 29.5254 | 29.5254 | 85.2174 | 0.7 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 62.7217 | 14.901 | 354644.4344 | 29.5537 | 29.5537 | 84.5527 | 0.8 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 62.7359 | 14.9153 | 354984.5251 | 29.582 | 29.582 | 83.888 | 0.9 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 62.7502 | 14.9296 | 355324.6157 | 29.6104 | 29.6104 | 83.2234 | 1 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 62.7645 | 14.9439 | 355664.7063 | 29.6387 | 29.6387 | 82.5587 | 70 | 55 | 27.0409 | 28 | 54
6/3/20XX 3:00:00 PM | 0.625 | 7 | 71.7 | 54.5 | 57.8326 | 69.6172 | 11.7846 | 50 | 71.7 |  | 71.7 | 63.1357 | 0.1 | 73.77 | 18.77 | 709506 | 59.1255 | 59.1255 | 62.673 | 14.8524 | 353487.2028 | 29.4573 | 29.4573 | 88.5828 | 0.2 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 62.7244 | 14.9038 | 354710.6057 | 29.5592 | 29.5592 | 87.9602 | 0.3 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 62.7758 | 14.9552 | 355934.0085 | 29.6612 | 29.6612 | 87.3377 | 0.4 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 62.8272 | 15.0066 | 357157.4114 | 29.7631 | 29.7631 | 86.7151 | 0.5 | 72.85 | 17.85 | 674730 | 56.2275 | 56.2275 | 62.8786 | 15.058 | 358380.8142 | 29.8651 | 29.8651 | 86.0926 | 0.6 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 62.9301 | 15.1094 | 359604.2171 | 29.967 | 29.967 | 85.47 | 0.7 | 72.39 | 17.39 | 657342 | 54.7785 | 54.7785 | 62.9815 | 15.1608 | 360827.6199 | 30.069 | 30.069 | 84.8475 | 0.8 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 63.0329 | 15.2122 | 362051.0228 | 30.1709 | 30.1709 | 84.2249 | 0.9 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 63.0843 | 15.2636 | 363274.4256 | 30.2729 | 30.2729 | 83.6024 | 1 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 63.1357 | 15.315 | 364497.8285 | 30.3748 | 30.3748 | 82.9798 | 70 | 55 | 27.0746 | 28 | 54.5
6/3/20XX 4:00:00 PM | 0.66667 | 7 | 71 | 57.2 | 56.4392 | 67.9365 | 11.4973 | 50 | 71 |  | 71 | 64.7172 | 0.1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 62.8312 | 15.0106 | 357251.2934 | 29.7709 | 29.7709 | 88.6759 | 0.2 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 63.0407 | 15.2201 | 362238.7868 | 30.1866 | 30.1866 | 88.1466 | 0.3 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 63.2503 | 15.4297 | 367226.2801 | 30.6022 | 30.6022 | 87.6172 | 0.4 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 63.4599 | 15.6392 | 372213.7735 | 31.0178 | 31.0178 | 87.0878 | 0.5 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 63.6694 | 15.8488 | 377201.2669 | 31.4334 | 31.4334 | 86.5584 | 0.6 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 63.879 | 16.0584 | 382188.7603 | 31.8491 | 31.8491 | 86.0291 | 0.7 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 64.0885 | 16.2679 | 387176.2536 | 32.2647 | 32.2647 | 85.4997 | 0.8 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 64.2981 | 16.4775 | 392163.747 | 32.6803 | 32.6803 | 84.9703 | 0.9 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 64.5077 | 16.687 | 397151.2404 | 33.0959 | 33.0959 | 84.4409 | 1 | 71 | 16 | 604800 | 50.4 | 50.4 | 64.7172 | 16.8966 | 402138.7338 | 33.5116 | 33.5116 | 83.9116 | 70 | 55 | 27.1508 | 28 | 57.2
6/3/20XX 5:00:00 PM | 0.70833 | 7 | 69.3 | 62.9 | 64.0011 | 74.8454 | 10.8443 | 60 | 69.3 |  | 69.3 | 67.146 | 0.1 | 73.53 | 18.53 | 700434 | 58.3695 | 58.3695 | 63.0741 | 15.2534 | 363031.6768 | 30.2526 | 30.2526 | 88.6221 | 0.2 | 73.06 | 18.06 | 682668 | 56.889 | 56.889 | 63.5265 | 15.7059 | 373799.5536 | 31.15 | 31.15 | 88.039 | 0.3 | 72.59 | 17.59 | 664902 | 55.4085 | 55.4085 | 63.9789 | 16.1583 | 384567.4303 | 32.0473 | 32.0473 | 87.4558 | 0.4 | 72.12 | 17.12 | 647136 | 53.928 | 53.928 | 64.4314 | 16.6107 | 395335.3071 | 32.9446 | 32.9446 | 86.8726 | 0.5 | 71.65 | 16.65 | 629370 | 52.4475 | 52.4475 | 64.8838 | 17.0632 | 406103.1839 | 33.8419 | 33.8419 | 86.2894 | 0.6 | 71.18 | 16.18 | 611604 | 50.967 | 50.967 | 65.3362 | 17.5156 | 416871.0607 | 34.7393 | 34.7393 | 85.7063 | 0.7 | 70.71 | 15.71 | 593838 | 49.4865 | 49.4865 | 65.7887 | 17.968 | 427638.9374 | 35.6366 | 35.6366 | 85.1231 | 0.8 | 70.24 | 15.24 | 576072 | 48.006 | 48.006 | 66.2411 | 18.4205 | 438406.8142 | 36.5339 | 36.5339 | 84.5399 | 0.9 | 69.77 | 14.77 | 558306 | 46.5255 | 46.5255 | 66.6935 | 18.8729 | 449174.691 | 37.4312 | 37.4312 | 83.9567 | 1 | 69.3 | 14.3 | 540540 | 45.045 | 45.045 | 67.146 | 19.3253 | 459942.5678 | 38.3285 | 38.3285 | 83.3735 | 70 | 65 | 27.115 | 28 | 62.9
6/3/20XX 6:00:00 PM | 0.75 | 7 | 68.3 | 66.8 | 61.7809 | 72.24 | 10.4591 | 60 | 68.3 |  | 68.3 | 68.8931 | 0.1 | 73.43 | 18.43 | 696654 | 58.0545 | 58.0545 | 63.2488 | 15.4281 | 367189.9291 | 30.5992 | 30.5992 | 88.6537 | 0.2 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 63.8759 | 16.0553 | 382116.0582 | 31.843 | 31.843 | 88.102 | 0.3 | 72.29 | 17.29 | 653562 | 54.4635 | 54.4635 | 64.5031 | 16.6824 | 397042.1873 | 33.0868 | 33.0868 | 87.5503 | 0.4 | 71.72 | 16.72 | 632016 | 52.668 | 52.668 | 65.1302 | 17.3096 | 411968.3164 | 34.3307 | 34.3307 | 86.9987 | 0.5 | 71.15 | 16.15 | 610470 | 50.8725 | 50.8725 | 65.7574 | 17.9367 | 426894.4455 | 35.5745 | 35.5745 | 86.447 | 0.6 | 70.58 | 15.58 | 588924 | 49.077 | 49.077 | 66.3845 | 18.5639 | 441820.5746 | 36.8184 | 36.8184 | 85.8954 | 0.7 | 70.01 | 15.01 | 567378 | 47.2815 | 47.2815 | 67.0117 | 19.191 | 456746.7037 | 38.0622 | 38.0622 | 85.3437 | 0.8 | 69.44 | 14.44 | 545832 | 45.486 | 45.486 | 67.6388 | 19.8182 | 471672.8328 | 39.3061 | 39.3061 | 84.7921 | 0.9 | 68.87 | 13.87 | 524286 | 43.6905 | 43.6905 | 68.266 | 20.4453 | 486598.9619 | 40.5499 | 40.5499 | 84.2404 | 1 | 68.3 | 13.3 | 502740 | 41.895 | 41.895 | 68.8931 | 21.0725 | 501525.091 | 41.7938 | 41.7938 | 83.6888 | 70 | 65 | 27.1434 | 28 | 66.8
6/3/20XX 7:00:00 PM | 0.79167 | 7 | 67.6 | 67.6 | 60.2675 | 70.4642 | 10.1967 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/3/20XX 8:00:00 PM | 0.83333 | 7 | 66.4 | 69 | 57.7497 | 67.51 | 9.7603 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/3/20XX 9:00:00 PM | 0.875 | 7 | 65.8 | 65.9 | 56.5264 | 66.0748 | 9.5484 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/3/20XX 10:00:00 PM | 0.91667 | 7 | 64.4 | 69 | 53.7621 | 62.8319 | 9.0698 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/3/20XX 11:00:00 PM | 0.95833 | 7 | 63.6 | 68.1 | 52.238 | 61.0441 | 8.8061 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/3/20XX 12:00:00 AM | 0 | 1 | 63 | 70 | 59.7337 | 68.4087 | 8.6749 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/4/20XX 1:00:00 AM | 0.041667 | 1 | 61.8 | 71.3 | 57.1898 | 65.4908 | 8.301 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/4/20XX 2:00:00 AM | 0.083333 | 1 | 61.6 | 71.7 | 56.7756 | 65.0158 | 8.2402 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/4/20XX 3:00:00 AM | 0.125 | 1 | 60.7 | 73.5 | 54.9457 | 62.9177 | 7.972 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/4/20XX 4:00:00 AM | 0.16667 | 1 | 60.3 | 74.4 | 54.1501 | 62.0055 | 7.8554 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/4/20XX 5:00:00 AM | 0.20833 | 1 | 60.2 | 74.7 | 53.9528 | 61.7794 | 7.8266 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/4/20XX 6:00:00 AM | 0.25 | 1 | 60.4 | 75.4 | 54.348 | 62.2324 | 7.8844 | 70 | 60.4 |  | 60.4 | 58.6055 | 1 | 60.4 | 5.4 | 204120 | 17.01 | 17.01 | 58.6055 | 10.7849 | 256680.8904 | 21.3901 | 21.3901 | 38.4001 | 1 | 60.4 | 5.4 | 204120 | 17.01 | 17.01 | 58.6055 | 10.7849 | 256680.8904 | 21.3901 | 21.3901 | 38.4001 | 1 | 60.4 | 5.4 | 204120 | 17.01 | 17.01 | 58.6055 | 10.7849 | 256680.8904 | 21.3901 | 21.3901 | 38.4001 | 1 | 60.4 | 5.4 | 204120 | 17.01 | 17.01 | 58.6055 | 10.7849 | 256680.8904 | 21.3901 | 21.3901 | 38.4001 | 1 | 60.4 | 5.4 | 204120 | 17.01 | 17.01 | 58.6055 | 10.7849 | 256680.8904 | 21.3901 | 21.3901 | 38.4001 | 1 | 60.4 | 5.4 | 204120 | 17.01 | 17.01 | 58.6055 | 10.7849 | 256680.8904 | 21.3901 | 21.3901 | 38.4001 | 1 | 60.4 | 5.4 | 204120 | 17.01 | 17.01 | 58.6055 | 10.7849 | 256680.8904 | 21.3901 | 21.3901 | 38.4001 | 1 | 60.4 | 5.4 | 204120 | 17.01 | 17.01 | 58.6055 | 10.7849 | 256680.8904 | 21.3901 | 21.3901 | 38.4001 | 1 | 60.4 | 5.4 | 204120 | 17.01 | 17.01 | 58.6055 | 10.7849 | 256680.8904 | 21.3901 | 21.3901 | 38.4001 | 1 | 60.4 | 5.4 | 204120 | 17.01 | 17.01 | 58.6055 | 10.7849 | 256680.8904 | 21.3901 | 21.3901 | 38.4001 | 60 | 75 | 23.6126 | 24 | 75.4
6/4/20XX 7:00:00 AM | 0.29167 | 1 | 61.4 | 73.7 | 56.3642 | 64.544 | 8.1799 | 70 | 61.4 |  | 61.4 | 59.3907 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 59.3907 | 11.5701 | 275368.0248 | 22.9473 | 22.9473 | 43.1073 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 59.3907 | 11.5701 | 275368.0248 | 22.9473 | 22.9473 | 43.1073 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 59.3907 | 11.5701 | 275368.0248 | 22.9473 | 22.9473 | 43.1073 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 59.3907 | 11.5701 | 275368.0248 | 22.9473 | 22.9473 | 43.1073 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 59.3907 | 11.5701 | 275368.0248 | 22.9473 | 22.9473 | 43.1073 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 59.3907 | 11.5701 | 275368.0248 | 22.9473 | 22.9473 | 43.1073 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 59.3907 | 11.5701 | 275368.0248 | 22.9473 | 22.9473 | 43.1073 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 59.3907 | 11.5701 | 275368.0248 | 22.9473 | 22.9473 | 43.1073 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 59.3907 | 11.5701 | 275368.0248 | 22.9473 | 22.9473 | 43.1073 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 59.3907 | 11.5701 | 275368.0248 | 22.9473 | 22.9473 | 43.1073 | 60 | 75 | 23.9785 | 24 | 73.7
6/4/20XX 8:00:00 AM | 0.33333 | 1 | 62.7 | 70.1 | 59.0882 | 67.6682 | 8.58 | 70 | 62.7 |  | 62.7 | 59.174 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 59.174 | 11.3534 | 270210.7561 | 22.5176 | 22.5176 | 46.7726 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 59.174 | 11.3534 | 270210.7561 | 22.5176 | 22.5176 | 46.7726 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 59.174 | 11.3534 | 270210.7561 | 22.5176 | 22.5176 | 46.7726 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 59.174 | 11.3534 | 270210.7561 | 22.5176 | 22.5176 | 46.7726 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 59.174 | 11.3534 | 270210.7561 | 22.5176 | 22.5176 | 46.7726 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 59.174 | 11.3534 | 270210.7561 | 22.5176 | 22.5176 | 46.7726 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 59.174 | 11.3534 | 270210.7561 | 22.5176 | 22.5176 | 46.7726 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 59.174 | 11.3534 | 270210.7561 | 22.5176 | 22.5176 | 46.7726 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 59.174 | 11.3534 | 270210.7561 | 22.5176 | 22.5176 | 46.7726 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 59.174 | 11.3534 | 270210.7561 | 22.5176 | 22.5176 | 46.7726 | 65 | 70 | 24.2616 | 24 | 70.1
6/4/20XX 9:00:00 AM | 0.375 | 1 | 64.4 | 68.1 | 53.7621 | 62.8319 | 9.0698 | 60 | 64.4 |  | 64.4 | 61.1087 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 61.1087 | 13.288 | 316255.0098 | 26.3546 | 26.3546 | 55.9646 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 61.1087 | 13.288 | 316255.0098 | 26.3546 | 26.3546 | 55.9646 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 61.1087 | 13.288 | 316255.0098 | 26.3546 | 26.3546 | 55.9646 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 61.1087 | 13.288 | 316255.0098 | 26.3546 | 26.3546 | 55.9646 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 61.1087 | 13.288 | 316255.0098 | 26.3546 | 26.3546 | 55.9646 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 61.1087 | 13.288 | 316255.0098 | 26.3546 | 26.3546 | 55.9646 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 61.1087 | 13.288 | 316255.0098 | 26.3546 | 26.3546 | 55.9646 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 61.1087 | 13.288 | 316255.0098 | 26.3546 | 26.3546 | 55.9646 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 61.1087 | 13.288 | 316255.0098 | 26.3546 | 26.3546 | 55.9646 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 61.1087 | 13.288 | 316255.0098 | 26.3546 | 26.3546 | 55.9646 | 65 | 70 | 24.9775 | 24 | 68.1
6/4/20XX 10:00:00 AM | 0.41667 | 1 | 66.3 | 66.4 | 57.5442 | 67.2689 | 9.7247 | 60 | 66.3 |  | 66.3 | 63.768 | 0.1 | 73.23 | 18.23 | 689094 | 57.4245 | 57.4245 | 62.7363 | 14.9156 | 354992.1385 | 29.5827 | 29.5827 | 87.0072 | 0.2 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 62.8509 | 15.0303 | 357720.477 | 29.81 | 29.81 | 84.809 | 0.3 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 62.9655 | 15.1449 | 360448.8155 | 30.0374 | 30.0374 | 82.6109 | 0.4 | 70.92 | 15.92 | 601776 | 50.148 | 50.148 | 63.0802 | 15.2595 | 363177.154 | 30.2648 | 30.2648 | 80.4128 | 0.5 | 70.15 | 15.15 | 572670 | 47.7225 | 47.7225 | 63.1948 | 15.3742 | 365905.4925 | 30.4921 | 30.4921 | 78.2146 | 0.6 | 69.38 | 14.38 | 543564 | 45.297 | 45.297 | 63.3094 | 15.4888 | 368633.831 | 30.7195 | 30.7195 | 76.0165 | 0.7 | 68.61 | 13.61 | 514458 | 42.8715 | 42.8715 | 63.4241 | 15.6035 | 371362.1696 | 30.9468 | 30.9468 | 73.8183 | 0.8 | 67.84 | 12.84 | 485352 | 40.446 | 40.446 | 63.5387 | 15.7181 | 374090.5081 | 31.1742 | 31.1742 | 71.6202 | 0.9 | 67.07 | 12.07 | 456246 | 38.0205 | 38.0205 | 63.6534 | 15.8327 | 376818.8466 | 31.4016 | 31.4016 | 69.4221 | 1 | 66.3 | 11.3 | 427140 | 35.595 | 35.595 | 63.768 | 15.9474 | 379547.1851 | 31.6289 | 31.6289 | 67.2239 | 65 | 65 | 25.8555 | 26 | 66.4
6/4/20XX 11:00:00 AM | 0.45833 | 1 | 68.4 | 61.3 | 61.9998 | 72.4969 | 10.4971 | 60 | 68.4 |  | 68.4 | 63.3644 | 0.1 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 62.6959 | 14.8753 | 354031.6893 | 29.5026 | 29.5026 | 87.5886 | 0.2 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 62.7702 | 14.9496 | 355799.5786 | 29.65 | 29.65 | 85.972 | 0.3 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 62.8445 | 15.0238 | 357567.4679 | 29.7973 | 29.7973 | 84.3553 | 0.4 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 62.9188 | 15.0981 | 359335.3573 | 29.9446 | 29.9446 | 82.7386 | 0.5 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 62.993 | 15.1724 | 361103.2466 | 30.0919 | 30.0919 | 81.1219 | 0.6 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 63.0673 | 15.2467 | 362871.1359 | 30.2393 | 30.2393 | 79.5053 | 0.7 | 70.08 | 15.08 | 570024 | 47.502 | 47.502 | 63.1416 | 15.321 | 364639.0252 | 30.3866 | 30.3866 | 77.8886 | 0.8 | 69.52 | 14.52 | 548856 | 45.738 | 45.738 | 63.2159 | 15.3952 | 366406.9145 | 30.5339 | 30.5339 | 76.2719 | 0.9 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 63.2902 | 15.4695 | 368174.8038 | 30.6812 | 30.6812 | 74.6552 | 1 | 68.4 | 13.4 | 506520 | 42.21 | 42.21 | 63.3644 | 15.5438 | 369942.6932 | 30.8286 | 30.8286 | 73.0386 | 70 | 60 | 26.305 | 26 | 61.3 | [9 empty] | New OAD
6/4/20XX 12:00:00 PM | 0.5 | 1 | 69.6 | 57.7 | 53.7396 | 64.6807 | 10.9411 | 50 | 69.6 |  | 69.6 | 62.1643 | 0.1 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 62.5759 | 14.7553 | 351175.2347 | 29.2646 | 29.2646 | 87.7286 | 0.2 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 62.5302 | 14.7095 | 350086.6694 | 29.1739 | 29.1739 | 86.2519 | 0.3 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 62.4844 | 14.6638 | 348998.1042 | 29.0832 | 29.0832 | 84.7752 | 0.4 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 62.4387 | 14.618 | 347909.5389 | 28.9925 | 28.9925 | 83.2985 | 0.5 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 62.3929 | 14.5723 | 346820.9736 | 28.9017 | 28.9017 | 81.8217 | 0.6 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 62.3472 | 14.5266 | 345732.4083 | 28.811 | 28.811 | 80.345 | 0.7 | 70.92 | 15.92 | 601776 | 50.148 | 50.148 | 62.3015 | 14.4808 | 344643.843 | 28.7203 | 28.7203 | 78.8683 | 0.8 | 70.48 | 15.48 | 585144 | 48.762 | 48.762 | 62.2557 | 14.4351 | 343555.2778 | 28.6296 | 28.6296 | 77.3916 | 0.9 | 70.04 | 15.04 | 568512 | 47.376 | 47.376 | 62.21 | 14.3894 | 342466.7125 | 28.5389 | 28.5389 | 75.9149 | 1 | 69.6 | 14.6 | 551880 | 45.99 | 45.99 | 62.1643 | 14.3436 | 341378.1472 | 28.4482 | 28.4482 | 74.4382 | 70 | 60 | 26.4105 | 26 | 57.7 | [9 empty] | #REF!
6/4/20XX 1:00:00 PM | 0.54167 | 1 | 70.6 | 54.8 | 55.6561 | 66.992 | 11.3359 | 50 | 70.6 |  | 70.6 | 61.0973 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 62.4692 | 14.6486 | 348635.9082 | 29.053 | 29.053 | 87.832 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 62.3168 | 14.4961 | 345008.0164 | 28.7507 | 28.7507 | 86.4587 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 62.1643 | 14.3437 | 341380.1246 | 28.4483 | 28.4483 | 85.0853 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 62.0119 | 14.1913 | 337752.2328 | 28.146 | 28.146 | 83.712 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 61.8595 | 14.0388 | 334124.3409 | 27.8437 | 27.8437 | 82.3387 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 61.707 | 13.8864 | 330496.4491 | 27.5414 | 27.5414 | 80.9654 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 61.5546 | 13.734 | 326868.5573 | 27.239 | 27.239 | 79.592 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 61.4022 | 13.5815 | 323240.6655 | 26.9367 | 26.9367 | 78.2187 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 61.2497 | 13.4291 | 319612.7737 | 26.6344 | 26.6344 | 76.8454 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 61.0973 | 13.2767 | 315984.8819 | 26.3321 | 26.3321 | 75.4721 | 70 | 55 | 26.4877 | 26 | 54.8 | [9 empty] | #REF!
6/4/20XX 2:00:00 PM | 0.58333 | 1 | 71.2 | 55.2 | 56.8343 | 68.413 | 11.5787 | 50 | 71.2 |  | 71.2 | 62.8552 | 0.1 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 62.645 | 14.8244 | 352819.7909 | 29.4016 | 29.4016 | 88.3696 | 0.2 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 62.6684 | 14.8477 | 353375.7818 | 29.448 | 29.448 | 87.534 | 0.3 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 62.6917 | 14.8711 | 353931.7727 | 29.4943 | 29.4943 | 86.6983 | 0.4 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 62.7151 | 14.8944 | 354487.7635 | 29.5406 | 29.5406 | 85.8626 | 0.5 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 62.7384 | 14.9178 | 355043.7544 | 29.587 | 29.587 | 85.027 | 0.6 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 62.7618 | 14.9412 | 355599.7453 | 29.6333 | 29.6333 | 84.1913 | 0.7 | 72.04 | 17.04 | 644112 | 53.676 | 53.676 | 62.7852 | 14.9645 | 356155.7362 | 29.6796 | 29.6796 | 83.3556 | 0.8 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 62.8085 | 14.9879 | 356711.7271 | 29.726 | 29.726 | 82.52 | 0.9 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 62.8319 | 15.0112 | 357267.718 | 29.7723 | 29.7723 | 81.6843 | 1 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 62.8552 | 15.0346 | 357823.7089 | 29.8186 | 29.8186 | 80.8486 | 70 | 55 | 26.9087 | 26 | 55.2 | [9 empty] | #REF!
6/4/20XX 3:00:00 PM | 0.625 | 1 | 71.3 | 55.4 | 57.0328 | 68.6524 | 11.6196 | 50 | 71.3 |  | 71.3 | 63.3074 | 0.1 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 62.6902 | 14.8696 | 353895.8554 | 29.4913 | 29.4913 | 88.4908 | 0.2 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 62.7588 | 14.9381 | 355527.9107 | 29.6273 | 29.6273 | 87.7763 | 0.3 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 62.8274 | 15.0067 | 357159.9661 | 29.7633 | 29.7633 | 87.0618 | 0.4 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 62.8959 | 15.0753 | 358792.0214 | 29.8993 | 29.8993 | 86.3473 | 0.5 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 62.9645 | 15.1439 | 360424.0768 | 30.0353 | 30.0353 | 85.6328 | 0.6 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 63.0331 | 15.2124 | 362056.1321 | 30.1713 | 30.1713 | 84.9183 | 0.7 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 63.1016 | 15.281 | 363688.1875 | 30.3073 | 30.3073 | 84.2038 | 0.8 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 63.1702 | 15.3496 | 365320.2428 | 30.4434 | 30.4434 | 83.4894 | 0.9 | 71.57 | 16.57 | 626346 | 52.1955 | 52.1955 | 63.2388 | 15.4182 | 366952.2982 | 30.5794 | 30.5794 | 82.7749 | 1 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 63.3074 | 15.4867 | 368584.3535 | 30.7154 | 30.7154 | 82.0604 | 70 | 55 | 27.0038 | 28 | 55.4 | [9 empty] | #REF!
6/4/20XX 4:00:00 PM | 0.66667 | 1 | 70.3 | 56.8 | 55.075 | 66.2911 | 11.2161 | 50 | 70.3 |  | 70.3 | 62.702 | 0.1 | 73.63 | 18.63 | 704214 | 58.6845 | 58.6845 | 62.6297 | 14.809 | 352454.9745 | 29.3712 | 29.3712 | 88.0557 | 0.2 | 73.26 | 18.26 | 690228 | 57.519 | 57.519 | 62.6377 | 14.8171 | 352646.149 | 29.3872 | 29.3872 | 86.9062 | 0.3 | 72.89 | 17.89 | 676242 | 56.3535 | 56.3535 | 62.6457 | 14.8251 | 352837.3234 | 29.4031 | 29.4031 | 85.7566 | 0.4 | 72.52 | 17.52 | 662256 | 55.188 | 55.188 | 62.6538 | 14.8331 | 353028.4979 | 29.419 | 29.419 | 84.607 | 0.5 | 72.15 | 17.15 | 648270 | 54.0225 | 54.0225 | 62.6618 | 14.8412 | 353219.6724 | 29.435 | 29.435 | 83.4575 | 0.6 | 71.78 | 16.78 | 634284 | 52.857 | 52.857 | 62.6698 | 14.8492 | 353410.8469 | 29.4509 | 29.4509 | 82.3079 | 0.7 | 71.41 | 16.41 | 620298 | 51.6915 | 51.6915 | 62.6779 | 14.8572 | 353602.0214 | 29.4668 | 29.4668 | 81.1583 | 0.8 | 71.04 | 16.04 | 606312 | 50.526 | 50.526 | 62.6859 | 14.8653 | 353793.1959 | 29.4828 | 29.4828 | 80.0088 | 0.9 | 70.67 | 15.67 | 592326 | 49.3605 | 49.3605 | 62.6939 | 14.8733 | 353984.3703 | 29.4987 | 29.4987 | 78.8592 | 1 | 70.3 | 15.3 | 578340 | 48.195 | 48.195 | 62.702 | 14.8813 | 354175.5448 | 29.5146 | 29.5146 | 77.7096 | 70 | 55 | 26.6652 | 26 | 56.8
6/4/20XX 5:00:00 PM | 0.70833 | 1 | 69.5 | 58.1 | 53.5511 | 64.4535 | 10.9023 | 50 | 69.5 |  | 69.5 | 62.382 | 0.1 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 62.5977 | 14.777 | 351693.5475 | 29.3078 | 29.3078 | 87.7403 | 0.2 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 62.5737 | 14.7531 | 351123.295 | 29.2603 | 29.2603 | 86.2753 | 0.3 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 62.5498 | 14.7291 | 350553.0424 | 29.2128 | 29.2128 | 84.8103 | 0.4 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 62.5258 | 14.7052 | 349982.7899 | 29.1652 | 29.1652 | 83.3452 | 0.5 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 62.5018 | 14.6812 | 349412.5374 | 29.1177 | 29.1177 | 81.8802 | 0.6 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 62.4779 | 14.6572 | 348842.2849 | 29.0702 | 29.0702 | 80.4152 | 0.7 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 62.4539 | 14.6333 | 348272.0324 | 29.0227 | 29.0227 | 78.9502 | 0.8 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 62.43 | 14.6093 | 347701.7799 | 28.9751 | 28.9751 | 77.4851 | 0.9 | 69.95 | 14.95 | 565110 | 47.0925 | 47.0925 | 62.406 | 14.5854 | 347131.5273 | 28.9276 | 28.9276 | 76.0201 | 1 | 69.5 | 14.5 | 548100 | 45.675 | 45.675 | 62.382 | 14.5614 | 346561.2748 | 28.8801 | 28.8801 | 74.5551 | 70 | 60 | 26.4201 | 26 | 58.1
6/4/20XX 6:00:00 PM | 0.75 | 1 | 68.6 | 60.5 | 62.4397 | 73.0131 | 10.5734 | 60 | 68.6 |  | 68.6 | 62.9684 | 0.1 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 62.6563 | 14.8357 | 353089.0708 | 29.4241 | 29.4241 | 87.5731 | 0.2 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 62.691 | 14.8704 | 353914.3416 | 29.4929 | 29.4929 | 85.9409 | 0.3 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 62.7257 | 14.905 | 354739.6124 | 29.5616 | 29.5616 | 84.3086 | 0.4 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 62.7603 | 14.9397 | 355564.8832 | 29.6304 | 29.6304 | 82.6764 | 0.5 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 62.795 | 14.9744 | 356390.154 | 29.6992 | 29.6992 | 81.0442 | 0.6 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 62.8297 | 15.0091 | 357215.4248 | 29.768 | 29.768 | 79.412 | 0.7 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 62.8644 | 15.0437 | 358040.6956 | 29.8367 | 29.8367 | 77.7797 | 0.8 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 62.899 | 15.0784 | 358865.9664 | 29.9055 | 29.9055 | 76.1475 | 0.9 | 69.14 | 14.14 | 534492 | 44.541 | 44.541 | 62.9337 | 15.1131 | 359691.2372 | 29.9743 | 29.9743 | 74.5153 | 1 | 68.6 | 13.6 | 514080 | 42.84 | 42.84 | 62.9684 | 15.1478 | 360516.508 | 30.043 | 30.043 | 72.883 | 70 | 60 | 26.292 | 26 | 60.5
6/4/20XX 7:00:00 PM | 0.79167 | 1 | 67.4 | 65.2 | 59.8412 | 69.964 | 10.1228 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/4/20XX 8:00:00 PM | 0.83333 | 1 | 66.2 | 67.3 | 57.3393 | 67.0285 | 9.6892 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/4/20XX 9:00:00 PM | 0.875 | 1 | 65.3 | 70.4 | 64.8997 | 74.3365 | 9.4368 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/4/20XX 10:00:00 PM | 0.91667 | 1 | 64.3 | 72 | 62.6059 | 71.704 | 9.0981 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/4/20XX 11:00:00 PM | 0.95833 | 1 | 63.8 | 73.6 | 61.4867 | 70.4198 | 8.9331 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/4/20XX 12:00:00 AM | 0 | 2 | 62.7 | 75.5 | 59.0882 | 67.6682 | 8.58 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/5/20XX 1:00:00 AM | 0.041667 | 2 | 62.2 | 76.6 | 58.0265 | 66.4504 | 8.4239 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/5/20XX 2:00:00 AM | 0.083333 | 2 | 61.6 | 77.9 | 56.7756 | 65.0158 | 8.2402 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/5/20XX 3:00:00 AM | 0.125 | 2 | 60.9 | 78.6 | 55.3476 | 63.3784 | 8.0308 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/5/20XX 4:00:00 AM | 0.16667 | 2 | 60.5 | 80.7 | 62.46 | 70.3375 | 7.8775 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/5/20XX 5:00:00 AM | 0.20833 | 2 | 60.3 | 80.7 | 62.0055 | 69.8243 | 7.8188 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/5/20XX 6:00:00 AM | 0.25 | 2 | 61.2 | 80.3 | 64.0754 | 72.1617 | 8.0863 | 80 | 61.2 |  | 61.2 | 64.318 | 1 | 61.2 | 6.2 | 234360 | 19.53 | 19.53 | 64.318 | 16.4974 | 392637.5659 | 32.7198 | 32.7198 | 52.2498 | 1 | 61.2 | 6.2 | 234360 | 19.53 | 19.53 | 64.318 | 16.4974 | 392637.5659 | 32.7198 | 32.7198 | 52.2498 | 1 | 61.2 | 6.2 | 234360 | 19.53 | 19.53 | 64.318 | 16.4974 | 392637.5659 | 32.7198 | 32.7198 | 52.2498 | 1 | 61.2 | 6.2 | 234360 | 19.53 | 19.53 | 64.318 | 16.4974 | 392637.5659 | 32.7198 | 32.7198 | 52.2498 | 1 | 61.2 | 6.2 | 234360 | 19.53 | 19.53 | 64.318 | 16.4974 | 392637.5659 | 32.7198 | 32.7198 | 52.2498 | 1 | 61.2 | 6.2 | 234360 | 19.53 | 19.53 | 64.318 | 16.4974 | 392637.5659 | 32.7198 | 32.7198 | 52.2498 | 1 | 61.2 | 6.2 | 234360 | 19.53 | 19.53 | 64.318 | 16.4974 | 392637.5659 | 32.7198 | 32.7198 | 52.2498 | 1 | 61.2 | 6.2 | 234360 | 19.53 | 19.53 | 64.318 | 16.4974 | 392637.5659 | 32.7198 | 32.7198 | 52.2498 | 1 | 61.2 | 6.2 | 234360 | 19.53 | 19.53 | 64.318 | 16.4974 | 392637.5659 | 32.7198 | 32.7198 | 52.2498 | 1 | 61.2 | 6.2 | 234360 | 19.53 | 19.53 | 64.318 | 16.4974 | 392637.5659 | 32.7198 | 32.7198 | 52.2498 | 60 | 80 | 24.6964 | 24 | 80.3
6/5/20XX 7:00:00 AM | 0.29167 | 2 | 62.4 | 77.5 | 58.4491 | 66.9351 | 8.486 | 70 | 62.4 |  | 62.4 | 64.8136 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 64.8136 | 16.993 | 404432.7319 | 33.7027 | 33.7027 | 57.0127 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 64.8136 | 16.993 | 404432.7319 | 33.7027 | 33.7027 | 57.0127 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 64.8136 | 16.993 | 404432.7319 | 33.7027 | 33.7027 | 57.0127 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 64.8136 | 16.993 | 404432.7319 | 33.7027 | 33.7027 | 57.0127 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 64.8136 | 16.993 | 404432.7319 | 33.7027 | 33.7027 | 57.0127 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 64.8136 | 16.993 | 404432.7319 | 33.7027 | 33.7027 | 57.0127 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 64.8136 | 16.993 | 404432.7319 | 33.7027 | 33.7027 | 57.0127 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 64.8136 | 16.993 | 404432.7319 | 33.7027 | 33.7027 | 57.0127 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 64.8136 | 16.993 | 404432.7319 | 33.7027 | 33.7027 | 57.0127 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 64.8136 | 16.993 | 404432.7319 | 33.7027 | 33.7027 | 57.0127 | 60 | 75 | 25.0665 | 26 | 77.5
6/5/20XX 8:00:00 AM | 0.33333 | 2 | 63.3 | 75.1 | 60.3857 | 69.1566 | 8.7709 | 70 | 63.3 |  | 63.3 | 64.8589 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 64.8589 | 17.0382 | 405509.5843 | 33.7925 | 33.7925 | 59.9375 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 64.8589 | 17.0382 | 405509.5843 | 33.7925 | 33.7925 | 59.9375 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 64.8589 | 17.0382 | 405509.5843 | 33.7925 | 33.7925 | 59.9375 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 64.8589 | 17.0382 | 405509.5843 | 33.7925 | 33.7925 | 59.9375 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 64.8589 | 17.0382 | 405509.5843 | 33.7925 | 33.7925 | 59.9375 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 64.8589 | 17.0382 | 405509.5843 | 33.7925 | 33.7925 | 59.9375 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 64.8589 | 17.0382 | 405509.5843 | 33.7925 | 33.7925 | 59.9375 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 64.8589 | 17.0382 | 405509.5843 | 33.7925 | 33.7925 | 59.9375 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 64.8589 | 17.0382 | 405509.5843 | 33.7925 | 33.7925 | 59.9375 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 64.8589 | 17.0382 | 405509.5843 | 33.7925 | 33.7925 | 59.9375 | 65 | 75 | 25.2932 | 26 | 75.1
6/5/20XX 9:00:00 AM | 0.375 | 2 | 64.3 | 73.2 | 62.6059 | 71.704 | 9.0981 | 70 | 64.3 |  | 64.3 | 65.5173 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.5173 | 17.6966 | 421179.9198 | 35.0983 | 35.0983 | 64.3933 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.5173 | 17.6966 | 421179.9198 | 35.0983 | 35.0983 | 64.3933 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.5173 | 17.6966 | 421179.9198 | 35.0983 | 35.0983 | 64.3933 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.5173 | 17.6966 | 421179.9198 | 35.0983 | 35.0983 | 64.3933 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.5173 | 17.6966 | 421179.9198 | 35.0983 | 35.0983 | 64.3933 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.5173 | 17.6966 | 421179.9198 | 35.0983 | 35.0983 | 64.3933 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.5173 | 17.6966 | 421179.9198 | 35.0983 | 35.0983 | 64.3933 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.5173 | 17.6966 | 421179.9198 | 35.0983 | 35.0983 | 64.3933 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.5173 | 17.6966 | 421179.9198 | 35.0983 | 35.0983 | 64.3933 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.5173 | 17.6966 | 421179.9198 | 35.0983 | 35.0983 | 64.3933 | 65 | 75 | 25.64 | 26 | 73.2
6/5/20XX 10:00:00 AM | 0.41667 | 2 | 65.6 | 72.2 | 65.6025 | 75.1431 | 9.5407 | 70 | 65.6 |  | 65.6 | 67.7014 | 0.1 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 63.1296 | 15.309 | 364353.7024 | 30.3628 | 30.3628 | 87.5668 | 0.2 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 63.6376 | 15.817 | 376443.6048 | 31.3703 | 31.3703 | 85.9283 | 0.3 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 64.1456 | 16.3249 | 388533.5073 | 32.3778 | 32.3778 | 84.2898 | 0.4 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 64.6535 | 16.8329 | 400623.4097 | 33.3853 | 33.3853 | 82.6513 | 0.5 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 65.1615 | 17.3409 | 412713.3121 | 34.3928 | 34.3928 | 81.0128 | 0.6 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 65.6695 | 17.8489 | 424803.2145 | 35.4003 | 35.4003 | 79.3743 | 0.7 | 68.12 | 13.12 | 495936 | 41.328 | 41.328 | 66.1775 | 18.3569 | 436893.117 | 36.4078 | 36.4078 | 77.7358 | 0.8 | 67.28 | 12.28 | 464184 | 38.682 | 38.682 | 66.6855 | 18.8648 | 448983.0194 | 37.4153 | 37.4153 | 76.0973 | 0.9 | 66.44 | 11.44 | 432432 | 36.036 | 36.036 | 67.1934 | 19.3728 | 461072.9218 | 38.4227 | 38.4227 | 74.4587 | 1 | 65.6 | 10.6 | 400680 | 33.39 | 33.39 | 67.7014 | 19.8808 | 473162.8242 | 39.4302 | 39.4302 | 72.8202 | 65 | 70 | 26.2978 | 26 | 72.2
6/5/20XX 11:00:00 AM | 0.45833 | 2 | 66.8 | 70.7 | 68.4823 | 78.4493 | 9.967 | 70 | 66.8 |  | 66.8 | 69.1799 | 0.1 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 63.2775 | 15.4568 | 367872.5843 | 30.656 | 30.656 | 88.238 | 0.2 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 63.9333 | 16.1127 | 383481.3687 | 31.9568 | 31.9568 | 87.2708 | 0.3 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 64.5891 | 16.7685 | 399090.153 | 33.2575 | 33.2575 | 86.3035 | 0.4 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 65.245 | 17.4243 | 414698.9373 | 34.5582 | 34.5582 | 85.3362 | 0.5 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 65.9008 | 18.0802 | 430307.7216 | 35.859 | 35.859 | 84.369 | 0.6 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 66.5566 | 18.736 | 445916.506 | 37.1597 | 37.1597 | 83.4017 | 0.7 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 67.2125 | 19.3918 | 461525.2903 | 38.4604 | 38.4604 | 82.4344 | 0.8 | 68.24 | 13.24 | 500472 | 41.706 | 41.706 | 67.8683 | 20.0477 | 477134.0746 | 39.7612 | 39.7612 | 81.4672 | 0.9 | 67.52 | 12.52 | 473256 | 39.438 | 39.438 | 68.5241 | 20.7035 | 492742.859 | 41.0619 | 41.0619 | 80.4999 | 1 | 66.8 | 11.8 | 446040 | 37.17 | 37.17 | 69.1799 | 21.3593 | 508351.6433 | 42.3626 | 42.3626 | 79.5326 | 65 | 70 | 26.8216 | 26 | 70.7
6/5/20XX 12:00:00 PM | 0.5 | 2 | 67.5 | 69.1 | 60.054 | 70.2137 | 10.1597 | 60 | 67.5 |  | 67.5 | 69.2994 | 0.1 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 63.2894 | 15.4688 | 368156.7914 | 30.6797 | 30.6797 | 88.4822 | 0.2 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 63.9572 | 16.1365 | 384049.7828 | 32.0041 | 32.0041 | 87.7591 | 0.3 | 72.05 | 17.05 | 644490 | 53.7075 | 53.7075 | 64.625 | 16.8043 | 399942.7742 | 33.3286 | 33.3286 | 87.0361 | 0.4 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 65.2927 | 17.4721 | 415835.7656 | 34.653 | 34.653 | 86.313 | 0.5 | 70.75 | 15.75 | 595350 | 49.6125 | 49.6125 | 65.9605 | 18.1399 | 431728.757 | 35.9774 | 35.9774 | 85.5899 | 0.6 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 66.6283 | 18.8076 | 447621.7484 | 37.3018 | 37.3018 | 84.8668 | 0.7 | 69.45 | 14.45 | 546210 | 45.5175 | 45.5175 | 67.296 | 19.4754 | 463514.7398 | 38.6262 | 38.6262 | 84.1437 | 0.8 | 68.8 | 13.8 | 521640 | 43.47 | 43.47 | 67.9638 | 20.1432 | 479407.7312 | 39.9506 | 39.9506 | 83.4206 | 0.9 | 68.15 | 13.15 | 497070 | 41.4225 | 41.4225 | 68.6316 | 20.811 | 495300.7226 | 41.2751 | 41.2751 | 82.6976 | 1 | 67.5 | 12.5 | 472500 | 39.375 | 39.375 | 69.2994 | 21.4787 | 511193.714 | 42.5995 | 42.5995 | 81.9745 | 65 | 70 | 27.0113 | 28 | 69.1
6/5/20XX 1:00:00 PM | 0.54167 | 2 | 67.8 | 68.3 | 60.6965 | 70.9676 | 10.2711 | 60 | 67.8 |  | 67.8 | 69.2215 | 0.1 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 63.2816 | 15.461 | 367971.5692 | 30.6643 | 30.6643 | 88.5613 | 0.2 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 63.9416 | 16.121 | 383679.3385 | 31.9733 | 31.9733 | 87.9173 | 0.3 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 64.6016 | 16.781 | 399387.1077 | 33.2823 | 33.2823 | 87.2733 | 0.4 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 65.2616 | 17.441 | 415094.8769 | 34.5912 | 34.5912 | 86.6292 | 0.5 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 65.9216 | 18.101 | 430802.6461 | 35.9002 | 35.9002 | 85.9852 | 0.6 | 70.28 | 15.28 | 577584 | 48.132 | 48.132 | 66.5816 | 18.7609 | 446510.4154 | 37.2092 | 37.2092 | 85.3412 | 0.7 | 69.66 | 14.66 | 554148 | 46.179 | 46.179 | 67.2416 | 19.4209 | 462218.1846 | 38.5182 | 38.5182 | 84.6972 | 0.8 | 69.04 | 14.04 | 530712 | 44.226 | 44.226 | 67.9016 | 20.0809 | 477925.9538 | 39.8272 | 39.8272 | 84.0532 | 0.9 | 68.42 | 13.42 | 507276 | 42.273 | 42.273 | 68.5615 | 20.7409 | 493633.7231 | 41.1361 | 41.1361 | 83.4091 | 1 | 67.8 | 12.8 | 483840 | 40.32 | 40.32 | 69.2215 | 21.4009 | 509341.4923 | 42.4451 | 42.4451 | 82.7651 | 70 | 70 | 27.0725 | 28 | 68.3
6/5/20XX 2:00:00 PM | 0.58333 | 2 | 68.4 | 67 | 61.9998 | 72.4969 | 10.4971 | 60 | 68.4 |  | 68.4 | 69.3478 | 0.1 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 63.2942 | 15.4736 | 368272.0713 | 30.6893 | 30.6893 | 88.7753 | 0.2 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 63.9669 | 16.1462 | 384280.3426 | 32.0234 | 32.0234 | 88.3454 | 0.3 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 64.6395 | 16.8188 | 400288.6139 | 33.3574 | 33.3574 | 87.9154 | 0.4 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 65.3121 | 17.4915 | 416296.8852 | 34.6914 | 34.6914 | 87.4854 | 0.5 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 65.9847 | 18.1641 | 432305.1564 | 36.0254 | 36.0254 | 87.0554 | 0.6 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 66.6573 | 18.8367 | 448313.4277 | 37.3595 | 37.3595 | 86.6255 | 0.7 | 70.08 | 15.08 | 570024 | 47.502 | 47.502 | 67.3299 | 19.5093 | 464321.699 | 38.6935 | 38.6935 | 86.1955 | 0.8 | 69.52 | 14.52 | 548856 | 45.738 | 45.738 | 68.0026 | 20.1819 | 480329.9703 | 40.0275 | 40.0275 | 85.7655 | 0.9 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 68.6752 | 20.8545 | 496338.2416 | 41.3615 | 41.3615 | 85.3355 | 1 | 68.4 | 13.4 | 506520 | 42.21 | 42.21 | 69.3478 | 21.5272 | 512346.5129 | 42.6955 | 42.6955 | 84.9055 | 70 | 65 | 27.2388 | 28 | 67
6/5/20XX 3:00:00 PM | 0.625 | 2 | 68.5 | 67.4 | 62.2194 | 72.7546 | 10.5352 | 60 | 68.5 |  | 68.5 | 70.0155 | 0.1 | 73.45 | 18.45 | 697410 | 58.1175 | 58.1175 | 63.361 | 15.5404 | 369861.1417 | 30.8218 | 30.8218 | 88.9393 | 0.2 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 64.1004 | 16.2798 | 387458.4835 | 32.2882 | 32.2882 | 88.6732 | 0.3 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 64.8398 | 17.0192 | 405055.8252 | 33.7547 | 33.7547 | 88.4072 | 0.4 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 65.5792 | 17.7585 | 422653.1669 | 35.2211 | 35.2211 | 88.1411 | 0.5 | 71.25 | 16.25 | 614250 | 51.1875 | 51.1875 | 66.3186 | 18.4979 | 440250.5086 | 36.6875 | 36.6875 | 87.875 | 0.6 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 67.0579 | 19.2373 | 457847.8504 | 38.154 | 38.154 | 87.609 | 0.7 | 70.15 | 15.15 | 572670 | 47.7225 | 47.7225 | 67.7973 | 19.9767 | 475445.1921 | 39.6204 | 39.6204 | 87.3429 | 0.8 | 69.6 | 14.6 | 551880 | 45.99 | 45.99 | 68.5367 | 20.7161 | 493042.5338 | 41.0869 | 41.0869 | 87.0769 | 0.9 | 69.05 | 14.05 | 531090 | 44.2575 | 44.2575 | 69.2761 | 21.4555 | 510639.8756 | 42.5533 | 42.5533 | 86.8108 | 1 | 68.5 | 13.5 | 510300 | 42.525 | 42.525 | 70.0155 | 22.1948 | 528237.2173 | 44.0198 | 44.0198 | 86.5448 | 70 | 65 | 27.3675 | 28 | 67.4
6/5/20XX 4:00:00 PM | 0.66667 | 2 | 68 | 67.5 | 61.1282 | 71.4742 | 10.346 | 60 | 68 |  | 68 | 68.8877 | 0.1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 63.2482 | 15.4276 | 367177.0446 | 30.5981 | 30.5981 | 88.5581 | 0.2 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 63.8748 | 16.0542 | 382090.2893 | 31.8409 | 31.8409 | 87.9109 | 0.3 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 64.5015 | 16.6808 | 397003.5339 | 33.0836 | 33.0836 | 87.2636 | 0.4 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 65.1281 | 17.3074 | 411916.7785 | 34.3264 | 34.3264 | 86.6164 | 0.5 | 71 | 16 | 604800 | 50.4 | 50.4 | 65.7547 | 17.934 | 426830.0232 | 35.5692 | 35.5692 | 85.9692 | 0.6 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 66.3813 | 18.5606 | 441743.2678 | 36.8119 | 36.8119 | 85.3219 | 0.7 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 67.0079 | 19.1872 | 456656.5125 | 38.0547 | 38.0547 | 84.6747 | 0.8 | 69.2 | 14.2 | 536760 | 44.73 | 44.73 | 67.6345 | 19.8139 | 471569.7571 | 39.2975 | 39.2975 | 84.0275 | 0.9 | 68.6 | 13.6 | 514080 | 42.84 | 42.84 | 68.2611 | 20.4405 | 486483.0017 | 40.5403 | 40.5403 | 83.3803 | 1 | 68 | 13 | 491400 | 40.95 | 40.95 | 68.8877 | 21.0671 | 501396.2464 | 41.783 | 41.783 | 82.733 | 70 | 65 | 27.0693 | 28 | 67.5
6/5/20XX 5:00:00 PM | 0.70833 | 2 | 68.3 | 67.5 | 61.7809 | 72.24 | 10.4591 | 60 | 68.3 |  | 68.3 | 69.6253 | 0.1 | 73.43 | 18.43 | 696654 | 58.0545 | 58.0545 | 63.322 | 15.5014 | 368932.422 | 30.7444 | 30.7444 | 88.7989 | 0.2 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 64.0224 | 16.2017 | 385601.044 | 32.1334 | 32.1334 | 88.3924 | 0.3 | 72.29 | 17.29 | 653562 | 54.4635 | 54.4635 | 64.7227 | 16.9021 | 402269.666 | 33.5225 | 33.5225 | 87.986 | 0.4 | 71.72 | 16.72 | 632016 | 52.668 | 52.668 | 65.4231 | 17.6024 | 418938.288 | 34.9115 | 34.9115 | 87.5795 | 0.5 | 71.15 | 16.15 | 610470 | 50.8725 | 50.8725 | 66.1234 | 18.3028 | 435606.9101 | 36.3006 | 36.3006 | 87.1731 | 0.6 | 70.58 | 15.58 | 588924 | 49.077 | 49.077 | 66.8238 | 19.0032 | 452275.5321 | 37.6896 | 37.6896 | 86.7666 | 0.7 | 70.01 | 15.01 | 567378 | 47.2815 | 47.2815 | 67.5242 | 19.7035 | 468944.1541 | 39.0787 | 39.0787 | 86.3602 | 0.8 | 69.44 | 14.44 | 545832 | 45.486 | 45.486 | 68.2245 | 20.4039 | 485612.7761 | 40.4677 | 40.4677 | 85.9537 | 0.9 | 68.87 | 13.87 | 524286 | 43.6905 | 43.6905 | 68.9249 | 21.1043 | 502281.3981 | 41.8568 | 41.8568 | 85.5473 | 1 | 68.3 | 13.3 | 502740 | 41.895 | 41.895 | 69.6253 | 21.8046 | 518950.0201 | 43.2458 | 43.2458 | 85.1408 | 70 | 65 | 27.2577 | 28 | 67.5
6/5/20XX 6:00:00 PM | 0.75 | 2 | 67.7 | 67.3 | 60.4817 | 70.7155 | 10.2338 | 60 | 67.7 |  | 67.7 | 67.9524 | 0.1 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 63.1547 | 15.3341 | 364951.014 | 30.4126 | 30.4126 | 88.2781 | 0.2 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 63.6878 | 15.8672 | 377638.2281 | 31.4699 | 31.4699 | 87.3509 | 0.3 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 64.2209 | 16.4002 | 390325.4421 | 32.5271 | 32.5271 | 86.4236 | 0.4 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 64.7539 | 16.9333 | 403012.6562 | 33.5844 | 33.5844 | 85.4964 | 0.5 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 65.287 | 17.4664 | 415699.8702 | 34.6417 | 34.6417 | 84.5692 | 0.6 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 65.8201 | 17.9995 | 428387.0843 | 35.6989 | 35.6989 | 83.6419 | 0.7 | 69.59 | 14.59 | 551502 | 45.9585 | 45.9585 | 66.3532 | 18.5325 | 441074.2983 | 36.7562 | 36.7562 | 82.7147 | 0.8 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 66.8862 | 19.0656 | 453761.5123 | 37.8135 | 37.8135 | 81.7875 | 0.9 | 68.33 | 13.33 | 503874 | 41.9895 | 41.9895 | 67.4193 | 19.5987 | 466448.7264 | 38.8707 | 38.8707 | 80.8602 | 1 | 67.7 | 12.7 | 480060 | 40.005 | 40.005 | 67.9524 | 20.1318 | 479135.9404 | 39.928 | 39.928 | 79.933 | 70 | 65 | 26.85 | 26 | 67.3
6/5/20XX 7:00:00 PM | 0.79167 | 2 | 66.6 | 68.7 | 58.1627 | 67.9946 | 9.8319 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/5/20XX 8:00:00 PM | 0.83333 | 2 | 65.8 | 70.8 | 66.0748 | 75.6853 | 9.6105 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/5/20XX 9:00:00 PM | 0.875 | 2 | 64.9 | 72.8 | 63.9732 | 73.2731 | 9.2999 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/5/20XX 10:00:00 PM | 0.91667 | 2 | 64.2 | 75.2 | 62.3806 | 71.4454 | 9.0649 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/5/20XX 11:00:00 PM | 0.95833 | 2 | 63.6 | 76.5 | 61.0441 | 69.912 | 8.8679 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/5/20XX 12:00:00 AM | 0 | 3 | 63.1 | 78.5 | 59.9503 | 68.6572 | 8.7068 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/6/20XX 1:00:00 AM | 0.041667 | 3 | 62.3 | 81.5 | 66.6924 | 75.1174 | 8.425 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/6/20XX 2:00:00 AM | 0.083333 | 3 | 61.6 | 82.6 | 65.0158 | 73.2238 | 8.2079 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/6/20XX 3:00:00 AM | 0.125 | 3 | 61.7 | 82.3 | 65.2529 | 73.4915 | 8.2386 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/6/20XX 4:00:00 AM | 0.16667 | 3 | 61.6 | 82.8 | 65.0158 | 73.2238 | 8.2079 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/6/20XX 5:00:00 AM | 0.20833 | 3 | 61.4 | 84 | 64.544 | 72.6909 | 8.1469 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/6/20XX 6:00:00 AM | 0.25 | 3 | 62 | 82.9 | 65.969 | 74.3004 | 8.3313 | 80 | 62 |  | 62 | 68.3851 | 1 | 62 | 7 | 264600 | 22.05 | 22.05 | 68.3851 | 20.5645 | 489434.6525 | 40.7862 | 40.7862 | 62.8362 | 1 | 62 | 7 | 264600 | 22.05 | 22.05 | 68.3851 | 20.5645 | 489434.6525 | 40.7862 | 40.7862 | 62.8362 | 1 | 62 | 7 | 264600 | 22.05 | 22.05 | 68.3851 | 20.5645 | 489434.6525 | 40.7862 | 40.7862 | 62.8362 | 1 | 62 | 7 | 264600 | 22.05 | 22.05 | 68.3851 | 20.5645 | 489434.6525 | 40.7862 | 40.7862 | 62.8362 | 1 | 62 | 7 | 264600 | 22.05 | 22.05 | 68.3851 | 20.5645 | 489434.6525 | 40.7862 | 40.7862 | 62.8362 | 1 | 62 | 7 | 264600 | 22.05 | 22.05 | 68.3851 | 20.5645 | 489434.6525 | 40.7862 | 40.7862 | 62.8362 | 1 | 62 | 7 | 264600 | 22.05 | 22.05 | 68.3851 | 20.5645 | 489434.6525 | 40.7862 | 40.7862 | 62.8362 | 1 | 62 | 7 | 264600 | 22.05 | 22.05 | 68.3851 | 20.5645 | 489434.6525 | 40.7862 | 40.7862 | 62.8362 | 1 | 62 | 7 | 264600 | 22.05 | 22.05 | 68.3851 | 20.5645 | 489434.6525 | 40.7862 | 40.7862 | 62.8362 | 1 | 62 | 7 | 264600 | 22.05 | 22.05 | 68.3851 | 20.5645 | 489434.6525 | 40.7862 | 40.7862 | 62.8362 | 60 | 85 | 25.5248 | 26 | 82.9
6/6/20XX 7:00:00 AM | 0.29167 | 3 | 63.3 | 79.7 | 60.3857 | 69.1566 | 8.7709 | 70 | 63.3 |  | 63.3 | 68.8935 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 68.8935 | 21.0728 | 501533.3667 | 41.7944 | 41.7944 | 67.9394 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 68.8935 | 21.0728 | 501533.3667 | 41.7944 | 41.7944 | 67.9394 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 68.8935 | 21.0728 | 501533.3667 | 41.7944 | 41.7944 | 67.9394 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 68.8935 | 21.0728 | 501533.3667 | 41.7944 | 41.7944 | 67.9394 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 68.8935 | 21.0728 | 501533.3667 | 41.7944 | 41.7944 | 67.9394 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 68.8935 | 21.0728 | 501533.3667 | 41.7944 | 41.7944 | 67.9394 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 68.8935 | 21.0728 | 501533.3667 | 41.7944 | 41.7944 | 67.9394 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 68.8935 | 21.0728 | 501533.3667 | 41.7944 | 41.7944 | 67.9394 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 68.8935 | 21.0728 | 501533.3667 | 41.7944 | 41.7944 | 67.9394 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 68.8935 | 21.0728 | 501533.3667 | 41.7944 | 41.7944 | 67.9394 | 65 | 80 | 25.9216 | 26 | 79.7
6/6/20XX 8:00:00 AM | 0.33333 | 3 | 64.6 | 74.6 | 63.2862 | 72.4847 | 9.1985 | 70 | 64.6 |  | 64.6 | 67.5175 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 67.5175 | 19.6969 | 468785.8771 | 39.0655 | 39.0655 | 69.3055 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 67.5175 | 19.6969 | 468785.8771 | 39.0655 | 39.0655 | 69.3055 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 67.5175 | 19.6969 | 468785.8771 | 39.0655 | 39.0655 | 69.3055 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 67.5175 | 19.6969 | 468785.8771 | 39.0655 | 39.0655 | 69.3055 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 67.5175 | 19.6969 | 468785.8771 | 39.0655 | 39.0655 | 69.3055 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 67.5175 | 19.6969 | 468785.8771 | 39.0655 | 39.0655 | 69.3055 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 67.5175 | 19.6969 | 468785.8771 | 39.0655 | 39.0655 | 69.3055 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 67.5175 | 19.6969 | 468785.8771 | 39.0655 | 39.0655 | 69.3055 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 67.5175 | 19.6969 | 468785.8771 | 39.0655 | 39.0655 | 69.3055 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 67.5175 | 19.6969 | 468785.8771 | 39.0655 | 39.0655 | 69.3055 | 65 | 75 | 26.0249 | 26 | 74.6
6/6/20XX 9:00:00 AM | 0.375 | 3 | 66.5 | 70.9 | 67.7519 | 77.6107 | 9.8588 | 70 | 66.5 |  | 66.5 | 68.6392 | 0.1 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 63.2234 | 15.4028 | 366585.6136 | 30.5488 | 30.5488 | 88.0363 | 0.2 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 63.8251 | 16.0045 | 380907.4273 | 31.7423 | 31.7423 | 86.8673 | 0.3 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 64.4269 | 16.6063 | 395229.2409 | 32.9358 | 32.9358 | 85.6983 | 0.4 | 71 | 16 | 604800 | 50.4 | 50.4 | 65.0287 | 17.208 | 409551.0546 | 34.1293 | 34.1293 | 84.5293 | 0.5 | 70.25 | 15.25 | 576450 | 48.0375 | 48.0375 | 65.6304 | 17.8098 | 423872.8682 | 35.3227 | 35.3227 | 83.3602 | 0.6 | 69.5 | 14.5 | 548100 | 45.675 | 45.675 | 66.2322 | 18.4115 | 438194.6818 | 36.5162 | 36.5162 | 82.1912 | 0.7 | 68.75 | 13.75 | 519750 | 43.3125 | 43.3125 | 66.8339 | 19.0133 | 452516.4955 | 37.7097 | 37.7097 | 81.0222 | 0.8 | 68 | 13 | 491400 | 40.95 | 40.95 | 67.4357 | 19.6151 | 466838.3091 | 38.9032 | 38.9032 | 79.8532 | 0.9 | 67.25 | 12.25 | 463050 | 38.5875 | 38.5875 | 68.0374 | 20.2168 | 481160.1227 | 40.0967 | 40.0967 | 78.6842 | 1 | 66.5 | 11.5 | 434700 | 36.225 | 36.225 | 68.6392 | 20.8186 | 495481.9364 | 41.2902 | 41.2902 | 77.5152 | 65 | 70 | 26.664 | 26 | 70.9
6/6/20XX 10:00:00 AM | 0.41667 | 3 | 68.6 | 64.2 | 62.4397 | 73.0131 | 10.5734 | 60 | 68.6 |  | 68.6 | 66.8805 | 0.1 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 63.0475 | 15.2269 | 362400.0209 | 30.2 | 30.2 | 88.349 | 0.2 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 63.4734 | 15.6528 | 372536.2418 | 31.0447 | 31.0447 | 87.4927 | 0.3 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 63.8993 | 16.0787 | 382672.4627 | 31.8894 | 31.8894 | 86.6364 | 0.4 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 64.3252 | 16.5046 | 392808.6836 | 32.7341 | 32.7341 | 85.7801 | 0.5 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 64.7511 | 16.9305 | 402944.9045 | 33.5787 | 33.5787 | 84.9237 | 0.6 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 65.177 | 17.3563 | 413081.1254 | 34.4234 | 34.4234 | 84.0674 | 0.7 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 65.6029 | 17.7822 | 423217.3463 | 35.2681 | 35.2681 | 83.2111 | 0.8 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 66.0288 | 18.2081 | 433353.5672 | 36.1128 | 36.1128 | 82.3548 | 0.9 | 69.14 | 14.14 | 534492 | 44.541 | 44.541 | 66.4547 | 18.634 | 443489.7881 | 36.9575 | 36.9575 | 81.4985 | 1 | 68.6 | 13.6 | 514080 | 42.84 | 42.84 | 66.8805 | 19.0599 | 453626.009 | 37.8022 | 37.8022 | 80.6422 | 70 | 65 | 26.9026 | 26 | 64.2
6/6/20XX 11:00:00 AM | 0.45833 | 3 | 70.5 | 59.5 | 55.4618 | 66.7576 | 11.2958 | 50 | 70.5 |  | 70.5 | 66.1928 | 0.1 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 62.9788 | 15.1581 | 360763.272 | 30.0636 | 30.0636 | 88.8111 | 0.2 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 63.3359 | 15.5152 | 369262.7439 | 30.7719 | 30.7719 | 88.4169 | 0.3 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 63.693 | 15.8724 | 377762.2159 | 31.4802 | 31.4802 | 88.0227 | 0.4 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 64.0501 | 16.2295 | 386261.6878 | 32.1885 | 32.1885 | 87.6285 | 0.5 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 64.4072 | 16.5866 | 394761.1598 | 32.8968 | 32.8968 | 87.2343 | 0.6 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 64.7644 | 16.9437 | 403260.6317 | 33.6051 | 33.6051 | 86.8401 | 0.7 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 65.1215 | 17.3008 | 411760.1037 | 34.3133 | 34.3133 | 86.4458 | 0.8 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 65.4786 | 17.658 | 420259.5756 | 35.0216 | 35.0216 | 86.0516 | 0.9 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 65.8357 | 18.0151 | 428759.0476 | 35.7299 | 35.7299 | 85.6574 | 1 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 66.1928 | 18.3722 | 437258.5195 | 36.4382 | 36.4382 | 85.2632 | 70 | 60 | 27.2593 | 28 | 59.5
6/6/20XX 12:00:00 PM | 0.5 | 3 | 71.8 | 56.3 | 58.0341 | 69.8602 | 11.8262 | 50 | 71.8 |  | 71.8 | 65.4845 | 0.1 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 62.9079 | 15.0873 | 359077.533 | 29.9231 | 29.9231 | 89.0801 | 0.2 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 63.1942 | 15.3736 | 365891.2661 | 30.4909 | 30.4909 | 88.9549 | 0.3 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 63.4805 | 15.6599 | 372704.9991 | 31.0587 | 31.0587 | 88.8297 | 0.4 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 63.7668 | 15.9462 | 379518.7322 | 31.6266 | 31.6266 | 88.7046 | 0.5 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 64.0531 | 16.2325 | 386332.4652 | 32.1944 | 32.1944 | 88.5794 | 0.6 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 64.3394 | 16.5187 | 393146.1983 | 32.7622 | 32.7622 | 88.4542 | 0.7 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 64.6257 | 16.805 | 399959.9313 | 33.33 | 33.33 | 88.329 | 0.8 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 64.912 | 17.0913 | 406773.6643 | 33.8978 | 33.8978 | 88.2038 | 0.9 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 65.1983 | 17.3776 | 413587.3974 | 34.4656 | 34.4656 | 88.0786 | 1 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 65.4845 | 17.6639 | 420401.1304 | 35.0334 | 35.0334 | 87.9534 | 70 | 55 | 27.466 | 28 | 56.3
6/6/20XX 1:00:00 PM | 0.54167 | 3 | 72.5 | 54.2 | 59.4614 | 71.5821 | 12.1207 | 50 | 72.5 |  | 72.5 | 64.552 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 62.8147 | 14.994 | 356858.185 | 29.7382 | 29.7382 | 89.1157 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 63.0077 | 15.1871 | 361452.5701 | 30.121 | 30.121 | 89.026 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 63.2008 | 15.3801 | 366046.9551 | 30.5039 | 30.5039 | 88.9364 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 63.3938 | 15.5732 | 370641.3401 | 30.8868 | 30.8868 | 88.8468 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 63.5868 | 15.7662 | 375235.7252 | 31.2696 | 31.2696 | 88.7571 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 63.7799 | 15.9592 | 379830.1102 | 31.6525 | 31.6525 | 88.6675 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 63.9729 | 16.1523 | 384424.4953 | 32.0354 | 32.0354 | 88.5779 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 64.166 | 16.3453 | 389018.8803 | 32.4182 | 32.4182 | 88.4882 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 64.359 | 16.5384 | 393613.2653 | 32.8011 | 32.8011 | 88.3986 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 64.552 | 16.7314 | 398207.6504 | 33.184 | 33.184 | 88.309 | 70 | 55 | 27.4912 | 28 | 54.2
6/6/20XX 2:00:00 PM | 0.58333 | 3 | 73.2 | 54.4 | 60.9187 | 73.3404 | 12.4216 | 50 | 73.2 |  | 73.2 | 66.3842 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 62.9979 | 15.1773 | 361218.8072 | 30.1016 | 30.1016 | 89.6996 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 63.3742 | 15.5535 | 370173.8145 | 30.8478 | 30.8478 | 90.1938 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 63.7504 | 15.9298 | 379128.8217 | 31.5941 | 31.5941 | 90.6881 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 64.1267 | 16.306 | 388083.8289 | 32.3403 | 32.3403 | 91.1823 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 64.5029 | 16.6823 | 397038.8362 | 33.0866 | 33.0866 | 91.6766 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 64.8792 | 17.0586 | 405993.8434 | 33.8328 | 33.8328 | 92.1708 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 65.2555 | 17.4348 | 414948.8506 | 34.5791 | 34.5791 | 92.6651 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 65.6317 | 17.8111 | 423903.8579 | 35.3253 | 35.3253 | 93.1593 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 66.008 | 18.1873 | 432858.8651 | 36.0716 | 36.0716 | 93.6536 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 66.3842 | 18.5636 | 441813.8723 | 36.8178 | 36.8178 | 94.1478 | 75 | 55 | 27.9485 | 28 | 54.4
6/6/20XX 3:00:00 PM | 0.625 | 3 | 73.2 | 53.4 | 60.9187 | 73.3404 | 12.4216 | 50 | 73.2 |  | 73.2 | 65.1421 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 62.8737 | 15.053 | 358262.4565 | 29.8552 | 29.8552 | 89.4532 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 63.1257 | 15.3051 | 364261.113 | 30.3551 | 30.3551 | 89.7011 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 63.3778 | 15.5571 | 370259.7695 | 30.855 | 30.855 | 89.949 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 63.6298 | 15.8092 | 376258.4261 | 31.3549 | 31.3549 | 90.1969 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 63.8819 | 16.0612 | 382257.0826 | 31.8548 | 31.8548 | 90.4448 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 64.1339 | 16.3133 | 388255.7391 | 32.3546 | 32.3546 | 90.6926 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 64.3859 | 16.5653 | 394254.3956 | 32.8545 | 32.8545 | 90.9405 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 64.638 | 16.8174 | 400253.0521 | 33.3544 | 33.3544 | 91.1884 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 64.89 | 17.0694 | 406251.7086 | 33.8543 | 33.8543 | 91.4363 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 65.1421 | 17.3214 | 412250.3651 | 34.3542 | 34.3542 | 91.6842 | 75 | 55 | 27.7543 | 28 | 53.4
6/6/20XX 4:00:00 PM | 0.66667 | 3 | 72 | 56 | 58.4388 | 70.3485 | 11.9097 | 50 | 72 |  | 72 | 65.5846 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 62.9179 | 15.0973 | 359315.7 | 29.943 | 29.943 | 89.163 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 63.2142 | 15.3936 | 366367.6 | 30.5306 | 30.5306 | 89.1206 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 63.5105 | 15.6899 | 373419.5 | 31.1183 | 31.1183 | 89.0783 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 63.8068 | 15.9862 | 380471.4001 | 31.706 | 31.706 | 89.036 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 64.1031 | 16.2825 | 387523.3001 | 32.2936 | 32.2936 | 88.9936 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 64.3994 | 16.5788 | 394575.2001 | 32.8813 | 32.8813 | 88.9513 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 64.6957 | 16.8751 | 401627.1001 | 33.4689 | 33.4689 | 88.9089 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 64.992 | 17.1714 | 408679.0001 | 34.0566 | 34.0566 | 88.8666 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 65.2883 | 17.4677 | 415730.9001 | 34.6442 | 34.6442 | 88.8242 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 65.5846 | 17.764 | 422782.8002 | 35.2319 | 35.2319 | 88.7819 | 70 | 55 | 27.5305 | 28 | 56
6/6/20XX 5:00:00 PM | 0.70833 | 3 | 72 | 54.5 | 58.4388 | 70.3485 | 11.9097 | 50 | 72 |  | 72 | 63.7982 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 62.7393 | 14.9187 | 355063.9475 | 29.5887 | 29.5887 | 88.8087 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 62.8569 | 15.0363 | 357864.0949 | 29.822 | 29.822 | 88.412 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 62.9746 | 15.154 | 360664.2424 | 30.0554 | 30.0554 | 88.0154 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 63.0922 | 15.2716 | 363464.3899 | 30.2887 | 30.2887 | 87.6187 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 63.2099 | 15.3893 | 366264.5373 | 30.522 | 30.522 | 87.222 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 63.3276 | 15.5069 | 369064.6848 | 30.7554 | 30.7554 | 86.8254 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 63.4452 | 15.6246 | 371864.8323 | 30.9887 | 30.9887 | 86.4287 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 63.5629 | 15.7422 | 374664.9798 | 31.2221 | 31.2221 | 86.0321 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 63.6805 | 15.8599 | 377465.1272 | 31.4554 | 31.4554 | 85.6354 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 63.7982 | 15.9775 | 380265.2747 | 31.6888 | 31.6888 | 85.2388 | 70 | 55 | 27.2513 | 28 | 54.5
6/6/20XX 6:00:00 PM | 0.75 | 3 | 70.6 | 57.3 | 55.6561 | 66.992 | 11.3359 | 50 | 70.6 |  | 70.6 | 63.9313 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 62.7526 | 14.932 | 355380.7481 | 29.6151 | 29.6151 | 88.3941 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 62.8836 | 15.0629 | 358497.6962 | 29.8748 | 29.8748 | 87.5828 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 63.0145 | 15.1939 | 361614.6443 | 30.1346 | 30.1346 | 86.7716 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 63.1455 | 15.3249 | 364731.5924 | 30.3943 | 30.3943 | 85.9603 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 63.2765 | 15.4558 | 367848.5405 | 30.654 | 30.654 | 85.149 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 63.4074 | 15.5868 | 370965.4886 | 30.9138 | 30.9138 | 84.3378 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 63.5384 | 15.7177 | 374082.4367 | 31.1735 | 31.1735 | 83.5265 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 63.6693 | 15.8487 | 377199.3848 | 31.4333 | 31.4333 | 82.7153 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 63.8003 | 15.9797 | 380316.3329 | 31.693 | 31.693 | 81.904 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 63.9313 | 16.1106 | 383433.2809 | 31.9528 | 31.9528 | 81.0928 | 70 | 55 | 26.9304 | 26 | 57.3
6/6/20XX 7:00:00 PM | 0.79167 | 3 | 68.6 | 59.6 | 51.881 | 62.4397 | 10.5587 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/6/20XX 8:00:00 PM | 0.83333 | 3 | 66 | 65.1 | 56.9316 | 66.5501 | 9.6186 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/6/20XX 9:00:00 PM | 0.875 | 3 | 65.5 | 65.6 | 55.9235 | 65.3675 | 9.444 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/6/20XX 10:00:00 PM | 0.91667 | 3 | 65 | 65.8 | 54.9315 | 64.2037 | 9.2722 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/6/20XX 11:00:00 PM | 0.95833 | 3 | 64.7 | 66.2 | 54.344 | 63.5145 | 9.1705 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/6/20XX 12:00:00 AM | 0 | 4 | 63.7 | 68.5 | 52.4264 | 61.265 | 8.8387 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/7/20XX 1:00:00 AM | 0.041667 | 4 | 63.1 | 67.9 | 51.3055 | 59.9503 | 8.6448 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/7/20XX 2:00:00 AM | 0.083333 | 4 | 62.5 | 70.6 | 58.6614 | 67.1787 | 8.5172 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/7/20XX 3:00:00 AM | 0.125 | 4 | 62.1 | 71.9 | 57.8163 | 66.2093 | 8.393 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/7/20XX 4:00:00 AM | 0.16667 | 4 | 61.5 | 73.1 | 56.5695 | 64.7795 | 8.21 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/7/20XX 5:00:00 AM | 0.20833 | 4 | 61 | 76.3 | 55.5495 | 63.61 | 8.0604 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/7/20XX 6:00:00 AM | 0.25 | 4 | 61.7 | 74.9 | 56.9823 | 65.2529 | 8.2706 | 70 | 61.7 |  | 61.7 | 61.0349 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 61.0349 | 13.2143 | 314500.4098 | 26.2084 | 26.2084 | 47.3134 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 61.0349 | 13.2143 | 314500.4098 | 26.2084 | 26.2084 | 47.3134 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 61.0349 | 13.2143 | 314500.4098 | 26.2084 | 26.2084 | 47.3134 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 61.0349 | 13.2143 | 314500.4098 | 26.2084 | 26.2084 | 47.3134 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 61.0349 | 13.2143 | 314500.4098 | 26.2084 | 26.2084 | 47.3134 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 61.0349 | 13.2143 | 314500.4098 | 26.2084 | 26.2084 | 47.3134 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 61.0349 | 13.2143 | 314500.4098 | 26.2084 | 26.2084 | 47.3134 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 61.0349 | 13.2143 | 314500.4098 | 26.2084 | 26.2084 | 47.3134 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 61.0349 | 13.2143 | 314500.4098 | 26.2084 | 26.2084 | 47.3134 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 61.0349 | 13.2143 | 314500.4098 | 26.2084 | 26.2084 | 47.3134 | 60 | 75 | 24.3075 | 24 | 74.9
6/7/20XX 7:00:00 AM | 0.29167 | 4 | 62.9 | 72.3 | 59.5179 | 68.161 | 8.6432 | 70 | 62.9 |  | 62.9 | 61.5058 | 1 | 62.9 | 7.9 | 298620 | 24.885 | 24.885 | 61.5058 | 13.6852 | 325706.7413 | 27.1422 | 27.1422 | 52.0272 | 1 | 62.9 | 7.9 | 298620 | 24.885 | 24.885 | 61.5058 | 13.6852 | 325706.7413 | 27.1422 | 27.1422 | 52.0272 | 1 | 62.9 | 7.9 | 298620 | 24.885 | 24.885 | 61.5058 | 13.6852 | 325706.7413 | 27.1422 | 27.1422 | 52.0272 | 1 | 62.9 | 7.9 | 298620 | 24.885 | 24.885 | 61.5058 | 13.6852 | 325706.7413 | 27.1422 | 27.1422 | 52.0272 | 1 | 62.9 | 7.9 | 298620 | 24.885 | 24.885 | 61.5058 | 13.6852 | 325706.7413 | 27.1422 | 27.1422 | 52.0272 | 1 | 62.9 | 7.9 | 298620 | 24.885 | 24.885 | 61.5058 | 13.6852 | 325706.7413 | 27.1422 | 27.1422 | 52.0272 | 1 | 62.9 | 7.9 | 298620 | 24.885 | 24.885 | 61.5058 | 13.6852 | 325706.7413 | 27.1422 | 27.1422 | 52.0272 | 1 | 62.9 | 7.9 | 298620 | 24.885 | 24.885 | 61.5058 | 13.6852 | 325706.7413 | 27.1422 | 27.1422 | 52.0272 | 1 | 62.9 | 7.9 | 298620 | 24.885 | 24.885 | 61.5058 | 13.6852 | 325706.7413 | 27.1422 | 27.1422 | 52.0272 | 1 | 62.9 | 7.9 | 298620 | 24.885 | 24.885 | 61.5058 | 13.6852 | 325706.7413 | 27.1422 | 27.1422 | 52.0272 | 65 | 70 | 24.6735 | 24 | 72.3
6/7/20XX 8:00:00 AM | 0.33333 | 4 | 65.1 | 65.4 | 55.1286 | 64.435 | 9.3063 | 60 | 65.1 |  | 65.1 | 60.1541 | 0.1 | 73.11 | 18.11 | 684558 | 57.0465 | 57.0465 | 62.3749 | 14.5542 | 346390.969 | 28.8659 | 28.8659 | 85.9124 | 0.2 | 72.22 | 17.22 | 650916 | 54.243 | 54.243 | 62.1281 | 14.3075 | 340518.138 | 28.3765 | 28.3765 | 82.6195 | 0.3 | 71.33 | 16.33 | 617274 | 51.4395 | 51.4395 | 61.8814 | 14.0607 | 334645.3069 | 27.8871 | 27.8871 | 79.3266 | 0.4 | 70.44 | 15.44 | 583632 | 48.636 | 48.636 | 61.6346 | 13.814 | 328772.4759 | 27.3977 | 27.3977 | 76.0337 | 0.5 | 69.55 | 14.55 | 549990 | 45.8325 | 45.8325 | 61.3878 | 13.5672 | 322899.6449 | 26.9083 | 26.9083 | 72.7408 | 0.6 | 68.66 | 13.66 | 516348 | 43.029 | 43.029 | 61.1411 | 13.3205 | 317026.8139 | 26.4189 | 26.4189 | 69.4479 | 0.7 | 67.77 | 12.77 | 482706 | 40.2255 | 40.2255 | 60.8943 | 13.0737 | 311153.9828 | 25.9295 | 25.9295 | 66.155 | 0.8 | 66.88 | 11.88 | 449064 | 37.422 | 37.422 | 60.6476 | 12.8269 | 305281.1518 | 25.4401 | 25.4401 | 62.8621 | 0.9 | 65.99 | 10.99 | 415422 | 34.6185 | 34.6185 | 60.4008 | 12.5802 | 299408.3208 | 24.9507 | 24.9507 | 59.5692 | 1 | 65.1 | 10.1 | 381780 | 31.815 | 31.815 | 60.1541 | 12.3334 | 293535.4898 | 24.4613 | 24.4613 | 56.2763 | 65 | 65 | 24.9994 | 24 | 65.4
6/7/20XX 9:00:00 AM | 0.375 | 4 | 67.5 | 61.6 | 60.054 | 70.2137 | 10.1597 | 60 | 67.5 |  | 67.5 | 61.6796 | 0.1 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 62.5274 | 14.7068 | 350021.7404 | 29.1685 | 29.1685 | 86.971 | 0.2 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 62.4332 | 14.6126 | 347779.6808 | 28.9816 | 28.9816 | 84.7366 | 0.3 | 72.05 | 17.05 | 644490 | 53.7075 | 53.7075 | 62.339 | 14.5184 | 345537.6212 | 28.7948 | 28.7948 | 82.5023 | 0.4 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 62.2448 | 14.4242 | 343295.5616 | 28.608 | 28.608 | 80.268 | 0.5 | 70.75 | 15.75 | 595350 | 49.6125 | 49.6125 | 62.1506 | 14.33 | 341053.502 | 28.4211 | 28.4211 | 78.0336 | 0.6 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 62.0564 | 14.2358 | 338811.4424 | 28.2343 | 28.2343 | 75.7993 | 0.7 | 69.45 | 14.45 | 546210 | 45.5175 | 45.5175 | 61.9622 | 14.1416 | 336569.3828 | 28.0474 | 28.0474 | 73.5649 | 0.8 | 68.8 | 13.8 | 521640 | 43.47 | 43.47 | 61.868 | 14.0474 | 334327.3232 | 27.8606 | 27.8606 | 71.3306 | 0.9 | 68.15 | 13.15 | 497070 | 41.4225 | 41.4225 | 61.7738 | 13.9532 | 332085.2636 | 27.6738 | 27.6738 | 69.0963 | 1 | 67.5 | 12.5 | 472500 | 39.375 | 39.375 | 61.6796 | 13.859 | 329843.204 | 27.4869 | 27.4869 | 66.8619 | 65 | 60 | 25.8226 | 26 | 61.6
6/7/20XX 10:00:00 AM | 0.41667 | 4 | 70.3 | 56.2 | 55.075 | 66.2911 | 11.2161 | 50 | 70.3 |  | 70.3 | 62.029 | 0.1 | 73.63 | 18.63 | 704214 | 58.6845 | 58.6845 | 62.5624 | 14.7417 | 350853.3105 | 29.2378 | 29.2378 | 87.9223 | 0.2 | 73.26 | 18.26 | 690228 | 57.519 | 57.519 | 62.5031 | 14.6825 | 349442.8211 | 29.1202 | 29.1202 | 86.6392 | 0.3 | 72.89 | 17.89 | 676242 | 56.3535 | 56.3535 | 62.4438 | 14.6232 | 348032.3316 | 29.0027 | 29.0027 | 85.3562 | 0.4 | 72.52 | 17.52 | 662256 | 55.188 | 55.188 | 62.3846 | 14.5639 | 346621.8421 | 28.8852 | 28.8852 | 84.0732 | 0.5 | 72.15 | 17.15 | 648270 | 54.0225 | 54.0225 | 62.3253 | 14.5047 | 345211.3527 | 28.7676 | 28.7676 | 82.7901 | 0.6 | 71.78 | 16.78 | 634284 | 52.857 | 52.857 | 62.266 | 14.4454 | 343800.8632 | 28.6501 | 28.6501 | 81.5071 | 0.7 | 71.41 | 16.41 | 620298 | 51.6915 | 51.6915 | 62.2068 | 14.3862 | 342390.3737 | 28.5325 | 28.5325 | 80.224 | 0.8 | 71.04 | 16.04 | 606312 | 50.526 | 50.526 | 62.1475 | 14.3269 | 340979.8843 | 28.415 | 28.415 | 78.941 | 0.9 | 70.67 | 15.67 | 592326 | 49.3605 | 49.3605 | 62.0883 | 14.2676 | 339569.3948 | 28.2974 | 28.2974 | 77.6579 | 1 | 70.3 | 15.3 | 578340 | 48.195 | 48.195 | 62.029 | 14.2084 | 338158.9054 | 28.1799 | 28.1799 | 76.3749 | 70 | 55 | 26.5601 | 26 | 56.2
6/7/20XX 11:00:00 AM | 0.45833 | 4 | 72.9 | 51.7 | 60.2904 | 72.5823 | 12.2919 | 50 | 72.9 |  | 72.9 | 62.38 | 0.1 | 73.89 | 18.89 | 714042 | 59.5035 | 59.5035 | 62.5975 | 14.7768 | 351688.8158 | 29.3074 | 29.3074 | 88.8109 | 0.2 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 62.5733 | 14.7527 | 351113.8315 | 29.2595 | 29.2595 | 88.4165 | 0.3 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 62.5492 | 14.7285 | 350538.8473 | 29.2116 | 29.2116 | 88.0221 | 0.4 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 62.525 | 14.7044 | 349963.863 | 29.1637 | 29.1637 | 87.6277 | 0.5 | 73.45 | 18.45 | 697410 | 58.1175 | 58.1175 | 62.5008 | 14.6802 | 349388.8788 | 29.1157 | 29.1157 | 87.2332 | 0.6 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 62.4767 | 14.656 | 348813.8945 | 29.0678 | 29.0678 | 86.8388 | 0.7 | 73.23 | 18.23 | 689094 | 57.4245 | 57.4245 | 62.4525 | 14.6319 | 348238.9103 | 29.0199 | 29.0199 | 86.4444 | 0.8 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 62.4284 | 14.6077 | 347663.9261 | 28.972 | 28.972 | 86.05 | 0.9 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 62.4042 | 14.5836 | 347088.9418 | 28.9241 | 28.9241 | 85.6556 | 1 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 62.38 | 14.5594 | 346513.9576 | 28.8762 | 28.8762 | 85.2612 | 75 | 50 | 27.2492 | 28 | 51.7
6/7/20XX 12:00:00 PM | 0.5 | 4 | 74 | 48.6 | 49.9649 | 62.6216 | 12.6567 | 40 | 74 |  | 74 | 60.8497 | 0.1 | 74 | 19 | 718200 | 59.85 | 59.85 | 62.4444 | 14.6238 | 348046.5851 | 29.0039 | 29.0039 | 88.8539 | 0.2 | 74 | 19 | 718200 | 59.85 | 59.85 | 62.2672 | 14.4466 | 343829.3702 | 28.6524 | 28.6524 | 88.5024 | 0.3 | 74 | 19 | 718200 | 59.85 | 59.85 | 62.0901 | 14.2694 | 339612.1553 | 28.301 | 28.301 | 88.151 | 0.4 | 74 | 19 | 718200 | 59.85 | 59.85 | 61.9129 | 14.0922 | 335394.9404 | 27.9496 | 27.9496 | 87.7996 | 0.5 | 74 | 19 | 718200 | 59.85 | 59.85 | 61.7357 | 13.915 | 331177.7255 | 27.5981 | 27.5981 | 87.4481 | 0.6 | 74 | 19 | 718200 | 59.85 | 59.85 | 61.5585 | 13.7378 | 326960.5106 | 27.2467 | 27.2467 | 87.0967 | 0.7 | 74 | 19 | 718200 | 59.85 | 59.85 | 61.3813 | 13.5606 | 322743.2957 | 26.8953 | 26.8953 | 86.7453 | 0.8 | 74 | 19 | 718200 | 59.85 | 59.85 | 61.2041 | 13.3834 | 318526.0808 | 26.5438 | 26.5438 | 86.3938 | 0.9 | 74 | 19 | 718200 | 59.85 | 59.85 | 61.0269 | 13.2063 | 314308.8658 | 26.1924 | 26.1924 | 86.0424 | 1 | 74 | 19 | 718200 | 59.85 | 59.85 | 60.8497 | 13.0291 | 310091.6509 | 25.841 | 25.841 | 85.691 | 75 | 50 | 27.2782 | 28 | 48.6
6/7/20XX 1:00:00 PM | 0.54167 | 4 | 74.7 | 47.1 | 51.1737 | 64.1448 | 12.9711 | 40 | 74.7 |  | 74.7 | 60.3832 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 62.3978 | 14.5772 | 346936.3015 | 28.9114 | 28.9114 | 88.9819 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 62.1739 | 14.3533 | 341608.803 | 28.4674 | 28.4674 | 88.7584 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 61.9501 | 14.1295 | 336281.3046 | 28.0234 | 28.0234 | 88.5349 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 61.7263 | 13.9056 | 330953.8061 | 27.5795 | 27.5795 | 88.3115 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 61.5024 | 13.6818 | 325626.3076 | 27.1355 | 27.1355 | 88.088 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 61.2786 | 13.4579 | 320298.8091 | 26.6916 | 26.6916 | 87.8646 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 61.0547 | 13.2341 | 314971.3106 | 26.2476 | 26.2476 | 87.6411 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 60.8309 | 13.0102 | 309643.8121 | 25.8037 | 25.8037 | 87.4177 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 60.607 | 12.7864 | 304316.3137 | 25.3597 | 25.3597 | 87.1942 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 60.3832 | 12.5626 | 298988.8152 | 24.9157 | 24.9157 | 86.9707 | 75 | 45 | 27.3759 | 28 | 47.1
6/7/20XX 2:00:00 PM | 0.58333 | 4 | 74.6 | 46.4 | 50.9995 | 63.9253 | 12.9258 | 40 | 74.6 |  | 74.6 | 59.272 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 62.2867 | 14.466 | 344291.717 | 28.691 | 28.691 | 88.73 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 61.9517 | 14.1311 | 336319.6339 | 28.0266 | 28.0266 | 88.2546 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 61.6167 | 13.7961 | 328347.5509 | 27.3623 | 27.3623 | 87.7793 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 61.2818 | 13.4612 | 320375.4678 | 26.698 | 26.698 | 87.304 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 60.9468 | 13.1262 | 312403.3848 | 26.0336 | 26.0336 | 86.8286 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 60.6119 | 12.7912 | 304431.3017 | 25.3693 | 25.3693 | 86.3533 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 60.2769 | 12.4563 | 296459.2187 | 24.7049 | 24.7049 | 85.8779 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 59.9419 | 12.1213 | 288487.1357 | 24.0406 | 24.0406 | 85.4026 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 59.607 | 11.7863 | 280515.0526 | 23.3763 | 23.3763 | 84.9273 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 59.272 | 11.4514 | 272542.9696 | 22.7119 | 22.7119 | 84.4519 | 75 | 45 | 27.1777 | 28 | 46.4
6/7/20XX 3:00:00 PM | 0.625 | 4 | 73.9 | 46.8 | 49.7942 | 62.4066 | 12.6123 | 40 | 73.9 |  | 73.9 | 58.3706 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 62.1965 | 14.3759 | 342146.4 | 28.5122 | 28.5122 | 88.3307 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 61.7714 | 13.9508 | 332029 | 27.6691 | 27.6691 | 87.4561 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 61.3463 | 13.5257 | 321911.6 | 26.826 | 26.826 | 86.5815 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 60.9212 | 13.1006 | 311794.2 | 25.9828 | 25.9828 | 85.7068 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 60.4961 | 12.6755 | 301676.8 | 25.1397 | 25.1397 | 84.8322 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 60.071 | 12.2504 | 291559.3999 | 24.2966 | 24.2966 | 83.9576 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 59.6459 | 11.8253 | 281441.9999 | 23.4535 | 23.4535 | 83.083 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 59.2208 | 11.4002 | 271324.5999 | 22.6104 | 22.6104 | 82.2084 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 58.7957 | 10.9751 | 261207.1999 | 21.7673 | 21.7673 | 81.3338 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 58.3706 | 10.55 | 251089.7999 | 20.9241 | 20.9241 | 80.4591 | 75 | 45 | 26.866 | 26 | 46.8
6/7/20XX 4:00:00 PM | 0.66667 | 4 | 72.5 | 51.5 | 59.4614 | 71.5821 | 12.1207 | 50 | 72.5 |  | 72.5 | 61.2795 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 62.4874 | 14.6668 | 349069.4206 | 29.0891 | 29.0891 | 88.4666 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 62.3532 | 14.5326 | 345875.0412 | 28.8229 | 28.8229 | 87.7279 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 62.219 | 14.3983 | 342680.6618 | 28.5567 | 28.5567 | 86.9892 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 62.0848 | 14.2641 | 339486.2824 | 28.2905 | 28.2905 | 86.2505 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 61.9505 | 14.1299 | 336291.903 | 28.0243 | 28.0243 | 85.5118 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 61.8163 | 13.9957 | 333097.5236 | 27.7581 | 27.7581 | 84.7731 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 61.6821 | 13.8615 | 329903.1442 | 27.4919 | 27.4919 | 84.0344 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 61.5479 | 13.7273 | 326708.7649 | 27.2257 | 27.2257 | 83.2957 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 61.4137 | 13.593 | 323514.3855 | 26.9595 | 26.9595 | 82.557 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 61.2795 | 13.4588 | 320320.0061 | 26.6933 | 26.6933 | 81.8183 | 70 | 50 | 26.9796 | 26 | 51.5
6/7/20XX 5:00:00 PM | 0.70833 | 4 | 71.7 | 52.7 | 57.8326 | 69.6172 | 11.7846 | 50 | 71.7 |  | 71.7 | 61.0144 | 0.1 | 73.77 | 18.77 | 709506 | 59.1255 | 59.1255 | 62.4609 | 14.6403 | 348438.6783 | 29.0366 | 29.0366 | 88.1621 | 0.2 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 62.3002 | 14.4796 | 344613.5567 | 28.7178 | 28.7178 | 87.1188 | 0.3 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 62.1395 | 14.3188 | 340788.435 | 28.399 | 28.399 | 86.0755 | 0.4 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 61.9788 | 14.1581 | 336963.3133 | 28.0803 | 28.0803 | 85.0323 | 0.5 | 72.85 | 17.85 | 674730 | 56.2275 | 56.2275 | 61.818 | 13.9974 | 333138.1917 | 27.7615 | 27.7615 | 83.989 | 0.6 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 61.6573 | 13.8367 | 329313.07 | 27.4428 | 27.4428 | 82.9458 | 0.7 | 72.39 | 17.39 | 657342 | 54.7785 | 54.7785 | 61.4966 | 13.676 | 325487.9483 | 27.124 | 27.124 | 81.9025 | 0.8 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 61.3359 | 13.5152 | 321662.8267 | 26.8052 | 26.8052 | 80.8592 | 0.9 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 61.1752 | 13.3545 | 317837.705 | 26.4865 | 26.4865 | 79.816 | 1 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 61.0144 | 13.1938 | 314012.5833 | 26.1677 | 26.1677 | 78.7727 | 70 | 55 | 26.7431 | 26 | 52.7
6/7/20XX 6:00:00 PM | 0.75 | 4 | 71.1 | 53.3 | 56.6364 | 68.1744 | 11.5379 | 50 | 71.1 |  | 71.1 | 60.444 | 0.1 | 73.71 | 18.71 | 707238 | 58.9365 | 58.9365 | 62.4039 | 14.5832 | 347080.9501 | 28.9234 | 28.9234 | 87.8599 | 0.2 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 62.1861 | 14.3655 | 341898.1003 | 28.4915 | 28.4915 | 86.5145 | 0.3 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 61.9683 | 14.1477 | 336715.2504 | 28.0596 | 28.0596 | 85.1691 | 0.4 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 61.7506 | 13.9299 | 331532.4005 | 27.6277 | 27.6277 | 83.8237 | 0.5 | 72.55 | 17.55 | 663390 | 55.2825 | 55.2825 | 61.5328 | 13.7122 | 326349.5506 | 27.1958 | 27.1958 | 82.4783 | 0.6 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 61.315 | 13.4944 | 321166.7008 | 26.7639 | 26.7639 | 81.1329 | 0.7 | 71.97 | 16.97 | 641466 | 53.4555 | 53.4555 | 61.0973 | 13.2766 | 315983.8509 | 26.332 | 26.332 | 79.7875 | 0.8 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 60.8795 | 13.0589 | 310801.001 | 25.9001 | 25.9001 | 78.4421 | 0.9 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 60.6617 | 12.8411 | 305618.1512 | 25.4682 | 25.4682 | 77.0967 | 1 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 60.444 | 12.6233 | 300435.3013 | 25.0363 | 25.0363 | 75.7513 | 70 | 55 | 26.5076 | 26 | 53.3
6/7/20XX 7:00:00 PM | 0.79167 | 4 | 69.6 | 56.3 | 53.7396 | 64.6807 | 10.9411 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/7/20XX 8:00:00 PM | 0.83333 | 4 | 68.5 | 59.7 | 51.6983 | 62.2194 | 10.5211 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/7/20XX 9:00:00 PM | 0.875 | 4 | 68.2 | 60 | 61.5627 | 71.984 | 10.4213 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/7/20XX 10:00:00 PM | 0.91667 | 4 | 67.2 | 62.6 | 59.4176 | 69.467 | 10.0494 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/7/20XX 11:00:00 PM | 0.95833 | 4 | 66.6 | 63.7 | 58.1627 | 67.9946 | 9.8319 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/7/20XX 12:00:00 AM | 0 | 5 | 65.6 | 67.1 | 56.1238 | 65.6025 | 9.4787 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/8/20XX 1:00:00 AM | 0.041667 | 5 | 65.3 | 67.9 | 55.5248 | 64.8997 | 9.3749 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/8/20XX 2:00:00 AM | 0.083333 | 5 | 64.4 | 69.9 | 53.7621 | 62.8319 | 9.0698 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/8/20XX 3:00:00 AM | 0.125 | 5 | 63.5 | 71.1 | 60.8239 | 69.6593 | 8.8354 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/8/20XX 4:00:00 AM | 0.16667 | 5 | 63.3 | 72.4 | 60.3857 | 69.1566 | 8.7709 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/8/20XX 5:00:00 AM | 0.20833 | 5 | 62.5 | 73.8 | 58.6614 | 67.1787 | 8.5172 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/8/20XX 6:00:00 AM | 0.25 | 5 | 63.4 | 74 | 60.6044 | 69.4076 | 8.8031 | 70 | 63.4 |  | 63.4 | 64.1257 | 1 | 63.4 | 8.4 | 317520 | 26.46 | 26.46 | 64.1257 | 16.3051 | 388060.3334 | 32.3384 | 32.3384 | 58.7984 | 1 | 63.4 | 8.4 | 317520 | 26.46 | 26.46 | 64.1257 | 16.3051 | 388060.3334 | 32.3384 | 32.3384 | 58.7984 | 1 | 63.4 | 8.4 | 317520 | 26.46 | 26.46 | 64.1257 | 16.3051 | 388060.3334 | 32.3384 | 32.3384 | 58.7984 | 1 | 63.4 | 8.4 | 317520 | 26.46 | 26.46 | 64.1257 | 16.3051 | 388060.3334 | 32.3384 | 32.3384 | 58.7984 | 1 | 63.4 | 8.4 | 317520 | 26.46 | 26.46 | 64.1257 | 16.3051 | 388060.3334 | 32.3384 | 32.3384 | 58.7984 | 1 | 63.4 | 8.4 | 317520 | 26.46 | 26.46 | 64.1257 | 16.3051 | 388060.3334 | 32.3384 | 32.3384 | 58.7984 | 1 | 63.4 | 8.4 | 317520 | 26.46 | 26.46 | 64.1257 | 16.3051 | 388060.3334 | 32.3384 | 32.3384 | 58.7984 | 1 | 63.4 | 8.4 | 317520 | 26.46 | 26.46 | 64.1257 | 16.3051 | 388060.3334 | 32.3384 | 32.3384 | 58.7984 | 1 | 63.4 | 8.4 | 317520 | 26.46 | 26.46 | 64.1257 | 16.3051 | 388060.3334 | 32.3384 | 32.3384 | 58.7984 | 1 | 63.4 | 8.4 | 317520 | 26.46 | 26.46 | 64.1257 | 16.3051 | 388060.3334 | 32.3384 | 32.3384 | 58.7984 | 65 | 75 | 25.2035 | 26 | 74
6/8/20XX 7:00:00 AM | 0.29167 | 5 | 65.2 | 68.2 | 55.3264 | 64.667 | 9.3406 | 60 | 65.2 |  | 65.2 | 62.9857 | 0.1 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 62.658 | 14.8374 | 353130.1898 | 29.4275 | 29.4275 | 86.5055 | 0.2 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 62.6944 | 14.8738 | 353996.5796 | 29.4997 | 29.4997 | 83.8057 | 0.3 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 62.7308 | 14.9102 | 354862.9694 | 29.5719 | 29.5719 | 81.1059 | 0.4 | 70.48 | 15.48 | 585144 | 48.762 | 48.762 | 62.7672 | 14.9466 | 355729.3592 | 29.6441 | 29.6441 | 78.4061 | 0.5 | 69.6 | 14.6 | 551880 | 45.99 | 45.99 | 62.8036 | 14.983 | 356595.749 | 29.7163 | 29.7163 | 75.7063 | 0.6 | 68.72 | 13.72 | 518616 | 43.218 | 43.218 | 62.84 | 15.0194 | 357462.1388 | 29.7885 | 29.7885 | 73.0065 | 0.7 | 67.84 | 12.84 | 485352 | 40.446 | 40.446 | 62.8765 | 15.0558 | 358328.5286 | 29.8607 | 29.8607 | 70.3067 | 0.8 | 66.96 | 11.96 | 452088 | 37.674 | 37.674 | 62.9129 | 15.0922 | 359194.9184 | 29.9329 | 29.9329 | 67.6069 | 0.9 | 66.08 | 11.08 | 418824 | 34.902 | 34.902 | 62.9493 | 15.1286 | 360061.3082 | 30.0051 | 30.0051 | 64.9071 | 1 | 65.2 | 10.2 | 385560 | 32.13 | 32.13 | 62.9857 | 15.165 | 360927.698 | 30.0773 | 30.0773 | 62.2073 | 65 | 70 | 25.4651 | 26 | 68.2
6/8/20XX 8:00:00 AM | 0.33333 | 5 | 67.3 | 65.5 | 59.6291 | 69.7151 | 10.086 | 60 | 67.3 |  | 67.3 | 65.1764 | 0.1 | 73.33 | 18.33 | 692874 | 57.7395 | 57.7395 | 62.8771 | 15.0565 | 358344.1162 | 29.862 | 29.862 | 87.6015 | 0.2 | 72.66 | 17.66 | 667548 | 55.629 | 55.629 | 63.1326 | 15.312 | 364424.4324 | 30.3687 | 30.3687 | 85.9977 | 0.3 | 71.99 | 16.99 | 642222 | 53.5185 | 53.5185 | 63.3881 | 15.5674 | 370504.7487 | 30.8754 | 30.8754 | 84.3939 | 0.4 | 71.32 | 16.32 | 616896 | 51.408 | 51.408 | 63.6435 | 15.8229 | 376585.0649 | 31.3821 | 31.3821 | 82.7901 | 0.5 | 70.65 | 15.65 | 591570 | 49.2975 | 49.2975 | 63.899 | 16.0784 | 382665.3811 | 31.8888 | 31.8888 | 81.1863 | 0.6 | 69.98 | 14.98 | 566244 | 47.187 | 47.187 | 64.1545 | 16.3339 | 388745.6973 | 32.3955 | 32.3955 | 79.5825 | 0.7 | 69.31 | 14.31 | 540918 | 45.0765 | 45.0765 | 64.41 | 16.5893 | 394826.0135 | 32.9022 | 32.9022 | 77.9787 | 0.8 | 68.64 | 13.64 | 515592 | 42.966 | 42.966 | 64.6654 | 16.8448 | 400906.3297 | 33.4089 | 33.4089 | 76.3749 | 0.9 | 67.97 | 12.97 | 490266 | 40.8555 | 40.8555 | 64.9209 | 17.1003 | 406986.646 | 33.9156 | 33.9156 | 74.7711 | 1 | 67.3 | 12.3 | 464940 | 38.745 | 38.745 | 65.1764 | 17.3558 | 413066.9622 | 34.4222 | 34.4222 | 73.1672 | 65 | 65 | 26.3193 | 26 | 65.5
6/8/20XX 9:00:00 AM | 0.375 | 5 | 69.1 | 62.1 | 63.5515 | 74.3178 | 10.7663 | 60 | 69.1 |  | 69.1 | 65.8124 | 0.1 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 62.9407 | 15.1201 | 359857.9305 | 29.9882 | 29.9882 | 88.2947 | 0.2 | 73.02 | 18.02 | 681156 | 56.763 | 56.763 | 63.2598 | 15.4392 | 367452.061 | 30.621 | 30.621 | 87.384 | 0.3 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 63.5789 | 15.7582 | 375046.1916 | 31.2538 | 31.2538 | 86.4733 | 0.4 | 72.04 | 17.04 | 644112 | 53.676 | 53.676 | 63.898 | 16.0773 | 382640.3221 | 31.8867 | 31.8867 | 85.5627 | 0.5 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 64.217 | 16.3964 | 390234.4526 | 32.5195 | 32.5195 | 84.652 | 0.6 | 71.06 | 16.06 | 607068 | 50.589 | 50.589 | 64.5361 | 16.7155 | 397828.5831 | 33.1524 | 33.1524 | 83.7414 | 0.7 | 70.57 | 15.57 | 588546 | 49.0455 | 49.0455 | 64.8552 | 17.0346 | 405422.7136 | 33.7852 | 33.7852 | 82.8307 | 0.8 | 70.08 | 15.08 | 570024 | 47.502 | 47.502 | 65.1743 | 17.3536 | 413016.8441 | 34.4181 | 34.4181 | 81.9201 | 0.9 | 69.59 | 14.59 | 551502 | 45.9585 | 45.9585 | 65.4934 | 17.6727 | 420610.9747 | 35.0509 | 35.0509 | 81.0094 | 1 | 69.1 | 14.1 | 532980 | 44.415 | 44.415 | 65.8124 | 17.9918 | 428205.1052 | 35.6838 | 35.6838 | 80.0988 | 70 | 60 | 26.858 | 26 | 62.1
6/8/20XX 10:00:00 AM | 0.41667 | 5 | 71.5 | 57.8 | 57.4315 | 69.1333 | 11.7019 | 50 | 71.5 |  | 71.5 | 66.5589 | 0.1 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 63.0154 | 15.1947 | 361634.5735 | 30.1362 | 30.1362 | 89.1987 | 0.2 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 63.4091 | 15.5885 | 371005.347 | 30.9171 | 30.9171 | 89.1921 | 0.3 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 63.8028 | 15.9822 | 380376.1205 | 31.698 | 31.698 | 89.1855 | 0.4 | 73 | 18 | 680400 | 56.7 | 56.7 | 64.1966 | 16.3759 | 389746.894 | 32.4789 | 32.4789 | 89.1789 | 0.5 | 72.75 | 17.75 | 670950 | 55.9125 | 55.9125 | 64.5903 | 16.7696 | 399117.6675 | 33.2598 | 33.2598 | 89.1723 | 0.6 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 64.984 | 17.1634 | 408488.4409 | 34.0407 | 34.0407 | 89.1657 | 0.7 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 65.3777 | 17.5571 | 417859.2144 | 34.8216 | 34.8216 | 89.1591 | 0.8 | 72 | 17 | 642600 | 53.55 | 53.55 | 65.7715 | 17.9508 | 427229.9879 | 35.6025 | 35.6025 | 89.1525 | 0.9 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 66.1652 | 18.3446 | 436600.7614 | 36.3834 | 36.3834 | 89.1459 | 1 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 66.5589 | 18.7383 | 445971.5349 | 37.1643 | 37.1643 | 89.1393 | 70 | 60 | 27.5607 | 28 | 57.8
6/8/20XX 11:00:00 AM | 0.45833 | 5 | 72.8 | 54.7 | 60.0822 | 72.3311 | 12.2489 | 50 | 72.8 |  | 72.8 | 65.8392 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 62.9434 | 15.1228 | 359921.6289 | 29.9935 | 29.9935 | 89.4655 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 63.2651 | 15.4445 | 367579.4579 | 30.6316 | 30.6316 | 89.7256 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 63.5869 | 15.7663 | 375237.2868 | 31.2698 | 31.2698 | 89.9858 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 63.9087 | 16.088 | 382895.1157 | 31.9079 | 31.9079 | 90.2459 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 64.2304 | 16.4098 | 390552.9446 | 32.5461 | 32.5461 | 90.5061 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 64.5522 | 16.7315 | 398210.7736 | 33.1842 | 33.1842 | 90.7662 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 64.8739 | 17.0533 | 405868.6025 | 33.8224 | 33.8224 | 91.0264 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 65.1957 | 17.3751 | 413526.4314 | 34.4605 | 34.4605 | 91.2865 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 65.5175 | 17.6968 | 421184.2603 | 35.0987 | 35.0987 | 91.5467 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 65.8392 | 18.0186 | 428842.0893 | 35.7368 | 35.7368 | 91.8068 | 75 | 55 | 27.7656 | 28 | 54.7
6/8/20XX 12:00:00 PM | 0.5 | 5 | 73.7 | 54.3 | 61.9783 | 74.6189 | 12.6406 | 50 | 73.7 |  | 73.7 | 67.4138 | 0.1 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 63.1008 | 15.2802 | 363669.1059 | 30.3058 | 30.3058 | 90.0613 | 0.2 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 63.5801 | 15.7594 | 375074.4117 | 31.2562 | 31.2562 | 90.9172 | 0.3 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 64.0593 | 16.2386 | 386479.7176 | 32.2066 | 32.2066 | 91.7731 | 0.4 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 64.5385 | 16.7179 | 397885.0235 | 33.1571 | 33.1571 | 92.6291 | 0.5 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 65.0177 | 17.1971 | 409290.3294 | 34.1075 | 34.1075 | 93.485 | 0.6 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 65.4969 | 17.6763 | 420695.6352 | 35.058 | 35.058 | 94.341 | 0.7 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 65.9761 | 18.1555 | 432100.9411 | 36.0084 | 36.0084 | 95.1969 | 0.8 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 66.4553 | 18.6347 | 443506.247 | 36.9589 | 36.9589 | 96.0529 | 0.9 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 66.9346 | 19.1139 | 454911.5528 | 37.9093 | 37.9093 | 96.9088 | 1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 67.4138 | 19.5931 | 466316.8587 | 38.8597 | 38.8597 | 97.7647 | 75 | 55 | 28.2317 | 28 | 54.3
6/8/20XX 1:00:00 PM | 0.54167 | 5 | 73.7 | 55.3 | 61.9783 | 74.6189 | 12.6406 | 50 | 73.7 |  | 73.7 | 68.6778 | 0.1 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 63.2273 | 15.4066 | 366677.5601 | 30.5565 | 30.5565 | 90.312 | 0.2 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 63.8329 | 16.0122 | 381091.3202 | 31.7576 | 31.7576 | 91.4186 | 0.3 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 64.4385 | 16.6179 | 395505.0804 | 32.9588 | 32.9588 | 92.5253 | 0.4 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.0441 | 17.2235 | 409918.8405 | 34.1599 | 34.1599 | 93.6319 | 0.5 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 65.6497 | 17.8291 | 424332.6006 | 35.3611 | 35.3611 | 94.7386 | 0.6 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 66.2554 | 18.4347 | 438746.3607 | 36.5622 | 36.5622 | 95.8452 | 0.7 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 66.861 | 19.0403 | 453160.1208 | 37.7633 | 37.7633 | 96.9518 | 0.8 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 67.4666 | 19.646 | 467573.8809 | 38.9645 | 38.9645 | 98.0585 | 0.9 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 68.0722 | 20.2516 | 481987.6411 | 40.1656 | 40.1656 | 99.1651 | 1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 68.6778 | 20.8572 | 496401.4012 | 41.3668 | 41.3668 | 100.2718 | 75 | 55 | 28.4294 | 28 | 55.3
6/8/20XX 2:00:00 PM | 0.58333 | 5 | 74.3 | 52.2 | 63.2706 | 76.1783 | 12.9077 | 50 | 74.3 |  | 74.3 | 66.1103 | 0.1 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 62.9705 | 15.1499 | 360566.8406 | 30.0472 | 30.0472 | 89.9917 | 0.2 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 63.3194 | 15.4987 | 368869.8811 | 30.7392 | 30.7392 | 90.7782 | 0.3 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 63.6682 | 15.8476 | 377172.9217 | 31.4311 | 31.4311 | 91.5646 | 0.4 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 64.0171 | 16.1965 | 385475.9622 | 32.123 | 32.123 | 92.351 | 0.5 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 64.366 | 16.5453 | 393779.0028 | 32.8149 | 32.8149 | 93.1374 | 0.6 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 64.7148 | 16.8942 | 402082.0433 | 33.5068 | 33.5068 | 93.9238 | 0.7 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 65.0637 | 17.2431 | 410385.0839 | 34.1988 | 34.1988 | 94.7103 | 0.8 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 65.4126 | 17.5919 | 418688.1244 | 34.8907 | 34.8907 | 95.4967 | 0.9 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 65.7614 | 17.9408 | 426991.165 | 35.5826 | 35.5826 | 96.2831 | 1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 66.1103 | 18.2897 | 435294.2056 | 36.2745 | 36.2745 | 97.0695 | 75 | 50 | 28.1743 | 28 | 52.2
6/8/20XX 3:00:00 PM | 0.625 | 5 | 74.3 | 55.4 | 63.2706 | 76.1783 | 12.9077 | 50 | 74.3 |  | 74.3 | 70.2408 | 0.1 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 63.3835 | 15.5629 | 370397.3346 | 30.8664 | 30.8664 | 90.8109 | 0.2 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 64.1455 | 16.3248 | 388530.8692 | 32.3776 | 32.3776 | 92.4166 | 0.3 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 64.9074 | 17.0867 | 406664.4037 | 33.8887 | 33.8887 | 94.0222 | 0.4 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.6693 | 17.8487 | 424797.9383 | 35.3998 | 35.3998 | 95.6278 | 0.5 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 66.4312 | 18.6106 | 442931.4729 | 36.911 | 36.911 | 97.2335 | 0.6 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 67.1931 | 19.3725 | 461065.0075 | 38.4221 | 38.4221 | 98.8391 | 0.7 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 67.955 | 20.1344 | 479198.542 | 39.9332 | 39.9332 | 100.4447 | 0.8 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 68.7169 | 20.8963 | 497332.0766 | 41.4443 | 41.4443 | 102.0503 | 0.9 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 69.4789 | 21.6582 | 515465.6112 | 42.9555 | 42.9555 | 103.656 | 1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 70.2408 | 22.4201 | 533599.1458 | 44.4666 | 44.4666 | 105.2616 | 75 | 55 | 28.8205 | 28 | 55.4
6/8/20XX 4:00:00 PM | 0.66667 | 5 | 73.9 | 56.5 | 62.4066 | 75.1356 | 12.7291 | 50 | 73.9 |  | 73.9 | 70.6805 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 63.4275 | 15.6069 | 371443.8184 | 30.9537 | 30.9537 | 90.7722 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 64.2334 | 16.4128 | 390623.8368 | 32.552 | 32.552 | 92.339 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 65.0393 | 17.2186 | 409803.8552 | 34.1503 | 34.1503 | 93.9058 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 65.8452 | 18.0245 | 428983.8736 | 35.7487 | 35.7487 | 95.4727 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 66.651 | 18.8304 | 448163.892 | 37.347 | 37.347 | 97.0395 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 67.4569 | 19.6363 | 467343.9104 | 38.9453 | 38.9453 | 98.6063 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 68.2628 | 20.4422 | 486523.9289 | 40.5437 | 40.5437 | 100.1732 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 69.0687 | 21.2481 | 505703.9473 | 42.142 | 42.142 | 101.74 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 69.8746 | 22.0539 | 524883.9657 | 43.7403 | 43.7403 | 103.3068 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 70.6805 | 22.8598 | 544063.9841 | 45.3387 | 45.3387 | 104.8737 | 75 | 55 | 28.7915 | 28 | 56.5
6/8/20XX 5:00:00 PM | 0.70833 | 5 | 73.4 | 53.5 | 61.3407 | 73.8495 | 12.5088 | 50 | 73.4 |  | 73.4 | 65.7188 | 0.1 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 62.9313 | 15.1107 | 359634.9978 | 29.9696 | 29.9696 | 89.6306 | 0.2 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 63.2411 | 15.4204 | 367006.1957 | 30.5838 | 30.5838 | 90.0558 | 0.3 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 63.5508 | 15.7301 | 374377.3935 | 31.1981 | 31.1981 | 90.4811 | 0.4 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 63.8605 | 16.0399 | 381748.5914 | 31.8124 | 31.8124 | 90.9064 | 0.5 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.1702 | 16.3496 | 389119.7892 | 32.4266 | 32.4266 | 91.3316 | 0.6 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 64.4799 | 16.6593 | 396490.9871 | 33.0409 | 33.0409 | 91.7569 | 0.7 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 64.7896 | 16.969 | 403862.1849 | 33.6552 | 33.6552 | 92.1822 | 0.8 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 65.0993 | 17.2787 | 411233.3827 | 34.2694 | 34.2694 | 92.6074 | 0.9 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 65.4091 | 17.5884 | 418604.5806 | 34.8837 | 34.8837 | 93.0327 | 1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 65.7188 | 17.8981 | 425975.7784 | 35.498 | 35.498 | 93.458 | 75 | 55 | 27.8933 | 28 | 53.5
6/8/20XX 6:00:00 PM | 0.75 | 5 | 73.1 | 53 | 60.7087 | 73.0869 | 12.3783 | 50 | 73.1 |  | 73.1 | 64.4221 | 0.1 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 62.8017 | 14.9811 | 356549.014 | 29.7124 | 29.7124 | 89.2789 | 0.2 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 62.9817 | 15.1611 | 360834.228 | 30.0695 | 30.0695 | 89.3525 | 0.3 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 63.1618 | 15.3412 | 365119.442 | 30.4266 | 30.4266 | 89.4261 | 0.4 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 63.3418 | 15.5212 | 369404.656 | 30.7837 | 30.7837 | 89.4997 | 0.5 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 63.5219 | 15.7013 | 373689.8701 | 31.1408 | 31.1408 | 89.5733 | 0.6 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 63.7019 | 15.8813 | 377975.0841 | 31.4979 | 31.4979 | 89.6469 | 0.7 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 63.882 | 16.0614 | 382260.2981 | 31.855 | 31.855 | 89.7205 | 0.8 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 64.062 | 16.2414 | 386545.5121 | 32.2121 | 32.2121 | 89.7941 | 0.9 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 64.2421 | 16.4215 | 390830.7261 | 32.5692 | 32.5692 | 89.8677 | 1 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 64.4221 | 16.6015 | 395115.9401 | 32.9263 | 32.9263 | 89.9413 | 75 | 55 | 27.6173 | 28 | 53
6/8/20XX 7:00:00 PM | 0.79167 | 5 | 72.1 | 52.3 | 58.6421 | 70.5937 | 11.9516 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/8/20XX 8:00:00 PM | 0.83333 | 5 | 71.5 | 52.3 | 57.4315 | 69.1333 | 11.7019 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/8/20XX 9:00:00 PM | 0.875 | 5 | 70.5 | 56.7 | 55.4618 | 66.7576 | 11.2958 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/8/20XX 10:00:00 PM | 0.91667 | 5 | 69.9 | 58.6 | 54.3084 | 65.3666 | 11.0582 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/8/20XX 11:00:00 PM | 0.95833 | 5 | 68.7 | 62.8 | 62.6607 | 73.2724 | 10.6117 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/8/20XX 12:00:00 AM | 0 | 6 | 67.7 | 66.7 | 60.4817 | 70.7155 | 10.2338 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/9/20XX 1:00:00 AM | 0.041667 | 6 | 66.6 | 69 | 58.1627 | 67.9946 | 9.8319 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/9/20XX 2:00:00 AM | 0.083333 | 6 | 66 | 69.4 | 56.9316 | 66.5501 | 9.6186 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/9/20XX 3:00:00 AM | 0.125 | 6 | 65.2 | 70.4 | 64.667 | 74.0694 | 9.4024 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/9/20XX 4:00:00 AM | 0.16667 | 6 | 63.7 | 75.6 | 61.265 | 70.1655 | 8.9004 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/9/20XX 5:00:00 AM | 0.20833 | 6 | 63.6 | 74.3 | 61.0441 | 69.912 | 8.8679 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/9/20XX 6:00:00 AM | 0.25 | 6 | 64.9 | 74.1 | 63.9732 | 73.2731 | 9.2999 | 70 | 64.9 |  | 64.9 | 67.7862 | 1 | 64.9 | 9.9 | 374220 | 31.185 | 31.185 | 67.7862 | 19.9656 | 475180.3624 | 39.5984 | 39.5984 | 70.7834 | 1 | 64.9 | 9.9 | 374220 | 31.185 | 31.185 | 67.7862 | 19.9656 | 475180.3624 | 39.5984 | 39.5984 | 70.7834 | 1 | 64.9 | 9.9 | 374220 | 31.185 | 31.185 | 67.7862 | 19.9656 | 475180.3624 | 39.5984 | 39.5984 | 70.7834 | 1 | 64.9 | 9.9 | 374220 | 31.185 | 31.185 | 67.7862 | 19.9656 | 475180.3624 | 39.5984 | 39.5984 | 70.7834 | 1 | 64.9 | 9.9 | 374220 | 31.185 | 31.185 | 67.7862 | 19.9656 | 475180.3624 | 39.5984 | 39.5984 | 70.7834 | 1 | 64.9 | 9.9 | 374220 | 31.185 | 31.185 | 67.7862 | 19.9656 | 475180.3624 | 39.5984 | 39.5984 | 70.7834 | 1 | 64.9 | 9.9 | 374220 | 31.185 | 31.185 | 67.7862 | 19.9656 | 475180.3624 | 39.5984 | 39.5984 | 70.7834 | 1 | 64.9 | 9.9 | 374220 | 31.185 | 31.185 | 67.7862 | 19.9656 | 475180.3624 | 39.5984 | 39.5984 | 70.7834 | 1 | 64.9 | 9.9 | 374220 | 31.185 | 31.185 | 67.7862 | 19.9656 | 475180.3624 | 39.5984 | 39.5984 | 70.7834 | 1 | 64.9 | 9.9 | 374220 | 31.185 | 31.185 | 67.7862 | 19.9656 | 475180.3624 | 39.5984 | 39.5984 | 70.7834 | 65 | 75 | 26.14 | 26 | 74.1
6/9/20XX 7:00:00 AM | 0.29167 | 6 | 65.9 | 70.9 | 66.3121 | 75.9577 | 9.6456 | 70 | 65.9 |  | 65.9 | 67.1802 | 0.1 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 63.0775 | 15.2569 | 363113.1265 | 30.2594 | 30.2594 | 87.5579 | 0.2 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 63.5333 | 15.7127 | 373962.4531 | 31.1635 | 31.1635 | 85.9105 | 0.3 | 71.57 | 16.57 | 626346 | 52.1955 | 52.1955 | 63.9892 | 16.1686 | 384811.7796 | 32.0676 | 32.0676 | 84.2631 | 0.4 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 64.445 | 16.6244 | 395661.1062 | 32.9718 | 32.9718 | 82.6158 | 0.5 | 69.95 | 14.95 | 565110 | 47.0925 | 47.0925 | 64.9009 | 17.0803 | 406510.4327 | 33.8759 | 33.8759 | 80.9684 | 0.6 | 69.14 | 14.14 | 534492 | 44.541 | 44.541 | 65.3568 | 17.5361 | 417359.7592 | 34.78 | 34.78 | 79.321 | 0.7 | 68.33 | 13.33 | 503874 | 41.9895 | 41.9895 | 65.8126 | 17.992 | 428209.0858 | 35.6841 | 35.6841 | 77.6736 | 0.8 | 67.52 | 12.52 | 473256 | 39.438 | 39.438 | 66.2685 | 18.4478 | 439058.4123 | 36.5882 | 36.5882 | 76.0262 | 0.9 | 66.71 | 11.71 | 442638 | 36.8865 | 36.8865 | 66.7243 | 18.9037 | 449907.7388 | 37.4923 | 37.4923 | 74.3788 | 1 | 65.9 | 10.9 | 412020 | 34.335 | 34.335 | 67.1802 | 19.3595 | 460757.0654 | 38.3964 | 38.3964 | 72.7314 | 65 | 70 | 26.2899 | 26 | 70.9
6/9/20XX 8:00:00 AM | 0.33333 | 6 | 67.3 | 67.6 | 59.6291 | 69.7151 | 10.086 | 60 | 67.3 |  | 67.3 | 67.2945 | 0.1 | 73.33 | 18.33 | 692874 | 57.7395 | 57.7395 | 63.0889 | 15.2683 | 363385.1092 | 30.2821 | 30.2821 | 88.0216 | 0.2 | 72.66 | 17.66 | 667548 | 55.629 | 55.629 | 63.5562 | 15.7356 | 374506.4184 | 31.2089 | 31.2089 | 86.8379 | 0.3 | 71.99 | 16.99 | 642222 | 53.5185 | 53.5185 | 64.0235 | 16.2028 | 385627.7276 | 32.1356 | 32.1356 | 85.6541 | 0.4 | 71.32 | 16.32 | 616896 | 51.408 | 51.408 | 64.4908 | 16.6701 | 396749.0367 | 33.0624 | 33.0624 | 84.4704 | 0.5 | 70.65 | 15.65 | 591570 | 49.2975 | 49.2975 | 64.958 | 17.1374 | 407870.3459 | 33.9892 | 33.9892 | 83.2867 | 0.6 | 69.98 | 14.98 | 566244 | 47.187 | 47.187 | 65.4253 | 17.6047 | 418991.6551 | 34.916 | 34.916 | 82.103 | 0.7 | 69.31 | 14.31 | 540918 | 45.0765 | 45.0765 | 65.8926 | 18.072 | 430112.9643 | 35.8427 | 35.8427 | 80.9192 | 0.8 | 68.64 | 13.64 | 515592 | 42.966 | 42.966 | 66.3599 | 18.5393 | 441234.2735 | 36.7695 | 36.7695 | 79.7355 | 0.9 | 67.97 | 12.97 | 490266 | 40.8555 | 40.8555 | 66.8272 | 19.0065 | 452355.5827 | 37.6963 | 37.6963 | 78.5518 | 1 | 67.3 | 12.3 | 464940 | 38.745 | 38.745 | 67.2945 | 19.4738 | 463476.8919 | 38.6231 | 38.6231 | 77.3681 | 65 | 70 | 26.6497 | 26 | 67.6
6/9/20XX 9:00:00 AM | 0.375 | 6 | 68.5 | 65.3 | 62.2194 | 72.7546 | 10.5352 | 60 | 68.5 |  | 68.5 | 67.8031 | 0.1 | 73.45 | 18.45 | 697410 | 58.1175 | 58.1175 | 63.1398 | 15.3191 | 364595.6471 | 30.383 | 30.383 | 88.5005 | 0.2 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 63.6579 | 15.8373 | 376927.4941 | 31.4106 | 31.4106 | 87.7956 | 0.3 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 64.1761 | 16.3554 | 389259.3412 | 32.4383 | 32.4383 | 87.0908 | 0.4 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 64.6942 | 16.8736 | 401591.1883 | 33.4659 | 33.4659 | 86.3859 | 0.5 | 71.25 | 16.25 | 614250 | 51.1875 | 51.1875 | 65.2124 | 17.3917 | 413923.0353 | 34.4936 | 34.4936 | 85.6811 | 0.6 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 65.7305 | 17.9099 | 426254.8824 | 35.5212 | 35.5212 | 84.9762 | 0.7 | 70.15 | 15.15 | 572670 | 47.7225 | 47.7225 | 66.2486 | 18.428 | 438586.7294 | 36.5489 | 36.5489 | 84.2714 | 0.8 | 69.6 | 14.6 | 551880 | 45.99 | 45.99 | 66.7668 | 18.9462 | 450918.5765 | 37.5765 | 37.5765 | 83.5665 | 0.9 | 69.05 | 14.05 | 531090 | 44.2575 | 44.2575 | 67.2849 | 19.4643 | 463250.4236 | 38.6042 | 38.6042 | 82.8617 | 1 | 68.5 | 13.5 | 510300 | 42.525 | 42.525 | 67.8031 | 19.9824 | 475582.2706 | 39.6319 | 39.6319 | 82.1569 | 70 | 65 | 27.0222 | 28 | 65.3
6/9/20XX 10:00:00 AM | 0.41667 | 6 | 70.5 | 61.6 | 66.7576 | 78.0804 | 11.3228 | 60 | 70.5 |  | 70.5 | 68.5693 | 0.1 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 63.2164 | 15.3958 | 366419.1912 | 30.5349 | 30.5349 | 89.2824 | 0.2 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 63.8112 | 15.9905 | 380574.5825 | 31.7145 | 31.7145 | 89.3595 | 0.3 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 64.4059 | 16.5853 | 394729.9737 | 32.8942 | 32.8942 | 89.4367 | 0.4 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 65.0007 | 17.1801 | 408885.365 | 34.0738 | 34.0738 | 89.5138 | 0.5 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 65.5955 | 17.7748 | 423040.7562 | 35.2534 | 35.2534 | 89.5909 | 0.6 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 66.1902 | 18.3696 | 437196.1475 | 36.433 | 36.433 | 89.668 | 0.7 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 66.785 | 18.9644 | 451351.5387 | 37.6126 | 37.6126 | 89.7451 | 0.8 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 67.3797 | 19.5591 | 465506.93 | 38.7922 | 38.7922 | 89.8222 | 0.9 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 67.9745 | 20.1539 | 479662.3212 | 39.9719 | 39.9719 | 89.8994 | 1 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 68.5693 | 20.7486 | 493817.7125 | 41.1515 | 41.1515 | 89.9765 | 70 | 60 | 27.6305 | 28 | 61.6
6/9/20XX 11:00:00 AM | 0.45833 | 6 | 72.9 | 59 | 60.2904 | 72.5823 | 12.2919 | 50 | 72.9 |  | 72.9 | 71.3531 | 0.1 | 73.89 | 18.89 | 714042 | 59.5035 | 59.5035 | 63.4948 | 15.6741 | 373044.7267 | 31.0871 | 31.0871 | 90.5906 | 0.2 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 64.3679 | 16.5473 | 393825.6534 | 32.8188 | 32.8188 | 91.9758 | 0.3 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 65.2411 | 17.4204 | 414606.5801 | 34.5505 | 34.5505 | 93.361 | 0.4 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 66.1142 | 18.2936 | 435387.5068 | 36.2823 | 36.2823 | 94.7463 | 0.5 | 73.45 | 18.45 | 697410 | 58.1175 | 58.1175 | 66.9874 | 19.1667 | 456168.4335 | 38.014 | 38.014 | 96.1315 | 0.6 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 67.8605 | 20.0399 | 476949.3603 | 39.7458 | 39.7458 | 97.5168 | 0.7 | 73.23 | 18.23 | 689094 | 57.4245 | 57.4245 | 68.7337 | 20.913 | 497730.287 | 41.4775 | 41.4775 | 98.902 | 0.8 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 69.6068 | 21.7862 | 518511.2137 | 43.2093 | 43.2093 | 100.2873 | 0.9 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 70.48 | 22.6593 | 539292.1404 | 44.941 | 44.941 | 101.6725 | 1 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 71.3531 | 23.5325 | 560073.0671 | 46.6728 | 46.6728 | 103.0578 | 75 | 60 | 28.6522 | 28 | 59
6/9/20XX 12:00:00 PM | 0.5 | 6 | 74 | 56.8 | 62.6216 | 75.3952 | 12.7735 | 50 | 74 |  | 74 | 71.3076 | 0.1 | 74 | 19 | 718200 | 59.85 | 59.85 | 63.4902 | 15.6696 | 372936.4648 | 31.078 | 31.078 | 90.928 | 0.2 | 74 | 19 | 718200 | 59.85 | 59.85 | 64.3588 | 16.5382 | 393609.1295 | 32.8008 | 32.8008 | 92.6508 | 0.3 | 74 | 19 | 718200 | 59.85 | 59.85 | 65.2274 | 17.4068 | 414281.7943 | 34.5235 | 34.5235 | 94.3735 | 0.4 | 74 | 19 | 718200 | 59.85 | 59.85 | 66.096 | 18.2754 | 434954.4591 | 36.2462 | 36.2462 | 96.0962 | 0.5 | 74 | 19 | 718200 | 59.85 | 59.85 | 66.9646 | 19.144 | 455627.1238 | 37.9689 | 37.9689 | 97.8189 | 0.6 | 74 | 19 | 718200 | 59.85 | 59.85 | 67.8332 | 20.0126 | 476299.7886 | 39.6916 | 39.6916 | 99.5416 | 0.7 | 74 | 19 | 718200 | 59.85 | 59.85 | 68.7018 | 20.8812 | 496972.4534 | 41.4144 | 41.4144 | 101.2644 | 0.8 | 74 | 19 | 718200 | 59.85 | 59.85 | 69.5704 | 21.7498 | 517645.1181 | 43.1371 | 43.1371 | 102.9871 | 0.9 | 74 | 19 | 718200 | 59.85 | 59.85 | 70.439 | 22.6184 | 538317.7829 | 44.8598 | 44.8598 | 104.7098 | 1 | 74 | 19 | 718200 | 59.85 | 59.85 | 71.3076 | 23.487 | 558990.4477 | 46.5825 | 46.5825 | 106.4325 | 75 | 55 | 28.914 | 28 | 56.8
6/9/20XX 1:00:00 PM | 0.54167 | 6 | 74.7 | 58.1 | 64.1448 | 77.2333 | 13.0885 | 50 | 74.7 |  | 74.7 | 74.7465 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 63.8341 | 16.0135 | 381120.9394 | 31.7601 | 31.7601 | 91.8306 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 65.0466 | 17.226 | 409978.0788 | 34.1648 | 34.1648 | 94.4558 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 66.2591 | 18.4385 | 438835.2181 | 36.5696 | 36.5696 | 97.0811 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 67.4716 | 19.6509 | 467692.3575 | 38.9744 | 38.9744 | 99.7064 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 68.6841 | 20.8634 | 496549.4969 | 41.3791 | 41.3791 | 102.3316 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 69.8965 | 22.0759 | 525406.6363 | 43.7839 | 43.7839 | 104.9569 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 71.109 | 23.2884 | 554263.7757 | 46.1886 | 46.1886 | 107.5821 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 72.3215 | 24.5009 | 583120.915 | 48.5934 | 48.5934 | 110.2074 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 73.534 | 25.7134 | 611978.0544 | 50.9982 | 50.9982 | 112.8327 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 74.7465 | 26.9258 | 640835.1938 | 53.4029 | 53.4029 | 115.4579 | 75 | 60 | 29.6233 | 30 | 58.1
6/9/20XX 2:00:00 PM | 0.58333 | 6 | 74.9 | 59.1 | 64.5858 | 77.7654 | 13.1797 | 50 | 74.9 |  | 74.9 | 76.5793 | 0.1 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 64.0174 | 16.1968 | 385482.9667 | 32.1236 | 32.1236 | 92.2571 | 0.2 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 65.4132 | 17.5925 | 418702.1334 | 34.8918 | 34.8918 | 95.3088 | 0.3 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 66.8089 | 18.9883 | 451921.3001 | 37.6601 | 37.6601 | 98.3606 | 0.4 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 68.2047 | 20.3841 | 485140.4668 | 40.4284 | 40.4284 | 101.4124 | 0.5 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 69.6004 | 21.7798 | 518359.6336 | 43.1966 | 43.1966 | 104.4641 | 0.6 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 70.9962 | 23.1756 | 551578.8003 | 45.9649 | 45.9649 | 107.5159 | 0.7 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 72.392 | 24.5713 | 584797.967 | 48.7332 | 48.7332 | 110.5677 | 0.8 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 73.7877 | 25.9671 | 618017.1337 | 51.5014 | 51.5014 | 113.6194 | 0.9 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 75.1835 | 27.3629 | 651236.3004 | 54.2697 | 54.2697 | 116.6712 | 1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 76.5793 | 28.7586 | 684455.4671 | 57.038 | 57.038 | 119.723 | 75 | 60 | 29.959 | 30 | 59.1
6/9/20XX 3:00:00 PM | 0.625 | 6 | 75.2 | 57.1 | 65.252 | 78.5695 | 13.3175 | 50 | 75.2 |  | 75.2 | 74.7074 | 0.1 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 63.8302 | 16.0096 | 381027.9796 | 31.7523 | 31.7523 | 91.9803 | 0.2 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 65.0388 | 17.2182 | 409792.1591 | 34.1493 | 34.1493 | 94.7553 | 0.3 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 66.2474 | 18.4267 | 438556.3387 | 36.5464 | 36.5464 | 97.5304 | 0.4 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 67.4559 | 19.6353 | 467320.5182 | 38.9434 | 38.9434 | 100.3054 | 0.5 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 68.6645 | 20.8439 | 496084.6978 | 41.3404 | 41.3404 | 103.0804 | 0.6 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 69.8731 | 22.0525 | 524848.8773 | 43.7374 | 43.7374 | 105.8554 | 0.7 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 71.0817 | 23.2611 | 553613.0569 | 46.1344 | 46.1344 | 108.6304 | 0.8 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 72.2903 | 24.4696 | 582377.2364 | 48.5314 | 48.5314 | 111.4054 | 0.9 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 73.4988 | 25.6782 | 611141.416 | 50.9285 | 50.9285 | 114.1805 | 1 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 74.7074 | 26.8868 | 639905.5955 | 53.3255 | 53.3255 | 116.9555 | 75 | 55 | 29.7395 | 30 | 57.1
6/9/20XX 4:00:00 PM | 0.66667 | 6 | 75.8 | 54.6 | 66.6019 | 80.1988 | 13.5969 | 50 | 75.8 |  | 75.8 | 72.8565 | 0.1 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 63.6451 | 15.8245 | 376622.755 | 31.3852 | 31.3852 | 91.8022 | 0.2 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 64.6686 | 16.848 | 400981.71 | 33.4151 | 33.4151 | 94.3991 | 0.3 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 65.6921 | 17.8715 | 425340.665 | 35.4451 | 35.4451 | 96.9961 | 0.4 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 66.7156 | 18.8949 | 449699.6201 | 37.475 | 37.475 | 99.593 | 0.5 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 67.7391 | 19.9184 | 474058.5751 | 39.5049 | 39.5049 | 102.1899 | 0.6 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 68.7625 | 20.9419 | 498417.5301 | 41.5348 | 41.5348 | 104.7868 | 0.7 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 69.786 | 21.9654 | 522776.4851 | 43.5647 | 43.5647 | 107.3837 | 0.8 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 70.8095 | 22.9889 | 547135.4401 | 45.5946 | 45.5946 | 109.9806 | 0.9 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 71.833 | 24.0124 | 571494.3951 | 47.6245 | 47.6245 | 112.5775 | 1 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 72.8565 | 25.0359 | 595853.3501 | 49.6544 | 49.6544 | 115.1744 | 75 | 55 | 29.5966 | 30 | 54.6
6/9/20XX 5:00:00 PM | 0.70833 | 6 | 74.6 | 56.1 | 63.9253 | 76.9684 | 13.0431 | 50 | 74.6 |  | 74.6 | 71.8816 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 63.5476 | 15.727 | 374302.4862 | 31.1919 | 31.1919 | 91.2309 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 64.4736 | 16.653 | 396341.1723 | 33.0284 | 33.0284 | 93.2564 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 65.3996 | 17.579 | 418379.8585 | 34.865 | 34.865 | 95.282 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 66.3256 | 18.505 | 440418.5447 | 36.7015 | 36.7015 | 97.3075 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 67.2516 | 19.431 | 462457.2309 | 38.5381 | 38.5381 | 99.3331 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 68.1776 | 20.357 | 484495.917 | 40.3747 | 40.3747 | 101.3587 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 69.1036 | 21.283 | 506534.6032 | 42.2112 | 42.2112 | 103.3842 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 70.0296 | 22.209 | 528573.2894 | 44.0478 | 44.0478 | 105.4098 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 70.9556 | 23.135 | 550611.9755 | 45.8843 | 45.8843 | 107.4353 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 71.8816 | 24.061 | 572650.6617 | 47.7209 | 47.7209 | 109.4609 | 75 | 55 | 29.1506 | 30 | 56.1
6/9/20XX 6:00:00 PM | 0.75 | 6 | 72.5 | 60.2 | 71.5821 | 83.7428 | 12.1608 | 60 | 72.5 |  | 72.5 | 71.8253 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 63.542 | 15.7214 | 374168.4581 | 31.1807 | 31.1807 | 90.5582 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.4624 | 16.6417 | 396073.1161 | 33.0061 | 33.0061 | 91.9111 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 65.3827 | 17.5621 | 417977.7742 | 34.8315 | 34.8315 | 93.264 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 66.3031 | 18.4825 | 439882.4323 | 36.6569 | 36.6569 | 94.6169 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 67.2235 | 19.4028 | 461787.0903 | 38.4823 | 38.4823 | 95.9698 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 68.1438 | 20.3232 | 483691.7484 | 40.3076 | 40.3076 | 97.3226 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 69.0642 | 21.2435 | 505596.4065 | 42.133 | 42.133 | 98.6755 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 69.9845 | 22.1639 | 527501.0645 | 43.9584 | 43.9584 | 100.0284 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 70.9049 | 23.0843 | 549405.7226 | 45.7838 | 45.7838 | 101.3813 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 71.8253 | 24.0046 | 571310.3807 | 47.6092 | 47.6092 | 102.7342 | 70 | 60 | 28.6282 | 28 | 60.2
6/9/20XX 7:00:00 PM | 0.79167 | 6 | 70.9 | 62.7 | 67.6992 | 79.1855 | 11.4863 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/9/20XX 8:00:00 PM | 0.83333 | 6 | 70 | 65.8 | 65.5967 | 76.7179 | 11.1212 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/9/20XX 9:00:00 PM | 0.875 | 6 | 69.3 | 66.6 | 64.0011 | 74.8454 | 10.8443 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/9/20XX 10:00:00 PM | 0.91667 | 6 | 68.7 | 68.5 | 62.6607 | 73.2724 | 10.6117 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/9/20XX 11:00:00 PM | 0.95833 | 6 | 67.7 | 70.5 | 70.7155 | 81.0138 | 10.2983 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/9/20XX 12:00:00 AM | 0 | 7 | 67.3 | 71.5 | 69.7151 | 79.8649 | 10.1498 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/10/20XX 1:00:00 AM | 0.041667 | 7 | 66.6 | 72.8 | 67.9946 | 77.8893 | 9.8947 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/10/20XX 2:00:00 AM | 0.083333 | 7 | 66.3 | 73.7 | 67.2689 | 77.0561 | 9.7873 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/10/20XX 3:00:00 AM | 0.125 | 7 | 65.6 | 75.5 | 65.6025 | 75.1431 | 9.5407 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/10/20XX 4:00:00 AM | 0.16667 | 7 | 64.9 | 76.3 | 63.9732 | 73.2731 | 9.2999 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/10/20XX 5:00:00 AM | 0.20833 | 7 | 64.7 | 76.2 | 63.5145 | 72.7466 | 9.2322 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/10/20XX 6:00:00 AM | 0.25 | 7 | 65.1 | 76 | 64.435 | 73.8031 | 9.3681 | 70 | 65.1 |  | 65.1 | 70.0558 | 0.1 | 73.11 | 18.11 | 684558 | 57.0465 | 57.0465 | 63.3651 | 15.5444 | 369957.2072 | 30.8298 | 30.8298 | 87.8763 | 0.2 | 72.22 | 17.22 | 650916 | 54.243 | 54.243 | 64.1085 | 16.2878 | 387650.6144 | 32.3042 | 32.3042 | 86.5472 | 0.3 | 71.33 | 16.33 | 617274 | 51.4395 | 51.4395 | 64.8519 | 17.0313 | 405344.0216 | 33.7787 | 33.7787 | 85.2182 | 0.4 | 70.44 | 15.44 | 583632 | 48.636 | 48.636 | 65.5953 | 17.7747 | 423037.4288 | 35.2531 | 35.2531 | 83.8891 | 0.5 | 69.55 | 14.55 | 549990 | 45.8325 | 45.8325 | 66.3387 | 18.5181 | 440730.836 | 36.7276 | 36.7276 | 82.5601 | 0.6 | 68.66 | 13.66 | 516348 | 43.029 | 43.029 | 67.0822 | 19.2615 | 458424.2432 | 38.202 | 38.202 | 81.231 | 0.7 | 67.77 | 12.77 | 482706 | 40.2255 | 40.2255 | 67.8256 | 20.0049 | 476117.6504 | 39.6765 | 39.6765 | 79.902 | 0.8 | 66.88 | 11.88 | 449064 | 37.422 | 37.422 | 68.569 | 20.7484 | 493811.0577 | 41.1509 | 41.1509 | 78.5729 | 0.9 | 65.99 | 10.99 | 415422 | 34.6185 | 34.6185 | 69.3124 | 21.4918 | 511504.4649 | 42.6254 | 42.6254 | 77.2439 | 1 | 65.1 | 10.1 | 381780 | 31.815 | 31.815 | 70.0558 | 22.2352 | 529197.8721 | 44.0998 | 44.0998 | 75.9148 | 65 | 75 | 26.5426 | 26 | 76
6/10/20XX 7:00:00 AM | 0.29167 | 7 | 66.2 | 73.8 | 67.0285 | 76.7802 | 9.7517 | 70 | 66.2 |  | 66.2 | 70.7342 | 0.1 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 63.4329 | 15.6123 | 371571.624 | 30.9643 | 30.9643 | 88.3573 | 0.2 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 64.2441 | 16.4235 | 390879.4481 | 32.5733 | 32.5733 | 87.5093 | 0.3 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 65.0554 | 17.2348 | 410187.2721 | 34.1823 | 34.1823 | 86.6613 | 0.4 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 65.8666 | 18.046 | 429495.0962 | 35.7913 | 35.7913 | 85.8133 | 0.5 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 66.6779 | 18.8573 | 448802.9202 | 37.4002 | 37.4002 | 84.9652 | 0.6 | 69.32 | 14.32 | 541296 | 45.108 | 45.108 | 67.4892 | 19.6685 | 468110.7443 | 39.0092 | 39.0092 | 84.1172 | 0.7 | 68.54 | 13.54 | 511812 | 42.651 | 42.651 | 68.3004 | 20.4798 | 487418.5683 | 40.6182 | 40.6182 | 83.2692 | 0.8 | 67.76 | 12.76 | 482328 | 40.194 | 40.194 | 69.1117 | 21.291 | 506726.3924 | 42.2272 | 42.2272 | 82.4212 | 0.9 | 66.98 | 11.98 | 452844 | 37.737 | 37.737 | 69.9229 | 22.1023 | 526034.2164 | 43.8362 | 43.8362 | 81.5732 | 1 | 66.2 | 11.2 | 423360 | 35.28 | 35.28 | 70.7342 | 22.9135 | 545342.0404 | 45.4452 | 45.4452 | 80.7252 | 65 | 75 | 26.9173 | 26 | 73.8
6/10/20XX 8:00:00 AM | 0.33333 | 7 | 67.8 | 71.9 | 70.9676 | 81.3033 | 10.3357 | 70 | 67.8 |  | 67.8 | 72.9314 | 0.1 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 63.6526 | 15.832 | 376801.0509 | 31.4001 | 31.4001 | 89.2971 | 0.2 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 64.6836 | 16.863 | 401338.3019 | 33.4449 | 33.4449 | 89.3889 | 0.3 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 65.7146 | 17.8939 | 425875.5528 | 35.4896 | 35.4896 | 89.4806 | 0.4 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 66.7455 | 18.9249 | 450412.8037 | 37.5344 | 37.5344 | 89.5724 | 0.5 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 67.7765 | 19.9559 | 474950.0547 | 39.5792 | 39.5792 | 89.6642 | 0.6 | 70.28 | 15.28 | 577584 | 48.132 | 48.132 | 68.8075 | 20.9869 | 499487.3056 | 41.6239 | 41.6239 | 89.7559 | 0.7 | 69.66 | 14.66 | 554148 | 46.179 | 46.179 | 69.8385 | 22.0178 | 524024.5566 | 43.6687 | 43.6687 | 89.8477 | 0.8 | 69.04 | 14.04 | 530712 | 44.226 | 44.226 | 70.8694 | 23.0488 | 548561.8075 | 45.7135 | 45.7135 | 89.9395 | 0.9 | 68.42 | 13.42 | 507276 | 42.273 | 42.273 | 71.9004 | 24.0798 | 573099.0584 | 47.7583 | 47.7583 | 90.0313 | 1 | 67.8 | 12.8 | 483840 | 40.32 | 40.32 | 72.9314 | 25.1108 | 597636.3094 | 49.803 | 49.803 | 90.123 | 70 | 70 | 27.6513 | 28 | 71.9
6/10/20XX 9:00:00 AM | 0.375 | 7 | 69.2 | 69.8 | 63.776 | 74.5812 | 10.8052 | 60 | 69.2 |  | 69.2 | 74.3651 | 0.1 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 63.796 | 15.9753 | 380213.2604 | 31.6844 | 31.6844 | 90.0224 | 0.2 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 64.9703 | 17.1497 | 408162.7208 | 34.0136 | 34.0136 | 90.8396 | 0.3 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 66.1447 | 18.324 | 436112.1812 | 36.3427 | 36.3427 | 91.6567 | 0.4 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 67.319 | 19.4984 | 464061.6416 | 38.6718 | 38.6718 | 92.4738 | 0.5 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 68.4934 | 20.6727 | 492011.102 | 41.0009 | 41.0009 | 93.2909 | 0.6 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 69.6677 | 21.8471 | 519960.5624 | 43.33 | 43.33 | 94.108 | 0.7 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 70.8421 | 23.0214 | 547910.0228 | 45.6592 | 45.6592 | 94.9252 | 0.8 | 70.16 | 15.16 | 573048 | 47.754 | 47.754 | 72.0164 | 24.1958 | 575859.4831 | 47.9883 | 47.9883 | 95.7423 | 0.9 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 73.1908 | 25.3701 | 603808.9435 | 50.3174 | 50.3174 | 96.5594 | 1 | 69.2 | 14.2 | 536760 | 44.73 | 44.73 | 74.3651 | 26.5445 | 631758.4039 | 52.6465 | 52.6465 | 97.3765 | 70 | 70 | 28.2176 | 28 | 69.8
6/10/20XX 10:00:00 AM | 0.41667 | 7 | 70.9 | 65.8 | 67.6992 | 79.1855 | 11.4863 | 60 | 70.9 |  | 70.9 | 74.3613 | 0.1 | 73.69 | 18.69 | 706482 | 58.8735 | 58.8735 | 63.7956 | 15.975 | 380204.1927 | 31.6837 | 31.6837 | 90.5572 | 0.2 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 64.9696 | 17.1489 | 408144.5854 | 34.012 | 34.012 | 91.909 | 0.3 | 73.07 | 18.07 | 683046 | 56.9205 | 56.9205 | 66.1435 | 18.3229 | 436084.978 | 36.3404 | 36.3404 | 93.2609 | 0.4 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 67.3175 | 19.4969 | 464025.3707 | 38.6688 | 38.6688 | 94.6128 | 0.5 | 72.45 | 17.45 | 659610 | 54.9675 | 54.9675 | 68.4915 | 20.6708 | 491965.7634 | 40.9971 | 40.9971 | 95.9646 | 0.6 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 69.6654 | 21.8448 | 519906.1561 | 43.3255 | 43.3255 | 97.3165 | 0.7 | 71.83 | 16.83 | 636174 | 53.0145 | 53.0145 | 70.8394 | 23.0188 | 547846.5487 | 45.6539 | 45.6539 | 98.6684 | 0.8 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 72.0134 | 24.1927 | 575786.9414 | 47.9822 | 47.9822 | 100.0202 | 0.9 | 71.21 | 16.21 | 612738 | 51.0615 | 51.0615 | 73.1873 | 25.3667 | 603727.3341 | 50.3106 | 50.3106 | 101.3721 | 1 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 74.3613 | 26.5407 | 631667.7268 | 52.639 | 52.639 | 102.724 | 70 | 65 | 28.6331 | 28 | 65.8
6/10/20XX 11:00:00 AM | 0.45833 | 7 | 73.2 | 63.4 | 73.3404 | 85.8067 | 12.4664 | 60 | 73.2 |  | 73.2 | 77.5789 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 64.1174 | 16.2967 | 387862.1524 | 32.3218 | 32.3218 | 91.9198 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 65.6131 | 17.7925 | 423460.5047 | 35.2884 | 35.2884 | 94.6344 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 67.1088 | 19.2882 | 459058.8571 | 38.2549 | 38.2549 | 97.3489 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 68.6045 | 20.7839 | 494657.2094 | 41.2214 | 41.2214 | 100.0634 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 70.1003 | 22.2796 | 530255.5618 | 44.188 | 44.188 | 102.778 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 71.596 | 23.7754 | 565853.9141 | 47.1545 | 47.1545 | 105.4925 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 73.0917 | 25.2711 | 601452.2665 | 50.121 | 50.121 | 108.207 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 74.5875 | 26.7668 | 637050.6188 | 53.0876 | 53.0876 | 110.9216 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 76.0832 | 28.2626 | 672648.9712 | 56.0541 | 56.0541 | 113.6361 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 77.5789 | 29.7583 | 708247.3235 | 59.0206 | 59.0206 | 116.3506 | 75 | 65 | 29.6991 | 30 | 63.4
6/10/20XX 12:00:00 PM | 0.5 | 7 | 74 | 62.1 | 75.3952 | 88.2187 | 12.8236 | 60 | 74 |  | 74 | 78.0881 | 0.1 | 74 | 19 | 718200 | 59.85 | 59.85 | 64.1683 | 16.3476 | 389074.0008 | 32.4228 | 32.4228 | 92.2728 | 0.2 | 74 | 19 | 718200 | 59.85 | 59.85 | 65.7149 | 17.8943 | 425884.2017 | 35.4904 | 35.4904 | 95.3404 | 0.3 | 74 | 19 | 718200 | 59.85 | 59.85 | 67.2616 | 19.4409 | 462694.4025 | 38.5579 | 38.5579 | 98.4079 | 0.4 | 74 | 19 | 718200 | 59.85 | 59.85 | 68.8082 | 20.9876 | 499504.6033 | 41.6254 | 41.6254 | 101.4754 | 0.5 | 74 | 19 | 718200 | 59.85 | 59.85 | 70.3549 | 22.5342 | 536314.8042 | 44.6929 | 44.6929 | 104.5429 | 0.6 | 74 | 19 | 718200 | 59.85 | 59.85 | 71.9015 | 24.0809 | 573125.005 | 47.7604 | 47.7604 | 107.6104 | 0.7 | 74 | 19 | 718200 | 59.85 | 59.85 | 73.4482 | 25.6275 | 609935.2058 | 50.8279 | 50.8279 | 110.6779 | 0.8 | 74 | 19 | 718200 | 59.85 | 59.85 | 74.9948 | 27.1742 | 646745.4067 | 53.8955 | 53.8955 | 113.7455 | 0.9 | 74 | 19 | 718200 | 59.85 | 59.85 | 76.5415 | 28.7208 | 683555.6075 | 56.963 | 56.963 | 116.813 | 1 | 74 | 19 | 718200 | 59.85 | 59.85 | 78.0881 | 30.2675 | 720365.8083 | 60.0305 | 60.0305 | 119.8805 | 75 | 60 | 29.9747 | 30 | 62.1
6/10/20XX 1:00:00 PM | 0.54167 | 7 | 74.7 | 60.9 | 77.2333 | 90.3765 | 13.1432 | 60 | 74.7 |  | 74.7 | 78.4162 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 64.2011 | 16.3805 | 389854.8217 | 32.4879 | 32.4879 | 92.5584 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 65.7805 | 17.9599 | 427445.8434 | 35.6205 | 35.6205 | 95.9115 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 67.36 | 19.5394 | 465036.8651 | 38.7531 | 38.7531 | 99.2646 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 68.9395 | 21.1188 | 502627.8869 | 41.8857 | 41.8857 | 102.6177 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 70.5189 | 22.6983 | 540218.9086 | 45.0182 | 45.0182 | 105.9707 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 72.0984 | 24.2777 | 577809.9303 | 48.1508 | 48.1508 | 109.3238 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 73.6778 | 25.8572 | 615400.952 | 51.2834 | 51.2834 | 112.6769 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 75.2573 | 27.4366 | 652991.9737 | 54.416 | 54.416 | 116.03 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 76.8367 | 29.0161 | 690582.9954 | 57.5486 | 57.5486 | 119.3831 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 78.4162 | 30.5955 | 728174.0171 | 60.6812 | 60.6812 | 122.7362 | 75 | 60 | 30.1975 | 30 | 60.9
6/10/20XX 2:00:00 PM | 0.58333 | 7 | 74.5 | 60.5 | 76.7042 | 89.7555 | 13.0512 | 60 | 74.5 |  | 74.5 | 77.3568 | 0.1 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 64.0952 | 16.2745 | 387333.5205 | 32.2778 | 32.2778 | 92.2853 | 0.2 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 65.5687 | 17.748 | 422403.2411 | 35.2003 | 35.2003 | 95.3653 | 0.3 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 67.0422 | 19.2216 | 457472.9616 | 38.1227 | 38.1227 | 98.4452 | 0.4 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 68.5157 | 20.6951 | 492542.6821 | 41.0452 | 41.0452 | 101.5252 | 0.5 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 69.9892 | 22.1686 | 527612.4027 | 43.9677 | 43.9677 | 104.6052 | 0.6 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 71.4627 | 23.6421 | 562682.1232 | 46.8902 | 46.8902 | 107.6852 | 0.7 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 72.9363 | 25.1156 | 597751.8437 | 49.8127 | 49.8127 | 110.7652 | 0.8 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 74.4098 | 26.5891 | 632821.5643 | 52.7351 | 52.7351 | 113.8451 | 0.9 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 75.8833 | 28.0627 | 667891.2848 | 55.6576 | 55.6576 | 116.9251 | 1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 77.3568 | 29.5362 | 702961.0054 | 58.5801 | 58.5801 | 120.0051 | 75 | 60 | 29.9827 | 30 | 60.5
6/10/20XX 3:00:00 PM | 0.625 | 7 | 73.7 | 63 | 74.6189 | 87.3075 | 12.6886 | 60 | 73.7 |  | 73.7 | 78.4255 | 0.1 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 64.202 | 16.3814 | 389876.9674 | 32.4897 | 32.4897 | 92.2452 | 0.2 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 65.7824 | 17.9618 | 427490.1348 | 35.6242 | 35.6242 | 95.2852 | 0.3 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 67.3628 | 19.5422 | 465103.3022 | 38.7586 | 38.7586 | 98.3251 | 0.4 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 68.9432 | 21.1225 | 502716.4696 | 41.893 | 41.893 | 101.365 | 0.5 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 70.5236 | 22.7029 | 540329.637 | 45.0275 | 45.0275 | 104.405 | 0.6 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 72.1039 | 24.2833 | 577942.8044 | 48.1619 | 48.1619 | 107.4449 | 0.7 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 73.6843 | 25.8637 | 615555.9718 | 51.2963 | 51.2963 | 110.4848 | 0.8 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 75.2647 | 27.4441 | 653169.1392 | 54.4308 | 54.4308 | 113.5248 | 0.9 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 76.8451 | 29.0245 | 690782.3066 | 57.5652 | 57.5652 | 116.5647 | 1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 78.4255 | 30.6049 | 728395.474 | 60.6996 | 60.6996 | 119.6046 | 75 | 65 | 29.9539 | 30 | 63
6/10/20XX 4:00:00 PM | 0.66667 | 7 | 73.9 | 61.8 | 75.1356 | 87.9141 | 12.7785 | 60 | 73.9 |  | 73.9 | 77.4358 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 64.103 | 16.2824 | 387521.4215 | 32.2935 | 32.2935 | 92.112 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 65.5845 | 17.7638 | 422779.043 | 35.2316 | 35.2316 | 95.0186 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 67.0659 | 19.2452 | 458036.6645 | 38.1697 | 38.1697 | 97.9252 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 68.5473 | 20.7267 | 493294.286 | 41.1079 | 41.1079 | 100.8319 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 70.0287 | 22.2081 | 528551.9075 | 44.046 | 44.046 | 103.7385 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 71.5101 | 23.6895 | 563809.529 | 46.9841 | 46.9841 | 106.6451 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 72.9915 | 25.1709 | 599067.1505 | 49.9223 | 49.9223 | 109.5518 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 74.4729 | 26.6523 | 634324.772 | 52.8604 | 52.8604 | 112.4584 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 75.9543 | 28.1337 | 669582.3935 | 55.7985 | 55.7985 | 115.365 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 77.4358 | 29.6151 | 704840.015 | 58.7367 | 58.7367 | 118.2717 | 75 | 60 | 29.8481 | 30 | 61.8
6/10/20XX 5:00:00 PM | 0.70833 | 7 | 73.6 | 62.3 | 74.3617 | 87.0056 | 12.6439 | 60 | 73.6 |  | 73.6 | 77.2698 | 0.1 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 64.0864 | 16.2658 | 387126.3683 | 32.2605 | 32.2605 | 91.9845 | 0.2 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 65.5513 | 17.7306 | 421988.9366 | 35.1657 | 35.1657 | 94.7637 | 0.3 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 67.0161 | 19.1954 | 456851.505 | 38.071 | 38.071 | 97.543 | 0.4 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 68.4809 | 20.6603 | 491714.0733 | 40.9762 | 40.9762 | 100.3222 | 0.5 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 69.9457 | 22.1251 | 526576.6416 | 43.8814 | 43.8814 | 103.1014 | 0.6 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 71.4105 | 23.5899 | 561439.2099 | 46.7866 | 46.7866 | 105.8806 | 0.7 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 72.8753 | 25.0547 | 596301.7782 | 49.6918 | 49.6918 | 108.6598 | 0.8 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 74.3401 | 26.5195 | 631164.3466 | 52.597 | 52.597 | 111.439 | 0.9 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 75.805 | 27.9843 | 666026.9149 | 55.5022 | 55.5022 | 114.2182 | 1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 77.2698 | 29.4491 | 700889.4832 | 58.4075 | 58.4075 | 116.9975 | 75 | 60 | 29.7487 | 30 | 62.3
6/10/20XX 6:00:00 PM | 0.75 | 7 | 72.5 | 65.8 | 71.5821 | 83.7428 | 12.1608 | 60 | 72.5 |  | 72.5 | 78.6353 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 64.223 | 16.4024 | 390376.3461 | 32.5314 | 32.5314 | 91.9089 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 65.8244 | 18.0037 | 428488.8921 | 35.7074 | 35.7074 | 94.6124 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 67.4257 | 19.6051 | 466601.4382 | 38.8835 | 38.8835 | 97.316 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 69.0271 | 21.2065 | 504713.9843 | 42.0595 | 42.0595 | 100.0195 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 70.6285 | 22.8078 | 542826.5303 | 45.2355 | 45.2355 | 102.723 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 72.2298 | 24.4092 | 580939.0764 | 48.4116 | 48.4116 | 105.4266 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 73.8312 | 26.0106 | 619051.6225 | 51.5876 | 51.5876 | 108.1301 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 75.4326 | 27.6119 | 657164.1685 | 54.7637 | 54.7637 | 110.8337 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 77.0339 | 29.2133 | 695276.7146 | 57.9397 | 57.9397 | 113.5372 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 78.6353 | 30.8147 | 733389.2607 | 61.1158 | 61.1158 | 116.2408 | 70 | 65 | 29.6928 | 30 | 65.8
6/10/20XX 7:00:00 PM | 0.79167 | 7 | 71.8 | 67.9 | 69.8602 | 81.7218 | 11.8616 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/10/20XX 8:00:00 PM | 0.83333 | 7 | 70.8 | 67.4 | 67.4628 | 78.908 | 11.4452 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/10/20XX 9:00:00 PM | 0.875 | 7 | 69.9 | 67 | 65.3666 | 76.4479 | 11.0813 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/10/20XX 10:00:00 PM | 0.91667 | 7 | 69.1 | 69.4 | 63.5515 | 74.3178 | 10.7663 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/10/20XX 11:00:00 PM | 0.95833 | 7 | 68.3 | 70.1 | 72.24 | 82.7647 | 10.5247 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/10/20XX 12:00:00 AM | 0 | 1 | 67.4 | 73.2 | 69.964 | 80.1508 | 10.1867 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/11/20XX 1:00:00 AM | 0.041667 | 1 | 66.7 | 74.8 | 68.238 | 78.1688 | 9.9308 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/11/20XX 2:00:00 AM | 0.083333 | 1 | 65.8 | 75.6 | 66.0748 | 75.6853 | 9.6105 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/11/20XX 3:00:00 AM | 0.125 | 1 | 65.1 | 78.8 | 64.435 | 73.8031 | 9.3681 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/11/20XX 4:00:00 AM | 0.16667 | 1 | 64.8 | 80.3 | 73.0095 | 82.2552 | 9.2457 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/11/20XX 5:00:00 AM | 0.20833 | 1 | 64.4 | 82.6 | 71.9634 | 81.0729 | 9.1095 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/11/20XX 6:00:00 AM | 0.25 | 1 | 65.7 | 80.3 | 75.4138 | 84.9729 | 9.5591 | 80 | 65.7 |  | 65.7 | 75.7006 | 0.1 | 73.17 | 18.17 | 686826 | 57.2355 | 57.2355 | 63.9295 | 16.1089 | 383391.6417 | 31.9493 | 31.9493 | 89.1848 | 0.2 | 72.34 | 17.34 | 655452 | 54.621 | 54.621 | 65.2374 | 17.4168 | 414519.4834 | 34.5433 | 34.5433 | 89.1643 | 0.3 | 71.51 | 16.51 | 624078 | 52.0065 | 52.0065 | 66.5453 | 18.7247 | 445647.3251 | 37.1373 | 37.1373 | 89.1438 | 0.4 | 70.68 | 15.68 | 592704 | 49.392 | 49.392 | 67.8532 | 20.0326 | 476775.1668 | 39.7313 | 39.7313 | 89.1233 | 0.5 | 69.85 | 14.85 | 561330 | 46.7775 | 46.7775 | 69.1611 | 21.3405 | 507903.0085 | 42.3253 | 42.3253 | 89.1028 | 0.6 | 69.02 | 14.02 | 529956 | 44.163 | 44.163 | 70.469 | 22.6484 | 539030.8502 | 44.9192 | 44.9192 | 89.0822 | 0.7 | 68.19 | 13.19 | 498582 | 41.5485 | 41.5485 | 71.7769 | 23.9562 | 570158.6919 | 47.5132 | 47.5132 | 89.0617 | 0.8 | 67.36 | 12.36 | 467208 | 38.934 | 38.934 | 73.0848 | 25.2641 | 601286.5336 | 50.1072 | 50.1072 | 89.0412 | 0.9 | 66.53 | 11.53 | 435834 | 36.3195 | 36.3195 | 74.3927 | 26.572 | 632414.3753 | 52.7012 | 52.7012 | 89.0207 | 1 | 65.7 | 10.7 | 404460 | 33.705 | 33.705 | 75.7006 | 27.8799 | 663542.217 | 55.2952 | 55.2952 | 89.0002 | 65 | 80 | 27.5693 | 28 | 80.3
6/11/20XX 7:00:00 AM | 0.29167 | 1 | 66.8 | 77.5 | 68.4823 | 78.4493 | 9.967 | 70 | 66.8 |  | 66.8 | 75.9575 | 0.1 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 63.9552 | 16.1346 | 384003.1799 | 32.0003 | 32.0003 | 89.5823 | 0.2 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 65.2888 | 17.4682 | 415742.5598 | 34.6452 | 34.6452 | 89.9592 | 0.3 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 66.6224 | 18.8018 | 447481.9397 | 37.2902 | 37.2902 | 90.3362 | 0.4 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 67.956 | 20.1353 | 479221.3196 | 39.9351 | 39.9351 | 90.7131 | 0.5 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 69.2896 | 21.4689 | 510960.6995 | 42.5801 | 42.5801 | 91.0901 | 0.6 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 70.6232 | 22.8025 | 542700.0794 | 45.225 | 45.225 | 91.467 | 0.7 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 71.9567 | 24.1361 | 574439.4593 | 47.87 | 47.87 | 91.844 | 0.8 | 68.24 | 13.24 | 500472 | 41.706 | 41.706 | 73.2903 | 25.4697 | 606178.8392 | 50.5149 | 50.5149 | 92.2209 | 0.9 | 67.52 | 12.52 | 473256 | 39.438 | 39.438 | 74.6239 | 26.8033 | 637918.2191 | 53.1599 | 53.1599 | 92.5979 | 1 | 66.8 | 11.8 | 446040 | 37.17 | 37.17 | 75.9575 | 28.1369 | 669657.599 | 55.8048 | 55.8048 | 92.9748 | 65 | 75 | 27.8787 | 28 | 77.5
6/11/20XX 8:00:00 AM | 0.33333 | 1 | 67.8 | 73.9 | 70.9676 | 81.3033 | 10.3357 | 70 | 67.8 |  | 67.8 | 74.9985 | 0.1 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 63.8593 | 16.0387 | 381720.839 | 31.8101 | 31.8101 | 89.7071 | 0.2 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 65.097 | 17.2764 | 411177.8781 | 34.2648 | 34.2648 | 90.2088 | 0.3 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 66.3347 | 18.5141 | 440634.9171 | 36.7196 | 36.7196 | 90.7106 | 0.4 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 67.5724 | 19.7518 | 470091.9562 | 39.1743 | 39.1743 | 91.2123 | 0.5 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 68.8101 | 20.9895 | 499548.9952 | 41.6291 | 41.6291 | 91.7141 | 0.6 | 70.28 | 15.28 | 577584 | 48.132 | 48.132 | 70.0478 | 22.2271 | 529006.0342 | 44.0838 | 44.0838 | 92.2158 | 0.7 | 69.66 | 14.66 | 554148 | 46.179 | 46.179 | 71.2855 | 23.4648 | 558463.0733 | 46.5386 | 46.5386 | 92.7176 | 0.8 | 69.04 | 14.04 | 530712 | 44.226 | 44.226 | 72.5232 | 24.7025 | 587920.1123 | 48.9933 | 48.9933 | 93.2193 | 0.9 | 68.42 | 13.42 | 507276 | 42.273 | 42.273 | 73.7608 | 25.9402 | 617377.1514 | 51.4481 | 51.4481 | 93.7211 | 1 | 67.8 | 12.8 | 483840 | 40.32 | 40.32 | 74.9985 | 27.1779 | 646834.1904 | 53.9028 | 53.9028 | 94.2228 | 70 | 75 | 27.9739 | 28 | 73.9
6/11/20XX 9:00:00 AM | 0.375 | 1 | 68.7 | 72.1 | 73.2724 | 83.9506 | 10.6782 | 70 | 68.7 |  | 68.7 | 75.5149 | 0.1 | 73.47 | 18.47 | 698166 | 58.1805 | 58.1805 | 63.911 | 16.0903 | 382949.6872 | 31.9125 | 31.9125 | 90.093 | 0.2 | 72.94 | 17.94 | 678132 | 56.511 | 56.511 | 65.2003 | 17.3796 | 413635.5744 | 34.4696 | 34.4696 | 90.9806 | 0.3 | 72.41 | 17.41 | 658098 | 54.8415 | 54.8415 | 66.4896 | 18.669 | 444321.4616 | 37.0268 | 37.0268 | 91.8683 | 0.4 | 71.88 | 16.88 | 638064 | 53.172 | 53.172 | 67.7789 | 19.9583 | 475007.3488 | 39.5839 | 39.5839 | 92.7559 | 0.5 | 71.35 | 16.35 | 618030 | 51.5025 | 51.5025 | 69.0682 | 21.2476 | 505693.2361 | 42.1411 | 42.1411 | 93.6436 | 0.6 | 70.82 | 15.82 | 597996 | 49.833 | 49.833 | 70.3576 | 22.5369 | 536379.1233 | 44.6983 | 44.6983 | 94.5313 | 0.7 | 70.29 | 15.29 | 577962 | 48.1635 | 48.1635 | 71.6469 | 23.8263 | 567065.0105 | 47.2554 | 47.2554 | 95.4189 | 0.8 | 69.76 | 14.76 | 557928 | 46.494 | 46.494 | 72.9362 | 25.1156 | 597750.8977 | 49.8126 | 49.8126 | 96.3066 | 0.9 | 69.23 | 14.23 | 537894 | 44.8245 | 44.8245 | 74.2255 | 26.4049 | 628436.7849 | 52.3697 | 52.3697 | 97.1942 | 1 | 68.7 | 13.7 | 517860 | 43.155 | 43.155 | 75.5149 | 27.6942 | 659122.6721 | 54.9269 | 54.9269 | 98.0819 | 70 | 70 | 28.2747 | 28 | 72.1
6/11/20XX 10:00:00 AM | 0.41667 | 1 | 70.4 | 68.9 | 66.524 | 77.8062 | 11.2822 | 60 | 70.4 |  | 70.4 | 76.5652 | 0.1 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 64.016 | 16.1954 | 385449.4835 | 32.1208 | 32.1208 | 90.8368 | 0.2 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 65.4103 | 17.5897 | 418635.1669 | 34.8863 | 34.8863 | 92.4683 | 0.3 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 66.8047 | 18.9841 | 451820.8504 | 37.6517 | 37.6517 | 94.0997 | 0.4 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 68.1991 | 20.3784 | 485006.5339 | 40.4172 | 40.4172 | 95.7312 | 0.5 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 69.5934 | 21.7728 | 518192.2173 | 43.1827 | 43.1827 | 97.3627 | 0.6 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 70.9878 | 23.1671 | 551377.9008 | 45.9482 | 45.9482 | 98.9942 | 0.7 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 72.3821 | 24.5615 | 584563.5842 | 48.7136 | 48.7136 | 100.6256 | 0.8 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 73.7765 | 25.9559 | 617749.2677 | 51.4791 | 51.4791 | 102.2571 | 0.9 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 75.1708 | 27.3502 | 650934.9512 | 54.2446 | 54.2446 | 103.8886 | 1 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 76.5652 | 28.7446 | 684120.6346 | 57.0101 | 57.0101 | 105.5201 | 70 | 70 | 28.8549 | 28 | 68.9
6/11/20XX 11:00:00 AM | 0.45833 | 1 | 72 | 65.6 | 70.3485 | 82.2949 | 11.9464 | 60 | 72 |  | 72 | 77.0385 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.0633 | 16.2427 | 386575.9275 | 32.2147 | 32.2147 | 91.4347 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 65.505 | 17.6844 | 420888.055 | 35.074 | 35.074 | 93.664 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 66.9467 | 19.1261 | 455200.1825 | 37.9333 | 37.9333 | 95.8933 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 68.3884 | 20.5677 | 489512.31 | 40.7927 | 40.7927 | 98.1227 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 69.8301 | 22.0094 | 523824.4375 | 43.652 | 43.652 | 100.352 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 71.2717 | 23.4511 | 558136.565 | 46.5114 | 46.5114 | 102.5814 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 72.7134 | 24.8928 | 592448.6925 | 49.3707 | 49.3707 | 104.8107 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 74.1551 | 26.3345 | 626760.82 | 52.2301 | 52.2301 | 107.0401 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 75.5968 | 27.7762 | 661072.9475 | 55.0894 | 55.0894 | 109.2694 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 77.0385 | 29.2179 | 695385.075 | 57.9488 | 57.9488 | 111.4988 | 70 | 65 | 29.3207 | 30 | 65.6
6/11/20XX 12:00:00 PM | 0.5 | 1 | 73.6 | 61.7 | 74.3617 | 87.0056 | 12.6439 | 60 | 73.6 |  | 73.6 | 76.5111 | 0.1 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 64.0106 | 16.19 | 385320.8196 | 32.1101 | 32.1101 | 91.8341 | 0.2 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 65.3995 | 17.5789 | 418377.8391 | 34.8648 | 34.8648 | 94.4628 | 0.3 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 66.7885 | 18.9679 | 451434.8587 | 37.6196 | 37.6196 | 97.0916 | 0.4 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 68.1774 | 20.3568 | 484491.8783 | 40.3743 | 40.3743 | 99.7203 | 0.5 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 69.5664 | 21.7458 | 517548.8978 | 43.1291 | 43.1291 | 102.3491 | 0.6 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 70.9553 | 23.1347 | 550605.9174 | 45.8838 | 45.8838 | 104.9778 | 0.7 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 72.3443 | 24.5237 | 583662.937 | 48.6386 | 48.6386 | 107.6066 | 0.8 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 73.7332 | 25.9126 | 616719.9565 | 51.3933 | 51.3933 | 110.2353 | 0.9 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 75.1222 | 27.3016 | 649776.9761 | 54.1481 | 54.1481 | 112.8641 | 1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 76.5111 | 28.6905 | 682833.9957 | 56.9028 | 56.9028 | 115.4928 | 75 | 60 | 29.63 | 30 | 61.7
6/11/20XX 1:00:00 PM | 0.54167 | 1 | 73.8 | 61.6 | 74.8769 | 87.6104 | 12.7335 | 60 | 73.8 |  | 73.8 | 76.9142 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 64.0509 | 16.2303 | 386280.2099 | 32.19 | 32.19 | 91.977 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 65.4802 | 17.6595 | 420296.6198 | 35.0247 | 35.0247 | 94.7487 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 66.9094 | 19.0888 | 454313.0297 | 37.8594 | 37.8594 | 97.5204 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 68.3387 | 20.518 | 488329.4396 | 40.6941 | 40.6941 | 100.2921 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 69.7679 | 21.9473 | 522345.8495 | 43.5288 | 43.5288 | 103.0638 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 71.1972 | 23.3766 | 556362.2594 | 46.3635 | 46.3635 | 105.8355 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 72.6265 | 24.8058 | 590378.6693 | 49.1982 | 49.1982 | 108.6072 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 74.0557 | 26.2351 | 624395.0791 | 52.0329 | 52.0329 | 111.3789 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 75.485 | 27.6643 | 658411.489 | 54.8676 | 54.8676 | 114.1506 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 76.9142 | 29.0936 | 692427.8989 | 57.7023 | 57.7023 | 116.9223 | 75 | 60 | 29.7421 | 30 | 61.6
6/11/20XX 2:00:00 PM | 0.58333 | 1 | 74.2 | 62.6 | 75.9165 | 88.8307 | 12.9142 | 60 | 74.2 |  | 74.2 | 79.2742 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 64.2869 | 16.4663 | 391896.8642 | 32.6581 | 32.6581 | 92.5711 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 65.9521 | 18.1315 | 431529.9284 | 35.9608 | 35.9608 | 95.9368 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 67.6174 | 19.7968 | 471162.9927 | 39.2636 | 39.2636 | 99.3026 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 69.2827 | 21.462 | 510796.0569 | 42.5663 | 42.5663 | 102.6683 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 70.9479 | 23.1273 | 550429.1211 | 45.8691 | 45.8691 | 106.0341 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 72.6132 | 24.7925 | 590062.1853 | 49.1718 | 49.1718 | 109.3998 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 74.2784 | 26.4578 | 629695.2496 | 52.4746 | 52.4746 | 112.7656 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 75.9437 | 28.123 | 669328.3138 | 55.7774 | 55.7774 | 116.1314 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 77.6089 | 29.7883 | 708961.378 | 59.0801 | 59.0801 | 119.4971 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 79.2742 | 31.4535 | 748594.4422 | 62.3829 | 62.3829 | 122.8629 | 75 | 65 | 30.2092 | 30 | 62.6
6/11/20XX 3:00:00 PM | 0.625 | 1 | 73.6 | 64.4 | 74.3617 | 87.0056 | 12.6439 | 60 | 73.6 |  | 73.6 | 79.925 | 0.1 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 64.352 | 16.5313 | 393445.789 | 32.7871 | 32.7871 | 92.5111 | 0.2 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 66.0823 | 18.2617 | 434627.7779 | 36.219 | 36.219 | 95.817 | 0.3 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 67.8126 | 19.992 | 475809.7669 | 39.6508 | 39.6508 | 99.1228 | 0.4 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 69.543 | 21.7223 | 516991.7558 | 43.0826 | 43.0826 | 102.4286 | 0.5 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 71.2733 | 23.4527 | 558173.7448 | 46.5145 | 46.5145 | 105.7345 | 0.6 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 73.0036 | 25.183 | 599355.7337 | 49.9463 | 49.9463 | 109.0403 | 0.7 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 74.734 | 26.9133 | 640537.7227 | 53.3781 | 53.3781 | 112.3461 | 0.8 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 76.4643 | 28.6437 | 681719.7116 | 56.81 | 56.81 | 115.652 | 0.9 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 78.1947 | 30.374 | 722901.7006 | 60.2418 | 60.2418 | 118.9578 | 1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 79.925 | 32.1044 | 764083.6895 | 63.6736 | 63.6736 | 122.2636 | 75 | 65 | 30.1639 | 30 | 64.4
6/11/20XX 4:00:00 PM | 0.66667 | 1 | 74.1 | 63.1 | 75.6554 | 88.5243 | 12.8688 | 60 | 74.1 |  | 74.1 | 79.6448 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 64.3239 | 16.5033 | 392778.8711 | 32.7316 | 32.7316 | 92.6131 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 66.0263 | 18.2056 | 433293.9422 | 36.1078 | 36.1078 | 96.0208 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 67.7286 | 19.9079 | 473809.0133 | 39.4841 | 39.4841 | 99.4286 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 69.4309 | 21.6103 | 514324.0844 | 42.8603 | 42.8603 | 102.8363 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 71.1332 | 23.3126 | 554839.1555 | 46.2366 | 46.2366 | 106.2441 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 72.8355 | 25.0149 | 595354.2266 | 49.6129 | 49.6129 | 109.6519 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 74.5378 | 26.7172 | 635869.2977 | 52.9891 | 52.9891 | 113.0596 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 76.2401 | 28.4195 | 676384.3688 | 56.3654 | 56.3654 | 116.4674 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 77.9425 | 30.1218 | 716899.4399 | 59.7416 | 59.7416 | 119.8751 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 79.6448 | 31.8241 | 757414.511 | 63.1179 | 63.1179 | 123.2829 | 75 | 65 | 30.2427 | 30 | 63.1
6/11/20XX 5:00:00 PM | 0.70833 | 1 | 73.8 | 63.7 | 74.8769 | 87.6104 | 12.7335 | 60 | 73.8 |  | 73.8 | 79.5883 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 64.3183 | 16.4977 | 392644.3975 | 32.7204 | 32.7204 | 92.5074 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 66.015 | 18.1943 | 433024.9951 | 36.0854 | 36.0854 | 95.8094 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 67.7116 | 19.891 | 473405.5926 | 39.4505 | 39.4505 | 99.1115 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 69.4083 | 21.5877 | 513786.1902 | 42.8155 | 42.8155 | 102.4135 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 71.105 | 23.2843 | 554166.7877 | 46.1806 | 46.1806 | 105.7156 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 72.8016 | 24.981 | 594547.3852 | 49.5456 | 49.5456 | 109.0176 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 74.4983 | 26.6776 | 634927.9828 | 52.9107 | 52.9107 | 112.3197 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 76.1949 | 28.3743 | 675308.5803 | 56.2757 | 56.2757 | 115.6217 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 77.8916 | 30.071 | 715689.1778 | 59.6408 | 59.6408 | 118.9238 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 79.5883 | 31.7676 | 756069.7754 | 63.0058 | 63.0058 | 122.2258 | 75 | 65 | 30.1603 | 30 | 63.7
6/11/20XX 6:00:00 PM | 0.75 | 1 | 73 | 63.4 | 72.8342 | 85.2126 | 12.3784 | 60 | 73 |  | 73 | 77.0429 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.0638 | 16.2431 | 386586.3923 | 32.2155 | 32.2155 | 91.7505 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 65.5059 | 17.6853 | 420908.9845 | 35.0757 | 35.0757 | 94.2957 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 66.948 | 19.1274 | 455231.5768 | 37.936 | 37.936 | 96.841 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 68.3901 | 20.5695 | 489554.1691 | 40.7962 | 40.7962 | 99.3862 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 69.8323 | 22.0116 | 523876.7613 | 43.6564 | 43.6564 | 101.9314 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 71.2744 | 23.4538 | 558199.3536 | 46.5166 | 46.5166 | 104.4766 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 72.7165 | 24.8959 | 592521.9459 | 49.3768 | 49.3768 | 107.0218 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 74.1586 | 26.338 | 626844.5382 | 52.237 | 52.237 | 109.567 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 75.6008 | 27.7801 | 661167.1304 | 55.0973 | 55.0973 | 112.1123 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 77.0429 | 29.2223 | 695489.7227 | 57.9575 | 57.9575 | 114.6575 | 75 | 65 | 29.5663 | 30 | 63.4
6/11/20XX 7:00:00 PM | 0.79167 | 1 | 72.2 | 65.2 | 70.8397 | 82.8715 | 12.0318 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/11/20XX 8:00:00 PM | 0.83333 | 1 | 71 | 67.7 | 67.9365 | 79.4639 | 11.5275 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/11/20XX 9:00:00 PM | 0.875 | 1 | 70.4 | 69.7 | 66.524 | 77.8062 | 11.2822 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/11/20XX 10:00:00 PM | 0.91667 | 1 | 69.8 | 71.1 | 76.1788 | 87.2896 | 11.1108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/11/20XX 11:00:00 PM | 0.95833 | 1 | 68.6 | 73.2 | 73.0131 | 83.6528 | 10.6396 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/11/20XX 12:00:00 AM | 0 | 2 | 68.4 | 74 | 72.4969 | 83.0598 | 10.5629 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/12/20XX 1:00:00 AM | 0.041667 | 2 | 67.8 | 74.5 | 70.9676 | 81.3033 | 10.3357 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/12/20XX 2:00:00 AM | 0.083333 | 2 | 67.4 | 77.4 | 69.964 | 80.1508 | 10.1867 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/12/20XX 3:00:00 AM | 0.125 | 2 | 67.1 | 77.4 | 69.2196 | 79.2959 | 10.0763 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/12/20XX 4:00:00 AM | 0.16667 | 2 | 66.6 | 77.2 | 67.9946 | 77.8893 | 9.8947 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/12/20XX 5:00:00 AM | 0.20833 | 2 | 66.3 | 75.5 | 67.2689 | 77.0561 | 9.7873 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/12/20XX 6:00:00 AM | 0.25 | 2 | 67 | 75.7 | 68.973 | 79.0128 | 10.0398 | 70 | 67 |  | 67 | 74.6957 | 0.1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 63.829 | 16.0084 | 381000.0864 | 31.75 | 31.75 | 89.395 | 0.2 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 65.0364 | 17.2158 | 409736.3728 | 34.1447 | 34.1447 | 89.5847 | 0.3 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 66.2439 | 18.4232 | 438472.6592 | 36.5394 | 36.5394 | 89.7744 | 0.4 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 67.4513 | 19.6306 | 467208.9455 | 38.9341 | 38.9341 | 89.9641 | 0.5 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 68.6587 | 20.838 | 495945.2319 | 41.3288 | 41.3288 | 90.1538 | 0.6 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 69.8661 | 22.0454 | 524681.5183 | 43.7235 | 43.7235 | 90.3435 | 0.7 | 69.1 | 14.1 | 532980 | 44.415 | 44.415 | 71.0735 | 23.2528 | 553417.8047 | 46.1182 | 46.1182 | 90.5332 | 0.8 | 68.4 | 13.4 | 506520 | 42.21 | 42.21 | 72.2809 | 24.4603 | 582154.0911 | 48.5128 | 48.5128 | 90.7228 | 0.9 | 67.7 | 12.7 | 480060 | 40.005 | 40.005 | 73.4883 | 25.6677 | 610890.3775 | 50.9075 | 50.9075 | 90.9125 | 1 | 67 | 12 | 453600 | 37.8 | 37.8 | 74.6957 | 26.8751 | 639626.6639 | 53.3022 | 53.3022 | 91.1022 | 65 | 75 | 27.7308 | 28 | 75.7
6/12/20XX 7:00:00 AM | 0.29167 | 2 | 67.5 | 74.6 | 70.2137 | 80.4375 | 10.2238 | 70 | 67.5 |  | 67.5 | 74.9167 | 0.1 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 63.8511 | 16.0305 | 381525.9958 | 31.7938 | 31.7938 | 89.5963 | 0.2 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 65.0806 | 17.26 | 410788.1916 | 34.2323 | 34.2323 | 89.9873 | 0.3 | 72.05 | 17.05 | 644490 | 53.7075 | 53.7075 | 66.3101 | 18.4895 | 440050.3874 | 36.6709 | 36.6709 | 90.3784 | 0.4 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 67.5396 | 19.719 | 469312.5832 | 39.1094 | 39.1094 | 90.7694 | 0.5 | 70.75 | 15.75 | 595350 | 49.6125 | 49.6125 | 68.7692 | 20.9485 | 498574.779 | 41.5479 | 41.5479 | 91.1604 | 0.6 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 69.9987 | 22.178 | 527836.9748 | 43.9864 | 43.9864 | 91.5514 | 0.7 | 69.45 | 14.45 | 546210 | 45.5175 | 45.5175 | 71.2282 | 23.4075 | 557099.1706 | 46.4249 | 46.4249 | 91.9424 | 0.8 | 68.8 | 13.8 | 521640 | 43.47 | 43.47 | 72.4577 | 24.637 | 586361.3664 | 48.8634 | 48.8634 | 92.3334 | 0.9 | 68.15 | 13.15 | 497070 | 41.4225 | 41.4225 | 73.6872 | 25.8665 | 615623.5622 | 51.302 | 51.302 | 92.7245 | 1 | 67.5 | 12.5 | 472500 | 39.375 | 39.375 | 74.9167 | 27.096 | 644885.758 | 53.7405 | 53.7405 | 93.1155 | 65 | 75 | 27.8877 | 28 | 74.6
6/12/20XX 8:00:00 AM | 0.33333 | 2 | 69.1 | 70.5 | 74.3178 | 85.1515 | 10.8337 | 70 | 69.1 |  | 69.1 | 74.8595 | 0.1 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 63.8454 | 16.0248 | 381389.9449 | 31.7825 | 31.7825 | 90.089 | 0.2 | 73.02 | 18.02 | 681156 | 56.763 | 56.763 | 65.0692 | 17.2486 | 410516.0898 | 34.2097 | 34.2097 | 90.9727 | 0.3 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 66.293 | 18.4724 | 439642.2347 | 36.6369 | 36.6369 | 91.8564 | 0.4 | 72.04 | 17.04 | 644112 | 53.676 | 53.676 | 67.5168 | 19.6962 | 468768.3796 | 39.064 | 39.064 | 92.74 | 0.5 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 68.7406 | 20.9199 | 497894.5245 | 41.4912 | 41.4912 | 93.6237 | 0.6 | 71.06 | 16.06 | 607068 | 50.589 | 50.589 | 69.9644 | 22.1437 | 527020.6694 | 43.9184 | 43.9184 | 94.5074 | 0.7 | 70.57 | 15.57 | 588546 | 49.0455 | 49.0455 | 71.1881 | 23.3675 | 556146.8143 | 46.3456 | 46.3456 | 95.3911 | 0.8 | 70.08 | 15.08 | 570024 | 47.502 | 47.502 | 72.4119 | 24.5913 | 585272.9592 | 48.7727 | 48.7727 | 96.2747 | 0.9 | 69.59 | 14.59 | 551502 | 45.9585 | 45.9585 | 73.6357 | 25.8151 | 614399.1041 | 51.1999 | 51.1999 | 97.1584 | 1 | 69.1 | 14.1 | 532980 | 44.415 | 44.415 | 74.8595 | 27.0389 | 643525.249 | 53.6271 | 53.6271 | 98.0421 | 70 | 70 | 28.2703 | 28 | 70.5
6/12/20XX 9:00:00 AM | 0.375 | 2 | 70.7 | 67.3 | 67.227 | 78.6313 | 11.4043 | 60 | 70.7 |  | 70.7 | 75.5521 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 63.9147 | 16.094 | 383038.3776 | 31.9199 | 31.9199 | 90.7304 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 65.2077 | 17.3871 | 413812.9551 | 34.4844 | 34.4844 | 92.2554 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 66.5008 | 18.6801 | 444587.5327 | 37.049 | 37.049 | 93.7805 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 67.7938 | 19.9732 | 475362.1103 | 39.6135 | 39.6135 | 95.3055 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 69.0869 | 21.2662 | 506136.6879 | 42.1781 | 42.1781 | 96.8306 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 70.3799 | 22.5593 | 536911.2654 | 44.7426 | 44.7426 | 98.3556 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 71.673 | 23.8523 | 567685.843 | 47.3072 | 47.3072 | 99.8807 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 72.966 | 25.1454 | 598460.4206 | 49.8717 | 49.8717 | 101.4057 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 74.2591 | 26.4384 | 629234.9982 | 52.4362 | 52.4362 | 102.9307 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 75.5521 | 27.7315 | 660009.5757 | 55.0008 | 55.0008 | 104.4558 | 70 | 65 | 28.7701 | 28 | 67.3
6/12/20XX 10:00:00 AM | 0.41667 | 2 | 72.5 | 63.5 | 71.5821 | 83.7428 | 12.1608 | 60 | 72.5 |  | 72.5 | 75.8383 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 63.9433 | 16.1227 | 383719.5349 | 31.9766 | 31.9766 | 91.3541 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 65.265 | 17.4443 | 415175.2699 | 34.5979 | 34.5979 | 93.5029 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 66.5866 | 18.766 | 446631.0048 | 37.2193 | 37.2193 | 95.6518 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 67.9083 | 20.0877 | 478086.7397 | 39.8406 | 39.8406 | 97.8006 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 69.23 | 21.4093 | 509542.4746 | 42.4619 | 42.4619 | 99.9494 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 70.5516 | 22.731 | 540998.2096 | 45.0832 | 45.0832 | 102.0982 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 71.8733 | 24.0527 | 572453.9445 | 47.7045 | 47.7045 | 104.247 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 73.195 | 25.3744 | 603909.6794 | 50.3258 | 50.3258 | 106.3958 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 74.5167 | 26.696 | 635365.4143 | 52.9471 | 52.9471 | 108.5446 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 75.8383 | 28.0177 | 666821.1493 | 55.5684 | 55.5684 | 110.6934 | 70 | 65 | 29.2555 | 30 | 63.5
6/12/20XX 11:00:00 AM | 0.45833 | 2 | 74 | 59.7 | 62.6216 | 75.3952 | 12.7735 | 50 | 74 |  | 74 | 75.0119 | 0.1 | 74 | 19 | 718200 | 59.85 | 59.85 | 63.8607 | 16.04 | 381752.7483 | 31.8127 | 31.8127 | 91.6627 | 0.2 | 74 | 19 | 718200 | 59.85 | 59.85 | 65.0997 | 17.2791 | 411241.6965 | 34.2701 | 34.2701 | 94.1201 | 0.3 | 74 | 19 | 718200 | 59.85 | 59.85 | 66.3387 | 18.5181 | 440730.6448 | 36.7276 | 36.7276 | 96.5776 | 0.4 | 74 | 19 | 718200 | 59.85 | 59.85 | 67.5778 | 19.7571 | 470219.5931 | 39.185 | 39.185 | 99.035 | 0.5 | 74 | 19 | 718200 | 59.85 | 59.85 | 68.8168 | 20.9962 | 499708.5414 | 41.6424 | 41.6424 | 101.4924 | 0.6 | 74 | 19 | 718200 | 59.85 | 59.85 | 70.0558 | 22.2352 | 529197.4896 | 44.0998 | 44.0998 | 103.9498 | 0.7 | 74 | 19 | 718200 | 59.85 | 59.85 | 71.2949 | 23.4742 | 558686.4379 | 46.5572 | 46.5572 | 106.4072 | 0.8 | 74 | 19 | 718200 | 59.85 | 59.85 | 72.5339 | 24.7133 | 588175.3862 | 49.0146 | 49.0146 | 108.8646 | 0.9 | 74 | 19 | 718200 | 59.85 | 59.85 | 73.7729 | 25.9523 | 617664.3344 | 51.472 | 51.472 | 111.322 | 1 | 74 | 19 | 718200 | 59.85 | 59.85 | 75.0119 | 27.1913 | 647153.2827 | 53.9294 | 53.9294 | 113.7794 | 75 | 60 | 29.4935 | 30 | 59.7
6/12/20XX 12:00:00 PM | 0.5 | 2 | 75.2 | 59.4 | 65.252 | 78.5695 | 13.3175 | 50 | 75.2 |  | 75.2 | 77.7705 | 0.1 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 64.1365 | 16.3159 | 388317.99 | 32.3598 | 32.3598 | 92.5878 | 0.2 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 65.6514 | 17.8308 | 424372.1799 | 35.3643 | 35.3643 | 95.9703 | 0.3 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 67.1663 | 19.3456 | 460426.3699 | 38.3689 | 38.3689 | 99.3529 | 0.4 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 68.6812 | 20.8605 | 496480.5598 | 41.3734 | 41.3734 | 102.7354 | 0.5 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 70.196 | 22.3754 | 532534.7498 | 44.3779 | 44.3779 | 106.1179 | 0.6 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 71.7109 | 23.8903 | 568588.9398 | 47.3824 | 47.3824 | 109.5004 | 0.7 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 73.2258 | 25.4052 | 604643.1297 | 50.3869 | 50.3869 | 112.8829 | 0.8 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 74.7407 | 26.9201 | 640697.3197 | 53.3914 | 53.3914 | 116.2654 | 0.9 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 76.2556 | 28.4349 | 676751.5096 | 56.396 | 56.396 | 119.648 | 1 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 77.7705 | 29.9498 | 712805.6996 | 59.4005 | 59.4005 | 123.0305 | 75 | 60 | 30.2189 | 30 | 59.4
6/12/20XX 1:00:00 PM | 0.54167 | 2 | 76.2 | 59.6 | 67.5149 | 81.3009 | 13.786 | 50 | 76.2 |  | 76.2 | 80.7494 | 0.1 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 64.4344 | 16.6138 | 395407.949 | 32.9507 | 32.9507 | 93.4937 | 0.2 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 66.2472 | 18.4266 | 438552.098 | 36.546 | 36.546 | 97.782 | 0.3 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 68.06 | 20.2393 | 481696.2469 | 40.1414 | 40.1414 | 102.0704 | 0.4 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 69.8727 | 22.0521 | 524840.3959 | 43.7367 | 43.7367 | 106.3587 | 0.5 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 71.6855 | 23.8649 | 567984.5449 | 47.332 | 47.332 | 110.647 | 0.6 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 73.4983 | 25.6777 | 611128.6939 | 50.9274 | 50.9274 | 114.9354 | 0.7 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 75.3111 | 27.4905 | 654272.8429 | 54.5227 | 54.5227 | 119.2237 | 0.8 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 77.1239 | 29.3032 | 697416.9918 | 58.1181 | 58.1181 | 123.5121 | 0.9 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 78.9366 | 31.116 | 740561.1408 | 61.7134 | 61.7134 | 127.8004 | 1 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 80.7494 | 32.9288 | 783705.2898 | 65.3088 | 65.3088 | 132.0888 | 75 | 60 | 30.9302 | 30 | 59.6
6/12/20XX 2:00:00 PM | 0.58333 | 2 | 76.7 | 58.8 | 68.6709 | 82.6964 | 14.0254 | 50 | 76.7 |  | 76.7 | 81.0133 | 0.1 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 64.4608 | 16.6402 | 396036.0214 | 33.003 | 33.003 | 93.7035 | 0.2 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 66.3 | 18.4793 | 439808.2428 | 36.6507 | 36.6507 | 98.2017 | 0.3 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 68.1391 | 20.3185 | 483580.4642 | 40.2984 | 40.2984 | 102.6999 | 0.4 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 69.9783 | 22.1577 | 527352.6856 | 43.9461 | 43.9461 | 107.1981 | 0.5 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 71.8175 | 23.9968 | 571124.9069 | 47.5937 | 47.5937 | 111.6962 | 0.6 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 73.6566 | 25.836 | 614897.1283 | 51.2414 | 51.2414 | 116.1944 | 0.7 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 75.4958 | 27.6752 | 658669.3497 | 54.8891 | 54.8891 | 120.6926 | 0.8 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 77.335 | 29.5144 | 702441.5711 | 58.5368 | 58.5368 | 125.1908 | 0.9 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 79.1742 | 31.3535 | 746213.7925 | 62.1845 | 62.1845 | 129.689 | 1 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 81.0133 | 33.1927 | 789986.0139 | 65.8322 | 65.8322 | 134.1872 | 75 | 60 | 31.0941 | 32 | 58.8
6/12/20XX 3:00:00 PM | 0.625 | 2 | 76.2 | 60.2 | 81.3009 | 95.1517 | 13.8508 | 60 | 76.2 |  | 76.2 | 81.5779 | 0.1 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 64.5173 | 16.6966 | 397379.6718 | 33.115 | 33.115 | 93.658 | 0.2 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 66.4129 | 18.5922 | 442495.5436 | 36.8746 | 36.8746 | 98.1106 | 0.3 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 68.3085 | 20.4879 | 487611.4154 | 40.6343 | 40.6343 | 102.5633 | 0.4 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 70.2041 | 22.3835 | 532727.2872 | 44.3939 | 44.3939 | 107.0159 | 0.5 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 72.0998 | 24.2791 | 577843.159 | 48.1536 | 48.1536 | 111.4686 | 0.6 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 73.9954 | 26.1747 | 622959.0308 | 51.9133 | 51.9133 | 115.9213 | 0.7 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 75.891 | 28.0704 | 668074.9026 | 55.6729 | 55.6729 | 120.3739 | 0.8 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 77.7866 | 29.966 | 713190.7744 | 59.4326 | 59.4326 | 124.8266 | 0.9 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 79.6823 | 31.8616 | 758306.6461 | 63.1922 | 63.1922 | 129.2792 | 1 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 81.5779 | 33.7572 | 803422.5179 | 66.9519 | 66.9519 | 133.7319 | 75 | 60 | 31.0599 | 32 | 60.2
6/12/20XX 4:00:00 PM | 0.66667 | 2 | 76.2 | 57.9 | 67.5149 | 81.3009 | 13.786 | 50 | 76.2 |  | 76.2 | 78.4058 | 0.1 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 64.2001 | 16.3794 | 389830.1433 | 32.4858 | 32.4858 | 93.0288 | 0.2 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 65.7785 | 17.9578 | 427396.4866 | 35.6164 | 35.6164 | 96.8524 | 0.3 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 67.3569 | 19.5363 | 464962.8299 | 38.7469 | 38.7469 | 100.6759 | 0.4 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 68.9353 | 21.1147 | 502529.1732 | 41.8774 | 41.8774 | 104.4994 | 0.5 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 70.5137 | 22.6931 | 540095.5165 | 45.008 | 45.008 | 108.323 | 0.6 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 72.0921 | 24.2715 | 577661.8597 | 48.1385 | 48.1385 | 112.1465 | 0.7 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 73.6706 | 25.8499 | 615228.203 | 51.269 | 51.269 | 115.97 | 0.8 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 75.249 | 27.4283 | 652794.5463 | 54.3995 | 54.3995 | 119.7935 | 0.9 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 76.8274 | 29.0068 | 690360.8896 | 57.5301 | 57.5301 | 123.6171 | 1 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 78.4058 | 30.5852 | 727927.2329 | 60.6606 | 60.6606 | 127.4406 | 75 | 60 | 30.5633 | 30 | 57.9
6/12/20XX 5:00:00 PM | 0.70833 | 2 | 75.1 | 61.9 | 78.3007 | 91.6296 | 13.3289 | 60 | 75.1 |  | 75.1 | 80.8332 | 0.1 | 74.11 | 19.11 | 722358 | 60.1965 | 60.1965 | 64.4428 | 16.6222 | 395607.2902 | 32.9673 | 32.9673 | 93.1638 | 0.2 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 66.2639 | 18.4433 | 438950.7804 | 36.5792 | 36.5792 | 97.1222 | 0.3 | 74.33 | 19.33 | 730674 | 60.8895 | 60.8895 | 68.0851 | 20.2645 | 482294.2707 | 40.1912 | 40.1912 | 101.0807 | 0.4 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 69.9063 | 22.0856 | 525637.7609 | 43.8031 | 43.8031 | 105.0391 | 0.5 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 71.7274 | 23.9068 | 568981.2511 | 47.4151 | 47.4151 | 108.9976 | 0.6 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 73.5486 | 25.7279 | 612324.7413 | 51.0271 | 51.0271 | 112.9561 | 0.7 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 75.3697 | 27.5491 | 655668.2316 | 54.639 | 54.639 | 116.9145 | 0.8 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 77.1909 | 29.3702 | 699011.7218 | 58.251 | 58.251 | 120.873 | 0.9 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 79.012 | 31.1914 | 742355.212 | 61.8629 | 61.8629 | 124.8314 | 1 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 80.8332 | 33.0126 | 785698.7022 | 65.4749 | 65.4749 | 128.7899 | 75 | 60 | 30.6737 | 30 | 61.9
6/12/20XX 6:00:00 PM | 0.75 | 2 | 74.1 | 63.4 | 75.6554 | 88.5243 | 12.8688 | 60 | 74.1 |  | 74.1 | 80.0308 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 64.3626 | 16.5419 | 393697.7057 | 32.8081 | 32.8081 | 92.6896 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 66.1035 | 18.2828 | 435131.6114 | 36.261 | 36.261 | 96.174 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 67.8444 | 20.0238 | 476565.517 | 39.7138 | 39.7138 | 99.6583 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 69.5853 | 21.7647 | 517999.4227 | 43.1666 | 43.1666 | 103.1426 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 71.3262 | 23.5056 | 559433.3284 | 46.6194 | 46.6194 | 106.6269 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 73.0672 | 25.2465 | 600867.2341 | 50.0723 | 50.0723 | 110.1113 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 74.8081 | 26.9874 | 642301.1398 | 53.5251 | 53.5251 | 113.5956 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 76.549 | 28.7284 | 683735.0454 | 56.9779 | 56.9779 | 117.0799 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 78.2899 | 30.4693 | 725168.9511 | 60.4307 | 60.4307 | 120.5642 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 80.0308 | 32.2102 | 766602.8568 | 63.8836 | 63.8836 | 124.0486 | 75 | 65 | 30.303 | 30 | 63.4
6/12/20XX 7:00:00 PM | 0.79167 | 2 | 73.7 | 63.3 | 74.6189 | 87.3075 | 12.6886 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/12/20XX 8:00:00 PM | 0.83333 | 2 | 72.6 | 64.7 | 71.831 | 84.035 | 12.204 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/12/20XX 9:00:00 PM | 0.875 | 2 | 71.9 | 66.6 | 70.104 | 82.008 | 11.904 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/12/20XX 10:00:00 PM | 0.91667 | 2 | 71.2 | 68.4 | 68.413 | 80.0233 | 11.6102 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/12/20XX 11:00:00 PM | 0.95833 | 2 | 70.7 | 69.2 | 67.227 | 78.6313 | 11.4043 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/12/20XX 12:00:00 AM | 0 | 3 | 70.3 | 71.2 | 77.5329 | 88.8456 | 11.3127 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/13/20XX 1:00:00 AM | 0.041667 | 3 | 69.5 | 72.3 | 75.3763 | 86.3676 | 10.9913 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/13/20XX 2:00:00 AM | 0.083333 | 3 | 68.6 | 74.5 | 73.0131 | 83.6528 | 10.6396 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/13/20XX 3:00:00 AM | 0.125 | 3 | 68.1 | 75.4 | 71.7287 | 82.1774 | 10.4487 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/13/20XX 4:00:00 AM | 0.16667 | 3 | 67.8 | 76.1 | 70.9676 | 81.3033 | 10.3357 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/13/20XX 5:00:00 AM | 0.20833 | 3 | 67.4 | 76 | 69.964 | 80.1508 | 10.1867 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/13/20XX 6:00:00 AM | 0.25 | 3 | 67.1 | 78.9 | 69.2196 | 79.2959 | 10.0763 | 70 | 67.1 |  | 67.1 | 78.1875 | 0.1 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 64.1782 | 16.3576 | 389310.6311 | 32.4426 | 32.4426 | 90.1191 | 0.2 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 65.7348 | 17.9142 | 426357.4623 | 35.5298 | 35.5298 | 91.0328 | 0.3 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 67.2914 | 19.4708 | 463404.2934 | 38.617 | 38.617 | 91.9465 | 0.4 | 71.24 | 16.24 | 613872 | 51.156 | 51.156 | 68.848 | 21.0274 | 500451.1245 | 41.7043 | 41.7043 | 92.8603 | 0.5 | 70.55 | 15.55 | 587790 | 48.9825 | 48.9825 | 70.4046 | 22.5839 | 537497.9556 | 44.7915 | 44.7915 | 93.774 | 0.6 | 69.86 | 14.86 | 561708 | 46.809 | 46.809 | 71.9612 | 24.1405 | 574544.7868 | 47.8787 | 47.8787 | 94.6877 | 0.7 | 69.17 | 14.17 | 535626 | 44.6355 | 44.6355 | 73.5178 | 25.6971 | 611591.6179 | 50.966 | 50.966 | 95.6015 | 0.8 | 68.48 | 13.48 | 509544 | 42.462 | 42.462 | 75.0743 | 27.2537 | 648638.449 | 54.0532 | 54.0532 | 96.5152 | 0.9 | 67.79 | 12.79 | 483462 | 40.2885 | 40.2885 | 76.6309 | 28.8103 | 685685.2802 | 57.1404 | 57.1404 | 97.4289 | 1 | 67.1 | 12.1 | 457380 | 38.115 | 38.115 | 78.1875 | 30.3669 | 722732.1113 | 60.2277 | 60.2277 | 98.3427 | 65 | 80 | 28.2999 | 28 | 78.9
6/13/20XX 7:00:00 AM | 0.29167 | 3 | 67.8 | 75.9 | 70.9676 | 81.3033 | 10.3357 | 70 | 67.8 |  | 67.8 | 77.0657 | 0.1 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 64.066 | 16.2454 | 386640.6271 | 32.2201 | 32.2201 | 90.1171 | 0.2 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 65.5104 | 17.6898 | 421017.4543 | 35.0848 | 35.0848 | 91.0288 | 0.3 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 66.9548 | 19.1342 | 455394.2814 | 37.9495 | 37.9495 | 91.9405 | 0.4 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 68.3993 | 20.5786 | 489771.1086 | 40.8143 | 40.8143 | 92.8523 | 0.5 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 69.8437 | 22.023 | 524147.9357 | 43.679 | 43.679 | 93.764 | 0.6 | 70.28 | 15.28 | 577584 | 48.132 | 48.132 | 71.2881 | 23.4674 | 558524.7629 | 46.5437 | 46.5437 | 94.6757 | 0.7 | 69.66 | 14.66 | 554148 | 46.179 | 46.179 | 72.7325 | 24.9118 | 592901.59 | 49.4085 | 49.4085 | 95.5875 | 0.8 | 69.04 | 14.04 | 530712 | 44.226 | 44.226 | 74.1769 | 26.3562 | 627278.4172 | 52.2732 | 52.2732 | 96.4992 | 0.9 | 68.42 | 13.42 | 507276 | 42.273 | 42.273 | 75.6213 | 27.8006 | 661655.2443 | 55.1379 | 55.1379 | 97.4109 | 1 | 67.8 | 12.8 | 483840 | 40.32 | 40.32 | 77.0657 | 29.245 | 696032.0714 | 58.0027 | 58.0027 | 98.3227 | 70 | 75 | 28.2964 | 28 | 75.9
6/13/20XX 8:00:00 AM | 0.33333 | 3 | 68.4 | 77.1 | 72.4969 | 83.0598 | 10.5629 | 70 | 68.4 |  | 68.4 | 79.9966 | 0.1 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 64.3591 | 16.5385 | 393616.1694 | 32.8013 | 32.8013 | 90.8873 | 0.2 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 66.0966 | 18.276 | 434968.5388 | 36.2474 | 36.2474 | 92.5694 | 0.3 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 67.8341 | 20.0135 | 476320.9082 | 39.6934 | 39.6934 | 94.2514 | 0.4 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 69.5716 | 21.751 | 517673.2776 | 43.1394 | 43.1394 | 95.9334 | 0.5 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 71.3091 | 23.4885 | 559025.647 | 46.5855 | 46.5855 | 97.6155 | 0.6 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 73.0466 | 25.226 | 600378.0164 | 50.0315 | 50.0315 | 99.2975 | 0.7 | 70.08 | 15.08 | 570024 | 47.502 | 47.502 | 74.7841 | 26.9635 | 641730.3858 | 53.4775 | 53.4775 | 100.9795 | 0.8 | 69.52 | 14.52 | 548856 | 45.738 | 45.738 | 76.5216 | 28.701 | 683082.7552 | 56.9236 | 56.9236 | 102.6616 | 0.9 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 78.2591 | 30.4385 | 724435.1246 | 60.3696 | 60.3696 | 104.3436 | 1 | 68.4 | 13.4 | 506520 | 42.21 | 42.21 | 79.9966 | 32.1759 | 765787.494 | 63.8156 | 63.8156 | 106.0256 | 70 | 75 | 28.9007 | 28 | 77.1
6/13/20XX 9:00:00 AM | 0.375 | 3 | 69.6 | 74.7 | 75.643 | 86.674 | 11.031 | 70 | 69.6 |  | 69.6 | 80.8275 | 0.1 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 64.4422 | 16.6216 | 395593.8608 | 32.9662 | 32.9662 | 91.4302 | 0.2 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 66.2628 | 18.4422 | 438923.9217 | 36.577 | 36.577 | 93.655 | 0.3 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 68.0834 | 20.2628 | 482253.9825 | 40.1878 | 40.1878 | 95.8798 | 0.4 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 69.904 | 22.0834 | 525584.0433 | 43.7987 | 43.7987 | 98.1047 | 0.5 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 71.7246 | 23.904 | 568914.1041 | 47.4095 | 47.4095 | 100.3295 | 0.6 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 73.5452 | 25.7245 | 612244.165 | 51.0203 | 51.0203 | 102.5543 | 0.7 | 70.92 | 15.92 | 601776 | 50.148 | 50.148 | 75.3658 | 27.5451 | 655574.2258 | 54.6312 | 54.6312 | 104.7792 | 0.8 | 70.48 | 15.48 | 585144 | 48.762 | 48.762 | 77.1864 | 29.3657 | 698904.2866 | 58.242 | 58.242 | 107.004 | 0.9 | 70.04 | 15.04 | 568512 | 47.376 | 47.376 | 79.0069 | 31.1863 | 742234.3474 | 61.8529 | 61.8529 | 109.2289 | 1 | 69.6 | 14.6 | 551880 | 45.99 | 45.99 | 80.8275 | 33.0069 | 785564.4083 | 65.4637 | 65.4637 | 111.4537 | 70 | 75 | 29.3246 | 30 | 74.7
6/13/20XX 10:00:00 AM | 0.41667 | 3 | 70.7 | 71.3 | 78.6313 | 90.1079 | 11.4766 | 70 | 70.7 |  | 70.7 | 80.1232 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 64.3718 | 16.5512 | 393917.626 | 32.8265 | 32.8265 | 91.637 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 66.122 | 18.3013 | 435571.452 | 36.2976 | 36.2976 | 94.0686 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 67.8721 | 20.0515 | 477225.278 | 39.7688 | 39.7688 | 96.5003 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 69.6223 | 21.8016 | 518879.1041 | 43.2399 | 43.2399 | 98.9319 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 71.3724 | 23.5518 | 560532.9301 | 46.7111 | 46.7111 | 101.3636 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 73.1226 | 25.302 | 602186.7561 | 50.1822 | 50.1822 | 103.7952 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 74.8728 | 27.0521 | 643840.5821 | 53.6534 | 53.6534 | 106.2269 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 76.6229 | 28.8023 | 685494.4081 | 57.1245 | 57.1245 | 108.6585 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 78.3731 | 30.5524 | 727148.2341 | 60.5957 | 60.5957 | 111.0902 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 80.1232 | 32.3026 | 768802.0601 | 64.0668 | 64.0668 | 113.5218 | 70 | 70 | 29.4842 | 30 | 71.3
6/13/20XX 11:00:00 AM | 0.45833 | 3 | 72.5 | 69.1 | 71.5821 | 83.7428 | 12.1608 | 60 | 72.5 |  | 72.5 | 82.6484 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 64.6243 | 16.8037 | 399927.4229 | 33.3273 | 33.3273 | 92.7048 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 66.627 | 18.8063 | 447591.0459 | 37.2993 | 37.2993 | 96.2043 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 68.6297 | 20.809 | 495254.6688 | 41.2712 | 41.2712 | 99.7037 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 70.6323 | 22.8117 | 542918.2917 | 45.2432 | 45.2432 | 103.2032 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 72.635 | 24.8144 | 590581.9146 | 49.2152 | 49.2152 | 106.7027 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 74.6377 | 26.817 | 638245.5376 | 53.1871 | 53.1871 | 110.2021 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 76.6403 | 28.8197 | 685909.1605 | 57.1591 | 57.1591 | 113.7016 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 78.643 | 30.8224 | 733572.7834 | 61.1311 | 61.1311 | 117.2011 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 80.6457 | 32.8251 | 781236.4063 | 65.103 | 65.103 | 120.7005 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 82.6484 | 34.8277 | 828900.0293 | 69.075 | 69.075 | 124.2 | 70 | 70 | 30.3201 | 30 | 69.1
6/13/20XX 12:00:00 PM | 0.5 | 3 | 73 | 66.5 | 72.8342 | 85.2126 | 12.3784 | 60 | 73 |  | 73 | 80.8802 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.4475 | 16.6269 | 395719.1709 | 32.9766 | 32.9766 | 92.5116 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 66.2733 | 18.4527 | 439174.5418 | 36.5979 | 36.5979 | 95.8179 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 68.0992 | 20.2786 | 482629.9128 | 40.2192 | 40.2192 | 99.1242 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 69.9251 | 22.1044 | 526085.2837 | 43.8404 | 43.8404 | 102.4304 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 71.7509 | 23.9303 | 569540.6546 | 47.4617 | 47.4617 | 105.7367 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 73.5768 | 25.7561 | 612996.0255 | 51.083 | 51.083 | 109.043 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 75.4026 | 27.582 | 656451.3964 | 54.7043 | 54.7043 | 112.3493 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 77.2285 | 29.4078 | 699906.7674 | 58.3256 | 58.3256 | 115.6556 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 79.0543 | 31.2337 | 743362.1383 | 61.9468 | 61.9468 | 118.9618 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 80.8802 | 33.0596 | 786817.5092 | 65.5681 | 65.5681 | 122.2681 | 75 | 65 | 30.1663 | 30 | 66.5
6/13/20XX 1:00:00 PM | 0.54167 | 3 | 74.1 | 65.4 | 75.6554 | 88.5243 | 12.8688 | 60 | 74.1 |  | 74.1 | 82.6046 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 64.6199 | 16.7993 | 399823.2695 | 33.3186 | 33.3186 | 93.2001 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 66.6182 | 18.7976 | 447382.7391 | 37.2819 | 37.2819 | 97.1949 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 68.6165 | 20.7959 | 494942.2086 | 41.2452 | 41.2452 | 101.1897 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 70.6148 | 22.7942 | 542501.6782 | 45.2085 | 45.2085 | 105.1845 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 72.6131 | 24.7925 | 590061.1477 | 49.1718 | 49.1718 | 109.1793 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 74.6114 | 26.7908 | 637620.6173 | 53.1351 | 53.1351 | 113.1741 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 76.6097 | 28.7891 | 685180.0868 | 57.0983 | 57.0983 | 117.1688 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 78.608 | 30.7874 | 732739.5564 | 61.0616 | 61.0616 | 121.1636 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 80.6063 | 32.7857 | 780299.0259 | 65.0249 | 65.0249 | 125.1584 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 82.6046 | 34.784 | 827858.4955 | 68.9882 | 68.9882 | 129.1532 | 75 | 65 | 30.7057 | 30 | 65.4
6/13/20XX 2:00:00 PM | 0.58333 | 3 | 73.9 | 66.1 | 75.1356 | 87.9141 | 12.7785 | 60 | 73.9 |  | 73.9 | 82.9305 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 64.6525 | 16.8319 | 400598.8923 | 33.3832 | 33.3832 | 93.2017 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 66.6834 | 18.8628 | 448933.9847 | 37.4112 | 37.4112 | 97.1982 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 68.7143 | 20.8937 | 497269.077 | 41.4391 | 41.4391 | 101.1946 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 70.7452 | 22.9245 | 545604.1694 | 45.467 | 45.467 | 105.191 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 72.7761 | 24.9554 | 593939.2617 | 49.4949 | 49.4949 | 109.1874 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 74.8069 | 26.9863 | 642274.354 | 53.5229 | 53.5229 | 113.1839 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 76.8378 | 29.0172 | 690609.4464 | 57.5508 | 57.5508 | 117.1803 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 78.8687 | 31.0481 | 738944.5387 | 61.5787 | 61.5787 | 121.1767 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 80.8996 | 33.079 | 787279.6311 | 65.6066 | 65.6066 | 125.1731 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 82.9305 | 35.1099 | 835614.7234 | 69.6346 | 69.6346 | 129.1696 | 75 | 65 | 30.7076 | 30 | 66.1
6/13/20XX 3:00:00 PM | 0.625 | 3 | 73.9 | 66.9 | 75.1356 | 87.9141 | 12.7785 | 60 | 73.9 |  | 73.9 | 83.9528 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 64.7547 | 16.9341 | 403031.9102 | 33.586 | 33.586 | 93.4045 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 66.8879 | 19.0672 | 453800.0203 | 37.8167 | 37.8167 | 97.6037 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 69.021 | 21.2003 | 504568.1305 | 42.0473 | 42.0473 | 101.8028 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 71.1541 | 23.3335 | 555336.2407 | 46.278 | 46.278 | 106.002 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 73.2872 | 25.4666 | 606104.3509 | 50.5087 | 50.5087 | 110.2012 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 75.4203 | 27.5997 | 656872.461 | 54.7394 | 54.7394 | 114.4004 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 77.5534 | 29.7328 | 707640.5712 | 58.97 | 58.97 | 118.5995 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 79.6865 | 31.8659 | 758408.6814 | 63.2007 | 63.2007 | 122.7987 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 81.8197 | 33.999 | 809176.7915 | 67.4314 | 67.4314 | 126.9979 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 83.9528 | 36.1321 | 859944.9017 | 71.6621 | 71.6621 | 131.1971 | 75 | 65 | 30.8675 | 30 | 66.9
6/13/20XX 4:00:00 PM | 0.66667 | 3 | 74 | 67.1 | 75.3952 | 88.2187 | 12.8236 | 60 | 74 |  | 74 | 84.4999 | 0.1 | 74 | 19 | 718200 | 59.85 | 59.85 | 64.8095 | 16.9888 | 404334.0562 | 33.6945 | 33.6945 | 93.5445 | 0.2 | 74 | 19 | 718200 | 59.85 | 59.85 | 66.9973 | 19.1767 | 456404.3123 | 38.0337 | 38.0337 | 97.8837 | 0.3 | 74 | 19 | 718200 | 59.85 | 59.85 | 69.1851 | 21.3645 | 508474.5685 | 42.3729 | 42.3729 | 102.2229 | 0.4 | 74 | 19 | 718200 | 59.85 | 59.85 | 71.3729 | 23.5523 | 560544.8246 | 46.7121 | 46.7121 | 106.5621 | 0.5 | 74 | 19 | 718200 | 59.85 | 59.85 | 73.5608 | 25.7401 | 612615.0808 | 51.0513 | 51.0513 | 110.9013 | 0.6 | 74 | 19 | 718200 | 59.85 | 59.85 | 75.7486 | 27.928 | 664685.3369 | 55.3904 | 55.3904 | 115.2404 | 0.7 | 74 | 19 | 718200 | 59.85 | 59.85 | 77.9364 | 30.1158 | 716755.5931 | 59.7296 | 59.7296 | 119.5796 | 0.8 | 74 | 19 | 718200 | 59.85 | 59.85 | 80.1242 | 32.3036 | 768825.8492 | 64.0688 | 64.0688 | 123.9188 | 0.9 | 74 | 19 | 718200 | 59.85 | 59.85 | 82.3121 | 34.4914 | 820896.1054 | 68.408 | 68.408 | 128.258 | 1 | 74 | 19 | 718200 | 59.85 | 59.85 | 84.4999 | 36.6793 | 872966.3616 | 72.7472 | 72.7472 | 132.5972 | 75 | 65 | 30.9776 | 30 | 67.1
6/13/20XX 5:00:00 PM | 0.70833 | 3 | 72.8 | 70 | 84.6221 | 96.9944 | 12.3723 | 70 | 72.8 |  | 72.8 | 84.6221 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 64.8217 | 17.001 | 404624.845 | 33.7187 | 33.7187 | 93.1907 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 67.0217 | 19.2011 | 456985.8901 | 38.0822 | 38.0822 | 97.1762 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 69.2218 | 21.4011 | 509346.9351 | 42.4456 | 42.4456 | 101.1616 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 71.4218 | 23.6012 | 561707.9802 | 46.809 | 46.809 | 105.147 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 73.6219 | 25.8012 | 614069.0252 | 51.1724 | 51.1724 | 109.1324 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 75.8219 | 28.0013 | 666430.0703 | 55.5358 | 55.5358 | 113.1178 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 78.0219 | 30.2013 | 718791.1153 | 59.8993 | 59.8993 | 117.1033 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 80.222 | 32.4014 | 771152.1604 | 64.2627 | 64.2627 | 121.0887 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 82.422 | 34.6014 | 823513.2054 | 68.6261 | 68.6261 | 125.0741 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 84.6221 | 36.8014 | 875874.2505 | 72.9895 | 72.9895 | 129.0595 | 75 | 70 | 30.7023 | 30 | 70
6/13/20XX 6:00:00 PM | 0.75 | 3 | 72 | 70.6 | 82.2949 | 94.3189 | 12.024 | 70 | 72 |  | 72 | 83.0164 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.6611 | 16.8405 | 400803.2718 | 33.4003 | 33.4003 | 92.6203 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 66.7006 | 18.8799 | 449342.7436 | 37.4452 | 37.4452 | 96.0352 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 68.7401 | 20.9194 | 497882.2155 | 41.4902 | 41.4902 | 99.4502 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 70.7795 | 22.9589 | 546421.6873 | 45.5351 | 45.5351 | 102.8651 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 72.819 | 24.9984 | 594961.1591 | 49.5801 | 49.5801 | 106.2801 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 74.8585 | 27.0378 | 643500.6309 | 53.6251 | 53.6251 | 109.6951 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 76.8979 | 29.0773 | 692040.1028 | 57.67 | 57.67 | 113.11 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 78.9374 | 31.1168 | 740579.5746 | 61.715 | 61.715 | 116.525 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 80.9769 | 33.1563 | 789119.0464 | 65.7599 | 65.7599 | 119.9399 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 83.0164 | 35.1957 | 837658.5182 | 69.8049 | 69.8049 | 123.3549 | 70 | 70 | 30.255 | 30 | 70.6
6/13/20XX 7:00:00 PM | 0.79167 | 3 | 71.6 | 70.2 | 81.1522 | 93.0054 | 11.8531 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/13/20XX 8:00:00 PM | 0.83333 | 3 | 70.1 | 73 | 76.9888 | 88.2203 | 11.2316 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/13/20XX 9:00:00 PM | 0.875 | 3 | 68.7 | 75.7 | 73.2724 | 83.9506 | 10.6782 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/13/20XX 10:00:00 PM | 0.91667 | 3 | 68.3 | 76.8 | 72.24 | 82.7647 | 10.5247 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/13/20XX 11:00:00 PM | 0.95833 | 3 | 67.8 | 78.4 | 70.9676 | 81.3033 | 10.3357 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/13/20XX 12:00:00 AM | 0 | 4 | 67.1 | 79.9 | 69.2196 | 79.2959 | 10.0763 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/14/20XX 1:00:00 AM | 0.041667 | 4 | 66.7 | 81.2 | 78.1688 | 88.0876 | 9.9188 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/14/20XX 2:00:00 AM | 0.083333 | 4 | 66.3 | 78.9 | 67.2689 | 77.0561 | 9.7873 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/14/20XX 3:00:00 AM | 0.125 | 4 | 65.2 | 81.6 | 74.0694 | 83.4531 | 9.3838 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/14/20XX 4:00:00 AM | 0.16667 | 4 | 64.4 | 82 | 71.9634 | 81.0729 | 9.1095 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/14/20XX 5:00:00 AM | 0.20833 | 4 | 64.3 | 81.2 | 71.704 | 80.7798 | 9.0758 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/14/20XX 6:00:00 AM | 0.25 | 4 | 64.4 | 80.3 | 71.9634 | 81.0729 | 9.1095 | 80 | 64.4 |  | 64.4 | 72.2366 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 72.2366 | 24.416 | 581101.0628 | 48.4251 | 48.4251 | 78.0351 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 72.2366 | 24.416 | 581101.0628 | 48.4251 | 48.4251 | 78.0351 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 72.2366 | 24.416 | 581101.0628 | 48.4251 | 48.4251 | 78.0351 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 72.2366 | 24.416 | 581101.0628 | 48.4251 | 48.4251 | 78.0351 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 72.2366 | 24.416 | 581101.0628 | 48.4251 | 48.4251 | 78.0351 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 72.2366 | 24.416 | 581101.0628 | 48.4251 | 48.4251 | 78.0351 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 72.2366 | 24.416 | 581101.0628 | 48.4251 | 48.4251 | 78.0351 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 72.2366 | 24.416 | 581101.0628 | 48.4251 | 48.4251 | 78.0351 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 72.2366 | 24.416 | 581101.0628 | 48.4251 | 48.4251 | 78.0351 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 72.2366 | 24.416 | 581101.0628 | 48.4251 | 48.4251 | 78.0351 | 65 | 80 | 26.7113 | 26 | 80.3
6/14/20XX 7:00:00 AM | 0.29167 | 4 | 65.4 | 76.5 | 65.1332 | 74.6045 | 9.4713 | 70 | 65.4 |  | 65.4 | 71.2896 | 0.1 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 63.4884 | 15.6678 | 372893.446 | 31.0745 | 31.0745 | 88.2155 | 0.2 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 64.3552 | 16.5346 | 393523.0919 | 32.7936 | 32.7936 | 87.2256 | 0.3 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 65.222 | 17.4014 | 414152.7379 | 34.5127 | 34.5127 | 86.2357 | 0.4 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 66.0888 | 18.2682 | 434782.3839 | 36.2319 | 36.2319 | 85.2459 | 0.5 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 66.9556 | 19.135 | 455412.0299 | 37.951 | 37.951 | 84.256 | 0.6 | 68.84 | 13.84 | 523152 | 43.596 | 43.596 | 67.8224 | 20.0018 | 476041.6758 | 39.6701 | 39.6701 | 83.2661 | 0.7 | 67.98 | 12.98 | 490644 | 40.887 | 40.887 | 68.6892 | 20.8685 | 496671.3218 | 41.3893 | 41.3893 | 82.2763 | 0.8 | 67.12 | 12.12 | 458136 | 38.178 | 38.178 | 69.556 | 21.7353 | 517300.9678 | 43.1084 | 43.1084 | 81.2864 | 0.9 | 66.26 | 11.26 | 425628 | 35.469 | 35.469 | 70.4228 | 22.6021 | 537930.6137 | 44.8276 | 44.8276 | 80.2966 | 1 | 65.4 | 10.4 | 393120 | 32.76 | 32.76 | 71.2896 | 23.4689 | 558560.2597 | 46.5467 | 46.5467 | 79.3067 | 65 | 75 | 26.8083 | 26 | 76.5
6/14/20XX 8:00:00 AM | 0.33333 | 4 | 66.5 | 74.4 | 67.7519 | 77.6107 | 9.8588 | 70 | 66.5 |  | 66.5 | 72.0898 | 0.1 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 63.5684 | 15.7478 | 374797.9858 | 31.2332 | 31.2332 | 88.7207 | 0.2 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 64.5153 | 16.6946 | 397332.1715 | 33.111 | 33.111 | 88.236 | 0.3 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 65.4621 | 17.6414 | 419866.3573 | 34.9889 | 34.9889 | 87.7514 | 0.4 | 71 | 16 | 604800 | 50.4 | 50.4 | 66.4089 | 18.5883 | 442400.543 | 36.8667 | 36.8667 | 87.2667 | 0.5 | 70.25 | 15.25 | 576450 | 48.0375 | 48.0375 | 67.3557 | 19.5351 | 464934.7288 | 38.7446 | 38.7446 | 86.7821 | 0.6 | 69.5 | 14.5 | 548100 | 45.675 | 45.675 | 68.3025 | 20.4819 | 487468.9146 | 40.6224 | 40.6224 | 86.2974 | 0.7 | 68.75 | 13.75 | 519750 | 43.3125 | 43.3125 | 69.2493 | 21.4287 | 510003.1003 | 42.5003 | 42.5003 | 85.8128 | 0.8 | 68 | 13 | 491400 | 40.95 | 40.95 | 70.1961 | 22.3755 | 532537.2861 | 44.3781 | 44.3781 | 85.3281 | 0.9 | 67.25 | 12.25 | 463050 | 38.5875 | 38.5875 | 71.143 | 23.3223 | 555071.4718 | 46.256 | 46.256 | 84.8435 | 1 | 66.5 | 11.5 | 434700 | 36.225 | 36.225 | 72.0898 | 24.2691 | 577605.6576 | 48.1338 | 48.1338 | 84.3588 | 65 | 75 | 27.2021 | 28 | 74.4
6/14/20XX 9:00:00 AM | 0.375 | 4 | 67.5 | 69.5 | 60.054 | 70.2137 | 10.1597 | 60 | 67.5 |  | 67.5 | 69.7057 | 0.1 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 63.33 | 15.5094 | 369123.9941 | 30.7603 | 30.7603 | 88.5628 | 0.2 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 64.0385 | 16.2178 | 385984.1882 | 32.1653 | 32.1653 | 87.9203 | 0.3 | 72.05 | 17.05 | 644490 | 53.7075 | 53.7075 | 64.7469 | 16.9262 | 402844.3824 | 33.5704 | 33.5704 | 87.2779 | 0.4 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 65.4553 | 17.6346 | 419704.5765 | 34.9754 | 34.9754 | 86.6354 | 0.5 | 70.75 | 15.75 | 595350 | 49.6125 | 49.6125 | 66.1637 | 18.3431 | 436564.7706 | 36.3804 | 36.3804 | 85.9929 | 0.6 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 66.8721 | 19.0515 | 453424.9647 | 37.7854 | 37.7854 | 85.3504 | 0.7 | 69.45 | 14.45 | 546210 | 45.5175 | 45.5175 | 67.5805 | 19.7599 | 470285.1589 | 39.1904 | 39.1904 | 84.7079 | 0.8 | 68.8 | 13.8 | 521640 | 43.47 | 43.47 | 68.2889 | 20.4683 | 487145.353 | 40.5954 | 40.5954 | 84.0654 | 0.9 | 68.15 | 13.15 | 497070 | 41.4225 | 41.4225 | 68.9973 | 21.1767 | 504005.5471 | 42.0005 | 42.0005 | 83.423 | 1 | 67.5 | 12.5 | 472500 | 39.375 | 39.375 | 69.7057 | 21.8851 | 520865.7412 | 43.4055 | 43.4055 | 82.7805 | 65 | 70 | 27.0747 | 28 | 69.5
6/14/20XX 10:00:00 AM | 0.41667 | 4 | 69.5 | 63.5 | 64.4535 | 75.3763 | 10.9228 | 60 | 69.5 |  | 69.5 | 68.2765 | 0.1 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 63.1871 | 15.3665 | 365722.2838 | 30.4769 | 30.4769 | 88.9094 | 0.2 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 63.7526 | 15.932 | 379180.7675 | 31.5984 | 31.5984 | 88.6134 | 0.3 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 64.3181 | 16.4974 | 392639.2513 | 32.7199 | 32.7199 | 88.3174 | 0.4 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 64.8836 | 17.0629 | 406097.7351 | 33.8415 | 33.8415 | 88.0215 | 0.5 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 65.449 | 17.6284 | 419556.2188 | 34.963 | 34.963 | 87.7255 | 0.6 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 66.0145 | 18.1939 | 433014.7026 | 36.0846 | 36.0846 | 87.4296 | 0.7 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 66.58 | 18.7594 | 446473.1864 | 37.2061 | 37.2061 | 87.1336 | 0.8 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 67.1455 | 19.3249 | 459931.6702 | 38.3276 | 38.3276 | 86.8376 | 0.9 | 69.95 | 14.95 | 565110 | 47.0925 | 47.0925 | 67.711 | 19.8903 | 473390.1539 | 39.4492 | 39.4492 | 86.5417 | 1 | 69.5 | 14.5 | 548100 | 45.675 | 45.675 | 68.2765 | 20.4558 | 486848.6377 | 40.5707 | 40.5707 | 86.2457 | 70 | 65 | 27.3404 | 28 | 63.5
6/14/20XX 11:00:00 AM | 0.45833 | 4 | 72.1 | 58.8 | 58.6421 | 70.5937 | 11.9516 | 50 | 72.1 |  | 72.1 | 69.1595 | 0.1 | 73.81 | 18.81 | 711018 | 59.2515 | 59.2515 | 63.2754 | 15.4548 | 367823.9815 | 30.652 | 30.652 | 89.9035 | 0.2 | 73.62 | 18.62 | 703836 | 58.653 | 58.653 | 63.9292 | 16.1086 | 383384.163 | 31.9487 | 31.9487 | 90.6017 | 0.3 | 73.43 | 18.43 | 696654 | 58.0545 | 58.0545 | 64.583 | 16.7624 | 398944.3444 | 33.2454 | 33.2454 | 91.2999 | 0.4 | 73.24 | 18.24 | 689472 | 57.456 | 57.456 | 65.2368 | 17.4162 | 414504.5259 | 34.542 | 34.542 | 91.998 | 0.5 | 73.05 | 18.05 | 682290 | 56.8575 | 56.8575 | 65.8906 | 18.0699 | 430064.7074 | 35.8387 | 35.8387 | 92.6962 | 0.6 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 66.5444 | 18.7237 | 445624.8889 | 37.1354 | 37.1354 | 93.3944 | 0.7 | 72.67 | 17.67 | 667926 | 55.6605 | 55.6605 | 67.1982 | 19.3775 | 461185.0703 | 38.4321 | 38.4321 | 94.0926 | 0.8 | 72.48 | 17.48 | 660744 | 55.062 | 55.062 | 67.8519 | 20.0313 | 476745.2518 | 39.7288 | 39.7288 | 94.7908 | 0.9 | 72.29 | 17.29 | 653562 | 54.4635 | 54.4635 | 68.5057 | 20.6851 | 492305.4333 | 41.0255 | 41.0255 | 95.489 | 1 | 72.1 | 17.1 | 646380 | 53.865 | 53.865 | 69.1595 | 21.3389 | 507865.6148 | 42.3221 | 42.3221 | 96.1871 | 70 | 60 | 28.1137 | 28 | 58.8
6/14/20XX 12:00:00 PM | 0.5 | 4 | 74.5 | 53.8 | 63.7064 | 76.7042 | 12.9978 | 50 | 74.5 |  | 74.5 | 68.6456 | 0.1 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 63.224 | 15.4034 | 366600.863 | 30.5501 | 30.5501 | 90.5576 | 0.2 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 63.8264 | 16.0058 | 380937.9261 | 31.7448 | 31.7448 | 91.9098 | 0.3 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 64.4288 | 16.6082 | 395274.9891 | 32.9396 | 32.9396 | 93.2621 | 0.4 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 65.0312 | 17.2106 | 409612.0521 | 34.1343 | 34.1343 | 94.6143 | 0.5 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 65.6336 | 17.813 | 423949.1152 | 35.3291 | 35.3291 | 95.9666 | 0.6 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 66.236 | 18.4154 | 438286.1782 | 36.5238 | 36.5238 | 97.3188 | 0.7 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 66.8384 | 19.0178 | 452623.2412 | 37.7186 | 37.7186 | 98.6711 | 0.8 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 67.4408 | 19.6202 | 466960.3043 | 38.9134 | 38.9134 | 100.0234 | 0.9 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 68.0432 | 20.2226 | 481297.3673 | 40.1081 | 40.1081 | 101.3756 | 1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 68.6456 | 20.825 | 495634.4303 | 41.3029 | 41.3029 | 102.7279 | 75 | 55 | 28.6198 | 28 | 53.8
6/14/20XX 1:00:00 PM | 0.54167 | 4 | 75.6 | 52.9 | 66.1493 | 79.6526 | 13.5032 | 50 | 75.6 |  | 75.6 | 70.0653 | 0.1 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 63.366 | 15.5454 | 369979.6541 | 30.8316 | 30.8316 | 91.1856 | 0.2 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 64.1104 | 16.2897 | 387695.5082 | 32.308 | 32.308 | 93.166 | 0.3 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 64.8547 | 17.0341 | 405411.3622 | 33.7843 | 33.7843 | 95.1463 | 0.4 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 65.5991 | 17.7785 | 423127.2163 | 35.2606 | 35.2606 | 97.1266 | 0.5 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 66.3435 | 18.5228 | 440843.0704 | 36.7369 | 36.7369 | 99.1069 | 0.6 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 67.0878 | 19.2672 | 458558.9245 | 38.2132 | 38.2132 | 101.0872 | 0.7 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 67.8322 | 20.0115 | 476274.7786 | 39.6896 | 39.6896 | 103.0676 | 0.8 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 68.5765 | 20.7559 | 493990.6326 | 41.1659 | 41.1659 | 105.0479 | 0.9 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 69.3209 | 21.5003 | 511706.4867 | 42.6422 | 42.6422 | 107.0282 | 1 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 70.0653 | 22.2446 | 529422.3408 | 44.1185 | 44.1185 | 109.0085 | 75 | 55 | 29.1108 | 30 | 52.9
6/14/20XX 2:00:00 PM | 0.58333 | 4 | 75.8 | 52.1 | 66.6019 | 80.1988 | 13.5969 | 50 | 75.8 |  | 75.8 | 69.4573 | 0.1 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 63.3052 | 15.4846 | 368532.5848 | 30.711 | 30.711 | 91.128 | 0.2 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 63.9888 | 16.1681 | 384801.3697 | 32.0668 | 32.0668 | 93.0508 | 0.3 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 64.6723 | 16.8517 | 401070.1545 | 33.4225 | 33.4225 | 94.9735 | 0.4 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 65.3559 | 17.5352 | 417338.9393 | 34.7782 | 34.7782 | 96.8962 | 0.5 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 66.0394 | 18.2188 | 433607.7241 | 36.134 | 36.134 | 98.819 | 0.6 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 66.723 | 18.9024 | 449876.509 | 37.4897 | 37.4897 | 100.7417 | 0.7 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 67.4066 | 19.5859 | 466145.2938 | 38.8454 | 38.8454 | 102.6644 | 0.8 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 68.0901 | 20.2695 | 482414.0786 | 40.2012 | 40.2012 | 104.5872 | 0.9 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 68.7737 | 20.9531 | 498682.8634 | 41.5569 | 41.5569 | 106.5099 | 1 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 69.4573 | 21.6366 | 514951.6483 | 42.9126 | 42.9126 | 108.4326 | 75 | 50 | 29.0645 | 30 | 52.1
6/14/20XX 3:00:00 PM | 0.625 | 4 | 75.2 | 53.2 | 65.252 | 78.5695 | 13.3175 | 50 | 75.2 |  | 75.2 | 69.5136 | 0.1 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 63.3108 | 15.4902 | 368666.6576 | 30.7222 | 30.7222 | 90.9502 | 0.2 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 64 | 16.1794 | 385069.5151 | 32.0891 | 32.0891 | 92.6951 | 0.3 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 64.6892 | 16.8686 | 401472.3727 | 33.456 | 33.456 | 94.44 | 0.4 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 65.3784 | 17.5578 | 417875.2302 | 34.8229 | 34.8229 | 96.1849 | 0.5 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 66.0676 | 18.247 | 434278.0878 | 36.1898 | 36.1898 | 97.9298 | 0.6 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 66.7568 | 18.9362 | 450680.9454 | 37.5567 | 37.5567 | 99.6747 | 0.7 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 67.446 | 19.6254 | 467083.8029 | 38.9237 | 38.9237 | 101.4197 | 0.8 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 68.1352 | 20.3146 | 483486.6605 | 40.2906 | 40.2906 | 103.1646 | 0.9 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 68.8244 | 21.0038 | 499889.5181 | 41.6575 | 41.6575 | 104.9095 | 1 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 69.5136 | 21.693 | 516292.3756 | 43.0244 | 43.0244 | 106.6544 | 75 | 55 | 28.9267 | 28 | 53.2
6/14/20XX 4:00:00 PM | 0.66667 | 4 | 74.7 | 53.1 | 64.1448 | 77.2333 | 13.0885 | 50 | 74.7 |  | 74.7 | 68.2022 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 63.1797 | 15.3591 | 365545.6596 | 30.4621 | 30.4621 | 90.5326 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 63.7378 | 15.9171 | 378827.5192 | 31.569 | 31.569 | 91.86 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 64.2958 | 16.4752 | 392109.3788 | 32.6758 | 32.6758 | 93.1873 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 64.8539 | 17.0332 | 405391.2384 | 33.7826 | 33.7826 | 94.5146 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 65.4119 | 17.5913 | 418673.098 | 34.8894 | 34.8894 | 95.8419 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 65.97 | 18.1494 | 431954.9576 | 35.9962 | 35.9962 | 97.1692 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 66.5281 | 18.7074 | 445236.8172 | 37.1031 | 37.1031 | 98.4966 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 67.0861 | 19.2655 | 458518.6768 | 38.2099 | 38.2099 | 99.8239 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 67.6442 | 19.8236 | 471800.5364 | 39.3167 | 39.3167 | 101.1512 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 68.2022 | 20.3816 | 485082.3959 | 40.4235 | 40.4235 | 102.4785 | 75 | 55 | 28.5993 | 28 | 53.1
6/14/20XX 5:00:00 PM | 0.70833 | 4 | 72.4 | 57.5 | 59.2556 | 71.3339 | 12.0782 | 50 | 72.4 |  | 72.4 | 68.3143 | 0.1 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 63.1909 | 15.3703 | 365812.3444 | 30.4844 | 30.4844 | 89.8304 | 0.2 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 63.7602 | 15.9395 | 379360.8887 | 31.6134 | 31.6134 | 90.4554 | 0.3 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 64.3294 | 16.5088 | 392909.4331 | 32.7425 | 32.7425 | 91.0805 | 0.4 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 64.8987 | 17.0781 | 406457.9774 | 33.8715 | 33.8715 | 91.7055 | 0.5 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 65.468 | 17.6473 | 420006.5218 | 35.0005 | 35.0005 | 92.3305 | 0.6 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 66.0372 | 18.2166 | 433555.0662 | 36.1296 | 36.1296 | 92.9556 | 0.7 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 66.6065 | 18.7859 | 447103.6105 | 37.2586 | 37.2586 | 93.5806 | 0.8 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 67.1758 | 19.3551 | 460652.1549 | 38.3877 | 38.3877 | 94.2057 | 0.9 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 67.745 | 19.9244 | 474200.6992 | 39.5167 | 39.5167 | 94.8307 | 1 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 68.3143 | 20.4937 | 487749.2436 | 40.6458 | 40.6458 | 95.4558 | 70 | 55 | 28.0549 | 28 | 57.5
6/14/20XX 6:00:00 PM | 0.75 | 4 | 71.6 | 59.5 | 57.6317 | 69.3749 | 11.7432 | 50 | 71.6 |  | 71.6 | 68.7877 | 0.1 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 63.2382 | 15.4176 | 366939.1532 | 30.5783 | 30.5783 | 89.6723 | 0.2 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 63.8549 | 16.0342 | 381614.5064 | 31.8012 | 31.8012 | 90.1392 | 0.3 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 64.4715 | 16.6508 | 396289.8596 | 33.0242 | 33.0242 | 90.6062 | 0.4 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 65.0881 | 17.2674 | 410965.2128 | 34.2471 | 34.2471 | 91.0731 | 0.5 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 65.7047 | 17.8841 | 425640.566 | 35.47 | 35.47 | 91.54 | 0.6 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 66.3213 | 18.5007 | 440315.9192 | 36.693 | 36.693 | 92.007 | 0.7 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 66.9379 | 19.1173 | 454991.2724 | 37.9159 | 37.9159 | 92.4739 | 0.8 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 67.5545 | 19.7339 | 469666.6255 | 39.1389 | 39.1389 | 92.9409 | 0.9 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 68.1711 | 20.3505 | 484341.9787 | 40.3618 | 40.3618 | 93.4078 | 1 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 68.7877 | 20.9671 | 499017.3319 | 41.5848 | 41.5848 | 93.8748 | 70 | 60 | 27.9334 | 28 | 59.5
6/14/20XX 7:00:00 PM | 0.79167 | 4 | 70.3 | 59.6 | 55.075 | 66.2911 | 11.2161 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/14/20XX 8:00:00 PM | 0.83333 | 4 | 69 | 59 | 52.6176 | 63.3278 | 10.7102 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/14/20XX 9:00:00 PM | 0.875 | 4 | 67.3 | 63.2 | 59.6291 | 69.7151 | 10.086 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/14/20XX 10:00:00 PM | 0.91667 | 4 | 66.1 | 67 | 57.1351 | 66.7889 | 9.6538 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/14/20XX 11:00:00 PM | 0.95833 | 4 | 65.3 | 69 | 55.5248 | 64.8997 | 9.3749 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/14/20XX 12:00:00 AM | 0 | 5 | 64.5 | 70.1 | 63.0587 | 72.2236 | 9.1649 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/15/20XX 1:00:00 AM | 0.041667 | 5 | 64.2 | 70.4 | 62.3806 | 71.4454 | 9.0649 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/15/20XX 2:00:00 AM | 0.083333 | 5 | 63.8 | 70.3 | 61.4867 | 70.4198 | 8.9331 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/15/20XX 3:00:00 AM | 0.125 | 5 | 63.6 | 72.6 | 61.0441 | 69.912 | 8.8679 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/15/20XX 4:00:00 AM | 0.16667 | 5 | 63.1 | 71.6 | 59.9503 | 68.6572 | 8.7068 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/15/20XX 5:00:00 AM | 0.20833 | 5 | 62.3 | 74.3 | 58.2375 | 66.6924 | 8.4549 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/15/20XX 6:00:00 AM | 0.25 | 5 | 63.3 | 73.8 | 60.3857 | 69.1566 | 8.7709 | 70 | 63.3 |  | 63.3 | 63.7186 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 63.7186 | 15.898 | 378372.4284 | 31.531 | 31.531 | 57.676 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 63.7186 | 15.898 | 378372.4284 | 31.531 | 31.531 | 57.676 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 63.7186 | 15.898 | 378372.4284 | 31.531 | 31.531 | 57.676 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 63.7186 | 15.898 | 378372.4284 | 31.531 | 31.531 | 57.676 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 63.7186 | 15.898 | 378372.4284 | 31.531 | 31.531 | 57.676 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 63.7186 | 15.898 | 378372.4284 | 31.531 | 31.531 | 57.676 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 63.7186 | 15.898 | 378372.4284 | 31.531 | 31.531 | 57.676 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 63.7186 | 15.898 | 378372.4284 | 31.531 | 31.531 | 57.676 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 63.7186 | 15.898 | 378372.4284 | 31.531 | 31.531 | 57.676 | 1 | 63.3 | 8.3 | 313740 | 26.145 | 26.145 | 63.7186 | 15.898 | 378372.4284 | 31.531 | 31.531 | 57.676 | 65 | 75 | 25.1157 | 26 | 73.8
6/15/20XX 7:00:00 AM | 0.29167 | 5 | 65 | 70.1 | 64.2037 | 73.5377 | 9.3339 | 70 | 65 |  | 65 | 64.2971 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 64.2971 | 16.4764 | 392139.1481 | 32.6783 | 32.6783 | 64.1783 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 64.2971 | 16.4764 | 392139.1481 | 32.6783 | 32.6783 | 64.1783 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 64.2971 | 16.4764 | 392139.1481 | 32.6783 | 32.6783 | 64.1783 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 64.2971 | 16.4764 | 392139.1481 | 32.6783 | 32.6783 | 64.1783 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 64.2971 | 16.4764 | 392139.1481 | 32.6783 | 32.6783 | 64.1783 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 64.2971 | 16.4764 | 392139.1481 | 32.6783 | 32.6783 | 64.1783 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 64.2971 | 16.4764 | 392139.1481 | 32.6783 | 32.6783 | 64.1783 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 64.2971 | 16.4764 | 392139.1481 | 32.6783 | 32.6783 | 64.1783 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 64.2971 | 16.4764 | 392139.1481 | 32.6783 | 32.6783 | 64.1783 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 64.2971 | 16.4764 | 392139.1481 | 32.6783 | 32.6783 | 64.1783 | 65 | 70 | 25.6207 | 26 | 70.1
6/15/20XX 8:00:00 AM | 0.33333 | 5 | 67.3 | 65.2 | 59.6291 | 69.7151 | 10.086 | 60 | 67.3 |  | 67.3 | 64.8738 | 0.1 | 73.33 | 18.33 | 692874 | 57.7395 | 57.7395 | 62.8468 | 15.0262 | 357623.9744 | 29.802 | 29.802 | 87.5415 | 0.2 | 72.66 | 17.66 | 667548 | 55.629 | 55.629 | 63.0721 | 15.2514 | 362984.1487 | 30.2487 | 30.2487 | 85.8777 | 0.3 | 71.99 | 16.99 | 642222 | 53.5185 | 53.5185 | 63.2973 | 15.4767 | 368344.3231 | 30.6954 | 30.6954 | 84.2139 | 0.4 | 71.32 | 16.32 | 616896 | 51.408 | 51.408 | 63.5225 | 15.7019 | 373704.4975 | 31.142 | 31.142 | 82.55 | 0.5 | 70.65 | 15.65 | 591570 | 49.2975 | 49.2975 | 63.7477 | 15.9271 | 379064.6718 | 31.5887 | 31.5887 | 80.8862 | 0.6 | 69.98 | 14.98 | 566244 | 47.187 | 47.187 | 63.9729 | 16.1523 | 384424.8462 | 32.0354 | 32.0354 | 79.2224 | 0.7 | 69.31 | 14.31 | 540918 | 45.0765 | 45.0765 | 64.1982 | 16.3775 | 389785.0205 | 32.4821 | 32.4821 | 77.5586 | 0.8 | 68.64 | 13.64 | 515592 | 42.966 | 42.966 | 64.4234 | 16.6027 | 395145.1949 | 32.9288 | 32.9288 | 75.8948 | 0.9 | 67.97 | 12.97 | 490266 | 40.8555 | 40.8555 | 64.6486 | 16.828 | 400505.3693 | 33.3754 | 33.3754 | 74.2309 | 1 | 67.3 | 12.3 | 464940 | 38.745 | 38.745 | 64.8738 | 17.0532 | 405865.5436 | 33.8221 | 33.8221 | 72.5671 | 65 | 65 | 26.2721 | 26 | 65.2
6/15/20XX 9:00:00 AM | 0.375 | 5 | 69.3 | 59.4 | 53.176 | 64.0011 | 10.8251 | 50 | 69.3 |  | 69.3 | 63.3516 | 0.1 | 73.53 | 18.53 | 700434 | 58.3695 | 58.3695 | 62.6946 | 14.874 | 354001.107 | 29.5001 | 29.5001 | 87.8696 | 0.2 | 73.06 | 18.06 | 682668 | 56.889 | 56.889 | 62.7676 | 14.947 | 355738.414 | 29.6449 | 29.6449 | 86.5339 | 0.3 | 72.59 | 17.59 | 664902 | 55.4085 | 55.4085 | 62.8406 | 15.02 | 357475.7211 | 29.7896 | 29.7896 | 85.1981 | 0.4 | 72.12 | 17.12 | 647136 | 53.928 | 53.928 | 62.9136 | 15.093 | 359213.0281 | 29.9344 | 29.9344 | 83.8624 | 0.5 | 71.65 | 16.65 | 629370 | 52.4475 | 52.4475 | 62.9866 | 15.166 | 360950.3351 | 30.0792 | 30.0792 | 82.5267 | 0.6 | 71.18 | 16.18 | 611604 | 50.967 | 50.967 | 63.0596 | 15.239 | 362687.6421 | 30.224 | 30.224 | 81.191 | 0.7 | 70.71 | 15.71 | 593838 | 49.4865 | 49.4865 | 63.1326 | 15.312 | 364424.9491 | 30.3687 | 30.3687 | 79.8552 | 0.8 | 70.24 | 15.24 | 576072 | 48.006 | 48.006 | 63.2056 | 15.385 | 366162.2561 | 30.5135 | 30.5135 | 78.5195 | 0.9 | 69.77 | 14.77 | 558306 | 46.5255 | 46.5255 | 63.2786 | 15.458 | 367899.5632 | 30.6583 | 30.6583 | 77.1838 | 1 | 69.3 | 14.3 | 540540 | 45.045 | 45.045 | 63.3516 | 15.531 | 369636.8702 | 30.8031 | 30.8031 | 75.8481 | 70 | 60 | 26.5226 | 26 | 59.4
6/15/20XX 10:00:00 AM | 0.41667 | 5 | 71.7 | 54.7 | 57.8326 | 69.6172 | 11.7846 | 50 | 71.7 |  | 71.7 | 63.3714 | 0.1 | 73.77 | 18.77 | 709506 | 59.1255 | 59.1255 | 62.6966 | 14.876 | 354048.15 | 29.504 | 29.504 | 88.6295 | 0.2 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 62.7716 | 14.9509 | 355832.5 | 29.6527 | 29.6527 | 88.0537 | 0.3 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 62.8466 | 15.0259 | 357616.85 | 29.8014 | 29.8014 | 87.4779 | 0.4 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 62.9215 | 15.1009 | 359401.2001 | 29.9501 | 29.9501 | 86.9021 | 0.5 | 72.85 | 17.85 | 674730 | 56.2275 | 56.2275 | 62.9965 | 15.1759 | 361185.5501 | 30.0988 | 30.0988 | 86.3263 | 0.6 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 63.0715 | 15.2508 | 362969.9001 | 30.2475 | 30.2475 | 85.7505 | 0.7 | 72.39 | 17.39 | 657342 | 54.7785 | 54.7785 | 63.1464 | 15.3258 | 364754.2501 | 30.3962 | 30.3962 | 85.1747 | 0.8 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 63.2214 | 15.4008 | 366538.6001 | 30.5449 | 30.5449 | 84.5989 | 0.9 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 63.2964 | 15.4758 | 368322.9501 | 30.6936 | 30.6936 | 84.0231 | 1 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 63.3714 | 15.5507 | 370107.3002 | 30.8423 | 30.8423 | 83.4473 | 70 | 55 | 27.1114 | 28 | 54.7
6/15/20XX 11:00:00 AM | 0.45833 | 5 | 74.2 | 49.9 | 50.3078 | 63.0537 | 12.7459 | 40 | 74.2 |  | 74.2 | 62.9262 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 62.6521 | 14.8315 | 352988.6578 | 29.4157 | 29.4157 | 89.3287 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 62.6825 | 14.8619 | 353713.5156 | 29.4761 | 29.4761 | 89.4521 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 62.713 | 14.8924 | 354438.3734 | 29.5365 | 29.5365 | 89.5755 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 62.7435 | 14.9228 | 355163.2312 | 29.5969 | 29.5969 | 89.6989 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 62.7739 | 14.9533 | 355888.089 | 29.6573 | 29.6573 | 89.8223 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 62.8044 | 14.9837 | 356612.9468 | 29.7177 | 29.7177 | 89.9457 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 62.8348 | 15.0142 | 357337.8046 | 29.7782 | 29.7782 | 90.0692 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 62.8653 | 15.0446 | 358062.6624 | 29.8386 | 29.8386 | 90.1926 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 62.8957 | 15.0751 | 358787.5202 | 29.899 | 29.899 | 90.316 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 62.9262 | 15.1056 | 359512.3781 | 29.9594 | 29.9594 | 90.4394 | 75 | 50 | 27.6518 | 28 | 49.9
6/15/20XX 12:00:00 PM | 0.5 | 5 | 76.7 | 45.8 | 54.764 | 68.6709 | 13.9069 | 40 | 76.7 |  | 76.7 | 62.83 | 0.1 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 62.6425 | 14.8218 | 352759.7926 | 29.3966 | 29.3966 | 90.0971 | 0.2 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 62.6633 | 14.8427 | 353255.7853 | 29.438 | 29.438 | 90.989 | 0.3 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 62.6842 | 14.8635 | 353751.7779 | 29.4793 | 29.4793 | 91.8808 | 0.4 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 62.705 | 14.8844 | 354247.7706 | 29.5206 | 29.5206 | 92.7726 | 0.5 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 62.7258 | 14.9052 | 354743.7632 | 29.562 | 29.562 | 93.6645 | 0.6 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 62.7467 | 14.926 | 355239.7559 | 29.6033 | 29.6033 | 94.5563 | 0.7 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 62.7675 | 14.9469 | 355735.7485 | 29.6446 | 29.6446 | 95.4481 | 0.8 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 62.7884 | 14.9677 | 356231.7412 | 29.686 | 29.686 | 96.34 | 0.9 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 62.8092 | 14.9886 | 356727.7338 | 29.7273 | 29.7273 | 97.2318 | 1 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 62.83 | 15.0094 | 357223.7265 | 29.7686 | 29.7686 | 98.1236 | 75 | 45 | 28.2467 | 28 | 45.8
6/15/20XX 1:00:00 PM | 0.54167 | 5 | 78.1 | 43.7 | 57.4008 | 71.9966 | 14.5957 | 40 | 78.1 |  | 78.1 | 62.8013 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 62.6396 | 14.819 | 352691.3129 | 29.3909 | 29.3909 | 90.5324 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 62.6576 | 14.8369 | 353118.8259 | 29.4266 | 29.4266 | 91.8596 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 62.6755 | 14.8549 | 353546.3388 | 29.4622 | 29.4622 | 93.1867 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 62.6935 | 14.8729 | 353973.8517 | 29.4978 | 29.4978 | 94.5138 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 62.7114 | 14.8908 | 354401.3647 | 29.5334 | 29.5334 | 95.8409 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 62.7294 | 14.9088 | 354828.8776 | 29.5691 | 29.5691 | 97.1681 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 62.7474 | 14.9267 | 355256.3906 | 29.6047 | 29.6047 | 98.4952 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 62.7653 | 14.9447 | 355683.9035 | 29.6403 | 29.6403 | 99.8223 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 62.7833 | 14.9627 | 356111.4164 | 29.676 | 29.676 | 101.1495 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 62.8013 | 14.9806 | 356538.9294 | 29.7116 | 29.7116 | 102.4766 | 80 | 45 | 28.5838 | 28 | 43.7
6/15/20XX 2:00:00 PM | 0.58333 | 5 | 77.1 | 45.3 | 55.5069 | 69.6077 | 14.1008 | 40 | 77.1 |  | 77.1 | 62.9803 | 0.1 | 74.31 | 19.31 | 729918 | 60.8265 | 60.8265 | 62.6575 | 14.8369 | 353117.4569 | 29.4265 | 29.4265 | 90.253 | 0.2 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 62.6934 | 14.8727 | 353971.1137 | 29.4976 | 29.4976 | 91.3006 | 0.3 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 62.7292 | 14.9086 | 354824.7706 | 29.5687 | 29.5687 | 92.3482 | 0.4 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 62.7651 | 14.9445 | 355678.4275 | 29.6399 | 29.6399 | 93.3959 | 0.5 | 75.55 | 20.55 | 776790 | 64.7325 | 64.7325 | 62.801 | 14.9803 | 356532.0843 | 29.711 | 29.711 | 94.4435 | 0.6 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 62.8368 | 15.0162 | 357385.7412 | 29.7821 | 29.7821 | 95.4911 | 0.7 | 76.17 | 21.17 | 800226 | 66.6855 | 66.6855 | 62.8727 | 15.0521 | 358239.3981 | 29.8533 | 29.8533 | 96.5388 | 0.8 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 62.9086 | 15.0879 | 359093.0549 | 29.9244 | 29.9244 | 97.5864 | 0.9 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 62.9444 | 15.1238 | 359946.7118 | 29.9956 | 29.9956 | 98.6341 | 1 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 62.9803 | 15.1597 | 360800.3687 | 30.0667 | 30.0667 | 99.6817 | 75 | 45 | 28.3679 | 28 | 45.3
6/15/20XX 3:00:00 PM | 0.625 | 5 | 76.5 | 46.9 | 54.3957 | 68.2065 | 13.8108 | 40 | 76.5 |  | 76.5 | 63.9252 | 0.1 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 62.752 | 14.9314 | 355366.2572 | 29.6139 | 29.6139 | 90.2514 | 0.2 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 62.8823 | 15.0617 | 358468.7143 | 29.8724 | 29.8724 | 91.2974 | 0.3 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 63.0127 | 15.1921 | 361571.1715 | 30.1309 | 30.1309 | 92.3434 | 0.4 | 75 | 20 | 756000 | 63 | 63 | 63.1431 | 15.3224 | 364673.6286 | 30.3895 | 30.3895 | 93.3895 | 0.5 | 75.25 | 20.25 | 765450 | 63.7875 | 63.7875 | 63.2734 | 15.4528 | 367776.0858 | 30.648 | 30.648 | 94.4355 | 0.6 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 63.4038 | 15.5831 | 370878.543 | 30.9065 | 30.9065 | 95.4815 | 0.7 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 63.5341 | 15.7135 | 373981.0001 | 31.1651 | 31.1651 | 96.5276 | 0.8 | 76 | 21 | 793800 | 66.15 | 66.15 | 63.6645 | 15.8438 | 377083.4573 | 31.4236 | 31.4236 | 97.5736 | 0.9 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 63.7948 | 15.9742 | 380185.9144 | 31.6822 | 31.6822 | 98.6197 | 1 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 63.9252 | 16.1046 | 383288.3716 | 31.9407 | 31.9407 | 99.6657 | 75 | 45 | 28.3694 | 28 | 46.9
6/15/20XX 4:00:00 PM | 0.66667 | 5 | 74.8 | 49.1 | 51.3484 | 64.365 | 13.0166 | 40 | 74.8 |  | 74.8 | 63.1935 | 0.1 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 62.6788 | 14.8582 | 353624.7805 | 29.4687 | 29.4687 | 89.5707 | 0.2 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 62.736 | 14.9154 | 354985.7611 | 29.5821 | 29.5821 | 89.9361 | 0.3 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 62.7932 | 14.9726 | 356346.7416 | 29.6956 | 29.6956 | 90.3016 | 0.4 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 62.8504 | 15.0297 | 357707.7221 | 29.809 | 29.809 | 90.667 | 0.5 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 62.9076 | 15.0869 | 359068.7026 | 29.9224 | 29.9224 | 91.0324 | 0.6 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 62.9647 | 15.1441 | 360429.6832 | 30.0358 | 30.0358 | 91.3978 | 0.7 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 63.0219 | 15.2013 | 361790.6637 | 30.1492 | 30.1492 | 91.7632 | 0.8 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 63.0791 | 15.2585 | 363151.6442 | 30.2626 | 30.2626 | 92.1286 | 0.9 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 63.1363 | 15.3157 | 364512.6248 | 30.3761 | 30.3761 | 92.4941 | 1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 63.1935 | 15.3728 | 365873.6053 | 30.4895 | 30.4895 | 92.8595 | 75 | 50 | 27.84 | 28 | 49.1
6/15/20XX 5:00:00 PM | 0.70833 | 5 | 73.1 | 52.3 | 60.7087 | 73.0869 | 12.3783 | 50 | 73.1 |  | 73.1 | 63.5557 | 0.1 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 62.715 | 14.8944 | 354486.7966 | 29.5406 | 29.5406 | 89.1071 | 0.2 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 62.8084 | 14.9878 | 356709.7933 | 29.7258 | 29.7258 | 89.0088 | 0.3 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 62.9018 | 15.0812 | 358932.7899 | 29.9111 | 29.9111 | 88.9106 | 0.4 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 62.9952 | 15.1746 | 361155.7866 | 30.0963 | 30.0963 | 88.8123 | 0.5 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 63.0886 | 15.268 | 363378.7832 | 30.2816 | 30.2816 | 88.7141 | 0.6 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 63.1821 | 15.3614 | 365601.7799 | 30.4668 | 30.4668 | 88.6158 | 0.7 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 63.2755 | 15.4548 | 367824.7765 | 30.6521 | 30.6521 | 88.5176 | 0.8 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 63.3689 | 15.5482 | 370047.7732 | 30.8373 | 30.8373 | 88.4193 | 0.9 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 63.4623 | 15.6416 | 372270.7698 | 31.0226 | 31.0226 | 88.3211 | 1 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 63.5557 | 15.735 | 374493.7665 | 31.2078 | 31.2078 | 88.2228 | 75 | 50 | 27.4818 | 28 | 52.3
6/15/20XX 6:00:00 PM | 0.75 | 5 | 72.3 | 54.4 | 59.0505 | 71.0864 | 12.0359 | 50 | 72.3 |  | 72.3 | 64.3463 | 0.1 | 73.83 | 18.83 | 711774 | 59.3145 | 59.3145 | 62.7941 | 14.9735 | 356368.5057 | 29.6974 | 29.6974 | 89.0119 | 0.2 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 62.9666 | 15.1459 | 360473.2115 | 30.0394 | 30.0394 | 88.8184 | 0.3 | 73.49 | 18.49 | 698922 | 58.2435 | 58.2435 | 63.139 | 15.3184 | 364577.9172 | 30.3815 | 30.3815 | 88.625 | 0.4 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 63.3115 | 15.4909 | 368682.623 | 30.7236 | 30.7236 | 88.4316 | 0.5 | 73.15 | 18.15 | 686070 | 57.1725 | 57.1725 | 63.484 | 15.6633 | 372787.3287 | 31.0656 | 31.0656 | 88.2381 | 0.6 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 63.6564 | 15.8358 | 376892.0345 | 31.4077 | 31.4077 | 88.0447 | 0.7 | 72.81 | 17.81 | 673218 | 56.1015 | 56.1015 | 63.8289 | 16.0083 | 380996.7402 | 31.7497 | 31.7497 | 87.8512 | 0.8 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 64.0014 | 16.1807 | 385101.446 | 32.0918 | 32.0918 | 87.6578 | 0.9 | 72.47 | 17.47 | 660366 | 55.0305 | 55.0305 | 64.1738 | 16.3532 | 389206.1517 | 32.4338 | 32.4338 | 87.4643 | 1 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 64.3463 | 16.5257 | 393310.8574 | 32.7759 | 32.7759 | 87.2709 | 70 | 55 | 27.4102 | 28 | 54.4
6/15/20XX 7:00:00 PM | 0.79167 | 5 | 71.1 | 55.1 | 56.6364 | 68.1744 | 11.5379 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/15/20XX 8:00:00 PM | 0.83333 | 5 | 69.3 | 59.2 | 53.176 | 64.0011 | 10.8251 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/15/20XX 9:00:00 PM | 0.875 | 5 | 68.8 | 59.2 | 52.2482 | 62.8824 | 10.6342 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/15/20XX 10:00:00 PM | 0.91667 | 5 | 68.1 | 61.5 | 61.3451 | 71.7287 | 10.3836 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/15/20XX 11:00:00 PM | 0.95833 | 5 | 67.3 | 63.6 | 59.6291 | 69.7151 | 10.086 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/15/20XX 12:00:00 AM | 0 | 6 | 66.6 | 66.2 | 58.1627 | 67.9946 | 9.8319 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/16/20XX 1:00:00 AM | 0.041667 | 6 | 65.8 | 69.8 | 56.5264 | 66.0748 | 9.5484 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/16/20XX 2:00:00 AM | 0.083333 | 6 | 65 | 70.7 | 64.2037 | 73.5377 | 9.3339 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/16/20XX 3:00:00 AM | 0.125 | 6 | 64.5 | 72.3 | 63.0587 | 72.2236 | 9.1649 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/16/20XX 4:00:00 AM | 0.16667 | 6 | 64 | 75.9 | 61.9322 | 70.9309 | 8.9987 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/16/20XX 5:00:00 AM | 0.20833 | 6 | 63.6 | 78.1 | 61.0441 | 69.912 | 8.8679 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/16/20XX 6:00:00 AM | 0.25 | 6 | 64.7 | 77.4 | 63.5145 | 72.7466 | 9.2322 | 70 | 64.7 |  | 64.7 | 70.3463 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 70.3463 | 22.5257 | 536110.5456 | 44.6759 | 44.6759 | 75.2309 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 70.3463 | 22.5257 | 536110.5456 | 44.6759 | 44.6759 | 75.2309 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 70.3463 | 22.5257 | 536110.5456 | 44.6759 | 44.6759 | 75.2309 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 70.3463 | 22.5257 | 536110.5456 | 44.6759 | 44.6759 | 75.2309 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 70.3463 | 22.5257 | 536110.5456 | 44.6759 | 44.6759 | 75.2309 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 70.3463 | 22.5257 | 536110.5456 | 44.6759 | 44.6759 | 75.2309 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 70.3463 | 22.5257 | 536110.5456 | 44.6759 | 44.6759 | 75.2309 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 70.3463 | 22.5257 | 536110.5456 | 44.6759 | 44.6759 | 75.2309 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 70.3463 | 22.5257 | 536110.5456 | 44.6759 | 44.6759 | 75.2309 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 70.3463 | 22.5257 | 536110.5456 | 44.6759 | 44.6759 | 75.2309 | 65 | 75 | 26.4901 | 26 | 77.4
6/16/20XX 7:00:00 AM | 0.29167 | 6 | 66.2 | 74.3 | 67.0285 | 76.7802 | 9.7517 | 70 | 66.2 |  | 66.2 | 71.2217 | 0.1 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 63.4816 | 15.661 | 372732.0728 | 31.061 | 31.061 | 88.454 | 0.2 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 64.3417 | 16.521 | 393200.3455 | 32.7667 | 32.7667 | 87.7027 | 0.3 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 65.2017 | 17.381 | 413668.6183 | 34.4724 | 34.4724 | 86.9514 | 0.4 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 66.0617 | 18.241 | 434136.891 | 36.1781 | 36.1781 | 86.2001 | 0.5 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 66.9217 | 19.1011 | 454605.1638 | 37.8838 | 37.8838 | 85.4488 | 0.6 | 69.32 | 14.32 | 541296 | 45.108 | 45.108 | 67.7817 | 19.9611 | 475073.4366 | 39.5895 | 39.5895 | 84.6975 | 0.7 | 68.54 | 13.54 | 511812 | 42.651 | 42.651 | 68.6417 | 20.8211 | 495541.7093 | 41.2951 | 41.2951 | 83.9461 | 0.8 | 67.76 | 12.76 | 482328 | 40.194 | 40.194 | 69.5017 | 21.6811 | 516009.9821 | 43.0008 | 43.0008 | 83.1948 | 0.9 | 66.98 | 11.98 | 452844 | 37.737 | 37.737 | 70.3617 | 22.5411 | 536478.2548 | 44.7065 | 44.7065 | 82.4435 | 1 | 66.2 | 11.2 | 423360 | 35.28 | 35.28 | 71.2217 | 23.4011 | 556946.5276 | 46.4122 | 46.4122 | 81.6922 | 65 | 75 | 26.9933 | 26 | 74.3
6/16/20XX 8:00:00 AM | 0.33333 | 6 | 68.3 | 69.1 | 61.7809 | 72.24 | 10.4591 | 60 | 68.3 |  | 68.3 | 71.2987 | 0.1 | 73.43 | 18.43 | 696654 | 58.0545 | 58.0545 | 63.4893 | 15.6687 | 372915.2629 | 31.0763 | 31.0763 | 89.1308 | 0.2 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 64.357 | 16.5364 | 393566.7259 | 32.7972 | 32.7972 | 89.0562 | 0.3 | 72.29 | 17.29 | 653562 | 54.4635 | 54.4635 | 65.2248 | 17.4041 | 414218.1888 | 34.5182 | 34.5182 | 88.9817 | 0.4 | 71.72 | 16.72 | 632016 | 52.668 | 52.668 | 66.0925 | 18.2718 | 434869.6518 | 36.2391 | 36.2391 | 88.9071 | 0.5 | 71.15 | 16.15 | 610470 | 50.8725 | 50.8725 | 66.9602 | 19.1395 | 455521.1147 | 37.9601 | 37.9601 | 88.8326 | 0.6 | 70.58 | 15.58 | 588924 | 49.077 | 49.077 | 67.8279 | 20.0073 | 476172.5777 | 39.681 | 39.681 | 88.758 | 0.7 | 70.01 | 15.01 | 567378 | 47.2815 | 47.2815 | 68.6956 | 20.875 | 496824.0406 | 41.402 | 41.402 | 88.6835 | 0.8 | 69.44 | 14.44 | 545832 | 45.486 | 45.486 | 69.5633 | 21.7427 | 517475.5036 | 43.123 | 43.123 | 88.609 | 0.9 | 68.87 | 13.87 | 524286 | 43.6905 | 43.6905 | 70.431 | 22.6104 | 538126.9665 | 44.8439 | 44.8439 | 88.5344 | 1 | 68.3 | 13.3 | 502740 | 41.895 | 41.895 | 71.2987 | 23.4781 | 558778.4295 | 46.5649 | 46.5649 | 88.4599 | 70 | 70 | 27.5188 | 28 | 69.1
6/16/20XX 9:00:00 AM | 0.375 | 6 | 70.4 | 65.9 | 66.524 | 77.8062 | 11.2822 | 60 | 70.4 |  | 70.4 | 73.1805 | 0.1 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 63.6775 | 15.8569 | 377393.9764 | 31.4495 | 31.4495 | 90.1655 | 0.2 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 64.7334 | 16.9128 | 402524.1528 | 33.5437 | 33.5437 | 91.1257 | 0.3 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 65.7893 | 17.9687 | 427654.3292 | 35.6379 | 35.6379 | 92.0859 | 0.4 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 66.8452 | 19.0246 | 452784.5056 | 37.732 | 37.732 | 93.046 | 0.5 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 67.9011 | 20.0804 | 477914.682 | 39.8262 | 39.8262 | 94.0062 | 0.6 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 68.957 | 21.1363 | 503044.8584 | 41.9204 | 41.9204 | 94.9664 | 0.7 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 70.0129 | 22.1922 | 528175.0348 | 44.0146 | 44.0146 | 95.9266 | 0.8 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 71.0688 | 23.2481 | 553305.2112 | 46.1088 | 46.1088 | 96.8868 | 0.9 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 72.1246 | 24.304 | 578435.3876 | 48.2029 | 48.2029 | 97.8469 | 1 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 73.1805 | 25.3599 | 603565.564 | 50.2971 | 50.2971 | 98.8071 | 70 | 65 | 28.3263 | 28 | 65.9
6/16/20XX 10:00:00 AM | 0.41667 | 6 | 71.8 | 61.6 | 69.8602 | 81.7218 | 11.8616 | 60 | 71.8 |  | 71.8 | 71.7581 | 0.1 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 63.5353 | 15.7146 | 374008.5584 | 31.1674 | 31.1674 | 90.3244 | 0.2 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 64.4489 | 16.6283 | 395753.3167 | 32.9794 | 32.9794 | 91.4434 | 0.3 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 65.3626 | 17.5419 | 417498.0751 | 34.7915 | 34.7915 | 92.5625 | 0.4 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 66.2762 | 18.4556 | 439242.8335 | 36.6036 | 36.6036 | 93.6816 | 0.5 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 67.1899 | 19.3692 | 460987.5919 | 38.4156 | 38.4156 | 94.8006 | 0.6 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 68.1035 | 20.2829 | 482732.3502 | 40.2277 | 40.2277 | 95.9197 | 0.7 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 69.0171 | 21.1965 | 504477.1086 | 42.0398 | 42.0398 | 97.0388 | 0.8 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 69.9308 | 22.1102 | 526221.867 | 43.8518 | 43.8518 | 98.1578 | 0.9 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 70.8444 | 23.0238 | 547966.6254 | 45.6639 | 45.6639 | 99.2769 | 1 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 71.7581 | 23.9375 | 569711.3837 | 47.4759 | 47.4759 | 100.3959 | 70 | 60 | 28.4465 | 28 | 61.6
6/16/20XX 11:00:00 AM | 0.45833 | 6 | 73.9 | 57.1 | 62.4066 | 75.1356 | 12.7291 | 50 | 73.9 |  | 73.9 | 71.4442 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 63.5039 | 15.6833 | 373261.5292 | 31.1051 | 31.1051 | 90.9236 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 64.3861 | 16.5655 | 394259.2584 | 32.8549 | 32.8549 | 92.6419 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 65.2684 | 17.4478 | 415256.9876 | 34.6047 | 34.6047 | 94.3602 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 66.1507 | 18.33 | 436254.7168 | 36.3546 | 36.3546 | 96.0786 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 67.0329 | 19.2123 | 457252.446 | 38.1044 | 38.1044 | 97.7969 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 67.9152 | 20.0945 | 478250.1752 | 39.8542 | 39.8542 | 99.5152 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 68.7974 | 20.9768 | 499247.9044 | 41.604 | 41.604 | 101.2335 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 69.6797 | 21.8591 | 520245.6336 | 43.3538 | 43.3538 | 102.9518 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 70.562 | 22.7413 | 541243.3628 | 45.1036 | 45.1036 | 104.6701 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 71.4442 | 23.6236 | 562241.092 | 46.8534 | 46.8534 | 106.3884 | 75 | 55 | 28.9109 | 28 | 57.1
6/16/20XX 12:00:00 PM | 0.5 | 6 | 74.5 | 56 | 63.7064 | 76.7042 | 12.9978 | 50 | 74.5 |  | 74.5 | 71.5051 | 0.1 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 63.51 | 15.6893 | 373406.5147 | 31.1172 | 31.1172 | 91.1247 | 0.2 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 64.3983 | 16.5777 | 394549.2294 | 32.8791 | 32.8791 | 93.0441 | 0.3 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 65.2867 | 17.466 | 415691.944 | 34.641 | 34.641 | 94.9635 | 0.4 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 66.175 | 18.3544 | 436834.6587 | 36.4029 | 36.4029 | 96.8829 | 0.5 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 67.0634 | 19.2427 | 457977.3734 | 38.1648 | 38.1648 | 98.8023 | 0.6 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 67.9517 | 20.1311 | 479120.0881 | 39.9267 | 39.9267 | 100.7217 | 0.7 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 68.8401 | 21.0194 | 500262.8028 | 41.6886 | 41.6886 | 102.6411 | 0.8 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 69.7284 | 21.9078 | 521405.5174 | 43.4505 | 43.4505 | 104.5605 | 0.9 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 70.6168 | 22.7961 | 542548.2321 | 45.2124 | 45.2124 | 106.4799 | 1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 71.5051 | 23.6845 | 563690.9468 | 46.9742 | 46.9742 | 108.3992 | 75 | 55 | 29.0672 | 30 | 56
6/16/20XX 1:00:00 PM | 0.54167 | 6 | 74.1 | 57.4 | 62.8373 | 75.6554 | 12.8181 | 50 | 74.1 |  | 74.1 | 72.3227 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 63.5917 | 15.7711 | 375352.4023 | 31.2794 | 31.2794 | 91.1609 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 64.5619 | 16.7412 | 398441.0046 | 33.2034 | 33.2034 | 93.1164 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 65.532 | 17.7113 | 421529.6069 | 35.1275 | 35.1275 | 95.072 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 66.5021 | 18.6814 | 444618.2092 | 37.0515 | 37.0515 | 97.0275 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 67.4722 | 19.6515 | 467706.8115 | 38.9756 | 38.9756 | 98.9831 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 68.4423 | 20.6217 | 490795.4138 | 40.8996 | 40.8996 | 100.9386 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 69.4124 | 21.5918 | 513884.0161 | 42.8237 | 42.8237 | 102.8942 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 70.3825 | 22.5619 | 536972.6184 | 44.7477 | 44.7477 | 104.8497 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 71.3526 | 23.532 | 560061.2207 | 46.6718 | 46.6718 | 106.8053 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 72.3227 | 24.5021 | 583149.823 | 48.5958 | 48.5958 | 108.7608 | 75 | 55 | 29.0973 | 30 | 57.4
6/16/20XX 2:00:00 PM | 0.58333 | 6 | 74.2 | 59.3 | 63.0537 | 75.9165 | 12.8628 | 50 | 74.2 |  | 74.2 | 75.0161 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 63.8611 | 16.0404 | 381762.596 | 31.8135 | 31.8135 | 91.7265 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 65.1005 | 17.2799 | 411261.3919 | 34.2718 | 34.2718 | 94.2478 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 66.34 | 18.5193 | 440760.1879 | 36.73 | 36.73 | 96.769 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 67.5794 | 19.7588 | 470258.9839 | 39.1882 | 39.1882 | 99.2902 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 68.8189 | 20.9982 | 499757.7798 | 41.6465 | 41.6465 | 101.8115 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 70.0583 | 22.2377 | 529256.5758 | 44.1047 | 44.1047 | 104.3327 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 71.2977 | 23.4771 | 558755.3717 | 46.5629 | 46.5629 | 106.8539 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 72.5372 | 24.7166 | 588254.1677 | 49.0212 | 49.0212 | 109.3752 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 73.7766 | 25.956 | 617752.9637 | 51.4794 | 51.4794 | 111.8964 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 75.0161 | 27.1955 | 647251.7596 | 53.9376 | 53.9376 | 114.4176 | 75 | 60 | 29.5431 | 30 | 59.3
6/16/20XX 3:00:00 PM | 0.625 | 6 | 74.3 | 59.8 | 63.2706 | 76.1783 | 12.9077 | 50 | 74.3 |  | 74.3 | 75.9201 | 0.1 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 63.9515 | 16.1309 | 383914.2639 | 31.9929 | 31.9929 | 91.9374 | 0.2 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 65.2813 | 17.4607 | 415564.7277 | 34.6304 | 34.6304 | 94.6694 | 0.3 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 66.6112 | 18.7906 | 447215.1916 | 37.2679 | 37.2679 | 97.4014 | 0.4 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 67.941 | 20.1204 | 478865.6554 | 39.9055 | 39.9055 | 100.1335 | 0.5 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 69.2709 | 21.4503 | 510516.1193 | 42.543 | 42.543 | 102.8655 | 0.6 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 70.6007 | 22.7801 | 542166.5831 | 45.1805 | 45.1805 | 105.5975 | 0.7 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 71.9306 | 24.11 | 573817.047 | 47.8181 | 47.8181 | 108.3296 | 0.8 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 73.2604 | 25.4398 | 605467.5109 | 50.4556 | 50.4556 | 111.0616 | 0.9 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 74.5903 | 26.7697 | 637117.9747 | 53.0932 | 53.0932 | 113.7937 | 1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 75.9201 | 28.0995 | 668768.4386 | 55.7307 | 55.7307 | 116.5257 | 75 | 60 | 29.709 | 30 | 59.8
6/16/20XX 4:00:00 PM | 0.66667 | 6 | 74.2 | 59.7 | 63.0537 | 75.9165 | 12.8628 | 50 | 74.2 |  | 74.2 | 75.5306 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 63.9125 | 16.0919 | 382987.1373 | 31.9156 | 31.9156 | 91.8286 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 65.2034 | 17.3828 | 413710.4746 | 34.4759 | 34.4759 | 94.4519 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 66.4943 | 18.6737 | 444433.812 | 37.0362 | 37.0362 | 97.0752 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 67.7852 | 19.9646 | 475157.1493 | 39.5964 | 39.5964 | 99.6984 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 69.0761 | 21.2555 | 505880.4866 | 42.1567 | 42.1567 | 102.3217 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 70.367 | 22.5464 | 536603.8239 | 44.717 | 44.717 | 104.945 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 71.6579 | 23.8373 | 567327.1612 | 47.2773 | 47.2773 | 107.5683 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 72.9488 | 25.1282 | 598050.4986 | 49.8375 | 49.8375 | 110.1915 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 74.2397 | 26.4191 | 628773.8359 | 52.3978 | 52.3978 | 112.8148 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 75.5306 | 27.71 | 659497.1732 | 54.9581 | 54.9581 | 115.4381 | 75 | 60 | 29.6236 | 30 | 59.7
6/16/20XX 5:00:00 PM | 0.70833 | 6 | 73.4 | 61.7 | 73.8495 | 86.4044 | 12.5549 | 60 | 73.4 |  | 73.4 | 75.9838 | 0.1 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 63.9579 | 16.1372 | 384065.8275 | 32.0055 | 32.0055 | 91.6665 | 0.2 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.2941 | 17.4734 | 415867.8549 | 34.6557 | 34.6557 | 94.1277 | 0.3 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 66.6303 | 18.8097 | 447669.8824 | 37.3058 | 37.3058 | 96.5888 | 0.4 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 67.9665 | 20.1459 | 479471.9098 | 39.956 | 39.956 | 99.05 | 0.5 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 69.3027 | 21.4821 | 511273.9373 | 42.6062 | 42.6062 | 101.5112 | 0.6 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 70.639 | 22.8183 | 543075.9647 | 45.2563 | 45.2563 | 103.9723 | 0.7 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 71.9752 | 24.1545 | 574877.9922 | 47.9065 | 47.9065 | 106.4335 | 0.8 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 73.3114 | 25.4908 | 606680.0197 | 50.5567 | 50.5567 | 108.8947 | 0.9 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 74.6476 | 26.827 | 638482.0471 | 53.2068 | 53.2068 | 111.3558 | 1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 75.9838 | 28.1632 | 670284.0746 | 55.857 | 55.857 | 113.817 | 75 | 60 | 29.4986 | 30 | 61.7
6/16/20XX 6:00:00 PM | 0.75 | 6 | 72.5 | 63.3 | 71.5821 | 83.7428 | 12.1608 | 60 | 72.5 |  | 72.5 | 75.5951 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 63.919 | 16.0983 | 383140.6818 | 31.9284 | 31.9284 | 91.3059 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 65.2163 | 17.3957 | 414017.5636 | 34.5015 | 34.5015 | 93.4065 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 66.5137 | 18.693 | 444894.4453 | 37.0745 | 37.0745 | 95.507 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 67.811 | 19.9904 | 475771.3271 | 39.6476 | 39.6476 | 97.6076 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 69.1084 | 21.2877 | 506648.2089 | 42.2207 | 42.2207 | 99.7082 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 70.4057 | 22.5851 | 537525.0907 | 44.7938 | 44.7938 | 101.8088 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 71.7031 | 23.8824 | 568401.9725 | 47.3668 | 47.3668 | 103.9093 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 73.0004 | 25.1798 | 599278.8543 | 49.9399 | 49.9399 | 106.0099 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 74.2978 | 26.4771 | 630155.736 | 52.513 | 52.513 | 108.1105 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 75.5951 | 27.7745 | 661032.6178 | 55.0861 | 55.0861 | 110.2111 | 70 | 65 | 29.2175 | 30 | 63.3
6/16/20XX 7:00:00 PM | 0.79167 | 6 | 71.3 | 66 | 68.6524 | 80.3042 | 11.6518 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/16/20XX 8:00:00 PM | 0.83333 | 6 | 70.6 | 68.5 | 66.992 | 78.3554 | 11.3635 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/16/20XX 9:00:00 PM | 0.875 | 6 | 69.7 | 70.5 | 75.9105 | 86.9813 | 11.0709 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/16/20XX 10:00:00 PM | 0.91667 | 6 | 69.1 | 70.6 | 74.3178 | 85.1515 | 10.8337 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/16/20XX 11:00:00 PM | 0.95833 | 6 | 69.1 | 70.9 | 74.3178 | 85.1515 | 10.8337 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/16/20XX 12:00:00 AM | 0 | 7 | 69 | 72 | 74.0553 | 84.8499 | 10.7946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/17/20XX 1:00:00 AM | 0.041667 | 7 | 67.6 | 76.8 | 70.4642 | 80.7252 | 10.261 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/17/20XX 2:00:00 AM | 0.083333 | 7 | 67.1 | 77.6 | 69.2196 | 79.2959 | 10.0763 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/17/20XX 3:00:00 AM | 0.125 | 7 | 66.5 | 80 | 77.6107 | 87.4565 | 9.8458 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/17/20XX 4:00:00 AM | 0.16667 | 7 | 66.3 | 81.7 | 77.0561 | 86.8295 | 9.7734 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/17/20XX 5:00:00 AM | 0.20833 | 7 | 66.6 | 81.2 | 77.8893 | 87.7716 | 9.8822 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/17/20XX 6:00:00 AM | 0.25 | 7 | 67.3 | 78.1 | 69.7151 | 79.8649 | 10.1498 | 70 | 67.3 |  | 67.3 | 77.9364 | 0.1 | 73.33 | 18.33 | 692874 | 57.7395 | 57.7395 | 64.1531 | 16.3325 | 388713.0303 | 32.3928 | 32.3928 | 90.1323 | 0.2 | 72.66 | 17.66 | 667548 | 55.629 | 55.629 | 65.6846 | 17.864 | 425162.2605 | 35.4302 | 35.4302 | 91.0592 | 0.3 | 71.99 | 16.99 | 642222 | 53.5185 | 53.5185 | 67.2161 | 19.3954 | 461611.4908 | 38.4676 | 38.4676 | 91.9861 | 0.4 | 71.32 | 16.32 | 616896 | 51.408 | 51.408 | 68.7476 | 20.9269 | 498060.7211 | 41.5051 | 41.5051 | 92.9131 | 0.5 | 70.65 | 15.65 | 591570 | 49.2975 | 49.2975 | 70.279 | 22.4584 | 534509.9514 | 44.5425 | 44.5425 | 93.84 | 0.6 | 69.98 | 14.98 | 566244 | 47.187 | 47.187 | 71.8105 | 23.9899 | 570959.1816 | 47.5799 | 47.5799 | 94.7669 | 0.7 | 69.31 | 14.31 | 540918 | 45.0765 | 45.0765 | 73.342 | 25.5214 | 607408.4119 | 50.6174 | 50.6174 | 95.6939 | 0.8 | 68.64 | 13.64 | 515592 | 42.966 | 42.966 | 74.8735 | 27.0528 | 643857.6422 | 53.6548 | 53.6548 | 96.6208 | 0.9 | 67.97 | 12.97 | 490266 | 40.8555 | 40.8555 | 76.405 | 28.5843 | 680306.8724 | 56.6922 | 56.6922 | 97.5477 | 1 | 67.3 | 12.3 | 464940 | 38.745 | 38.745 | 77.9364 | 30.1158 | 716756.1027 | 59.7297 | 59.7297 | 98.4747 | 65 | 80 | 28.3098 | 28 | 78.1
6/17/20XX 7:00:00 AM | 0.29167 | 7 | 68.7 | 73.4 | 73.2724 | 83.9506 | 10.6782 | 70 | 68.7 |  | 68.7 | 76.903 | 0.1 | 73.47 | 18.47 | 698166 | 58.1805 | 58.1805 | 64.0498 | 16.2291 | 386253.5183 | 32.1878 | 32.1878 | 90.3683 | 0.2 | 72.94 | 17.94 | 678132 | 56.511 | 56.511 | 65.4779 | 17.6573 | 420243.2366 | 35.0203 | 35.0203 | 91.5313 | 0.3 | 72.41 | 17.41 | 658098 | 54.8415 | 54.8415 | 66.9061 | 19.0854 | 454232.9549 | 37.8527 | 37.8527 | 92.6942 | 0.4 | 71.88 | 16.88 | 638064 | 53.172 | 53.172 | 68.3342 | 20.5136 | 488222.6732 | 40.6852 | 40.6852 | 93.8572 | 0.5 | 71.35 | 16.35 | 618030 | 51.5025 | 51.5025 | 69.7623 | 21.9417 | 522212.3915 | 43.5177 | 43.5177 | 95.0202 | 0.6 | 70.82 | 15.82 | 597996 | 49.833 | 49.833 | 71.1905 | 23.3698 | 556202.1098 | 46.3502 | 46.3502 | 96.1832 | 0.7 | 70.29 | 15.29 | 577962 | 48.1635 | 48.1635 | 72.6186 | 24.798 | 590191.8281 | 49.1827 | 49.1827 | 97.3462 | 0.8 | 69.76 | 14.76 | 557928 | 46.494 | 46.494 | 74.0467 | 26.2261 | 624181.5464 | 52.0151 | 52.0151 | 98.5091 | 0.9 | 69.23 | 14.23 | 537894 | 44.8245 | 44.8245 | 75.4749 | 27.6543 | 658171.2647 | 54.8476 | 54.8476 | 99.6721 | 1 | 68.7 | 13.7 | 517860 | 43.155 | 43.155 | 76.903 | 29.0824 | 692160.983 | 57.6801 | 57.6801 | 100.8351 | 70 | 75 | 28.4914 | 28 | 73.4
6/17/20XX 8:00:00 AM | 0.33333 | 7 | 70.2 | 70.5 | 77.2604 | 88.5325 | 11.2721 | 70 | 70.2 |  | 70.2 | 77.824 | 0.1 | 73.62 | 18.62 | 703836 | 58.653 | 58.653 | 64.1419 | 16.3212 | 388445.4829 | 32.3705 | 32.3705 | 91.0235 | 0.2 | 73.24 | 18.24 | 689472 | 57.456 | 57.456 | 65.6621 | 17.8415 | 424627.1658 | 35.3856 | 35.3856 | 92.8416 | 0.3 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 67.1823 | 19.3617 | 460808.8487 | 38.4007 | 38.4007 | 94.6597 | 0.4 | 72.48 | 17.48 | 660744 | 55.062 | 55.062 | 68.7026 | 20.882 | 496990.5316 | 41.4159 | 41.4159 | 96.4779 | 0.5 | 72.1 | 17.1 | 646380 | 53.865 | 53.865 | 70.2228 | 22.4022 | 533172.2145 | 44.431 | 44.431 | 98.296 | 0.6 | 71.72 | 16.72 | 632016 | 52.668 | 52.668 | 71.7431 | 23.9224 | 569353.8974 | 47.4462 | 47.4462 | 100.1142 | 0.7 | 71.34 | 16.34 | 617652 | 51.471 | 51.471 | 73.2633 | 25.4427 | 605535.5803 | 50.4613 | 50.4613 | 101.9323 | 0.8 | 70.96 | 15.96 | 603288 | 50.274 | 50.274 | 74.7835 | 26.9629 | 641717.2632 | 53.4764 | 53.4764 | 103.7504 | 0.9 | 70.58 | 15.58 | 588924 | 49.077 | 49.077 | 76.3038 | 28.4831 | 677898.9461 | 56.4916 | 56.4916 | 105.5686 | 1 | 70.2 | 15.2 | 574560 | 47.88 | 47.88 | 77.824 | 30.0034 | 714080.629 | 59.5067 | 59.5067 | 107.3867 | 70 | 70 | 29.0026 | 30 | 70.5
6/17/20XX 9:00:00 AM | 0.375 | 7 | 71.6 | 66.7 | 69.3749 | 81.1522 | 11.7773 | 60 | 71.6 |  | 71.6 | 77.2657 | 0.1 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 64.086 | 16.2654 | 387116.6946 | 32.2597 | 32.2597 | 91.3537 | 0.2 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 65.5504 | 17.7298 | 421969.5893 | 35.1641 | 35.1641 | 93.5021 | 0.3 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 67.0149 | 19.1942 | 456822.4839 | 38.0685 | 38.0685 | 95.6505 | 0.4 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 68.4793 | 20.6586 | 491675.3786 | 40.9729 | 40.9729 | 97.7989 | 0.5 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 69.9437 | 22.123 | 526528.2732 | 43.8774 | 43.8774 | 99.9474 | 0.6 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 71.4081 | 23.5874 | 561381.1679 | 46.7818 | 46.7818 | 102.0958 | 0.7 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 72.8725 | 25.0519 | 596234.0625 | 49.6862 | 49.6862 | 104.2442 | 0.8 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 74.3369 | 26.5163 | 631086.9572 | 52.5906 | 52.5906 | 106.3926 | 0.9 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 75.8013 | 27.9807 | 665939.8518 | 55.495 | 55.495 | 108.541 | 1 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 77.2657 | 29.4451 | 700792.7464 | 58.3994 | 58.3994 | 110.6894 | 70 | 65 | 29.2582 | 30 | 66.7
6/17/20XX 10:00:00 AM | 0.41667 | 7 | 73.5 | 63.4 | 74.1052 | 86.7045 | 12.5993 | 60 | 73.5 |  | 73.5 | 78.389 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 64.1984 | 16.3777 | 389790.0762 | 32.4825 | 32.4825 | 92.175 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 65.7751 | 17.9545 | 427316.3524 | 35.6097 | 35.6097 | 95.1447 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 67.3518 | 19.5312 | 464842.6286 | 38.7369 | 38.7369 | 98.1144 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 68.9286 | 21.1079 | 502368.9048 | 41.8641 | 41.8641 | 101.0841 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 70.5053 | 22.6847 | 539895.181 | 44.9913 | 44.9913 | 104.0538 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 72.082 | 24.2614 | 577421.4572 | 48.1185 | 48.1185 | 107.0235 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 73.6588 | 25.8381 | 614947.7334 | 51.2456 | 51.2456 | 109.9931 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 75.2355 | 27.4149 | 652474.0096 | 54.3728 | 54.3728 | 112.9628 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 76.8122 | 28.9916 | 690000.2858 | 57.5 | 57.5 | 115.9325 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 78.389 | 30.5683 | 727526.562 | 60.6272 | 60.6272 | 118.9022 | 75 | 65 | 29.8992 | 30 | 63.4
6/17/20XX 11:00:00 AM | 0.45833 | 7 | 75.6 | 58.6 | 66.1493 | 79.6526 | 13.5032 | 50 | 75.6 |  | 75.6 | 77.7621 | 0.1 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 64.1357 | 16.315 | 388298.1436 | 32.3582 | 32.3582 | 92.7122 | 0.2 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 65.6497 | 17.8291 | 424332.4872 | 35.361 | 35.361 | 96.219 | 0.3 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 67.1638 | 19.3431 | 460366.8308 | 38.3639 | 38.3639 | 99.7259 | 0.4 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 68.6778 | 20.8572 | 496401.1743 | 41.3668 | 41.3668 | 103.2328 | 0.5 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 70.1919 | 22.3712 | 532435.5179 | 44.3696 | 44.3696 | 106.7396 | 0.6 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 71.7059 | 23.8853 | 568469.8615 | 47.3725 | 47.3725 | 110.2465 | 0.7 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 73.22 | 25.3993 | 604504.2051 | 50.3754 | 50.3754 | 113.7534 | 0.8 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 74.734 | 26.9134 | 640538.5487 | 53.3782 | 53.3782 | 117.2602 | 0.9 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 76.2481 | 28.4274 | 676572.8923 | 56.3811 | 56.3811 | 120.7671 | 1 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 77.7621 | 29.9415 | 712607.2358 | 59.3839 | 59.3839 | 124.2739 | 75 | 60 | 30.3156 | 30 | 58.6
6/17/20XX 12:00:00 PM | 0.5 | 7 | 76.2 | 58 | 67.5149 | 81.3009 | 13.786 | 50 | 76.2 |  | 76.2 | 78.5437 | 0.1 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 64.2138 | 16.3932 | 390158.2495 | 32.5132 | 32.5132 | 93.0562 | 0.2 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 65.806 | 17.9854 | 428052.699 | 35.6711 | 35.6711 | 96.9071 | 0.3 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 67.3982 | 19.5776 | 465947.1485 | 38.8289 | 38.8289 | 100.7579 | 0.4 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 68.9904 | 21.1698 | 503841.598 | 41.9868 | 41.9868 | 104.6088 | 0.5 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 70.5827 | 22.762 | 541736.0475 | 45.1447 | 45.1447 | 108.4597 | 0.6 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 72.1749 | 24.3542 | 579630.497 | 48.3025 | 48.3025 | 112.3105 | 0.7 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 73.7671 | 25.9464 | 617524.9466 | 51.4604 | 51.4604 | 116.1614 | 0.8 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 75.3593 | 27.5386 | 655419.3961 | 54.6183 | 54.6183 | 120.0123 | 0.9 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 76.9515 | 29.1308 | 693313.8456 | 57.7762 | 57.7762 | 123.8632 | 1 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 78.5437 | 30.723 | 731208.2951 | 60.934 | 60.934 | 127.714 | 75 | 60 | 30.5849 | 30 | 58
6/17/20XX 1:00:00 PM | 0.54167 | 7 | 75.4 | 58.5 | 65.6994 | 79.1095 | 13.4101 | 50 | 75.4 |  | 75.4 | 77.0979 | 0.1 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 64.0693 | 16.2486 | 386717.4277 | 32.2265 | 32.2265 | 92.5175 | 0.2 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 65.5169 | 17.6963 | 421171.0554 | 35.0976 | 35.0976 | 95.8296 | 0.3 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 66.9645 | 19.1439 | 455624.6832 | 37.9687 | 37.9687 | 99.1417 | 0.4 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 68.4122 | 20.5915 | 490078.3109 | 40.8399 | 40.8399 | 102.4539 | 0.5 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 69.8598 | 22.0392 | 524531.9386 | 43.711 | 43.711 | 105.766 | 0.6 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 71.3074 | 23.4868 | 558985.5663 | 46.5821 | 46.5821 | 109.0781 | 0.7 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 72.7551 | 24.9344 | 593439.194 | 49.4533 | 49.4533 | 112.3903 | 0.8 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 74.2027 | 26.3821 | 627892.8218 | 52.3244 | 52.3244 | 115.7024 | 0.9 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 75.6503 | 27.8297 | 662346.4495 | 55.1955 | 55.1955 | 119.0145 | 1 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 77.0979 | 29.2773 | 696800.0772 | 58.0667 | 58.0667 | 122.3267 | 75 | 60 | 30.1626 | 30 | 58.5
6/17/20XX 2:00:00 PM | 0.58333 | 7 | 75.7 | 58.4 | 66.3753 | 79.9253 | 13.55 | 50 | 75.7 |  | 75.7 | 77.7573 | 0.1 | 74.17 | 19.17 | 724626 | 60.3855 | 60.3855 | 64.1352 | 16.3146 | 388286.6872 | 32.3572 | 32.3572 | 92.7427 | 0.2 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 65.6488 | 17.8281 | 424309.5745 | 35.3591 | 35.3591 | 96.2801 | 0.3 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 67.1623 | 19.3417 | 460332.4617 | 38.361 | 38.361 | 99.8175 | 0.4 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 68.6759 | 20.8553 | 496355.3489 | 41.3629 | 41.3629 | 103.3549 | 0.5 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 70.1895 | 22.3688 | 532378.2362 | 44.3649 | 44.3649 | 106.8924 | 0.6 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 71.703 | 23.8824 | 568401.1234 | 47.3668 | 47.3668 | 110.4298 | 0.7 | 75.19 | 20.19 | 763182 | 63.5985 | 63.5985 | 73.2166 | 25.396 | 604424.0106 | 50.3687 | 50.3687 | 113.9672 | 0.8 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 74.7302 | 26.9095 | 640446.8978 | 53.3706 | 53.3706 | 117.5046 | 0.9 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 76.2437 | 28.4231 | 676469.7851 | 56.3725 | 56.3725 | 121.042 | 1 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 77.7573 | 29.9367 | 712492.6723 | 59.3744 | 59.3744 | 124.5794 | 75 | 60 | 30.3393 | 30 | 58.4
6/17/20XX 3:00:00 PM | 0.625 | 7 | 74.2 | 62 | 75.9165 | 88.8307 | 12.9142 | 60 | 74.2 |  | 74.2 | 78.4993 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 64.2094 | 16.3888 | 390052.7133 | 32.5044 | 32.5044 | 92.4174 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 65.7972 | 17.9765 | 427841.6265 | 35.6535 | 35.6535 | 95.6295 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 67.3849 | 19.5643 | 465630.5398 | 38.8025 | 38.8025 | 98.8415 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 68.9727 | 21.1521 | 503419.453 | 41.9516 | 41.9516 | 102.0536 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 70.5605 | 22.7398 | 541208.3663 | 45.1007 | 45.1007 | 105.2657 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 72.1482 | 24.3276 | 578997.2795 | 48.2498 | 48.2498 | 108.4778 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 73.736 | 25.9154 | 616786.1928 | 51.3988 | 51.3988 | 111.6898 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 75.3238 | 27.5032 | 654575.106 | 54.5479 | 54.5479 | 114.9019 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 76.9116 | 29.0909 | 692364.0193 | 57.697 | 57.697 | 118.114 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 78.4993 | 30.6787 | 730152.9325 | 60.8461 | 60.8461 | 121.3261 | 75 | 60 | 30.088 | 30 | 62
6/17/20XX 4:00:00 PM | 0.66667 | 7 | 73.5 | 62.5 | 74.1052 | 86.7045 | 12.5993 | 60 | 73.5 |  | 73.5 | 77.255 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 64.085 | 16.2643 | 387091.303 | 32.2576 | 32.2576 | 91.9501 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 65.5483 | 17.7277 | 421918.8059 | 35.1599 | 35.1599 | 94.6949 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 67.0117 | 19.191 | 456746.3089 | 38.0622 | 38.0622 | 97.4397 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 68.475 | 20.6544 | 491573.8119 | 40.9645 | 40.9645 | 100.1845 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 69.9383 | 22.1177 | 526401.3149 | 43.8668 | 43.8668 | 102.9293 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 71.4017 | 23.581 | 561228.8178 | 46.7691 | 46.7691 | 105.6741 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 72.865 | 25.0444 | 596056.3208 | 49.6714 | 49.6714 | 108.4189 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 74.3284 | 26.5077 | 630883.8238 | 52.5737 | 52.5737 | 111.1637 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 75.7917 | 27.9711 | 665711.3267 | 55.4759 | 55.4759 | 113.9084 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 77.255 | 29.4344 | 700538.8297 | 58.3782 | 58.3782 | 116.6532 | 75 | 60 | 29.7219 | 30 | 62.5
6/17/20XX 5:00:00 PM | 0.70833 | 7 | 72.5 | 62.6 | 71.5821 | 83.7428 | 12.1608 | 60 | 72.5 |  | 72.5 | 74.7439 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 63.8339 | 16.0132 | 381114.6958 | 31.7596 | 31.7596 | 91.1371 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 65.0461 | 17.2254 | 409965.5916 | 34.1638 | 34.1638 | 93.0688 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 66.2583 | 18.4377 | 438816.4873 | 36.568 | 36.568 | 95.0005 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 67.4705 | 19.6499 | 467667.3831 | 38.9723 | 38.9723 | 96.9323 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 68.6827 | 20.8621 | 496518.2789 | 41.3765 | 41.3765 | 98.864 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 69.895 | 22.0743 | 525369.1747 | 43.7808 | 43.7808 | 100.7958 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 71.1072 | 23.2866 | 554220.0705 | 46.185 | 46.185 | 102.7275 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 72.3194 | 24.4988 | 583070.9663 | 48.5892 | 48.5892 | 104.6592 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 73.5316 | 25.711 | 611921.862 | 50.9935 | 50.9935 | 106.591 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 74.7439 | 26.9232 | 640772.7578 | 53.3977 | 53.3977 | 108.5227 | 70 | 65 | 29.0844 | 30 | 62.6
6/17/20XX 6:00:00 PM | 0.75 | 7 | 71.9 | 64.1 | 70.104 | 82.008 | 11.904 | 60 | 71.9 |  | 71.9 | 74.9846 | 0.1 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 63.8579 | 16.0373 | 381687.6959 | 31.8073 | 31.8073 | 90.9958 | 0.2 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 65.0942 | 17.2736 | 411111.5918 | 34.2593 | 34.2593 | 92.7863 | 0.3 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 66.3305 | 18.5099 | 440535.4876 | 36.7113 | 36.7113 | 94.5768 | 0.4 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 67.5668 | 19.7462 | 469959.3835 | 39.1633 | 39.1633 | 96.3673 | 0.5 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 68.8031 | 20.9825 | 499383.2794 | 41.6153 | 41.6153 | 98.1578 | 0.6 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 70.0394 | 22.2188 | 528807.1753 | 44.0673 | 44.0673 | 99.9483 | 0.7 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 71.2757 | 23.4551 | 558231.0711 | 46.5193 | 46.5193 | 101.7388 | 0.8 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 72.512 | 24.6914 | 587654.967 | 48.9712 | 48.9712 | 103.5292 | 0.9 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 73.7483 | 25.9277 | 617078.8629 | 51.4232 | 51.4232 | 105.3197 | 1 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 74.9846 | 27.164 | 646502.7588 | 53.8752 | 53.8752 | 107.1102 | 70 | 65 | 28.9752 | 28 | 64.1
6/17/20XX 7:00:00 PM | 0.79167 | 7 | 70.7 | 67.2 | 67.227 | 78.6313 | 11.4043 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/17/20XX 8:00:00 PM | 0.83333 | 7 | 69.9 | 68.7 | 65.3666 | 76.4479 | 11.0813 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/17/20XX 9:00:00 PM | 0.875 | 7 | 69.2 | 69.9 | 63.776 | 74.5812 | 10.8052 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/17/20XX 10:00:00 PM | 0.91667 | 7 | 68.8 | 71.8 | 73.5326 | 84.2494 | 10.7169 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/17/20XX 11:00:00 PM | 0.95833 | 7 | 68.1 | 73.4 | 71.7287 | 82.1774 | 10.4487 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/17/20XX 12:00:00 AM | 0 | 1 | 67.9 | 75.4 | 71.2205 | 81.5937 | 10.3732 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/18/20XX 1:00:00 AM | 0.041667 | 1 | 67.1 | 77.9 | 69.2196 | 79.2959 | 10.0763 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/18/20XX 2:00:00 AM | 0.083333 | 1 | 67 | 79.3 | 68.973 | 79.0128 | 10.0398 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/18/20XX 3:00:00 AM | 0.125 | 1 | 66.6 | 80.4 | 77.8893 | 87.7716 | 9.8822 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/18/20XX 4:00:00 AM | 0.16667 | 1 | 66.3 | 81 | 77.0561 | 86.8295 | 9.7734 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/18/20XX 5:00:00 AM | 0.20833 | 1 | 66.6 | 79.1 | 67.9946 | 77.8893 | 9.8947 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/18/20XX 6:00:00 AM | 0.25 | 1 | 67.1 | 78.5 | 69.2196 | 79.2959 | 10.0763 | 70 | 67.1 |  | 67.1 | 77.7845 | 0.1 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 64.1379 | 16.3173 | 388351.3662 | 32.3626 | 32.3626 | 90.0391 | 0.2 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 65.6542 | 17.8336 | 424438.9323 | 35.3699 | 35.3699 | 90.8729 | 0.3 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 67.1705 | 19.3499 | 460526.4985 | 38.3772 | 38.3772 | 91.7067 | 0.4 | 71.24 | 16.24 | 613872 | 51.156 | 51.156 | 68.6868 | 20.8661 | 496614.0647 | 41.3845 | 41.3845 | 92.5405 | 0.5 | 70.55 | 15.55 | 587790 | 48.9825 | 48.9825 | 70.2031 | 22.3824 | 532701.6309 | 44.3918 | 44.3918 | 93.3743 | 0.6 | 69.86 | 14.86 | 561708 | 46.809 | 46.809 | 71.7193 | 23.8987 | 568789.197 | 47.3991 | 47.3991 | 94.2081 | 0.7 | 69.17 | 14.17 | 535626 | 44.6355 | 44.6355 | 73.2356 | 25.415 | 604876.7632 | 50.4064 | 50.4064 | 95.0419 | 0.8 | 68.48 | 13.48 | 509544 | 42.462 | 42.462 | 74.7519 | 26.9313 | 640964.3294 | 53.4137 | 53.4137 | 95.8757 | 0.9 | 67.79 | 12.79 | 483462 | 40.2885 | 40.2885 | 76.2682 | 28.4476 | 677051.8956 | 56.421 | 56.421 | 96.7095 | 1 | 67.1 | 12.1 | 457380 | 38.115 | 38.115 | 77.7845 | 29.9638 | 713139.4617 | 59.4283 | 59.4283 | 97.5433 | 65 | 80 | 28.2371 | 28 | 78.5
6/18/20XX 7:00:00 AM | 0.29167 | 1 | 68.7 | 75.1 | 73.2724 | 83.9506 | 10.6782 | 70 | 68.7 |  | 68.7 | 78.7183 | 0.1 | 73.47 | 18.47 | 698166 | 58.1805 | 58.1805 | 64.2313 | 16.4107 | 390573.9128 | 32.5478 | 32.5478 | 90.7283 | 0.2 | 72.94 | 17.94 | 678132 | 56.511 | 56.511 | 65.841 | 18.0203 | 428884.0256 | 35.7403 | 35.7403 | 92.2513 | 0.3 | 72.41 | 17.41 | 658098 | 54.8415 | 54.8415 | 67.4506 | 19.63 | 467194.1384 | 38.9328 | 38.9328 | 93.7743 | 0.4 | 71.88 | 16.88 | 638064 | 53.172 | 53.172 | 69.0603 | 21.2397 | 505504.2512 | 42.1254 | 42.1254 | 95.2974 | 0.5 | 71.35 | 16.35 | 618030 | 51.5025 | 51.5025 | 70.67 | 22.8493 | 543814.364 | 45.3179 | 45.3179 | 96.8204 | 0.6 | 70.82 | 15.82 | 597996 | 49.833 | 49.833 | 72.2796 | 24.459 | 582124.4768 | 48.5104 | 48.5104 | 98.3434 | 0.7 | 70.29 | 15.29 | 577962 | 48.1635 | 48.1635 | 73.8893 | 26.0687 | 620434.5895 | 51.7029 | 51.7029 | 99.8664 | 0.8 | 69.76 | 14.76 | 557928 | 46.494 | 46.494 | 75.499 | 27.6783 | 658744.7023 | 54.8954 | 54.8954 | 101.3894 | 0.9 | 69.23 | 14.23 | 537894 | 44.8245 | 44.8245 | 77.1086 | 29.288 | 697054.8151 | 58.0879 | 58.0879 | 102.9124 | 1 | 68.7 | 13.7 | 517860 | 43.155 | 43.155 | 78.7183 | 30.8977 | 735364.9279 | 61.2804 | 61.2804 | 104.4354 | 70 | 75 | 28.7747 | 28 | 75.1
6/18/20XX 8:00:00 AM | 0.33333 | 1 | 70.8 | 72.4 | 78.908 | 90.4259 | 11.5179 | 70 | 70.8 |  | 70.8 | 81.6723 | 0.1 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 64.5267 | 16.7061 | 397604.3388 | 33.1337 | 33.1337 | 91.9757 | 0.2 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 66.4318 | 18.6111 | 442944.8776 | 36.9121 | 36.9121 | 94.7461 | 0.3 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 68.3368 | 20.5162 | 488285.4164 | 40.6905 | 40.6905 | 97.5165 | 0.4 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 70.2419 | 22.4213 | 533625.9553 | 44.4688 | 44.4688 | 100.2868 | 0.5 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 72.147 | 24.3263 | 578966.4941 | 48.2472 | 48.2472 | 103.0572 | 0.6 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 74.052 | 26.2314 | 624307.0329 | 52.0256 | 52.0256 | 105.8276 | 0.7 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 75.9571 | 28.1365 | 669647.5717 | 55.804 | 55.804 | 108.598 | 0.8 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 77.8621 | 30.0415 | 714988.1105 | 59.5823 | 59.5823 | 111.3683 | 0.9 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 79.7672 | 31.9466 | 760328.6493 | 63.3607 | 63.3607 | 114.1387 | 1 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 81.6723 | 33.8516 | 805669.1881 | 67.1391 | 67.1391 | 116.9091 | 70 | 70 | 29.7507 | 30 | 72.4
6/18/20XX 9:00:00 AM | 0.375 | 1 | 72.7 | 68.2 | 72.0807 | 84.3281 | 12.2474 | 60 | 72.7 |  | 72.7 | 82.1236 | 0.1 | 73.87 | 18.87 | 713286 | 59.4405 | 59.4405 | 64.5718 | 16.7512 | 398678.4277 | 33.2232 | 33.2232 | 92.6637 | 0.2 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 66.522 | 18.7014 | 445093.0554 | 37.0911 | 37.0911 | 96.1221 | 0.3 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 68.4722 | 20.6516 | 491507.6832 | 40.959 | 40.959 | 99.5805 | 0.4 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 70.4224 | 22.6018 | 537922.3109 | 44.8269 | 44.8269 | 103.0389 | 0.5 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 72.3726 | 24.552 | 584336.9386 | 48.6947 | 48.6947 | 106.4972 | 0.6 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 74.3228 | 26.5022 | 630751.5663 | 52.5626 | 52.5626 | 109.9556 | 0.7 | 73.09 | 18.09 | 683802 | 56.9835 | 56.9835 | 76.273 | 28.4524 | 677166.194 | 56.4305 | 56.4305 | 113.414 | 0.8 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 78.2232 | 30.4026 | 723580.8217 | 60.2984 | 60.2984 | 116.8724 | 0.9 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 80.1734 | 32.3527 | 769995.4495 | 64.1663 | 64.1663 | 120.3308 | 1 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 82.1236 | 34.3029 | 816410.0772 | 68.0342 | 68.0342 | 123.7892 | 75 | 70 | 30.2871 | 30 | 68.2
6/18/20XX 10:00:00 AM | 0.41667 | 1 | 74.9 | 64.8 | 77.7654 | 91.0012 | 13.2358 | 60 | 74.9 |  | 74.9 | 84.1186 | 0.1 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 64.7713 | 16.9507 | 403426.5889 | 33.6189 | 33.6189 | 93.7524 | 0.2 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 66.921 | 19.1004 | 454589.3778 | 37.8824 | 37.8824 | 98.2994 | 0.3 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 69.0707 | 21.2501 | 505752.1667 | 42.146 | 42.146 | 102.8465 | 0.4 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 71.2204 | 23.3998 | 556914.9556 | 46.4096 | 46.4096 | 107.3936 | 0.5 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 73.3701 | 25.5495 | 608077.7445 | 50.6731 | 50.6731 | 111.9406 | 0.6 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 75.5198 | 27.6992 | 659240.5334 | 54.9367 | 54.9367 | 116.4877 | 0.7 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 77.6695 | 29.8489 | 710403.3223 | 59.2003 | 59.2003 | 121.0348 | 0.8 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 79.8192 | 31.9986 | 761566.1112 | 63.4638 | 63.4638 | 125.5818 | 0.9 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 81.9689 | 34.1483 | 812728.9001 | 67.7274 | 67.7274 | 130.1289 | 1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 84.1186 | 36.298 | 863891.689 | 71.991 | 71.991 | 134.676 | 75 | 65 | 31.1388 | 32 | 64.8
6/18/20XX 11:00:00 AM | 0.45833 | 1 | 77.8 | 60.2 | 85.8376 | 100.478 | 14.6404 | 60 | 77.8 |  | 77.8 | 86.1304 | 0.1 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 64.9725 | 17.1519 | 408214.6863 | 34.0179 | 34.0179 | 95.0649 | 0.2 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 67.3234 | 19.5028 | 464165.5726 | 38.6805 | 38.6805 | 100.9245 | 0.3 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 69.6743 | 21.8536 | 520116.459 | 43.343 | 43.343 | 106.784 | 0.4 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 72.0251 | 24.2045 | 576067.3453 | 48.0056 | 48.0056 | 112.6436 | 0.5 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 74.376 | 26.5554 | 632018.2316 | 52.6682 | 52.6682 | 118.5032 | 0.6 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 76.7269 | 28.9063 | 687969.1179 | 57.3308 | 57.3308 | 124.3628 | 0.7 | 76.66 | 21.66 | 818748 | 68.229 | 68.229 | 79.0778 | 31.2571 | 743920.0042 | 61.9933 | 61.9933 | 130.2223 | 0.8 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 81.4287 | 33.608 | 799870.8905 | 66.6559 | 66.6559 | 136.0819 | 0.9 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 83.7795 | 35.9589 | 855821.7769 | 71.3185 | 71.3185 | 141.9415 | 1 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 86.1304 | 38.3098 | 911772.6632 | 75.9811 | 75.9811 | 147.8011 | 80 | 60 | 32.1654 | 32 | 60.2
6/18/20XX 12:00:00 PM | 0.5 | 1 | 79.3 | 56.9 | 74.9531 | 90.2816 | 15.3285 | 50 | 79.3 |  | 79.3 | 85.5297 | 0.1 | 74.53 | 19.53 | 738234 | 61.5195 | 61.5195 | 64.9124 | 17.0918 | 406785.0451 | 33.8988 | 33.8988 | 95.4183 | 0.2 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 67.2032 | 19.3826 | 461306.2902 | 38.4422 | 38.4422 | 101.6312 | 0.3 | 75.59 | 20.59 | 778302 | 64.8585 | 64.8585 | 69.4941 | 21.6734 | 515827.5353 | 42.9856 | 42.9856 | 107.8441 | 0.4 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 71.7849 | 23.9642 | 570348.7804 | 47.5291 | 47.5291 | 114.0571 | 0.5 | 76.65 | 21.65 | 818370 | 68.1975 | 68.1975 | 74.0757 | 26.255 | 624870.0255 | 52.0725 | 52.0725 | 120.27 | 0.6 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 76.3665 | 28.5459 | 679391.2706 | 56.6159 | 56.6159 | 126.4829 | 0.7 | 77.71 | 22.71 | 858438 | 71.5365 | 71.5365 | 78.6573 | 30.8367 | 733912.5158 | 61.1594 | 61.1594 | 132.6959 | 0.8 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 80.9481 | 33.1275 | 788433.7609 | 65.7028 | 65.7028 | 138.9088 | 0.9 | 78.77 | 23.77 | 898506 | 74.8755 | 74.8755 | 83.2389 | 35.4183 | 842955.006 | 70.2463 | 70.2463 | 145.1218 | 1 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 85.5297 | 37.7091 | 897476.2511 | 74.7897 | 74.7897 | 151.3347 | 80 | 55 | 32.4395 | 32 | 56.9
6/18/20XX 1:00:00 PM | 0.54167 | 1 | 78.9 | 56.7 | 73.9565 | 89.0782 | 15.1216 | 50 | 78.9 |  | 78.9 | 84.088 | 0.1 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 64.7683 | 16.9476 | 403353.8253 | 33.6128 | 33.6128 | 95.0063 | 0.2 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 66.9149 | 19.0943 | 454443.8506 | 37.8703 | 37.8703 | 100.8073 | 0.3 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 69.0616 | 21.2409 | 505533.8759 | 42.1278 | 42.1278 | 106.6083 | 0.4 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 71.2082 | 23.3876 | 556623.9012 | 46.3853 | 46.3853 | 112.4093 | 0.5 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 73.3548 | 25.5342 | 607713.9265 | 50.6428 | 50.6428 | 118.2103 | 0.6 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 75.5015 | 27.6808 | 658803.9518 | 54.9003 | 54.9003 | 124.0113 | 0.7 | 77.43 | 22.43 | 847854 | 70.6545 | 70.6545 | 77.6481 | 29.8275 | 709893.9771 | 59.1578 | 59.1578 | 129.8123 | 0.8 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 79.7948 | 31.9741 | 760984.0024 | 63.4153 | 63.4153 | 135.6133 | 0.9 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 81.9414 | 34.1208 | 812074.0277 | 67.6728 | 67.6728 | 141.4143 | 1 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 84.088 | 36.2674 | 863164.053 | 71.9303 | 71.9303 | 147.2153 | 80 | 55 | 32.1153 | 32 | 56.7
6/18/20XX 2:00:00 PM | 0.58333 | 1 | 78.5 | 59.4 | 72.9711 | 87.8882 | 14.9171 | 50 | 78.5 |  | 78.5 | 86.9931 | 0.1 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 65.0588 | 17.2382 | 410267.9784 | 34.189 | 34.189 | 95.4565 | 0.2 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 67.4959 | 19.6753 | 468272.1567 | 39.0227 | 39.0227 | 101.7077 | 0.3 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 69.9331 | 22.1125 | 526276.3351 | 43.8564 | 43.8564 | 107.9589 | 0.4 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 72.3702 | 24.5496 | 584280.5134 | 48.69 | 48.69 | 114.21 | 0.5 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 74.8074 | 26.9868 | 642284.6918 | 53.5237 | 53.5237 | 120.4612 | 0.6 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 77.2445 | 29.4239 | 700288.8702 | 58.3574 | 58.3574 | 126.7124 | 0.7 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 79.6817 | 31.8611 | 758293.0485 | 63.1911 | 63.1911 | 132.9636 | 0.8 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 82.1188 | 34.2982 | 816297.2269 | 68.0248 | 68.0248 | 139.2148 | 0.9 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 84.556 | 36.7354 | 874301.4052 | 72.8585 | 72.8585 | 145.466 | 1 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 86.9931 | 39.1725 | 932305.5836 | 77.6921 | 77.6921 | 151.7171 | 80 | 60 | 32.4724 | 32 | 59.4
6/18/20XX 3:00:00 PM | 0.625 | 1 | 77.1 | 61.1 | 83.8273 | 98.1177 | 14.2905 | 60 | 77.1 |  | 77.1 | 85.3992 | 0.1 | 74.31 | 19.31 | 729918 | 60.8265 | 60.8265 | 64.8994 | 17.0788 | 406474.4514 | 33.8729 | 33.8729 | 94.6994 | 0.2 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 67.1771 | 19.3565 | 460685.1027 | 38.3904 | 38.3904 | 100.1934 | 0.3 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 69.4549 | 21.6343 | 514895.7541 | 42.908 | 42.908 | 105.6875 | 0.4 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 71.7327 | 23.912 | 569106.4055 | 47.4255 | 47.4255 | 111.1815 | 0.5 | 75.55 | 20.55 | 776790 | 64.7325 | 64.7325 | 74.0104 | 26.1898 | 623317.0568 | 51.9431 | 51.9431 | 116.6756 | 0.6 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 76.2882 | 28.4676 | 677527.7082 | 56.4606 | 56.4606 | 122.1696 | 0.7 | 76.17 | 21.17 | 800226 | 66.6855 | 66.6855 | 78.5659 | 30.7453 | 731738.3596 | 60.9782 | 60.9782 | 127.6637 | 0.8 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 80.8437 | 33.0231 | 785949.0109 | 65.4958 | 65.4958 | 133.1578 | 0.9 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 83.1215 | 35.3008 | 840159.6623 | 70.0133 | 70.0133 | 138.6518 | 1 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 85.3992 | 37.5786 | 894370.3137 | 74.5309 | 74.5309 | 144.1459 | 75 | 60 | 31.8791 | 32 | 61.1
6/18/20XX 4:00:00 PM | 0.66667 | 1 | 76.8 | 62.8 | 82.9779 | 97.1205 | 14.1426 | 60 | 76.8 |  | 76.8 | 86.9378 | 0.1 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 65.0533 | 17.2326 | 410136.3336 | 34.178 | 34.178 | 94.91 | 0.2 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 67.4849 | 19.6642 | 468008.8672 | 39.0007 | 39.0007 | 100.6147 | 0.3 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 69.9165 | 22.0959 | 525881.4008 | 43.8235 | 43.8235 | 106.3195 | 0.4 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 72.3481 | 24.5275 | 583753.9344 | 48.6462 | 48.6462 | 112.0242 | 0.5 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 74.7797 | 26.9591 | 641626.468 | 53.4689 | 53.4689 | 117.7289 | 0.6 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 77.2113 | 29.3907 | 699499.0016 | 58.2916 | 58.2916 | 123.4336 | 0.7 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 79.643 | 31.8223 | 757371.5352 | 63.1143 | 63.1143 | 129.1383 | 0.8 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 82.0746 | 34.254 | 815244.0688 | 67.937 | 67.937 | 134.843 | 0.9 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 84.5062 | 36.6856 | 873116.6023 | 72.7597 | 72.7597 | 140.5477 | 1 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 86.9378 | 39.1172 | 930989.1359 | 77.5824 | 77.5824 | 146.2524 | 75 | 65 | 32.0464 | 32 | 62.8
6/18/20XX 5:00:00 PM | 0.70833 | 1 | 75.8 | 63.1 | 80.1988 | 93.8579 | 13.6591 | 60 | 75.8 |  | 75.8 | 84.4331 | 0.1 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 64.8028 | 16.9822 | 404175.1731 | 33.6813 | 33.6813 | 94.0983 | 0.2 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 66.9839 | 19.1633 | 456086.5461 | 38.0072 | 38.0072 | 98.9912 | 0.3 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 69.1651 | 21.3445 | 507997.9192 | 42.3332 | 42.3332 | 103.8842 | 0.4 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 71.3462 | 23.5256 | 559909.2922 | 46.6591 | 46.6591 | 108.7771 | 0.5 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 73.5274 | 25.7068 | 611820.6653 | 50.9851 | 50.9851 | 113.6701 | 0.6 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 75.7085 | 27.8879 | 663732.0383 | 55.311 | 55.311 | 118.563 | 0.7 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 77.8897 | 30.0691 | 715643.4114 | 59.637 | 59.637 | 123.456 | 0.8 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 80.0708 | 32.2502 | 767554.7844 | 63.9629 | 63.9629 | 128.3489 | 0.9 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 82.252 | 34.4314 | 819466.1575 | 68.2888 | 68.2888 | 133.2418 | 1 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 84.4331 | 36.6125 | 871377.5305 | 72.6148 | 72.6148 | 138.1348 | 75 | 65 | 31.4088 | 32 | 63.1
6/18/20XX 6:00:00 PM | 0.75 | 1 | 75.4 | 62.5 | 79.1095 | 92.579 | 13.4695 | 60 | 75.4 |  | 75.4 | 82.4768 | 0.1 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 64.6072 | 16.7865 | 399519.2113 | 33.2933 | 33.2933 | 93.5843 | 0.2 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 66.5927 | 18.772 | 446774.6227 | 37.2312 | 37.2312 | 97.9632 | 0.3 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 68.5782 | 20.7576 | 494030.034 | 41.1692 | 41.1692 | 102.3422 | 0.4 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 70.5637 | 22.7431 | 541285.4453 | 45.1071 | 45.1071 | 106.7211 | 0.5 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 72.5492 | 24.7286 | 588540.8567 | 49.0451 | 49.0451 | 111.1001 | 0.6 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 74.5348 | 26.7141 | 635796.268 | 52.983 | 52.983 | 115.479 | 0.7 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 76.5203 | 28.6997 | 683051.6793 | 56.921 | 56.921 | 119.858 | 0.8 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 78.5058 | 30.6852 | 730307.0907 | 60.8589 | 60.8589 | 124.2369 | 0.9 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 80.4913 | 32.6707 | 777562.502 | 64.7969 | 64.7969 | 128.6159 | 1 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 82.4768 | 34.6562 | 824817.9133 | 68.7348 | 68.7348 | 132.9948 | 75 | 60 | 31.0045 | 32 | 62.5
6/18/20XX 7:00:00 PM | 0.79167 | 1 | 74.1 | 64.9 | 75.6554 | 88.5243 | 12.8688 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/18/20XX 8:00:00 PM | 0.83333 | 1 | 72.3 | 70.3 | 83.1611 | 95.3147 | 12.1536 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/18/20XX 9:00:00 PM | 0.875 | 1 | 71.7 | 71.5 | 81.4366 | 93.3322 | 11.8956 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/18/20XX 10:00:00 PM | 0.91667 | 1 | 71.4 | 72.4 | 80.586 | 92.3545 | 11.7685 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/18/20XX 11:00:00 PM | 0.95833 | 1 | 71.1 | 73 | 79.7432 | 91.3858 | 11.6426 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/18/20XX 12:00:00 AM | 0 | 2 | 70.5 | 74.1 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/19/20XX 1:00:00 AM | 0.041667 | 2 | 70.1 | 75.7 | 76.9888 | 88.2203 | 11.2316 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/19/20XX 2:00:00 AM | 0.083333 | 2 | 68.1 | 78 | 71.7287 | 82.1774 | 10.4487 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/19/20XX 3:00:00 AM | 0.125 | 2 | 69.5 | 77.1 | 75.3763 | 86.3676 | 10.9913 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/19/20XX 4:00:00 AM | 0.16667 | 2 | 69.1 | 77.4 | 74.3178 | 85.1515 | 10.8337 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/19/20XX 5:00:00 AM | 0.20833 | 2 | 68.8 | 78.5 | 73.5326 | 84.2494 | 10.7169 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/19/20XX 6:00:00 AM | 0.25 | 2 | 69.2 | 78.8 | 74.5812 | 85.4541 | 10.8729 | 70 | 69.2 |  | 69.2 | 84.1494 | 0.1 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 64.7744 | 16.9538 | 403499.8239 | 33.625 | 33.625 | 91.963 | 0.2 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 66.9272 | 19.1065 | 454735.8478 | 37.8947 | 37.8947 | 94.7207 | 0.3 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 69.08 | 21.2593 | 505971.8717 | 42.1643 | 42.1643 | 97.4783 | 0.4 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 71.2327 | 23.4121 | 557207.8956 | 46.434 | 46.434 | 100.236 | 0.5 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 73.3855 | 25.5649 | 608443.9195 | 50.7037 | 50.7037 | 102.9937 | 0.6 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 75.5383 | 27.7176 | 659679.9434 | 54.9733 | 54.9733 | 105.7513 | 0.7 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 77.6911 | 29.8704 | 710915.9673 | 59.243 | 59.243 | 108.509 | 0.8 | 70.16 | 15.16 | 573048 | 47.754 | 47.754 | 79.8438 | 32.0232 | 762151.9912 | 63.5127 | 63.5127 | 111.2667 | 0.9 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 81.9966 | 34.176 | 813388.0151 | 67.7823 | 67.7823 | 114.0243 | 1 | 69.2 | 14.2 | 536760 | 44.73 | 44.73 | 84.1494 | 36.3287 | 864624.0391 | 72.052 | 72.052 | 116.782 | 70 | 80 | 29.7451 | 30 | 78.8
6/19/20XX 7:00:00 AM | 0.29167 | 2 | 69.8 | 76.2 | 76.1788 | 87.2896 | 11.1108 | 70 | 69.8 |  | 69.8 | 83.0675 | 0.1 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 64.6662 | 16.8456 | 400925.0039 | 33.4104 | 33.4104 | 91.9374 | 0.2 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 66.7108 | 18.8902 | 449586.2078 | 37.4655 | 37.4655 | 94.6695 | 0.3 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 68.7554 | 20.9348 | 498247.4117 | 41.5206 | 41.5206 | 97.4016 | 0.4 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 70.8 | 22.9794 | 546908.6156 | 45.5757 | 45.5757 | 100.1337 | 0.5 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 72.8446 | 25.0239 | 595569.8195 | 49.6308 | 49.6308 | 102.8658 | 0.6 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 74.8892 | 27.0685 | 644231.0234 | 53.6859 | 53.6859 | 105.5979 | 0.7 | 71.06 | 16.06 | 607068 | 50.589 | 50.589 | 76.9338 | 29.1131 | 692892.2273 | 57.741 | 57.741 | 108.33 | 0.8 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 78.9783 | 31.1577 | 741553.4312 | 61.7961 | 61.7961 | 111.0621 | 0.9 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 81.0229 | 33.2023 | 790214.6351 | 65.8512 | 65.8512 | 113.7942 | 1 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 83.0675 | 35.2469 | 838875.839 | 69.9063 | 69.9063 | 116.5263 | 70 | 75 | 29.7234 | 30 | 76.2
6/19/20XX 8:00:00 AM | 0.33333 | 2 | 71.3 | 72.2 | 80.3042 | 92.0306 | 11.7264 | 70 | 71.3 |  | 71.3 | 82.884 | 0.1 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 64.6479 | 16.8272 | 400488.3199 | 33.374 | 33.374 | 92.3735 | 0.2 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 66.6741 | 18.8535 | 448712.8399 | 37.3927 | 37.3927 | 95.5417 | 0.3 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 68.7004 | 20.8797 | 496937.3598 | 41.4114 | 41.4114 | 98.7099 | 0.4 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 70.7266 | 22.906 | 545161.8797 | 45.4302 | 45.4302 | 101.8782 | 0.5 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 72.7528 | 24.9322 | 593386.3996 | 49.4489 | 49.4489 | 105.0464 | 0.6 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 74.7791 | 26.9584 | 641610.9196 | 53.4676 | 53.4676 | 108.2146 | 0.7 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 76.8053 | 28.9847 | 689835.4395 | 57.4863 | 57.4863 | 111.3828 | 0.8 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 78.8316 | 31.0109 | 738059.9594 | 61.505 | 61.505 | 114.551 | 0.9 | 71.57 | 16.57 | 626346 | 52.1955 | 52.1955 | 80.8578 | 33.0372 | 786284.4793 | 65.5237 | 65.5237 | 117.7192 | 1 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 82.884 | 35.0634 | 834508.9993 | 69.5424 | 69.5424 | 120.8874 | 70 | 70 | 30.0626 | 30 | 72.2
6/19/20XX 9:00:00 AM | 0.375 | 2 | 73 | 68.1 | 72.8342 | 85.2126 | 12.3784 | 60 | 73 |  | 73 | 82.8607 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.6455 | 16.8249 | 400432.8631 | 33.3694 | 33.3694 | 92.9044 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 66.6695 | 18.8488 | 448601.9263 | 37.3835 | 37.3835 | 96.6035 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 68.6934 | 20.8727 | 496770.9894 | 41.3976 | 41.3976 | 100.3026 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 70.7173 | 22.8966 | 544940.0525 | 45.4117 | 45.4117 | 104.0017 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 72.7412 | 24.9206 | 593109.1156 | 49.4258 | 49.4258 | 107.7008 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 74.7651 | 26.9445 | 641278.1788 | 53.4398 | 53.4398 | 111.3998 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 76.789 | 28.9684 | 689447.2419 | 57.4539 | 57.4539 | 115.0989 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 78.8129 | 30.9923 | 737616.305 | 61.468 | 61.468 | 118.798 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 80.8368 | 33.0162 | 785785.3681 | 65.4821 | 65.4821 | 122.4971 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 82.8607 | 35.0401 | 833954.4313 | 69.4962 | 69.4962 | 126.1962 | 75 | 70 | 30.4759 | 30 | 68.1
6/19/20XX 10:00:00 AM | 0.41667 | 2 | 74.7 | 65.1 | 77.2333 | 90.3765 | 13.1432 | 60 | 74.7 |  | 74.7 | 83.9363 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 64.7531 | 16.9325 | 402992.7765 | 33.5827 | 33.5827 | 93.6532 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 66.8846 | 19.0639 | 453721.7529 | 37.8101 | 37.8101 | 98.1011 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 69.016 | 21.1954 | 504450.7294 | 42.0376 | 42.0376 | 102.5491 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 71.1475 | 23.3269 | 555179.7058 | 46.265 | 46.265 | 106.997 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 73.279 | 25.4583 | 605908.6823 | 50.4924 | 50.4924 | 111.4449 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 75.4104 | 27.5898 | 656637.6587 | 54.7198 | 54.7198 | 115.8928 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 77.5419 | 29.7213 | 707366.6352 | 58.9472 | 58.9472 | 120.3407 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 79.6734 | 31.8528 | 758095.6117 | 63.1746 | 63.1746 | 124.7886 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 81.8049 | 33.9842 | 808824.5881 | 67.402 | 67.402 | 129.2365 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 83.9363 | 36.1157 | 859553.5646 | 71.6295 | 71.6295 | 133.6845 | 75 | 65 | 31.0612 | 32 | 65.1
6/19/20XX 11:00:00 AM | 0.45833 | 2 | 77.6 | 58.5 | 70.7937 | 85.2591 | 14.4654 | 50 | 77.6 |  | 77.6 | 83.0893 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 64.6684 | 16.8478 | 400976.8978 | 33.4147 | 33.4147 | 94.3987 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 66.7152 | 18.8945 | 449689.9957 | 37.4742 | 37.4742 | 99.5922 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 68.7619 | 20.9413 | 498403.0935 | 41.5336 | 41.5336 | 104.7856 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 70.8087 | 22.9881 | 547116.1914 | 45.593 | 45.593 | 109.979 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 72.8555 | 25.0348 | 595829.2892 | 49.6524 | 49.6524 | 115.1724 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 74.9022 | 27.0816 | 644542.3871 | 53.7119 | 53.7119 | 120.3659 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 76.949 | 29.1284 | 693255.4849 | 57.7713 | 57.7713 | 125.5593 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 78.9958 | 31.1752 | 741968.5828 | 61.8307 | 61.8307 | 130.7527 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 81.0426 | 33.2219 | 790681.6806 | 65.8901 | 65.8901 | 135.9461 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 83.0893 | 35.2687 | 839394.7785 | 69.9496 | 69.9496 | 141.1396 | 80 | 60 | 31.6399 | 32 | 58.5
6/19/20XX 12:00:00 PM | 0.5 | 2 | 79.5 | 55.2 | 75.4555 | 90.8883 | 15.4328 | 50 | 79.5 |  | 79.5 | 83.4805 | 0.1 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 64.7075 | 16.8869 | 401908.0011 | 33.4923 | 33.4923 | 95.0748 | 0.2 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 66.7934 | 18.9728 | 451552.2021 | 37.6294 | 37.6294 | 100.9444 | 0.3 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 68.8793 | 21.0587 | 501196.4032 | 41.7664 | 41.7664 | 106.8139 | 0.4 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 70.9652 | 23.1446 | 550840.6043 | 45.9034 | 45.9034 | 112.6834 | 0.5 | 76.75 | 21.75 | 822150 | 68.5125 | 68.5125 | 73.0511 | 25.2305 | 600484.8053 | 50.0404 | 50.0404 | 118.5529 | 0.6 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 75.137 | 27.3163 | 650129.0064 | 54.1774 | 54.1774 | 124.4224 | 0.7 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 77.2229 | 29.4022 | 699773.2075 | 58.3144 | 58.3144 | 130.2919 | 0.8 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 79.3088 | 31.4881 | 749417.4086 | 62.4515 | 62.4515 | 136.1615 | 0.9 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 81.3946 | 33.574 | 799061.6096 | 66.5885 | 66.5885 | 142.031 | 1 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 83.4805 | 35.6599 | 848705.8107 | 70.7255 | 70.7255 | 147.9005 | 80 | 55 | 32.1673 | 32 | 55.2
6/19/20XX 1:00:00 PM | 0.54167 | 2 | 80 | 52.8 | 76.7237 | 92.42 | 15.6963 | 50 | 80 |  | 80 | 81.1187 | 0.1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 64.4713 | 16.6507 | 396286.7518 | 33.0239 | 33.0239 | 94.7639 | 0.2 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 66.321 | 18.5004 | 440309.7035 | 36.6925 | 36.6925 | 100.3225 | 0.3 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 68.1707 | 20.3501 | 484332.6553 | 40.3611 | 40.3611 | 105.8811 | 0.4 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 70.0204 | 22.1998 | 528355.6071 | 44.0296 | 44.0296 | 111.4396 | 0.5 | 77 | 22 | 831600 | 69.3 | 69.3 | 71.8702 | 24.0495 | 572378.5589 | 47.6982 | 47.6982 | 116.9982 | 0.6 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 73.7199 | 25.8992 | 616401.5106 | 51.3668 | 51.3668 | 122.5568 | 0.7 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 75.5696 | 27.7489 | 660424.4624 | 55.0354 | 55.0354 | 128.1154 | 0.8 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 77.4193 | 29.5986 | 704447.4142 | 58.704 | 58.704 | 133.674 | 0.9 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 79.269 | 31.4483 | 748470.366 | 62.3725 | 62.3725 | 139.2325 | 1 | 80 | 25 | 945000 | 78.75 | 78.75 | 81.1187 | 33.298 | 792493.3177 | 66.0411 | 66.0411 | 144.7911 | 80 | 55 | 31.9196 | 32 | 52.8
6/19/20XX 2:00:00 PM | 0.58333 | 2 | 79.6 | 53.7 | 75.7077 | 91.1929 | 15.4852 | 50 | 79.6 |  | 79.6 | 81.4373 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 64.5032 | 16.6826 | 397044.9732 | 33.0871 | 33.0871 | 94.7011 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 66.3848 | 18.5641 | 441826.1465 | 36.8188 | 36.8188 | 100.1968 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 68.2663 | 20.4457 | 486607.3197 | 40.5506 | 40.5506 | 105.6926 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 70.1479 | 22.3272 | 531388.4929 | 44.2824 | 44.2824 | 111.1884 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 72.0294 | 24.2088 | 576169.6662 | 48.0141 | 48.0141 | 116.6841 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 73.911 | 26.0904 | 620950.8394 | 51.7459 | 51.7459 | 122.1799 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 75.7926 | 27.9719 | 665732.0127 | 55.4777 | 55.4777 | 127.6757 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 77.6741 | 29.8535 | 710513.1859 | 59.2094 | 59.2094 | 133.1714 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 79.5557 | 31.7351 | 755294.3591 | 62.9412 | 62.9412 | 138.6672 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 81.4373 | 33.6166 | 800075.5324 | 66.673 | 66.673 | 144.163 | 80 | 55 | 31.8715 | 32 | 53.7
6/19/20XX 3:00:00 PM | 0.625 | 2 | 79.2 | 55 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 82.3412 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 64.5936 | 16.773 | 399196.2936 | 33.2664 | 33.2664 | 94.7544 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 66.5655 | 18.7449 | 446128.7871 | 37.1774 | 37.1774 | 100.3034 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 68.5375 | 20.7169 | 493061.2807 | 41.0884 | 41.0884 | 105.8524 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 70.5094 | 22.6888 | 539993.7743 | 44.9995 | 44.9995 | 111.4015 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 72.4814 | 24.6608 | 586926.2678 | 48.9105 | 48.9105 | 116.9505 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 74.4534 | 26.6327 | 633858.7614 | 52.8216 | 52.8216 | 122.4996 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 76.4253 | 28.6047 | 680791.255 | 56.7326 | 56.7326 | 128.0486 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 78.3973 | 30.5766 | 727723.7485 | 60.6436 | 60.6436 | 133.5976 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 80.3692 | 32.5486 | 774656.2421 | 64.5547 | 64.5547 | 139.1467 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 82.3412 | 34.5205 | 821588.7357 | 68.4657 | 68.4657 | 144.6957 | 80 | 55 | 31.9151 | 32 | 55
6/19/20XX 4:00:00 PM | 0.66667 | 2 | 78.7 | 55.7 | 73.4624 | 88.4815 | 15.0191 | 50 | 78.7 |  | 78.7 | 82.0233 | 0.1 | 74.47 | 19.47 | 735966 | 61.3305 | 61.3305 | 64.5618 | 16.7412 | 398439.7668 | 33.2033 | 33.2033 | 94.5338 | 0.2 | 74.94 | 19.94 | 753732 | 62.811 | 62.811 | 66.502 | 18.6813 | 444615.7337 | 37.0513 | 37.0513 | 99.8623 | 0.3 | 75.41 | 20.41 | 771498 | 64.2915 | 64.2915 | 68.4421 | 20.6215 | 490791.7005 | 40.8993 | 40.8993 | 105.1908 | 0.4 | 75.88 | 20.88 | 789264 | 65.772 | 65.772 | 70.3823 | 22.5617 | 536967.6673 | 44.7473 | 44.7473 | 110.5193 | 0.5 | 76.35 | 21.35 | 807030 | 67.2525 | 67.2525 | 72.3225 | 24.5018 | 583143.6341 | 48.5953 | 48.5953 | 115.8478 | 0.6 | 76.82 | 21.82 | 824796 | 68.733 | 68.733 | 74.2626 | 26.442 | 629319.601 | 52.4433 | 52.4433 | 121.1763 | 0.7 | 77.29 | 22.29 | 842562 | 70.2135 | 70.2135 | 76.2028 | 28.3822 | 675495.5678 | 56.2913 | 56.2913 | 126.5048 | 0.8 | 77.76 | 22.76 | 860328 | 71.694 | 71.694 | 78.143 | 30.3223 | 721671.5346 | 60.1393 | 60.1393 | 131.8333 | 0.9 | 78.23 | 23.23 | 878094 | 73.1745 | 73.1745 | 80.0831 | 32.2625 | 767847.5015 | 63.9873 | 63.9873 | 137.1618 | 1 | 78.7 | 23.7 | 895860 | 74.655 | 74.655 | 82.0233 | 34.2027 | 814023.4683 | 67.8353 | 67.8353 | 142.4903 | 80 | 55 | 31.7427 | 32 | 55.7
6/19/20XX 5:00:00 PM | 0.70833 | 2 | 76.9 | 58.4 | 69.138 | 83.2602 | 14.1222 | 50 | 76.9 |  | 76.9 | 81.0006 | 0.1 | 74.29 | 19.29 | 729162 | 60.7635 | 60.7635 | 64.4595 | 16.6389 | 396005.8605 | 33.0005 | 33.0005 | 93.764 | 0.2 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 66.2974 | 18.4768 | 439747.921 | 36.6457 | 36.6457 | 98.3227 | 0.3 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 68.1353 | 20.3147 | 483489.9815 | 40.2908 | 40.2908 | 102.8813 | 0.4 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 69.9732 | 22.1526 | 527232.042 | 43.936 | 43.936 | 107.44 | 0.5 | 75.45 | 20.45 | 773010 | 64.4175 | 64.4175 | 71.8111 | 23.9905 | 570974.1025 | 47.5812 | 47.5812 | 111.9987 | 0.6 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 73.649 | 25.8284 | 614716.1629 | 51.2263 | 51.2263 | 116.5573 | 0.7 | 76.03 | 21.03 | 794934 | 66.2445 | 66.2445 | 75.4869 | 27.6663 | 658458.2234 | 54.8715 | 54.8715 | 121.116 | 0.8 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 77.3248 | 29.5042 | 702200.2839 | 58.5167 | 58.5167 | 125.6747 | 0.9 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 79.1627 | 31.3421 | 745942.3444 | 62.1619 | 62.1619 | 130.2334 | 1 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 81.0006 | 33.18 | 789684.4049 | 65.807 | 65.807 | 134.792 | 75 | 60 | 31.1412 | 32 | 58.4
6/19/20XX 6:00:00 PM | 0.75 | 2 | 75.8 | 60 | 80.1988 | 93.8579 | 13.6591 | 60 | 75.8 |  | 75.8 | 80.1988 | 0.1 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 64.3794 | 16.5587 | 394097.5226 | 32.8415 | 32.8415 | 93.2585 | 0.2 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 66.1371 | 18.3164 | 435931.2452 | 36.3276 | 36.3276 | 97.3116 | 0.3 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 67.8948 | 20.0742 | 477764.9679 | 39.8137 | 39.8137 | 101.3647 | 0.4 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 69.6525 | 21.8319 | 519598.6905 | 43.2999 | 43.2999 | 105.4179 | 0.5 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 71.4102 | 23.5896 | 561432.4131 | 46.786 | 46.786 | 109.471 | 0.6 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 73.1679 | 25.3473 | 603266.1357 | 50.2722 | 50.2722 | 113.5242 | 0.7 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 74.9257 | 27.105 | 645099.8583 | 53.7583 | 53.7583 | 117.5773 | 0.8 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 76.6834 | 28.8628 | 686933.581 | 57.2445 | 57.2445 | 121.6305 | 0.9 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 78.4411 | 30.6205 | 728767.3036 | 60.7306 | 60.7306 | 125.6836 | 1 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 80.1988 | 32.3782 | 770601.0262 | 64.2168 | 64.2168 | 129.7368 | 75 | 60 | 30.746 | 30 | 60
6/19/20XX 7:00:00 PM | 0.79167 | 2 | 74.4 | 62.4 | 76.4409 | 89.4463 | 13.0054 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/19/20XX 8:00:00 PM | 0.83333 | 2 | 72.6 | 66.9 | 71.831 | 84.035 | 12.204 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/19/20XX 9:00:00 PM | 0.875 | 2 | 71.7 | 69.3 | 69.6172 | 81.4366 | 11.8194 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/19/20XX 10:00:00 PM | 0.91667 | 2 | 71.1 | 70.2 | 79.7432 | 91.3858 | 11.6426 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/19/20XX 11:00:00 PM | 0.95833 | 2 | 70.6 | 72 | 78.3554 | 89.7909 | 11.4354 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/19/20XX 12:00:00 AM | 0 | 3 | 69.3 | 72.3 | 74.8454 | 85.7577 | 10.9122 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/20/20XX 1:00:00 AM | 0.041667 | 3 | 69.7 | 70.1 | 75.9105 | 86.9813 | 11.0709 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/20/20XX 2:00:00 AM | 0.083333 | 3 | 69.1 | 69.3 | 63.5515 | 74.3178 | 10.7663 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/20/20XX 3:00:00 AM | 0.125 | 3 | 68.6 | 70.4 | 73.0131 | 83.6528 | 10.6396 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/20/20XX 4:00:00 AM | 0.16667 | 3 | 67.9 | 72.6 | 71.2205 | 81.5937 | 10.3732 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/20/20XX 5:00:00 AM | 0.20833 | 3 | 67.7 | 73.2 | 70.7155 | 81.0138 | 10.2983 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/20/20XX 6:00:00 AM | 0.25 | 3 | 68.1 | 72.5 | 71.7287 | 82.1774 | 10.4487 | 70 | 68.1 |  | 68.1 | 74.3409 | 0.1 | 73.41 | 18.41 | 695898 | 57.9915 | 57.9915 | 63.7936 | 15.9729 | 380155.5415 | 31.6796 | 31.6796 | 89.6711 | 0.2 | 72.82 | 17.82 | 673596 | 56.133 | 56.133 | 64.9655 | 17.1448 | 408047.283 | 34.0039 | 34.0039 | 90.1369 | 0.3 | 72.23 | 17.23 | 651294 | 54.2745 | 54.2745 | 66.1374 | 18.3168 | 435939.0245 | 36.3283 | 36.3283 | 90.6028 | 0.4 | 71.64 | 16.64 | 628992 | 52.416 | 52.416 | 67.3093 | 19.4887 | 463830.766 | 38.6526 | 38.6526 | 91.0686 | 0.5 | 71.05 | 16.05 | 606690 | 50.5575 | 50.5575 | 68.4812 | 20.6606 | 491722.5076 | 40.9769 | 40.9769 | 91.5344 | 0.6 | 70.46 | 15.46 | 584388 | 48.699 | 48.699 | 69.6532 | 21.8325 | 519614.2491 | 43.3012 | 43.3012 | 92.0002 | 0.7 | 69.87 | 14.87 | 562086 | 46.8405 | 46.8405 | 70.8251 | 23.0045 | 547505.9906 | 45.6255 | 45.6255 | 92.466 | 0.8 | 69.28 | 14.28 | 539784 | 44.982 | 44.982 | 71.997 | 24.1764 | 575397.7321 | 47.9498 | 47.9498 | 92.9318 | 0.9 | 68.69 | 13.69 | 517482 | 43.1235 | 43.1235 | 73.1689 | 25.3483 | 603289.4736 | 50.2741 | 50.2741 | 93.3976 | 1 | 68.1 | 13.1 | 495180 | 41.265 | 41.265 | 74.3409 | 26.5202 | 631181.2151 | 52.5984 | 52.5984 | 93.8634 | 70 | 70 | 27.9447 | 28 | 72.5
6/20/20XX 7:00:00 AM | 0.29167 | 3 | 69.3 | 70.7 | 74.8454 | 85.7577 | 10.9122 | 70 | 69.3 |  | 69.3 | 75.6093 | 0.1 | 73.53 | 18.53 | 700434 | 58.3695 | 58.3695 | 63.9204 | 16.0998 | 383174.378 | 31.9312 | 31.9312 | 90.3007 | 0.2 | 73.06 | 18.06 | 682668 | 56.889 | 56.889 | 65.2192 | 17.3985 | 414084.9561 | 34.5071 | 34.5071 | 91.3961 | 0.3 | 72.59 | 17.59 | 664902 | 55.4085 | 55.4085 | 66.5179 | 18.6973 | 444995.5341 | 37.083 | 37.083 | 92.4915 | 0.4 | 72.12 | 17.12 | 647136 | 53.928 | 53.928 | 67.8167 | 19.9961 | 475906.1121 | 39.6588 | 39.6588 | 93.5868 | 0.5 | 71.65 | 16.65 | 629370 | 52.4475 | 52.4475 | 69.1155 | 21.2948 | 506816.6902 | 42.2347 | 42.2347 | 94.6822 | 0.6 | 71.18 | 16.18 | 611604 | 50.967 | 50.967 | 70.4142 | 22.5936 | 537727.2682 | 44.8106 | 44.8106 | 95.7776 | 0.7 | 70.71 | 15.71 | 593838 | 49.4865 | 49.4865 | 71.713 | 23.8923 | 568637.8462 | 47.3865 | 47.3865 | 96.873 | 0.8 | 70.24 | 15.24 | 576072 | 48.006 | 48.006 | 73.0117 | 25.1911 | 599548.4242 | 49.9624 | 49.9624 | 97.9684 | 0.9 | 69.77 | 14.77 | 558306 | 46.5255 | 46.5255 | 74.3105 | 26.4899 | 630459.0023 | 52.5383 | 52.5383 | 99.0638 | 1 | 69.3 | 14.3 | 540540 | 45.045 | 45.045 | 75.6093 | 27.7886 | 661369.5803 | 55.1141 | 55.1141 | 100.1591 | 70 | 70 | 28.4363 | 28 | 70.7
6/20/20XX 8:00:00 AM | 0.33333 | 3 | 71 | 66.8 | 67.9365 | 79.4639 | 11.5275 | 60 | 71 |  | 71 | 75.7751 | 0.1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 63.937 | 16.1164 | 383569.14 | 31.9641 | 31.9641 | 90.8691 | 0.2 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 65.2523 | 17.4317 | 414874.4799 | 34.5729 | 34.5729 | 92.5329 | 0.3 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 66.5677 | 18.7471 | 446179.8199 | 37.1817 | 37.1817 | 94.1967 | 0.4 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 67.883 | 20.0624 | 477485.1599 | 39.7904 | 39.7904 | 95.8604 | 0.5 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 69.1984 | 21.3778 | 508790.4998 | 42.3992 | 42.3992 | 97.5242 | 0.6 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 70.5137 | 22.6931 | 540095.8398 | 45.008 | 45.008 | 99.188 | 0.7 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 71.8291 | 24.0085 | 571401.1798 | 47.6168 | 47.6168 | 100.8518 | 0.8 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 73.1444 | 25.3238 | 602706.5197 | 50.2255 | 50.2255 | 102.5155 | 0.9 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 74.4598 | 26.6392 | 634011.8597 | 52.8343 | 52.8343 | 104.1793 | 1 | 71 | 16 | 604800 | 50.4 | 50.4 | 75.7751 | 27.9545 | 665317.1997 | 55.4431 | 55.4431 | 105.8431 | 70 | 65 | 28.8784 | 28 | 66.8
6/20/20XX 9:00:00 AM | 0.375 | 3 | 73 | 62.6 | 72.8342 | 85.2126 | 12.3784 | 60 | 73 |  | 73 | 76.0526 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 63.9647 | 16.1441 | 384229.5462 | 32.0191 | 32.0191 | 91.5541 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 65.3078 | 17.4872 | 416195.2923 | 34.6829 | 34.6829 | 93.9029 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 66.6509 | 18.8303 | 448161.0385 | 37.3468 | 37.3468 | 96.2518 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 67.994 | 20.1734 | 480126.7847 | 40.0106 | 40.0106 | 98.6006 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 69.3371 | 21.5165 | 512092.5308 | 42.6744 | 42.6744 | 100.9494 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 70.6802 | 22.8596 | 544058.277 | 45.3382 | 45.3382 | 103.2982 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 72.0233 | 24.2027 | 576024.0232 | 48.002 | 48.002 | 105.647 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 73.3664 | 25.5458 | 607989.7693 | 50.6658 | 50.6658 | 107.9958 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 74.7095 | 26.8889 | 639955.5155 | 53.3296 | 53.3296 | 110.3446 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 76.0526 | 28.232 | 671921.2617 | 55.9934 | 55.9934 | 112.6934 | 75 | 65 | 29.4114 | 30 | 62.6
6/20/20XX 10:00:00 AM | 0.41667 | 3 | 75.1 | 58.3 | 65.0293 | 78.3007 | 13.2714 | 50 | 75.1 |  | 75.1 | 76.0446 | 0.1 | 74.11 | 19.11 | 722358 | 60.1965 | 60.1965 | 63.9639 | 16.1433 | 384210.3563 | 32.0175 | 32.0175 | 92.214 | 0.2 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 65.3062 | 17.4856 | 416156.9127 | 34.6797 | 34.6797 | 95.2227 | 0.3 | 74.33 | 19.33 | 730674 | 60.8895 | 60.8895 | 66.6485 | 18.8279 | 448103.469 | 37.342 | 37.342 | 98.2315 | 0.4 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 67.9908 | 20.1702 | 480050.0254 | 40.0042 | 40.0042 | 101.2402 | 0.5 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 69.3331 | 21.5125 | 511996.5817 | 42.6664 | 42.6664 | 104.2489 | 0.6 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 70.6754 | 22.8548 | 543943.1381 | 45.3286 | 45.3286 | 107.2576 | 0.7 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 72.0177 | 24.197 | 575889.6944 | 47.9908 | 47.9908 | 110.2663 | 0.8 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 73.36 | 25.5393 | 607836.2508 | 50.653 | 50.653 | 113.275 | 0.9 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 74.7023 | 26.8816 | 639782.8071 | 53.3152 | 53.3152 | 116.2837 | 1 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 76.0446 | 28.2239 | 671729.3635 | 55.9774 | 55.9774 | 119.2924 | 75 | 60 | 29.9243 | 30 | 58.3
6/20/20XX 11:00:00 AM | 0.45833 | 3 | 77.1 | 56.3 | 69.6077 | 83.8273 | 14.2196 | 50 | 77.1 |  | 77.1 | 78.566 | 0.1 | 74.31 | 19.31 | 729918 | 60.8265 | 60.8265 | 64.2161 | 16.3954 | 390211.4558 | 32.5176 | 32.5176 | 93.3441 | 0.2 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 65.8105 | 17.9899 | 428159.1116 | 35.6799 | 35.6799 | 97.4829 | 0.3 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 67.405 | 19.5843 | 466106.7674 | 38.8422 | 38.8422 | 101.6217 | 0.4 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 68.9994 | 21.1788 | 504054.4233 | 42.0045 | 42.0045 | 105.7605 | 0.5 | 75.55 | 20.55 | 776790 | 64.7325 | 64.7325 | 70.5938 | 22.7732 | 542002.0791 | 45.1668 | 45.1668 | 109.8993 | 0.6 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 72.1883 | 24.3676 | 579949.7349 | 48.3291 | 48.3291 | 114.0381 | 0.7 | 76.17 | 21.17 | 800226 | 66.6855 | 66.6855 | 73.7827 | 25.9621 | 617897.3907 | 51.4914 | 51.4914 | 118.1769 | 0.8 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 75.3771 | 27.5565 | 655845.0465 | 54.6538 | 54.6538 | 122.3158 | 0.9 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 76.9716 | 29.151 | 693792.7023 | 57.8161 | 57.8161 | 126.4546 | 1 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 78.566 | 30.7454 | 731740.3581 | 60.9784 | 60.9784 | 130.5934 | 75 | 55 | 30.8089 | 30 | 56.3
6/20/20XX 12:00:00 PM | 0.5 | 3 | 77.7 | 57.2 | 71.0329 | 85.548 | 14.515 | 50 | 77.7 |  | 77.7 | 81.4837 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 64.5078 | 16.6872 | 397155.6323 | 33.0963 | 33.0963 | 94.1118 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 66.3941 | 18.5734 | 442047.4647 | 36.8373 | 36.8373 | 99.0183 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 68.2803 | 20.4596 | 486939.297 | 40.5783 | 40.5783 | 103.9248 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 70.1665 | 22.3458 | 531831.1293 | 44.3193 | 44.3193 | 108.8313 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 72.0527 | 24.2321 | 576722.9616 | 48.0602 | 48.0602 | 113.7377 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 73.9389 | 26.1183 | 621614.794 | 51.8012 | 51.8012 | 118.6442 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 75.8251 | 28.0045 | 666506.6263 | 55.5422 | 55.5422 | 123.5507 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 77.7113 | 29.8907 | 711398.4586 | 59.2832 | 59.2832 | 128.4572 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 79.5975 | 31.7769 | 756290.2909 | 63.0242 | 63.0242 | 133.3637 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 81.4837 | 33.6631 | 801182.1233 | 66.7652 | 66.7652 | 138.2702 | 80 | 55 | 31.4129 | 32 | 57.2
6/20/20XX 1:00:00 PM | 0.54167 | 3 | 78.6 | 55.3 | 73.2164 | 88.1844 | 14.968 | 50 | 78.6 |  | 78.6 | 81.1495 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 64.4744 | 16.6538 | 396360.0096 | 33.03 | 33.03 | 94.329 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 66.3272 | 18.5066 | 440456.2191 | 36.7047 | 36.7047 | 99.4527 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 68.18 | 20.3593 | 484552.4287 | 40.3794 | 40.3794 | 104.5764 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 70.0328 | 22.2121 | 528648.6382 | 44.0541 | 44.0541 | 109.7001 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 71.8855 | 24.0649 | 572744.8478 | 47.7287 | 47.7287 | 114.8237 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 73.7383 | 25.9177 | 616841.0573 | 51.4034 | 51.4034 | 119.9474 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 75.5911 | 27.7705 | 660937.2669 | 55.0781 | 55.0781 | 125.0711 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 77.4439 | 29.6233 | 705033.4764 | 58.7528 | 58.7528 | 130.1948 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 79.2967 | 31.476 | 749129.686 | 62.4275 | 62.4275 | 135.3185 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 81.1495 | 33.3288 | 793225.8955 | 66.1022 | 66.1022 | 140.4422 | 80 | 55 | 31.5812 | 32 | 55.3
6/20/20XX 2:00:00 PM | 0.58333 | 3 | 78.9 | 54.3 | 73.9565 | 89.0782 | 15.1216 | 50 | 78.9 |  | 78.9 | 80.4588 | 0.1 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 64.4054 | 16.5847 | 394716.3595 | 32.893 | 32.893 | 94.2865 | 0.2 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 66.1891 | 18.3684 | 437168.919 | 36.4307 | 36.4307 | 99.3677 | 0.3 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 67.9728 | 20.1522 | 479621.4785 | 39.9685 | 39.9685 | 104.449 | 0.4 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 69.7565 | 21.9359 | 522074.038 | 43.5062 | 43.5062 | 109.5302 | 0.5 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 71.5402 | 23.7196 | 564526.5975 | 47.0439 | 47.0439 | 114.6114 | 0.6 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 73.324 | 25.5033 | 606979.1569 | 50.5816 | 50.5816 | 119.6926 | 0.7 | 77.43 | 22.43 | 847854 | 70.6545 | 70.6545 | 75.1077 | 27.287 | 649431.7164 | 54.1193 | 54.1193 | 124.7738 | 0.8 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 76.8914 | 29.0708 | 691884.2759 | 57.657 | 57.657 | 129.855 | 0.9 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 78.6751 | 30.8545 | 734336.8354 | 61.1947 | 61.1947 | 134.9362 | 1 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 80.4588 | 32.6382 | 776789.3949 | 64.7324 | 64.7324 | 140.0174 | 80 | 55 | 31.5465 | 32 | 54.3
6/20/20XX 3:00:00 PM | 0.625 | 3 | 78 | 56.4 | 71.7546 | 86.4193 | 14.6647 | 50 | 78 |  | 78 | 81.14 | 0.1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 64.4735 | 16.6528 | 396337.6316 | 33.0281 | 33.0281 | 94.1381 | 0.2 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 66.3253 | 18.5047 | 440411.4633 | 36.701 | 36.701 | 99.071 | 0.3 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 68.1772 | 20.3565 | 484485.2949 | 40.3738 | 40.3738 | 104.0038 | 0.4 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 70.029 | 22.2084 | 528559.1266 | 44.0466 | 44.0466 | 108.9366 | 0.5 | 76 | 21 | 793800 | 66.15 | 66.15 | 71.8808 | 24.0602 | 572632.9582 | 47.7194 | 47.7194 | 113.8694 | 0.6 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 73.7327 | 25.912 | 616706.7898 | 51.3922 | 51.3922 | 118.8022 | 0.7 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 75.5845 | 27.7639 | 660780.6215 | 55.0651 | 55.0651 | 123.7351 | 0.8 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 77.4364 | 29.6157 | 704854.4531 | 58.7379 | 58.7379 | 128.6679 | 0.9 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 79.2882 | 31.4676 | 748928.2848 | 62.4107 | 62.4107 | 133.6007 | 1 | 78 | 23 | 869400 | 72.45 | 72.45 | 81.14 | 33.3194 | 793002.1164 | 66.0835 | 66.0835 | 138.5335 | 80 | 55 | 31.4326 | 32 | 56.4
6/20/20XX 4:00:00 PM | 0.66667 | 3 | 77.6 | 56.8 | 70.7937 | 85.2591 | 14.4654 | 50 | 77.6 |  | 77.6 | 80.6302 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 64.4225 | 16.6019 | 395124.1817 | 32.927 | 32.927 | 93.911 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 66.2233 | 18.4027 | 437984.5634 | 36.4987 | 36.4987 | 98.6167 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 68.0242 | 20.2036 | 480844.9451 | 40.0704 | 40.0704 | 103.3224 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 69.8251 | 22.0044 | 523705.3268 | 43.6421 | 43.6421 | 108.0281 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 71.6259 | 23.8053 | 566565.7085 | 47.2138 | 47.2138 | 112.7338 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 73.4268 | 25.6061 | 609426.0902 | 50.7855 | 50.7855 | 117.4395 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 75.2276 | 27.407 | 652286.4719 | 54.3572 | 54.3572 | 122.1452 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 77.0285 | 29.2079 | 695146.8536 | 57.9289 | 57.9289 | 126.8509 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 78.8293 | 31.0087 | 738007.2353 | 61.5006 | 61.5006 | 131.5566 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 80.6302 | 32.8096 | 780867.617 | 65.0723 | 65.0723 | 136.2623 | 80 | 55 | 31.2547 | 32 | 56.8
6/20/20XX 5:00:00 PM | 0.70833 | 3 | 77.8 | 56 | 71.2728 | 85.8376 | 14.5648 | 50 | 77.8 |  | 77.8 | 80.0117 | 0.1 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 64.3606 | 16.54 | 393652.1236 | 32.8043 | 32.8043 | 93.8513 | 0.2 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 66.0996 | 18.279 | 435040.4471 | 36.2534 | 36.2534 | 98.4974 | 0.3 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 67.8386 | 20.018 | 476428.7707 | 39.7024 | 39.7024 | 103.1434 | 0.4 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 69.5777 | 21.757 | 517817.0942 | 43.1514 | 43.1514 | 107.7894 | 0.5 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 71.3167 | 23.496 | 559205.4178 | 46.6005 | 46.6005 | 112.4355 | 0.6 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 73.0557 | 25.235 | 600593.7414 | 50.0495 | 50.0495 | 117.0815 | 0.7 | 76.66 | 21.66 | 818748 | 68.229 | 68.229 | 74.7947 | 26.974 | 641982.0649 | 53.4985 | 53.4985 | 121.7275 | 0.8 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 76.5337 | 28.713 | 683370.3885 | 56.9475 | 56.9475 | 126.3735 | 0.9 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 78.2727 | 30.452 | 724758.7121 | 60.3966 | 60.3966 | 131.0196 | 1 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 80.0117 | 32.1911 | 766147.0356 | 63.8456 | 63.8456 | 135.6656 | 80 | 55 | 31.2068 | 32 | 56
6/20/20XX 6:00:00 PM | 0.75 | 3 | 77.2 | 56.1 | 69.8436 | 84.112 | 14.2685 | 50 | 77.2 |  | 77.2 | 78.5473 | 0.1 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 64.2142 | 16.3936 | 390166.9236 | 32.5139 | 32.5139 | 93.3719 | 0.2 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 65.8068 | 17.9861 | 428070.0473 | 35.6725 | 35.6725 | 97.5385 | 0.3 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 67.3993 | 19.5787 | 465973.1709 | 38.8311 | 38.8311 | 101.7051 | 0.4 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 68.9919 | 21.1713 | 503876.2946 | 41.9897 | 41.9897 | 105.8717 | 0.5 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 70.5845 | 22.7638 | 541779.4182 | 45.1483 | 45.1483 | 110.0383 | 0.6 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 72.177 | 24.3564 | 579682.5419 | 48.3069 | 48.3069 | 114.2049 | 0.7 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 73.7696 | 25.949 | 617585.6655 | 51.4655 | 51.4655 | 118.3715 | 0.8 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 75.3622 | 27.5415 | 655488.7892 | 54.6241 | 54.6241 | 122.5381 | 0.9 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 76.9547 | 29.1341 | 693391.9128 | 57.7827 | 57.7827 | 126.7047 | 1 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 78.5473 | 30.7267 | 731295.0365 | 60.9413 | 60.9413 | 130.8713 | 75 | 55 | 30.8304 | 30 | 56.1
6/20/20XX 7:00:00 PM | 0.79167 | 3 | 76.6 | 57.3 | 68.4384 | 82.4157 | 13.9773 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/20/20XX 8:00:00 PM | 0.83333 | 3 | 75.5 | 60 | 79.3806 | 92.8973 | 13.5167 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/20/20XX 9:00:00 PM | 0.875 | 3 | 75.3 | 60.1 | 78.8391 | 92.2616 | 13.4225 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/20/20XX 10:00:00 PM | 0.91667 | 3 | 74.7 | 61.3 | 77.2333 | 90.3765 | 13.1432 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/20/20XX 11:00:00 PM | 0.95833 | 3 | 73.7 | 64 | 74.6189 | 87.3075 | 12.6886 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/20/20XX 12:00:00 AM | 0 | 4 | 73.3 | 65.3 | 73.5946 | 86.1051 | 12.5105 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/21/20XX 1:00:00 AM | 0.041667 | 4 | 72.1 | 67.8 | 70.5937 | 82.5828 | 11.9891 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/21/20XX 2:00:00 AM | 0.083333 | 4 | 71.6 | 68.8 | 69.3749 | 81.1522 | 11.7773 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/21/20XX 3:00:00 AM | 0.125 | 4 | 71 | 70.1 | 79.4639 | 91.0648 | 11.6009 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/21/20XX 4:00:00 AM | 0.16667 | 4 | 70.3 | 73 | 77.5329 | 88.8456 | 11.3127 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/21/20XX 5:00:00 AM | 0.20833 | 4 | 69.5 | 74.2 | 75.3763 | 86.3676 | 10.9913 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/21/20XX 6:00:00 AM | 0.25 | 4 | 70.1 | 73.9 | 76.9888 | 88.2203 | 11.2316 | 70 | 70.1 |  | 70.1 | 81.3691 | 0.1 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 64.4964 | 16.6757 | 396882.7112 | 33.0736 | 33.0736 | 91.6951 | 0.2 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 66.3711 | 18.5505 | 441501.6224 | 36.7918 | 36.7918 | 94.1848 | 0.3 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 68.2459 | 20.4252 | 486120.5336 | 40.51 | 40.51 | 96.6745 | 0.4 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 70.1206 | 22.3 | 530739.4448 | 44.2283 | 44.2283 | 99.1643 | 0.5 | 72.05 | 17.05 | 644490 | 53.7075 | 53.7075 | 71.9954 | 24.1747 | 575358.356 | 47.9465 | 47.9465 | 101.654 | 0.6 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 73.8701 | 26.0495 | 619977.2673 | 51.6648 | 51.6648 | 104.1438 | 0.7 | 71.27 | 16.27 | 615006 | 51.2505 | 51.2505 | 75.7448 | 27.9242 | 664596.1785 | 55.383 | 55.383 | 106.6335 | 0.8 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 77.6196 | 29.799 | 709215.0897 | 59.1013 | 59.1013 | 109.1233 | 0.9 | 70.49 | 15.49 | 585522 | 48.7935 | 48.7935 | 79.4943 | 31.6737 | 753834.0009 | 62.8195 | 62.8195 | 111.613 | 1 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 81.3691 | 33.5484 | 798452.9121 | 66.5377 | 66.5377 | 114.1027 | 70 | 75 | 29.5317 | 30 | 73.9
6/21/20XX 7:00:00 AM | 0.29167 | 4 | 70.7 | 72.7 | 78.6313 | 90.1079 | 11.4766 | 70 | 70.7 |  | 70.7 | 81.73 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 64.5325 | 16.7118 | 397741.6269 | 33.1451 | 33.1451 | 91.9556 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 66.4433 | 18.6227 | 443219.4538 | 36.935 | 36.935 | 94.706 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 68.3541 | 20.5335 | 488697.2807 | 40.7248 | 40.7248 | 97.4563 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 70.265 | 22.4443 | 534175.1076 | 44.5146 | 44.5146 | 100.2066 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 72.1758 | 24.3552 | 579652.9346 | 48.3044 | 48.3044 | 102.9569 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 74.0866 | 26.266 | 625130.7615 | 52.0942 | 52.0942 | 105.7072 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 75.9975 | 28.1768 | 670608.5884 | 55.884 | 55.884 | 108.4575 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 77.9083 | 30.0877 | 716086.4153 | 59.6739 | 59.6739 | 111.2079 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 79.8191 | 31.9985 | 761564.2422 | 63.4637 | 63.4637 | 113.9582 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 81.73 | 33.9093 | 807042.0691 | 67.2535 | 67.2535 | 116.7085 | 70 | 75 | 29.7352 | 30 | 72.7
6/21/20XX 8:00:00 AM | 0.33333 | 4 | 72.3 | 68.2 | 71.0864 | 83.1611 | 12.0747 | 60 | 72.3 |  | 72.3 | 80.9876 | 0.1 | 73.83 | 18.83 | 711774 | 59.3145 | 59.3145 | 64.4582 | 16.6376 | 395974.85 | 32.9979 | 32.9979 | 92.3124 | 0.2 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 66.2948 | 18.4742 | 439685.9 | 36.6405 | 36.6405 | 95.4195 | 0.3 | 73.49 | 18.49 | 698922 | 58.2435 | 58.2435 | 68.1314 | 20.3108 | 483396.95 | 40.2831 | 40.2831 | 98.5266 | 0.4 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 69.968 | 22.1474 | 527108 | 43.9257 | 43.9257 | 101.6337 | 0.5 | 73.15 | 18.15 | 686070 | 57.1725 | 57.1725 | 71.8046 | 23.984 | 570819.05 | 47.5683 | 47.5683 | 104.7408 | 0.6 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 73.6412 | 25.8206 | 614530.1 | 51.2108 | 51.2108 | 107.8478 | 0.7 | 72.81 | 17.81 | 673218 | 56.1015 | 56.1015 | 75.4778 | 27.6572 | 658241.15 | 54.8534 | 54.8534 | 110.9549 | 0.8 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 77.3144 | 29.4938 | 701952.2 | 58.496 | 58.496 | 114.062 | 0.9 | 72.47 | 17.47 | 660366 | 55.0305 | 55.0305 | 79.151 | 31.3304 | 745663.25 | 62.1386 | 62.1386 | 117.1691 | 1 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 80.9876 | 33.167 | 789374.3 | 65.7812 | 65.7812 | 120.2762 | 70 | 70 | 30.0115 | 30 | 68.2
6/21/20XX 9:00:00 AM | 0.375 | 4 | 74.6 | 64.6 | 76.9684 | 90.0655 | 13.0971 | 60 | 74.6 |  | 74.6 | 82.9931 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 64.6588 | 16.8381 | 400747.8152 | 33.3957 | 33.3957 | 93.4347 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 66.6959 | 18.8753 | 449231.8305 | 37.436 | 37.436 | 97.664 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 68.7331 | 20.9124 | 497715.8457 | 41.4763 | 41.4763 | 101.8933 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 70.7702 | 22.9496 | 546199.861 | 45.5167 | 45.5167 | 106.1227 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 72.8073 | 24.9867 | 594683.8762 | 49.557 | 49.557 | 110.352 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 74.8445 | 27.0239 | 643167.8915 | 53.5973 | 53.5973 | 114.5813 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 76.8816 | 29.061 | 691651.9067 | 57.6377 | 57.6377 | 118.8107 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 78.9188 | 31.0981 | 740135.922 | 61.678 | 61.678 | 123.04 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 80.9559 | 33.1353 | 788619.9372 | 65.7183 | 65.7183 | 127.2693 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 82.9931 | 35.1724 | 837103.9525 | 69.7587 | 69.7587 | 131.4987 | 75 | 65 | 30.8891 | 30 | 64.6
6/21/20XX 10:00:00 AM | 0.41667 | 4 | 76.5 | 58.9 | 68.2065 | 82.1358 | 13.9292 | 50 | 76.5 |  | 76.5 | 80.6036 | 0.1 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 64.4198 | 16.5992 | 395060.7649 | 32.9217 | 32.9217 | 93.5592 | 0.2 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 66.218 | 18.3974 | 437857.7298 | 36.4881 | 36.4881 | 97.9131 | 0.3 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 68.0162 | 20.1956 | 480654.6947 | 40.0546 | 40.0546 | 102.2671 | 0.4 | 75 | 20 | 756000 | 63 | 63 | 69.8144 | 21.9938 | 523451.6596 | 43.621 | 43.621 | 106.621 | 0.5 | 75.25 | 20.25 | 765450 | 63.7875 | 63.7875 | 71.6126 | 23.792 | 566248.6245 | 47.1874 | 47.1874 | 110.9749 | 0.6 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 73.4108 | 25.5902 | 609045.5894 | 50.7538 | 50.7538 | 115.3288 | 0.7 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 75.209 | 27.3883 | 651842.5543 | 54.3202 | 54.3202 | 119.6827 | 0.8 | 76 | 21 | 793800 | 66.15 | 66.15 | 77.0072 | 29.1865 | 694639.5192 | 57.8866 | 57.8866 | 124.0366 | 0.9 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 78.8054 | 30.9847 | 737436.4841 | 61.453 | 61.453 | 128.3905 | 1 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 80.6036 | 32.7829 | 780233.449 | 65.0195 | 65.0195 | 132.7445 | 75 | 60 | 30.9809 | 30 | 58.9
6/21/20XX 11:00:00 AM | 0.45833 | 4 | 79.6 | 52.2 | 75.7077 | 91.1929 | 15.4852 | 50 | 79.6 |  | 79.6 | 79.1145 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 64.2709 | 16.4503 | 391516.7507 | 32.6264 | 32.6264 | 94.2404 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 65.9202 | 18.0996 | 430769.7014 | 35.8975 | 35.8975 | 99.2755 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 67.5695 | 19.7489 | 470022.652 | 39.1686 | 39.1686 | 104.3106 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 69.2188 | 21.3981 | 509275.6027 | 42.4396 | 42.4396 | 109.3456 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 70.8681 | 23.0474 | 548528.5534 | 45.7107 | 45.7107 | 114.3807 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 72.5173 | 24.6967 | 587781.5041 | 48.9818 | 48.9818 | 119.4158 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 74.1666 | 26.346 | 627034.4547 | 52.2529 | 52.2529 | 124.4509 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 75.8159 | 27.9953 | 666287.4054 | 55.524 | 55.524 | 129.486 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 77.4652 | 29.6446 | 705540.3561 | 58.795 | 58.795 | 134.521 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 79.1145 | 31.2938 | 744793.3068 | 62.0661 | 62.0661 | 139.5561 | 80 | 50 | 31.5073 | 32 | 52.2
6/21/20XX 12:00:00 PM | 0.5 | 4 | 81.4 | 49.1 | 64.0347 | 80.3687 | 16.334 | 40 | 81.4 |  | 81.4 | 78.8987 | 0.1 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 64.2493 | 16.4287 | 391003.106 | 32.5836 | 32.5836 | 94.7646 | 0.2 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 65.877 | 18.0564 | 429742.412 | 35.8119 | 35.8119 | 100.3239 | 0.3 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 67.5047 | 19.6841 | 468481.718 | 39.0401 | 39.0401 | 105.8831 | 0.4 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 69.1324 | 21.3118 | 507221.0239 | 42.2684 | 42.2684 | 111.4424 | 0.5 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 70.7601 | 22.9395 | 545960.3299 | 45.4967 | 45.4967 | 117.0017 | 0.6 | 78.44 | 23.44 | 886032 | 73.836 | 73.836 | 72.3878 | 24.5672 | 584699.6359 | 48.725 | 48.725 | 122.561 | 0.7 | 79.18 | 24.18 | 914004 | 76.167 | 76.167 | 74.0155 | 26.1949 | 623438.9419 | 51.9532 | 51.9532 | 128.1202 | 0.8 | 79.92 | 24.92 | 941976 | 78.498 | 78.498 | 75.6432 | 27.8226 | 662178.2479 | 55.1815 | 55.1815 | 133.6795 | 0.9 | 80.66 | 25.66 | 969948 | 80.829 | 80.829 | 77.2709 | 29.4503 | 700917.5539 | 58.4098 | 58.4098 | 139.2388 | 1 | 81.4 | 26.4 | 997920 | 83.16 | 83.16 | 78.8987 | 31.078 | 739656.8598 | 61.6381 | 61.6381 | 144.7981 | 80 | 50 | 31.9145 | 32 | 49.1
6/21/20XX 1:00:00 PM | 0.54167 | 4 | 82.1 | 47.3 | 65.5198 | 82.2439 | 16.7241 | 40 | 82.1 |  | 82.1 | 77.7284 | 0.1 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 64.1323 | 16.3117 | 388217.7942 | 32.3515 | 32.3515 | 94.753 | 0.2 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 65.643 | 17.8223 | 424171.7885 | 35.3476 | 35.3476 | 100.3006 | 0.3 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 67.1536 | 19.333 | 460125.7827 | 38.3438 | 38.3438 | 105.8483 | 0.4 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 68.6643 | 20.8437 | 496079.7769 | 41.34 | 41.34 | 111.396 | 0.5 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 70.175 | 22.3544 | 532033.7712 | 44.3361 | 44.3361 | 116.9436 | 0.6 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 71.6857 | 23.865 | 567987.7654 | 47.3323 | 47.3323 | 122.4913 | 0.7 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 73.1963 | 25.3757 | 603941.7597 | 50.3285 | 50.3285 | 128.039 | 0.8 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 74.707 | 26.8864 | 639895.7539 | 53.3246 | 53.3246 | 133.5866 | 0.9 | 81.29 | 26.29 | 993762 | 82.8135 | 82.8135 | 76.2177 | 28.397 | 675849.7481 | 56.3208 | 56.3208 | 139.1343 | 1 | 82.1 | 27.1 | 1024380 | 85.365 | 85.365 | 77.7284 | 29.9077 | 711803.7424 | 59.317 | 59.317 | 144.682 | 80 | 45 | 31.9024 | 32 | 47.3
6/21/20XX 2:00:00 PM | 0.58333 | 4 | 83 | 45.4 | 67.4702 | 84.7072 | 17.2369 | 40 | 83 |  | 83 | 76.7782 | 0.1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 64.0373 | 16.2167 | 385956.4112 | 32.163 | 32.163 | 94.848 | 0.2 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 65.4529 | 17.6323 | 419649.0224 | 34.9708 | 34.9708 | 100.4908 | 0.3 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 66.8686 | 19.048 | 453341.6336 | 37.7785 | 37.7785 | 106.1335 | 0.4 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 68.2843 | 20.4636 | 487034.2447 | 40.5862 | 40.5862 | 111.7762 | 0.5 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 69.6999 | 21.8793 | 520726.8559 | 43.3939 | 43.3939 | 117.4189 | 0.6 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 71.1156 | 23.2949 | 554419.4671 | 46.2016 | 46.2016 | 123.0616 | 0.7 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 72.5312 | 24.7106 | 588112.0783 | 49.0093 | 49.0093 | 128.7043 | 0.8 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 73.9469 | 26.1262 | 621804.6895 | 51.8171 | 51.8171 | 134.3471 | 0.9 | 82.1 | 27.1 | 1024380 | 85.365 | 85.365 | 75.3625 | 27.5419 | 655497.3007 | 54.6248 | 54.6248 | 139.9898 | 1 | 83 | 28 | 1058400 | 88.2 | 88.2 | 76.7782 | 28.9576 | 689189.9119 | 57.4325 | 57.4325 | 145.6325 | 85 | 45 | 31.9736 | 32 | 45.4
6/21/20XX 3:00:00 PM | 0.625 | 4 | 82.7 | 46.3 | 66.8149 | 83.8795 | 17.0646 | 40 | 82.7 |  | 82.7 | 77.5656 | 0.1 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 64.116 | 16.2954 | 387830.4089 | 32.3192 | 32.3192 | 94.9097 | 0.2 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 65.6104 | 17.7898 | 423397.0178 | 35.2831 | 35.2831 | 100.6141 | 0.3 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 67.1048 | 19.2842 | 458963.6268 | 38.247 | 38.247 | 106.3185 | 0.4 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 68.5992 | 20.7786 | 494530.2357 | 41.2109 | 41.2109 | 112.0229 | 0.5 | 78.35 | 23.35 | 882630 | 73.5525 | 73.5525 | 70.0936 | 22.273 | 530096.8446 | 44.1747 | 44.1747 | 117.7272 | 0.6 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 71.588 | 23.7674 | 565663.4535 | 47.1386 | 47.1386 | 123.4316 | 0.7 | 80.09 | 25.09 | 948402 | 79.0335 | 79.0335 | 73.0824 | 25.2618 | 601230.0624 | 50.1025 | 50.1025 | 129.136 | 0.8 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 74.5768 | 26.7562 | 636796.6714 | 53.0664 | 53.0664 | 134.8404 | 0.9 | 81.83 | 26.83 | 1014174 | 84.5145 | 84.5145 | 76.0712 | 28.2506 | 672363.2803 | 56.0303 | 56.0303 | 140.5448 | 1 | 82.7 | 27.7 | 1047060 | 87.255 | 87.255 | 77.5656 | 29.745 | 707929.8892 | 58.9942 | 58.9942 | 146.2492 | 85 | 45 | 32.0238 | 32 | 46.3
6/21/20XX 4:00:00 PM | 0.66667 | 4 | 82 | 46.9 | 65.3059 | 81.9738 | 16.6679 | 40 | 82 |  | 82 | 76.8068 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 64.0401 | 16.2195 | 386024.4023 | 32.1687 | 32.1687 | 94.5387 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 65.4587 | 17.638 | 419785.0046 | 34.9821 | 34.9821 | 99.8721 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 66.8772 | 19.0565 | 453545.6069 | 37.7955 | 37.7955 | 105.2055 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 68.2957 | 20.4751 | 487306.2092 | 40.6089 | 40.6089 | 110.5389 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 69.7142 | 21.8936 | 521066.8115 | 43.4222 | 43.4222 | 115.8722 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 71.1327 | 23.3121 | 554827.4138 | 46.2356 | 46.2356 | 121.2056 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 72.5512 | 24.7306 | 588588.0161 | 49.049 | 49.049 | 126.539 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 73.9697 | 26.1491 | 622348.6184 | 51.8624 | 51.8624 | 131.8724 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 75.3882 | 27.5676 | 656109.2207 | 54.6758 | 54.6758 | 137.2058 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 76.8068 | 28.9861 | 689869.823 | 57.4892 | 57.4892 | 142.5392 | 80 | 45 | 31.7332 | 32 | 46.9
6/21/20XX 5:00:00 PM | 0.70833 | 4 | 80.9 | 50.2 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 79.3745 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 64.2969 | 16.4763 | 392135.6628 | 32.678 | 32.678 | 94.7015 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 65.9722 | 18.1516 | 432007.5257 | 36.0006 | 36.0006 | 100.1976 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 67.6475 | 19.8269 | 471879.3885 | 39.3233 | 39.3233 | 105.6938 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 69.3228 | 21.5022 | 511751.2513 | 42.6459 | 42.6459 | 111.1899 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 70.9981 | 23.1774 | 551623.1141 | 45.9686 | 45.9686 | 116.6861 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 72.6734 | 24.8527 | 591494.977 | 49.2912 | 49.2912 | 122.1822 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 74.3487 | 26.528 | 631366.8398 | 52.6139 | 52.6139 | 127.6784 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 76.0239 | 28.2033 | 671238.7026 | 55.9366 | 55.9366 | 133.1746 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 77.6992 | 29.8786 | 711110.5655 | 59.2592 | 59.2592 | 138.6707 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 79.3745 | 31.5539 | 750982.4283 | 62.5819 | 62.5819 | 144.1669 | 80 | 50 | 31.8666 | 32 | 50.2
6/21/20XX 6:00:00 PM | 0.75 | 4 | 79.5 | 53.2 | 75.4555 | 90.8883 | 15.4328 | 50 | 79.5 |  | 79.5 | 80.394 | 0.1 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 64.3989 | 16.5782 | 394561.9747 | 32.8802 | 32.8802 | 94.4627 | 0.2 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 66.1761 | 18.3555 | 436860.1495 | 36.405 | 36.405 | 99.72 | 0.3 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 67.9533 | 20.1327 | 479158.3242 | 39.9299 | 39.9299 | 104.9774 | 0.4 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 69.7306 | 21.9099 | 521456.4989 | 43.4547 | 43.4547 | 110.2347 | 0.5 | 76.75 | 21.75 | 822150 | 68.5125 | 68.5125 | 71.5078 | 23.6872 | 563754.6737 | 46.9796 | 46.9796 | 115.4921 | 0.6 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 73.285 | 25.4644 | 606052.8484 | 50.5044 | 50.5044 | 120.7494 | 0.7 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 75.0623 | 27.2416 | 648351.0231 | 54.0293 | 54.0293 | 126.0068 | 0.8 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 76.8395 | 29.0189 | 690649.1979 | 57.5541 | 57.5541 | 131.2641 | 0.9 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 78.6167 | 30.7961 | 732947.3726 | 61.0789 | 61.0789 | 136.5214 | 1 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 80.394 | 32.5733 | 775245.5473 | 64.6038 | 64.6038 | 141.7788 | 80 | 55 | 31.6834 | 32 | 53.2
6/21/20XX 7:00:00 PM | 0.79167 | 4 | 78.2 | 56.1 | 72.2392 | 87.0044 | 14.7652 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/21/20XX 8:00:00 PM | 0.83333 | 4 | 77.1 | 54.1 | 69.6077 | 83.8273 | 14.2196 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/21/20XX 9:00:00 PM | 0.875 | 4 | 76.2 | 56.7 | 67.5149 | 81.3009 | 13.786 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/21/20XX 10:00:00 PM | 0.91667 | 4 | 74.7 | 61.2 | 77.2333 | 90.3765 | 13.1432 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/21/20XX 11:00:00 PM | 0.95833 | 4 | 73.6 | 62.6 | 74.3617 | 87.0056 | 12.6439 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/21/20XX 12:00:00 AM | 0 | 5 | 72.5 | 66 | 71.5821 | 83.7428 | 12.1608 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/22/20XX 1:00:00 AM | 0.041667 | 5 | 72 | 65.5 | 70.3485 | 82.2949 | 11.9464 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/22/20XX 2:00:00 AM | 0.083333 | 5 | 71.4 | 65.4 | 68.8925 | 80.586 | 11.6935 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/22/20XX 3:00:00 AM | 0.125 | 5 | 70.5 | 68.7 | 66.7576 | 78.0804 | 11.3228 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/22/20XX 4:00:00 AM | 0.16667 | 5 | 69.9 | 67.2 | 65.3666 | 76.4479 | 11.0813 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/22/20XX 5:00:00 AM | 0.20833 | 5 | 69.9 | 68.8 | 65.3666 | 76.4479 | 11.0813 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/22/20XX 6:00:00 AM | 0.25 | 5 | 70.5 | 68.8 | 66.7576 | 78.0804 | 11.3228 | 60 | 70.5 |  | 70.5 | 76.7217 | 0.1 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 64.0316 | 16.211 | 385821.9113 | 32.1518 | 32.1518 | 90.8993 | 0.2 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 65.4416 | 17.621 | 419380.0226 | 34.9483 | 34.9483 | 92.5933 | 0.3 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 66.8516 | 19.031 | 452938.1338 | 37.7448 | 37.7448 | 94.2873 | 0.4 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 68.2617 | 20.441 | 486496.2451 | 40.5414 | 40.5414 | 95.9814 | 0.5 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 69.6717 | 21.851 | 520054.3564 | 43.3379 | 43.3379 | 97.6754 | 0.6 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 71.0817 | 23.261 | 553612.4677 | 46.1344 | 46.1344 | 99.3694 | 0.7 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 72.4917 | 24.671 | 587170.5789 | 48.9309 | 48.9309 | 101.0634 | 0.8 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 73.9017 | 26.081 | 620728.6902 | 51.7274 | 51.7274 | 102.7574 | 0.9 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 75.3117 | 27.491 | 654286.8015 | 54.5239 | 54.5239 | 104.4514 | 1 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 76.7217 | 28.901 | 687844.9128 | 57.3204 | 57.3204 | 106.1454 | 70 | 70 | 28.9039 | 28 | 68.8
6/22/20XX 7:00:00 AM | 0.29167 | 5 | 71.3 | 67.1 | 68.6524 | 80.3042 | 11.6518 | 60 | 71.3 |  | 71.3 | 76.9252 | 0.1 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 64.052 | 16.2314 | 386306.2874 | 32.1922 | 32.1922 | 91.1917 | 0.2 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 65.4823 | 17.6617 | 420348.7748 | 35.0291 | 35.0291 | 93.1781 | 0.3 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 66.9127 | 19.0921 | 454391.2622 | 37.8659 | 37.8659 | 95.1644 | 0.4 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 68.3431 | 20.5224 | 488433.7495 | 40.7028 | 40.7028 | 97.1508 | 0.5 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 69.7734 | 21.9528 | 522476.2369 | 43.5397 | 43.5397 | 99.1372 | 0.6 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 71.2038 | 23.3831 | 556518.7243 | 46.3766 | 46.3766 | 101.1236 | 0.7 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 72.6341 | 24.8135 | 590561.2117 | 49.2134 | 49.2134 | 103.1099 | 0.8 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 74.0645 | 26.2439 | 624603.6991 | 52.0503 | 52.0503 | 105.0963 | 0.9 | 71.57 | 16.57 | 626346 | 52.1955 | 52.1955 | 75.4948 | 27.6742 | 658646.1865 | 54.8872 | 54.8872 | 107.0827 | 1 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 76.9252 | 29.1046 | 692688.6739 | 57.7241 | 57.7241 | 109.0691 | 70 | 65 | 29.1316 | 30 | 67.1
6/22/20XX 8:00:00 AM | 0.33333 | 5 | 73.6 | 59.4 | 61.7652 | 74.3617 | 12.5965 | 50 | 73.6 |  | 73.6 | 73.6059 | 0.1 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 63.7201 | 15.8994 | 378406.316 | 31.5339 | 31.5339 | 91.2579 | 0.2 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 64.8185 | 16.9979 | 404548.832 | 33.7124 | 33.7124 | 93.3104 | 0.3 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.9169 | 18.0963 | 430691.3481 | 35.8909 | 35.8909 | 95.3629 | 0.4 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 67.0153 | 19.1947 | 456833.8641 | 38.0695 | 38.0695 | 97.4155 | 0.5 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 68.1138 | 20.2931 | 482976.3801 | 40.248 | 40.248 | 99.468 | 0.6 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 69.2122 | 21.3916 | 509118.8961 | 42.4266 | 42.4266 | 101.5206 | 0.7 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 70.3106 | 22.49 | 535261.4121 | 44.6051 | 44.6051 | 103.5731 | 0.8 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 71.409 | 23.5884 | 561403.9281 | 46.7837 | 46.7837 | 105.6257 | 0.9 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 72.5075 | 24.6868 | 587546.4442 | 48.9622 | 48.9622 | 107.6782 | 1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 73.6059 | 25.7853 | 613688.9602 | 51.1407 | 51.1407 | 109.7307 | 75 | 60 | 29.1757 | 30 | 59.4
6/22/20XX 9:00:00 AM | 0.375 | 5 | 74.9 | 58.8 | 64.5858 | 77.7654 | 13.1797 | 50 | 74.9 |  | 74.9 | 76.1839 | 0.1 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 63.9779 | 16.1572 | 384541.9376 | 32.0452 | 32.0452 | 92.1787 | 0.2 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 65.3341 | 17.5134 | 416820.0752 | 34.735 | 34.735 | 95.152 | 0.3 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 66.6903 | 18.8697 | 449098.2128 | 37.4249 | 37.4249 | 98.1254 | 0.4 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 68.0465 | 20.2259 | 481376.3504 | 40.1147 | 40.1147 | 101.0987 | 0.5 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 69.4028 | 21.5821 | 513654.488 | 42.8045 | 42.8045 | 104.072 | 0.6 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 70.759 | 22.9383 | 545932.6256 | 45.4944 | 45.4944 | 107.0454 | 0.7 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 72.1152 | 24.2946 | 578210.7632 | 48.1842 | 48.1842 | 110.0187 | 0.8 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 73.4714 | 25.6508 | 610488.9008 | 50.8741 | 50.8741 | 112.9921 | 0.9 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 74.8277 | 27.007 | 642767.0384 | 53.5639 | 53.5639 | 115.9654 | 1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 76.1839 | 28.3632 | 675045.1761 | 56.2538 | 56.2538 | 118.9388 | 75 | 60 | 29.8971 | 30 | 58.8
6/22/20XX 10:00:00 AM | 0.41667 | 5 | 76.6 | 57.8 | 68.4384 | 82.4157 | 13.9773 | 50 | 76.6 |  | 76.6 | 79.3407 | 0.1 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 64.2935 | 16.4729 | 392055.1087 | 32.6713 | 32.6713 | 93.3403 | 0.2 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 65.9654 | 18.1448 | 431846.4173 | 35.9872 | 35.9872 | 97.4752 | 0.3 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 67.6373 | 19.8167 | 471637.726 | 39.3031 | 39.3031 | 101.6101 | 0.4 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 69.3092 | 21.4886 | 511429.0347 | 42.6191 | 42.6191 | 105.7451 | 0.5 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 70.9812 | 23.1605 | 551220.3434 | 45.935 | 45.935 | 109.88 | 0.6 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 72.6531 | 24.8324 | 591011.652 | 49.251 | 49.251 | 114.015 | 0.7 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 74.325 | 26.5043 | 630802.9607 | 52.5669 | 52.5669 | 118.1499 | 0.8 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 75.9969 | 28.1762 | 670594.2694 | 55.8829 | 55.8829 | 122.2849 | 0.9 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 77.6688 | 29.8481 | 710385.578 | 59.1988 | 59.1988 | 126.4198 | 1 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 79.3407 | 31.52 | 750176.8867 | 62.5147 | 62.5147 | 130.5547 | 75 | 60 | 30.8077 | 30 | 57.8
6/22/20XX 11:00:00 AM | 0.45833 | 5 | 79.1 | 52.6 | 74.4534 | 89.6782 | 15.2248 | 50 | 79.1 |  | 79.1 | 78.4119 | 0.1 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 64.2007 | 16.38 | 389844.5315 | 32.487 | 32.487 | 93.9435 | 0.2 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 65.7797 | 17.959 | 427425.2629 | 35.6188 | 35.6188 | 98.6818 | 0.3 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 67.3587 | 19.5381 | 465005.9944 | 38.7505 | 38.7505 | 103.42 | 0.4 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 68.9377 | 21.1171 | 502586.7258 | 41.8822 | 41.8822 | 108.1582 | 0.5 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 70.5167 | 22.6961 | 540167.4573 | 45.014 | 45.014 | 112.8965 | 0.6 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 72.0958 | 24.2751 | 577748.1887 | 48.1457 | 48.1457 | 117.6347 | 0.7 | 77.57 | 22.57 | 853146 | 71.0955 | 71.0955 | 73.6748 | 25.8542 | 615328.9202 | 51.2774 | 51.2774 | 122.3729 | 0.8 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 75.2538 | 27.4332 | 652909.6516 | 54.4091 | 54.4091 | 127.1111 | 0.9 | 78.59 | 23.59 | 891702 | 74.3085 | 74.3085 | 76.8328 | 29.0122 | 690490.3831 | 57.5409 | 57.5409 | 131.8494 | 1 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 78.4119 | 30.5912 | 728071.1145 | 60.6726 | 60.6726 | 136.5876 | 80 | 55 | 31.2747 | 32 | 52.6
6/22/20XX 12:00:00 PM | 0.5 | 5 | 79.7 | 52.2 | 75.9607 | 91.4984 | 15.5378 | 50 | 79.7 |  | 79.7 | 79.379 | 0.1 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 64.2974 | 16.4767 | 392146.2786 | 32.6789 | 32.6789 | 94.3244 | 0.2 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 65.9731 | 18.1525 | 432028.7572 | 36.0024 | 36.0024 | 99.4434 | 0.3 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 67.6488 | 19.8282 | 471911.2358 | 39.3259 | 39.3259 | 104.5624 | 0.4 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 69.3246 | 21.5039 | 511793.7144 | 42.6495 | 42.6495 | 109.6815 | 0.5 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 71.0003 | 23.1797 | 551676.1931 | 45.973 | 45.973 | 114.8005 | 0.6 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 72.676 | 24.8554 | 591558.6717 | 49.2966 | 49.2966 | 119.9196 | 0.7 | 77.99 | 22.99 | 869022 | 72.4185 | 72.4185 | 74.3518 | 26.5311 | 631441.1503 | 52.6201 | 52.6201 | 125.0386 | 0.8 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 76.0275 | 28.2069 | 671323.6289 | 55.9436 | 55.9436 | 130.1576 | 0.9 | 79.13 | 24.13 | 912114 | 76.0095 | 76.0095 | 77.7032 | 29.8826 | 711206.1075 | 59.2672 | 59.2672 | 135.2767 | 1 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 79.379 | 31.5583 | 751088.5861 | 62.5907 | 62.5907 | 140.3957 | 80 | 50 | 31.5733 | 32 | 52.2
6/22/20XX 1:00:00 PM | 0.54167 | 5 | 79.9 | 51.6 | 76.4687 | 92.1119 | 15.6433 | 50 | 79.9 |  | 79.9 | 78.9716 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 64.2566 | 16.436 | 391176.7024 | 32.5981 | 32.5981 | 94.3066 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 65.8916 | 18.071 | 430089.6048 | 35.8408 | 35.8408 | 99.4078 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 67.5266 | 19.706 | 469002.5071 | 39.0835 | 39.0835 | 104.509 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 69.1616 | 21.341 | 507915.4095 | 42.3263 | 42.3263 | 109.6103 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 70.7966 | 22.976 | 546828.3119 | 45.569 | 45.569 | 114.7115 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 72.4316 | 24.611 | 585741.2143 | 48.8118 | 48.8118 | 119.8128 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 74.0666 | 26.246 | 624654.1167 | 52.0545 | 52.0545 | 124.914 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 75.7016 | 27.881 | 663567.019 | 55.2973 | 55.2973 | 130.0153 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 77.3366 | 29.516 | 702479.9214 | 58.54 | 58.54 | 135.1165 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 78.9716 | 31.151 | 741392.8238 | 61.7827 | 61.7827 | 140.2177 | 80 | 50 | 31.5584 | 32 | 51.6
6/22/20XX 2:00:00 PM | 0.58333 | 5 | 79.3 | 55.4 | 74.9531 | 90.2816 | 15.3285 | 50 | 79.3 |  | 79.3 | 83.2304 | 0.1 | 74.53 | 19.53 | 738234 | 61.5195 | 61.5195 | 64.6825 | 16.8619 | 401312.7716 | 33.4427 | 33.4427 | 94.9622 | 0.2 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 66.7434 | 18.9228 | 450361.7431 | 37.5301 | 37.5301 | 100.7191 | 0.3 | 75.59 | 20.59 | 778302 | 64.8585 | 64.8585 | 68.8043 | 20.9836 | 499410.7147 | 41.6176 | 41.6176 | 106.4761 | 0.4 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 70.8652 | 23.0445 | 548459.6863 | 45.705 | 45.705 | 112.233 | 0.5 | 76.65 | 21.65 | 818370 | 68.1975 | 68.1975 | 72.926 | 25.1054 | 597508.6578 | 49.7924 | 49.7924 | 117.9899 | 0.6 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 74.9869 | 27.1663 | 646557.6294 | 53.8798 | 53.8798 | 123.7468 | 0.7 | 77.71 | 22.71 | 858438 | 71.5365 | 71.5365 | 77.0478 | 29.2272 | 695606.6009 | 57.9672 | 57.9672 | 129.5037 | 0.8 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 79.1087 | 31.288 | 744655.5725 | 62.0546 | 62.0546 | 135.2606 | 0.9 | 78.77 | 23.77 | 898506 | 74.8755 | 74.8755 | 81.1696 | 33.3489 | 793704.5441 | 66.142 | 66.142 | 141.0175 | 1 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 83.2304 | 35.4098 | 842753.5156 | 70.2295 | 70.2295 | 146.7745 | 80 | 55 | 32.079 | 32 | 55.4
6/22/20XX 3:00:00 PM | 0.625 | 5 | 78.3 | 57.6 | 72.4824 | 87.2982 | 14.8157 | 50 | 78.3 |  | 78.3 | 83.7424 | 0.1 | 74.43 | 19.43 | 734454 | 61.2045 | 61.2045 | 64.7337 | 16.9131 | 402531.1889 | 33.5443 | 33.5443 | 94.7488 | 0.2 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 66.8458 | 19.0252 | 452798.5778 | 37.7332 | 37.7332 | 100.2922 | 0.3 | 75.29 | 20.29 | 766962 | 63.9135 | 63.9135 | 68.9579 | 21.1372 | 503065.9666 | 41.9222 | 41.9222 | 105.8357 | 0.4 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 71.0699 | 23.2493 | 553333.3555 | 46.1111 | 46.1111 | 111.3791 | 0.5 | 76.15 | 21.15 | 799470 | 66.6225 | 66.6225 | 73.182 | 25.3614 | 603600.7444 | 50.3001 | 50.3001 | 116.9226 | 0.6 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 75.2941 | 27.4735 | 653868.1333 | 54.489 | 54.489 | 122.466 | 0.7 | 77.01 | 22.01 | 831978 | 69.3315 | 69.3315 | 77.4062 | 29.5855 | 704135.5222 | 58.678 | 58.678 | 128.0095 | 0.8 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 79.5182 | 31.6976 | 754402.911 | 62.8669 | 62.8669 | 133.5529 | 0.9 | 77.87 | 22.87 | 864486 | 72.0405 | 72.0405 | 81.6303 | 33.8097 | 804670.2999 | 67.0559 | 67.0559 | 139.0964 | 1 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 83.7424 | 35.9218 | 854937.6888 | 71.2448 | 71.2448 | 144.6398 | 80 | 60 | 31.914 | 32 | 57.6
6/22/20XX 4:00:00 PM | 0.66667 | 5 | 77.6 | 57.3 | 70.7937 | 85.2591 | 14.4654 | 50 | 77.6 |  | 77.6 | 81.3535 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 64.4948 | 16.6742 | 396845.5688 | 33.0705 | 33.0705 | 94.0545 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 66.368 | 18.5474 | 441427.3376 | 36.7856 | 36.7856 | 98.9036 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 68.2412 | 20.4206 | 486009.1064 | 40.5008 | 40.5008 | 103.7528 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 70.1144 | 22.2937 | 530590.8752 | 44.2159 | 44.2159 | 108.6019 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 71.9876 | 24.1669 | 575172.644 | 47.9311 | 47.9311 | 113.4511 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 73.8607 | 26.0401 | 619754.4128 | 51.6462 | 51.6462 | 118.3002 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 75.7339 | 27.9133 | 664336.1816 | 55.3613 | 55.3613 | 123.1493 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 77.6071 | 29.7865 | 708917.9504 | 59.0765 | 59.0765 | 127.9985 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 79.4803 | 31.6597 | 753499.7192 | 62.7916 | 62.7916 | 132.8476 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 81.3535 | 33.5328 | 798081.488 | 66.5068 | 66.5068 | 137.6968 | 80 | 55 | 31.368 | 32 | 57.3
6/22/20XX 5:00:00 PM | 0.70833 | 5 | 77.2 | 56.5 | 69.8436 | 84.112 | 14.2685 | 50 | 77.2 |  | 77.2 | 79.1181 | 0.1 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 64.2713 | 16.4506 | 391525.2809 | 32.6271 | 32.6271 | 93.4851 | 0.2 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 65.9209 | 18.1003 | 430786.7618 | 35.8989 | 35.8989 | 97.7649 | 0.3 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 67.5706 | 19.7499 | 470048.2426 | 39.1707 | 39.1707 | 102.0447 | 0.4 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 69.2202 | 21.3996 | 509309.7235 | 42.4425 | 42.4425 | 106.3245 | 0.5 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 70.8698 | 23.0492 | 548571.2044 | 45.7143 | 45.7143 | 110.6043 | 0.6 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 72.5195 | 24.6989 | 587832.6853 | 48.9861 | 48.9861 | 114.8841 | 0.7 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 74.1691 | 26.3485 | 627094.1662 | 52.2578 | 52.2578 | 119.1638 | 0.8 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 75.8188 | 27.9981 | 666355.647 | 55.5296 | 55.5296 | 123.4436 | 0.9 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 77.4684 | 29.6478 | 705617.1279 | 58.8014 | 58.8014 | 127.7234 | 1 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 79.1181 | 31.2974 | 744878.6088 | 62.0732 | 62.0732 | 132.0032 | 75 | 55 | 30.9198 | 30 | 56.5
6/22/20XX 6:00:00 PM | 0.75 | 5 | 75.8 | 61.4 | 80.1988 | 93.8579 | 13.6591 | 60 | 75.8 |  | 75.8 | 82.1111 | 0.1 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 64.5706 | 16.7499 | 398648.7196 | 33.2207 | 33.2207 | 93.6377 | 0.2 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 66.5195 | 18.6989 | 445033.6392 | 37.0861 | 37.0861 | 98.0701 | 0.3 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 68.4685 | 20.6478 | 491418.5588 | 40.9515 | 40.9515 | 102.5025 | 0.4 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 70.4174 | 22.5968 | 537803.4784 | 44.817 | 44.817 | 106.935 | 0.5 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 72.3664 | 24.5457 | 584188.398 | 48.6824 | 48.6824 | 111.3674 | 0.6 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 74.3153 | 26.4947 | 630573.3175 | 52.5478 | 52.5478 | 115.7998 | 0.7 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 76.2643 | 28.4436 | 676958.2371 | 56.4132 | 56.4132 | 120.2322 | 0.8 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 78.2132 | 30.3926 | 723343.1567 | 60.2786 | 60.2786 | 124.6646 | 0.9 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 80.1621 | 32.3415 | 769728.0763 | 64.144 | 64.144 | 129.097 | 1 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 82.1111 | 34.2905 | 816112.9959 | 68.0094 | 68.0094 | 133.5294 | 75 | 60 | 31.0453 | 32 | 61.4
6/22/20XX 7:00:00 PM | 0.79167 | 5 | 74.5 | 65.9 | 76.7042 | 89.7555 | 13.0512 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/22/20XX 8:00:00 PM | 0.83333 | 5 | 73.3 | 68 | 73.5946 | 86.1051 | 12.5105 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/22/20XX 9:00:00 PM | 0.875 | 5 | 72.6 | 70.2 | 84.035 | 96.3195 | 12.2844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/22/20XX 10:00:00 PM | 0.91667 | 5 | 72.7 | 69.5 | 72.0807 | 84.3281 | 12.2474 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/22/20XX 11:00:00 PM | 0.95833 | 5 | 71.9 | 73.4 | 82.008 | 93.989 | 11.9811 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/22/20XX 12:00:00 AM | 0 | 6 | 71.3 | 73.2 | 80.3042 | 92.0306 | 11.7264 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/23/20XX 1:00:00 AM | 0.041667 | 6 | 71.3 | 74.3 | 80.3042 | 92.0306 | 11.7264 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/23/20XX 2:00:00 AM | 0.083333 | 6 | 70.7 | 75.8 | 78.6313 | 90.1079 | 11.4766 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/23/20XX 3:00:00 AM | 0.125 | 6 | 70.6 | 77 | 78.3554 | 89.7909 | 11.4354 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/23/20XX 4:00:00 AM | 0.16667 | 6 | 70.2 | 76.6 | 77.2604 | 88.5325 | 11.2721 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/23/20XX 5:00:00 AM | 0.20833 | 6 | 70.1 | 76.4 | 76.9888 | 88.2203 | 11.2316 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/23/20XX 6:00:00 AM | 0.25 | 6 | 70.6 | 77.3 | 78.3554 | 89.7909 | 11.4354 | 70 | 70.6 |  | 70.6 | 86.7033 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 65.0298 | 17.2092 | 409578.1382 | 34.1315 | 34.1315 | 92.9105 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 67.438 | 19.6173 | 466892.4763 | 38.9077 | 38.9077 | 96.6157 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 69.8461 | 22.0255 | 524206.8145 | 43.6839 | 43.6839 | 100.3209 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 72.2543 | 24.4337 | 581521.1527 | 48.4601 | 48.4601 | 104.0261 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 74.6625 | 26.8418 | 638835.4908 | 53.2363 | 53.2363 | 107.7313 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 77.0706 | 29.25 | 696149.829 | 58.0125 | 58.0125 | 111.4365 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 79.4788 | 31.6582 | 753464.1672 | 62.7887 | 62.7887 | 115.1417 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 81.887 | 34.0663 | 810778.5053 | 67.5649 | 67.5649 | 118.8469 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 84.2951 | 36.4745 | 868092.8435 | 72.3411 | 72.3411 | 122.5521 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 86.7033 | 38.8827 | 925407.1817 | 77.1173 | 77.1173 | 126.2573 | 70 | 75 | 30.4875 | 30 | 77.3
6/23/20XX 7:00:00 AM | 0.29167 | 6 | 71.4 | 75.8 | 80.586 | 92.3545 | 11.7685 | 70 | 71.4 |  | 71.4 | 87.4118 | 0.1 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 65.1006 | 17.28 | 411264.331 | 34.272 | 34.272 | 93.303 | 0.2 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 67.5797 | 19.759 | 470264.8621 | 39.1887 | 39.1887 | 97.4007 | 0.3 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 70.0587 | 22.238 | 529265.3931 | 44.1054 | 44.1054 | 101.4984 | 0.4 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 72.5377 | 24.7171 | 588265.9242 | 49.0222 | 49.0222 | 105.5962 | 0.5 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 75.0167 | 27.1961 | 647266.4552 | 53.9389 | 53.9389 | 109.6939 | 0.6 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 77.4957 | 29.6751 | 706266.9863 | 58.8556 | 58.8556 | 113.7916 | 0.7 | 72.18 | 17.18 | 649404 | 54.117 | 54.117 | 79.9747 | 32.1541 | 765267.5173 | 63.7723 | 63.7723 | 117.8893 | 0.8 | 71.92 | 16.92 | 639576 | 53.298 | 53.298 | 82.4537 | 34.6331 | 824268.0484 | 68.689 | 68.689 | 121.987 | 0.9 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 84.9328 | 37.1121 | 883268.5794 | 73.6057 | 73.6057 | 126.0847 | 1 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 87.4118 | 39.5911 | 942269.1105 | 78.5224 | 78.5224 | 130.1824 | 70 | 75 | 30.7946 | 30 | 75.8
6/23/20XX 8:00:00 AM | 0.33333 | 6 | 73 | 71.6 | 85.2126 | 97.6734 | 12.4608 | 70 | 73 |  | 73 | 87.2064 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 65.0801 | 17.2595 | 410775.4516 | 34.2313 | 34.2313 | 93.7663 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 67.5386 | 19.7179 | 469287.1032 | 39.1073 | 39.1073 | 98.3273 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 69.9971 | 22.1764 | 527798.7547 | 43.9832 | 43.9832 | 102.8882 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 72.4555 | 24.6349 | 586310.4063 | 48.8592 | 48.8592 | 107.4492 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 74.914 | 27.0934 | 644822.0579 | 53.7352 | 53.7352 | 112.0102 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 77.3725 | 29.5518 | 703333.7095 | 58.6111 | 58.6111 | 116.5711 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 79.8309 | 32.0103 | 761845.3611 | 63.4871 | 63.4871 | 121.1321 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 82.2894 | 34.4688 | 820357.0127 | 68.3631 | 68.3631 | 125.6931 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 84.7479 | 36.9273 | 878868.6642 | 73.2391 | 73.2391 | 130.2541 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 87.2064 | 39.3857 | 937380.3158 | 78.115 | 78.115 | 134.815 | 75 | 70 | 31.1554 | 32 | 71.6
6/23/20XX 9:00:00 AM | 0.375 | 6 | 74.8 | 69.2 | 77.499 | 90.6884 | 13.1894 | 60 | 74.8 |  | 74.8 | 89.6332 | 0.1 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 65.3228 | 17.5022 | 416551.4258 | 34.7126 | 34.7126 | 94.8146 | 0.2 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 68.024 | 20.2033 | 480839.0515 | 40.0699 | 40.0699 | 100.4239 | 0.3 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 70.7251 | 22.9045 | 545126.6773 | 45.4272 | 45.4272 | 106.0332 | 0.4 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 73.4263 | 25.6056 | 609414.303 | 50.7845 | 50.7845 | 111.6425 | 0.5 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 76.1274 | 28.3068 | 673701.9288 | 56.1418 | 56.1418 | 117.2518 | 0.6 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 78.8286 | 31.008 | 737989.5545 | 61.4991 | 61.4991 | 122.8611 | 0.7 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 81.5298 | 33.7091 | 802277.1803 | 66.8564 | 66.8564 | 128.4704 | 0.8 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 84.2309 | 36.4103 | 866564.806 | 72.2137 | 72.2137 | 134.0797 | 0.9 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 86.9321 | 39.1114 | 930852.4318 | 77.571 | 77.571 | 139.689 | 1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 89.6332 | 41.8126 | 995140.0575 | 82.9283 | 82.9283 | 145.2983 | 75 | 70 | 31.9771 | 32 | 69.2
6/23/20XX 10:00:00 AM | 0.41667 | 6 | 76.2 | 66.2 | 81.3009 | 95.1517 | 13.8508 | 60 | 76.2 |  | 76.2 | 89.8884 | 0.1 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 65.3483 | 17.5277 | 417158.6101 | 34.7632 | 34.7632 | 95.3062 | 0.2 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 68.075 | 20.2543 | 482053.4203 | 40.1711 | 40.1711 | 101.4071 | 0.3 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 70.8017 | 22.981 | 546948.2304 | 45.579 | 45.579 | 107.508 | 0.4 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 73.5283 | 25.7077 | 611843.0406 | 50.9869 | 50.9869 | 113.6089 | 0.5 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 76.255 | 28.4344 | 676737.8507 | 56.3948 | 56.3948 | 119.7098 | 0.6 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 78.9817 | 31.161 | 741632.6609 | 61.8027 | 61.8027 | 125.8107 | 0.7 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 81.7083 | 33.8877 | 806527.471 | 67.2106 | 67.2106 | 131.9116 | 0.8 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 84.435 | 36.6144 | 871422.2811 | 72.6185 | 72.6185 | 138.0125 | 0.9 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 87.1617 | 39.3411 | 936317.0913 | 78.0264 | 78.0264 | 144.1134 | 1 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 89.8884 | 42.0677 | 1001211.9014 | 83.4343 | 83.4343 | 150.2143 | 75 | 65 | 32.361 | 32 | 66.2
6/23/20XX 11:00:00 AM | 0.45833 | 6 | 77.4 | 64.9 | 84.6839 | 99.1235 | 14.4396 | 60 | 77.4 |  | 77.4 | 91.7593 | 0.1 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 65.5354 | 17.7148 | 421611.524 | 35.1343 | 35.1343 | 96.0553 | 0.2 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 68.4492 | 20.6285 | 490959.248 | 40.9133 | 40.9133 | 102.9053 | 0.3 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 71.3629 | 23.5423 | 560306.972 | 46.6922 | 46.6922 | 109.7552 | 0.4 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 74.2767 | 26.4561 | 629654.6959 | 52.4712 | 52.4712 | 116.6052 | 0.5 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 77.1905 | 29.3698 | 699002.4199 | 58.2502 | 58.2502 | 123.4552 | 0.6 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 80.1043 | 32.2836 | 768350.1439 | 64.0292 | 64.0292 | 130.3052 | 0.7 | 76.38 | 21.38 | 808164 | 67.347 | 67.347 | 83.018 | 35.1974 | 837697.8679 | 69.8082 | 69.8082 | 137.1552 | 0.8 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 85.9318 | 38.1112 | 907045.5919 | 75.5871 | 75.5871 | 144.0051 | 0.9 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 88.8456 | 41.0249 | 976393.3159 | 81.3661 | 81.3661 | 150.8551 | 1 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 91.7593 | 43.9387 | 1045741.0399 | 87.1451 | 87.1451 | 157.7051 | 75 | 65 | 32.9489 | 32 | 64.9
6/23/20XX 12:00:00 PM | 0.5 | 6 | 78.1 | 61.4 | 86.7115 | 101.504 | 14.7925 | 60 | 78.1 |  | 78.1 | 88.7824 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 65.2377 | 17.4171 | 414526.4519 | 34.5439 | 34.5439 | 95.6854 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 67.8538 | 20.0332 | 476789.1037 | 39.7324 | 39.7324 | 102.1654 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 70.4699 | 22.6492 | 539051.7556 | 44.921 | 44.921 | 108.6455 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 73.0859 | 25.2653 | 601314.4075 | 50.1095 | 50.1095 | 115.1255 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 75.702 | 27.8814 | 663577.0594 | 55.2981 | 55.2981 | 121.6056 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 78.3181 | 30.4975 | 725839.7112 | 60.4866 | 60.4866 | 128.0856 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 80.9342 | 33.1135 | 788102.3631 | 65.6752 | 65.6752 | 134.5657 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 83.5503 | 35.7296 | 850365.015 | 70.8638 | 70.8638 | 141.0458 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 86.1663 | 38.3457 | 912627.6669 | 76.0523 | 76.0523 | 147.5258 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 88.7824 | 40.9618 | 974890.3187 | 81.2409 | 81.2409 | 154.0059 | 80 | 60 | 32.6546 | 32 | 61.4
6/23/20XX 1:00:00 PM | 0.54167 | 6 | 78 | 63.8 | 86.4193 | 101.161 | 14.7417 | 60 | 78 |  | 78 | 92.0212 | 0.1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 65.5616 | 17.741 | 422234.7267 | 35.1862 | 35.1862 | 96.2962 | 0.2 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 68.5015 | 20.6809 | 492205.6534 | 41.0171 | 41.0171 | 103.3871 | 0.3 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 71.4415 | 23.6209 | 562176.5802 | 46.848 | 46.848 | 110.478 | 0.4 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 74.3815 | 26.5608 | 632147.5069 | 52.679 | 52.679 | 117.569 | 0.5 | 76 | 21 | 793800 | 66.15 | 66.15 | 77.3214 | 29.5008 | 702118.4336 | 58.5099 | 58.5099 | 124.6599 | 0.6 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 80.2614 | 32.4407 | 772089.3603 | 64.3408 | 64.3408 | 131.7508 | 0.7 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 83.2013 | 35.3807 | 842060.287 | 70.1717 | 70.1717 | 138.8417 | 0.8 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 86.1413 | 38.3206 | 912031.2138 | 76.0026 | 76.0026 | 145.9326 | 0.9 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 89.0812 | 41.2606 | 982002.1405 | 81.8335 | 81.8335 | 153.0235 | 1 | 78 | 23 | 869400 | 72.45 | 72.45 | 92.0212 | 44.2005 | 1051973.0672 | 87.6644 | 87.6644 | 160.1144 | 80 | 65 | 33.1375 | 34 | 63.8
6/23/20XX 2:00:00 PM | 0.58333 | 6 | 79.2 | 61.6 | 89.9794 | 105.341 | 15.3616 | 60 | 79.2 |  | 79.2 | 92.4373 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 65.6032 | 17.7826 | 423225.0794 | 35.2688 | 35.2688 | 96.7568 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 68.5848 | 20.7641 | 494186.3587 | 41.1822 | 41.1822 | 104.3082 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 71.5663 | 23.7457 | 565147.6381 | 47.0956 | 47.0956 | 111.8596 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 74.5479 | 26.7273 | 636108.9175 | 53.0091 | 53.0091 | 119.4111 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 77.5295 | 29.7088 | 707070.1969 | 58.9225 | 58.9225 | 126.9625 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 80.511 | 32.6904 | 778031.4762 | 64.836 | 64.836 | 134.514 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 83.4926 | 35.672 | 848992.7556 | 70.7494 | 70.7494 | 142.0654 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 86.4742 | 38.6535 | 919954.035 | 76.6628 | 76.6628 | 149.6168 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 89.4557 | 41.6351 | 990915.3143 | 82.5763 | 82.5763 | 157.1683 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 92.4373 | 44.6167 | 1061876.5937 | 88.4897 | 88.4897 | 164.7197 | 80 | 60 | 33.4977 | 34 | 61.6
6/23/20XX 3:00:00 PM | 0.625 | 6 | 79.3 | 60.5 | 90.2816 | 105.6957 | 15.4142 | 60 | 79.3 |  | 79.3 | 91.0523 | 0.1 | 74.53 | 19.53 | 738234 | 61.5195 | 61.5195 | 65.4647 | 17.6441 | 419928.6984 | 34.9941 | 34.9941 | 96.5136 | 0.2 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 68.3078 | 20.4871 | 487593.5968 | 40.6328 | 40.6328 | 103.8218 | 0.3 | 75.59 | 20.59 | 778302 | 64.8585 | 64.8585 | 71.1508 | 23.3302 | 555258.4951 | 46.2715 | 46.2715 | 111.13 | 0.4 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 73.9939 | 26.1733 | 622923.3935 | 51.9103 | 51.9103 | 118.4383 | 0.5 | 76.65 | 21.65 | 818370 | 68.1975 | 68.1975 | 76.8369 | 29.0163 | 690588.2919 | 57.549 | 57.549 | 125.7465 | 0.6 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 79.68 | 31.8594 | 758253.1903 | 63.1878 | 63.1878 | 133.0548 | 0.7 | 77.71 | 22.71 | 858438 | 71.5365 | 71.5365 | 82.5231 | 34.7024 | 825918.0887 | 68.8265 | 68.8265 | 140.363 | 0.8 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 85.3661 | 37.5455 | 893582.987 | 74.4652 | 74.4652 | 147.6712 | 0.9 | 78.77 | 23.77 | 898506 | 74.8755 | 74.8755 | 88.2092 | 40.3886 | 961247.8854 | 80.104 | 80.104 | 154.9795 | 1 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 91.0523 | 43.2316 | 1028912.7838 | 85.7427 | 85.7427 | 162.2877 | 80 | 60 | 33.3052 | 34 | 60.5
6/23/20XX 4:00:00 PM | 0.66667 | 6 | 78.8 | 60.1 | 88.7794 | 103.932 | 15.1526 | 60 | 78.8 |  | 78.8 | 88.9309 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 65.2526 | 17.4319 | 414879.9429 | 34.5733 | 34.5733 | 95.9353 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 67.8835 | 20.0629 | 477496.0858 | 39.7913 | 39.7913 | 102.6653 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 70.5144 | 22.6938 | 540112.2287 | 45.0094 | 45.0094 | 109.3954 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 73.1454 | 25.3247 | 602728.3715 | 50.2274 | 50.2274 | 116.1254 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 75.7763 | 27.9557 | 665344.5144 | 55.4454 | 55.4454 | 122.8554 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 78.4072 | 30.5866 | 727960.6573 | 60.6634 | 60.6634 | 129.5854 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 81.0381 | 33.2175 | 790576.8002 | 65.8814 | 65.8814 | 136.3154 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 83.6691 | 35.8484 | 853192.9431 | 71.0994 | 71.0994 | 143.0454 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 86.3 | 38.4794 | 915809.086 | 76.3174 | 76.3174 | 149.7754 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 88.9309 | 41.1103 | 978425.2288 | 81.5354 | 81.5354 | 156.5054 | 80 | 60 | 32.8498 | 32 | 60.1
6/23/20XX 5:00:00 PM | 0.70833 | 6 | 78.8 | 61 | 88.7794 | 103.932 | 15.1526 | 60 | 78.8 |  | 78.8 | 90.2947 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 65.3889 | 17.5683 | 418125.6277 | 34.8438 | 34.8438 | 96.2058 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 68.1562 | 20.3356 | 483987.4554 | 40.3323 | 40.3323 | 103.2063 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 70.9235 | 23.1029 | 549849.2831 | 45.8208 | 45.8208 | 110.2068 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 73.6908 | 25.8702 | 615711.1108 | 51.3093 | 51.3093 | 117.2073 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 76.4582 | 28.6375 | 681572.9385 | 56.7977 | 56.7977 | 124.2077 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 79.2255 | 31.4048 | 747434.7662 | 62.2862 | 62.2862 | 131.2082 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 81.9928 | 34.1721 | 813296.594 | 67.7747 | 67.7747 | 138.2087 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 84.7601 | 36.9394 | 879158.4217 | 73.2632 | 73.2632 | 145.2092 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 87.5274 | 39.7067 | 945020.2494 | 78.7517 | 78.7517 | 152.2097 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 90.2947 | 42.474 | 1010882.0771 | 84.2402 | 84.2402 | 159.2102 | 80 | 60 | 33.0635 | 34 | 61
6/23/20XX 6:00:00 PM | 0.75 | 6 | 77.9 | 61.9 | 86.1281 | 100.819 | 14.691 | 60 | 77.9 |  | 77.9 | 88.9193 | 0.1 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 65.2514 | 17.4308 | 414852.3552 | 34.571 | 34.571 | 95.6495 | 0.2 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 67.8812 | 20.0605 | 477440.9103 | 39.7867 | 39.7867 | 102.0937 | 0.3 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 70.5109 | 22.6903 | 540029.4655 | 45.0025 | 45.0025 | 108.538 | 0.4 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 73.1407 | 25.3201 | 602618.0206 | 50.2182 | 50.2182 | 114.9822 | 0.5 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 75.7705 | 27.9499 | 665206.5758 | 55.4339 | 55.4339 | 121.4264 | 0.6 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 78.4003 | 30.5796 | 727795.1309 | 60.6496 | 60.6496 | 127.8706 | 0.7 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 81.03 | 33.2094 | 790383.6861 | 65.8653 | 65.8653 | 134.3148 | 0.8 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 83.6598 | 35.8392 | 852972.2412 | 71.081 | 71.081 | 140.759 | 0.9 | 77.51 | 22.51 | 850878 | 70.9065 | 70.9065 | 86.2896 | 38.4689 | 915560.7964 | 76.2967 | 76.2967 | 147.2032 | 1 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 88.9193 | 41.0987 | 978149.3515 | 81.5124 | 81.5124 | 153.6474 | 80 | 60 | 32.6269 | 32 | 61.9
6/23/20XX 7:00:00 PM | 0.79167 | 6 | 76.1 | 67.9 | 81.0242 | 94.8268 | 13.8027 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/23/20XX 8:00:00 PM | 0.83333 | 6 | 74.6 | 71.9 | 90.0655 | 103.2545 | 13.1889 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/23/20XX 9:00:00 PM | 0.875 | 6 | 73.9 | 75.5 | 87.9141 | 100.78 | 12.8659 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/23/20XX 10:00:00 PM | 0.91667 | 6 | 73.1 | 75.5 | 85.5092 | 98.0145 | 12.5053 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/23/20XX 11:00:00 PM | 0.95833 | 6 | 73 | 75.4 | 85.2126 | 97.6734 | 12.4608 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/23/20XX 12:00:00 AM | 0 | 7 | 72.4 | 74.3 | 83.4515 | 95.6486 | 12.1971 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/24/20XX 1:00:00 AM | 0.041667 | 7 | 71.5 | 76.4 | 80.8687 | 92.6795 | 11.8108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/24/20XX 2:00:00 AM | 0.083333 | 7 | 69.9 | 77.9 | 76.4479 | 87.5989 | 11.151 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/24/20XX 3:00:00 AM | 0.125 | 7 | 70.3 | 79.5 | 77.5329 | 88.8456 | 11.3127 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/24/20XX 4:00:00 AM | 0.16667 | 7 | 70 | 79.7 | 76.7179 | 87.9091 | 11.1912 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/24/20XX 5:00:00 AM | 0.20833 | 7 | 69.8 | 77.7 | 76.1788 | 87.2896 | 11.1108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/24/20XX 6:00:00 AM | 0.25 | 7 | 70.4 | 77 | 77.8062 | 89.1597 | 11.3535 | 70 | 70.4 |  | 70.4 | 85.7537 | 0.1 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 64.9348 | 17.1142 | 407318.0826 | 33.9432 | 33.9432 | 92.6592 | 0.2 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 67.248 | 19.4274 | 462372.3652 | 38.531 | 38.531 | 96.113 | 0.3 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 69.5612 | 21.7406 | 517426.6477 | 43.1189 | 43.1189 | 99.5669 | 0.4 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 71.8745 | 24.0538 | 572480.9303 | 47.7067 | 47.7067 | 103.0207 | 0.5 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 74.1877 | 26.367 | 627535.2129 | 52.2946 | 52.2946 | 106.4746 | 0.6 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 76.5009 | 28.6802 | 682589.4955 | 56.8825 | 56.8825 | 109.9285 | 0.7 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 78.8141 | 30.9934 | 737643.778 | 61.4703 | 61.4703 | 113.3823 | 0.8 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 81.1273 | 33.3066 | 792698.0606 | 66.0582 | 66.0582 | 116.8362 | 0.9 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 83.4405 | 35.6198 | 847752.3432 | 70.646 | 70.646 | 120.29 | 1 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 85.7537 | 37.9331 | 902806.6258 | 75.2339 | 75.2339 | 123.7439 | 70 | 75 | 30.2901 | 30 | 77
6/24/20XX 7:00:00 AM | 0.29167 | 7 | 71.2 | 74.3 | 80.0233 | 91.7077 | 11.6844 | 70 | 71.2 |  | 71.2 | 85.0476 | 0.1 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 64.8642 | 17.0436 | 405637.5595 | 33.8031 | 33.8031 | 92.7711 | 0.2 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 67.1068 | 19.2862 | 459011.319 | 38.2509 | 38.2509 | 96.3369 | 0.3 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 69.3494 | 21.5288 | 512385.0785 | 42.6988 | 42.6988 | 99.9028 | 0.4 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 71.592 | 23.7714 | 565758.838 | 47.1466 | 47.1466 | 103.4686 | 0.5 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 73.8346 | 26.014 | 619132.5975 | 51.5944 | 51.5944 | 107.0344 | 0.6 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 76.0772 | 28.2566 | 672506.357 | 56.0422 | 56.0422 | 110.6002 | 0.7 | 72.04 | 17.04 | 644112 | 53.676 | 53.676 | 78.3198 | 30.4992 | 725880.1165 | 60.49 | 60.49 | 114.166 | 0.8 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 80.5624 | 32.7418 | 779253.876 | 64.9378 | 64.9378 | 117.7318 | 0.9 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 82.805 | 34.9844 | 832627.6355 | 69.3856 | 69.3856 | 121.2976 | 1 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 85.0476 | 37.2269 | 886001.395 | 73.8334 | 73.8334 | 124.8634 | 70 | 75 | 30.3761 | 30 | 74.3
6/24/20XX 8:00:00 AM | 0.33333 | 7 | 72.5 | 71.3 | 83.7428 | 95.9835 | 12.2407 | 70 | 72.5 |  | 72.5 | 85.3341 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 64.8929 | 17.0722 | 406319.5287 | 33.86 | 33.86 | 93.2375 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 67.1641 | 19.3435 | 460375.2574 | 38.3646 | 38.3646 | 97.2696 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 69.4354 | 21.6147 | 514430.986 | 42.8692 | 42.8692 | 101.3017 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 71.7066 | 23.886 | 568486.7147 | 47.3739 | 47.3739 | 105.3339 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 73.9779 | 26.1572 | 622542.4434 | 51.8785 | 51.8785 | 109.366 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 76.2491 | 28.4285 | 676598.1721 | 56.3832 | 56.3832 | 113.3982 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 78.5204 | 30.6997 | 730653.9008 | 60.8878 | 60.8878 | 117.4303 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 80.7916 | 32.971 | 784709.6295 | 65.3925 | 65.3925 | 121.4625 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 83.0629 | 35.2422 | 838765.3581 | 69.8971 | 69.8971 | 125.4946 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 85.3341 | 37.5135 | 892821.0868 | 74.4018 | 74.4018 | 129.5268 | 70 | 70 | 30.74 | 30 | 71.3
6/24/20XX 9:00:00 AM | 0.375 | 7 | 74.3 | 68.5 | 76.1783 | 89.138 | 12.9597 | 60 | 74.3 |  | 74.3 | 87.1941 | 0.1 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 65.0789 | 17.2582 | 410746.2414 | 34.2289 | 34.2289 | 94.1734 | 0.2 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 67.5361 | 19.7155 | 469228.6827 | 39.1024 | 39.1024 | 99.1414 | 0.3 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 69.9934 | 22.1727 | 527711.1241 | 43.9759 | 43.9759 | 104.1094 | 0.4 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 72.4506 | 24.63 | 586193.5655 | 48.8495 | 48.8495 | 109.0775 | 0.5 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 74.9079 | 27.0872 | 644676.0068 | 53.723 | 53.723 | 114.0455 | 0.6 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 77.3651 | 29.5445 | 703158.4482 | 58.5965 | 58.5965 | 119.0135 | 0.7 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 79.8224 | 32.0017 | 761640.8896 | 63.4701 | 63.4701 | 123.9816 | 0.8 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 82.2796 | 34.459 | 820123.331 | 68.3436 | 68.3436 | 128.9496 | 0.9 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 84.7368 | 36.9162 | 878605.7723 | 73.2171 | 73.2171 | 133.9176 | 1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 87.1941 | 39.3735 | 937088.2137 | 78.0907 | 78.0907 | 138.8857 | 75 | 70 | 31.4727 | 32 | 68.5
6/24/20XX 10:00:00 AM | 0.41667 | 7 | 76.7 | 63.6 | 82.6964 | 96.79 | 14.0936 | 60 | 76.7 |  | 76.7 | 87.7701 | 0.1 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 65.1365 | 17.3158 | 412117.1163 | 34.3431 | 34.3431 | 95.0436 | 0.2 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 67.6513 | 19.8307 | 471970.4325 | 39.3309 | 39.3309 | 100.8819 | 0.3 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 70.1662 | 22.3455 | 531823.7488 | 44.3186 | 44.3186 | 106.7201 | 0.4 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 72.681 | 24.8604 | 591677.065 | 49.3064 | 49.3064 | 112.5584 | 0.5 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 75.1959 | 27.3752 | 651530.3813 | 54.2942 | 54.2942 | 118.3967 | 0.6 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 77.7107 | 29.8901 | 711383.6975 | 59.282 | 59.282 | 124.235 | 0.7 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 80.2255 | 32.4049 | 771237.0138 | 64.2698 | 64.2698 | 130.0733 | 0.8 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 82.7404 | 34.9198 | 831090.33 | 69.2575 | 69.2575 | 135.9115 | 0.9 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 85.2552 | 37.4346 | 890943.6463 | 74.2453 | 74.2453 | 141.7498 | 1 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 87.7701 | 39.9495 | 950796.9625 | 79.2331 | 79.2331 | 147.5881 | 75 | 65 | 32.1522 | 32 | 63.6
6/24/20XX 11:00:00 AM | 0.45833 | 7 | 80.1 | 56.7 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 87.5316 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 65.1126 | 17.292 | 411549.4497 | 34.2958 | 34.2958 | 96.0673 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 67.6036 | 19.783 | 470835.0993 | 39.2363 | 39.2363 | 102.9293 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 70.0946 | 22.274 | 530120.749 | 44.1767 | 44.1767 | 109.7912 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 72.5856 | 24.765 | 589406.3986 | 49.1172 | 49.1172 | 116.6532 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 75.0766 | 27.256 | 648692.0483 | 54.0577 | 54.0577 | 123.5152 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 77.5676 | 29.747 | 707977.6979 | 58.9981 | 58.9981 | 130.3771 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 80.0586 | 32.238 | 767263.3476 | 63.9386 | 63.9386 | 137.2391 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 82.5496 | 34.7289 | 826548.9972 | 68.8791 | 68.8791 | 144.1011 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 85.0406 | 37.2199 | 885834.6469 | 73.8196 | 73.8196 | 150.9631 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 87.5316 | 39.7109 | 945120.2965 | 78.76 | 78.76 | 157.825 | 80 | 55 | 32.9497 | 32 | 56.7
6/24/20XX 12:00:00 PM | 0.5 | 7 | 80.6 | 53.1 | 78.2688 | 94.2862 | 16.0174 | 50 | 80.6 |  | 80.6 | 83.2342 | 0.1 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 64.6829 | 16.8623 | 401321.681 | 33.4435 | 33.4435 | 95.3725 | 0.2 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 66.7441 | 18.9235 | 450379.562 | 37.5316 | 37.5316 | 101.5396 | 0.3 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 68.8054 | 20.9848 | 499437.443 | 41.6198 | 41.6198 | 107.7068 | 0.4 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 70.8667 | 23.046 | 548495.3241 | 45.7079 | 45.7079 | 113.8739 | 0.5 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 72.9279 | 25.1073 | 597553.2051 | 49.7961 | 49.7961 | 120.0411 | 0.6 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 74.9892 | 27.1685 | 646611.0861 | 53.8843 | 53.8843 | 126.2083 | 0.7 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 77.0504 | 29.2298 | 695668.9671 | 57.9724 | 57.9724 | 132.3754 | 0.8 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 79.1117 | 31.291 | 744726.8481 | 62.0606 | 62.0606 | 138.5426 | 0.9 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 81.1729 | 33.3523 | 793784.7291 | 66.1487 | 66.1487 | 144.7097 | 1 | 80.6 | 25.6 | 967680 | 80.64 | 80.64 | 83.2342 | 35.4136 | 842842.6101 | 70.2369 | 70.2369 | 150.8769 | 80 | 55 | 32.3985 | 32 | 53.1
6/24/20XX 1:00:00 PM | 0.54167 | 7 | 80.3 | 55.3 | 77.4931 | 93.3492 | 15.8561 | 50 | 80.3 |  | 80.3 | 85.8968 | 0.1 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 64.9492 | 17.1285 | 407658.78 | 33.9716 | 33.9716 | 95.8061 | 0.2 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 67.2767 | 19.456 | 463053.7601 | 38.5878 | 38.5878 | 102.4068 | 0.3 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 69.6042 | 21.7836 | 518448.7401 | 43.2041 | 43.2041 | 109.0076 | 0.4 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 71.9317 | 24.1111 | 573843.7202 | 47.8203 | 47.8203 | 115.6083 | 0.5 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 74.2592 | 26.4386 | 629238.7002 | 52.4366 | 52.4366 | 122.2091 | 0.6 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 76.5868 | 28.7661 | 684633.6803 | 57.0528 | 57.0528 | 128.8098 | 0.7 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 78.9143 | 31.0936 | 740028.6603 | 61.6691 | 61.6691 | 135.4106 | 0.8 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 81.2418 | 33.4212 | 795423.6404 | 66.2853 | 66.2853 | 142.0113 | 0.9 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 83.5693 | 35.7487 | 850818.6204 | 70.9016 | 70.9016 | 148.6121 | 1 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 85.8968 | 38.0762 | 906213.6004 | 75.5178 | 75.5178 | 155.2128 | 80 | 55 | 32.7425 | 32 | 55.3
6/24/20XX 2:00:00 PM | 0.58333 | 7 | 79.8 | 56.2 | 76.2143 | 91.8048 | 15.5904 | 50 | 79.8 |  | 79.8 | 85.8804 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 64.9475 | 17.1269 | 407619.6498 | 33.9683 | 33.9683 | 95.6453 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 67.2734 | 19.4528 | 462975.4995 | 38.5813 | 38.5813 | 102.0853 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 69.5993 | 21.7786 | 518331.3493 | 43.1943 | 43.1943 | 108.5253 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 71.9251 | 24.1045 | 573687.1991 | 47.8073 | 47.8073 | 114.9653 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 74.251 | 26.4304 | 629043.0488 | 52.4203 | 52.4203 | 121.4053 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 76.5769 | 28.7563 | 684398.8986 | 57.0332 | 57.0332 | 127.8452 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 78.9028 | 31.0821 | 739754.7484 | 61.6462 | 61.6462 | 134.2852 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 81.2286 | 33.408 | 795110.5982 | 66.2592 | 66.2592 | 140.7252 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 83.5545 | 35.7339 | 850466.4479 | 70.8722 | 70.8722 | 147.1652 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 85.8804 | 38.0598 | 905822.2977 | 75.4852 | 75.4852 | 153.6052 | 80 | 55 | 32.6172 | 32 | 56.2
6/24/20XX 3:00:00 PM | 0.625 | 7 | 80.1 | 56.9 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 87.8466 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 65.1441 | 17.3235 | 412299.1213 | 34.3583 | 34.3583 | 96.1298 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 67.6666 | 19.846 | 472334.4426 | 39.3612 | 39.3612 | 103.0542 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 70.1891 | 22.3685 | 532369.7639 | 44.3641 | 44.3641 | 109.9786 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 72.7116 | 24.891 | 592405.0852 | 49.3671 | 49.3671 | 116.9031 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 75.2341 | 27.4135 | 652440.4065 | 54.37 | 54.37 | 123.8275 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 77.7566 | 29.936 | 712475.7278 | 59.373 | 59.373 | 130.752 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 80.2791 | 32.4584 | 772511.0491 | 64.3759 | 64.3759 | 137.6764 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 82.8016 | 34.9809 | 832546.3704 | 69.3789 | 69.3789 | 144.6009 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 85.3241 | 37.5034 | 892581.6917 | 74.3818 | 74.3818 | 151.5253 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 87.8466 | 40.0259 | 952617.013 | 79.3848 | 79.3848 | 158.4498 | 80 | 55 | 32.9991 | 32 | 56.9
6/24/20XX 4:00:00 PM | 0.66667 | 7 | 79.4 | 57.7 | 75.2039 | 90.5845 | 15.3806 | 50 | 79.4 |  | 79.4 | 87.047 | 0.1 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 65.0642 | 17.2435 | 410396.0987 | 34.1997 | 34.1997 | 95.7507 | 0.2 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 67.5067 | 19.6861 | 468528.3975 | 39.044 | 39.044 | 102.296 | 0.3 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 69.9492 | 22.1286 | 526660.6962 | 43.8884 | 43.8884 | 108.8414 | 0.4 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 72.3918 | 24.5711 | 584792.9949 | 48.7327 | 48.7327 | 115.3867 | 0.5 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 74.8343 | 27.0137 | 642925.2937 | 53.5771 | 53.5771 | 121.9321 | 0.6 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 77.2768 | 29.4562 | 701057.5924 | 58.4215 | 58.4215 | 128.4775 | 0.7 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 79.7194 | 31.8987 | 759189.8911 | 63.2658 | 63.2658 | 135.0228 | 0.8 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 82.1619 | 34.3413 | 817322.1899 | 68.1102 | 68.1102 | 141.5682 | 0.9 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 84.6044 | 36.7838 | 875454.4886 | 72.9545 | 72.9545 | 148.1135 | 1 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 87.047 | 39.2263 | 933586.7873 | 77.7989 | 77.7989 | 154.6589 | 80 | 60 | 32.7019 | 32 | 57.7
6/24/20XX 5:00:00 PM | 0.70833 | 7 | 79 | 58.3 | 74.2046 | 89.3778 | 15.1731 | 50 | 79 |  | 79 | 86.7983 | 0.1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 65.0393 | 17.2187 | 409804.3205 | 34.1504 | 34.1504 | 95.5754 | 0.2 | 75 | 20 | 756000 | 63 | 63 | 67.457 | 19.6363 | 467344.841 | 38.9454 | 38.9454 | 101.9454 | 0.3 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 69.8746 | 22.054 | 524885.3615 | 43.7404 | 43.7404 | 108.3154 | 0.4 | 76 | 21 | 793800 | 66.15 | 66.15 | 72.2923 | 24.4717 | 582425.882 | 48.5355 | 48.5355 | 114.6855 | 0.5 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 74.71 | 26.8893 | 639966.4026 | 53.3305 | 53.3305 | 121.0555 | 0.6 | 77 | 22 | 831600 | 69.3 | 69.3 | 77.1276 | 29.307 | 697506.9231 | 58.1256 | 58.1256 | 127.4256 | 0.7 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 79.5453 | 31.7247 | 755047.4436 | 62.9206 | 62.9206 | 133.7956 | 0.8 | 78 | 23 | 869400 | 72.45 | 72.45 | 81.963 | 34.1424 | 812587.9641 | 67.7157 | 67.7157 | 140.1657 | 0.9 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 84.3807 | 36.56 | 870128.4846 | 72.5107 | 72.5107 | 146.5357 | 1 | 79 | 24 | 907200 | 75.6 | 75.6 | 86.7983 | 38.9777 | 927669.0051 | 77.3058 | 77.3058 | 152.9058 | 80 | 60 | 32.5647 | 32 | 58.3
6/24/20XX 6:00:00 PM | 0.75 | 7 | 78.2 | 58.3 | 72.2392 | 87.0044 | 14.7652 | 50 | 78.2 |  | 78.2 | 84.4943 | 0.1 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 64.8089 | 16.9883 | 404320.7552 | 33.6934 | 33.6934 | 94.8664 | 0.2 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 66.9962 | 19.1755 | 456377.7103 | 38.0315 | 38.0315 | 100.5275 | 0.3 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 69.1834 | 21.3628 | 508434.6655 | 42.3696 | 42.3696 | 106.1886 | 0.4 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 71.3707 | 23.5501 | 560491.6207 | 46.7076 | 46.7076 | 111.8496 | 0.5 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 73.558 | 25.7373 | 612548.5758 | 51.0457 | 51.0457 | 117.5107 | 0.6 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 75.7452 | 27.9246 | 664605.531 | 55.3838 | 55.3838 | 123.1718 | 0.7 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 77.9325 | 30.1119 | 716662.4861 | 59.7219 | 59.7219 | 128.8329 | 0.8 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 80.1198 | 32.2991 | 768719.4413 | 64.06 | 64.06 | 134.494 | 0.9 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 82.307 | 34.4864 | 820776.3965 | 68.398 | 68.398 | 140.155 | 1 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 84.4943 | 36.6737 | 872833.3516 | 72.7361 | 72.7361 | 145.8161 | 80 | 60 | 32.0072 | 32 | 58.3
6/24/20XX 7:00:00 PM | 0.79167 | 7 | 77.1 | 60.8 | 83.8273 | 98.1177 | 14.2905 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/24/20XX 8:00:00 PM | 0.83333 | 7 | 76.1 | 61.5 | 81.0242 | 94.8268 | 13.8027 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/24/20XX 9:00:00 PM | 0.875 | 7 | 73.8 | 67.4 | 74.8769 | 87.6104 | 12.7335 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/24/20XX 10:00:00 PM | 0.91667 | 7 | 73.7 | 66 | 74.6189 | 87.3075 | 12.6886 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/24/20XX 11:00:00 PM | 0.95833 | 7 | 72.1 | 69.7 | 70.5937 | 82.5828 | 11.9891 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/24/20XX 12:00:00 AM | 0 | 1 | 71.1 | 71.9 | 79.7432 | 91.3858 | 11.6426 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/25/20XX 1:00:00 AM | 0.041667 | 1 | 70.5 | 73 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/25/20XX 2:00:00 AM | 0.083333 | 1 | 70.2 | 75 | 77.2604 | 88.5325 | 11.2721 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/25/20XX 3:00:00 AM | 0.125 | 1 | 69.5 | 77.1 | 75.3763 | 86.3676 | 10.9913 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/25/20XX 4:00:00 AM | 0.16667 | 1 | 68.8 | 78.5 | 73.5326 | 84.2494 | 10.7169 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/25/20XX 5:00:00 AM | 0.20833 | 1 | 68.1 | 80.8 | 82.1774 | 92.6206 | 10.4432 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/25/20XX 6:00:00 AM | 0.25 | 1 | 69 | 78.8 | 74.0553 | 84.8499 | 10.7946 | 70 | 69 |  | 69 | 83.5545 | 0.1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 64.7149 | 16.8943 | 402084.1144 | 33.507 | 33.507 | 91.782 | 0.2 | 73 | 18 | 680400 | 56.7 | 56.7 | 66.8082 | 18.9876 | 451904.4288 | 37.6587 | 37.6587 | 94.3587 | 0.3 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 68.9015 | 21.0809 | 501724.7433 | 41.8104 | 41.8104 | 96.9354 | 0.4 | 72 | 17 | 642600 | 53.55 | 53.55 | 70.9948 | 23.1742 | 551545.0577 | 45.9621 | 45.9621 | 99.5121 | 0.5 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 73.0881 | 25.2675 | 601365.3721 | 50.1138 | 50.1138 | 102.0888 | 0.6 | 71 | 16 | 604800 | 50.4 | 50.4 | 75.1814 | 27.3607 | 651185.6865 | 54.2655 | 54.2655 | 104.6655 | 0.7 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 77.2747 | 29.454 | 701006.001 | 58.4172 | 58.4172 | 107.2422 | 0.8 | 70 | 15 | 567000 | 47.25 | 47.25 | 79.368 | 31.5473 | 750826.3154 | 62.5689 | 62.5689 | 109.8189 | 0.9 | 69.5 | 14.5 | 548100 | 45.675 | 45.675 | 81.4612 | 33.6406 | 800646.6298 | 66.7206 | 66.7206 | 112.3956 | 1 | 69 | 14 | 529200 | 44.1 | 44.1 | 83.5545 | 35.7339 | 850466.9442 | 70.8722 | 70.8722 | 114.9722 | 70 | 80 | 29.6032 | 30 | 78.8
6/25/20XX 7:00:00 AM | 0.29167 | 1 | 69.7 | 75.4 | 75.9105 | 86.9813 | 11.0709 | 70 | 69.7 |  | 69.7 | 81.8887 | 0.1 | 73.57 | 18.57 | 701946 | 58.4955 | 58.4955 | 64.5483 | 16.7277 | 398119.4942 | 33.1766 | 33.1766 | 91.6721 | 0.2 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 66.4751 | 18.6544 | 443975.1883 | 36.9979 | 36.9979 | 94.1389 | 0.3 | 72.71 | 17.71 | 669438 | 55.7865 | 55.7865 | 68.4018 | 20.5811 | 489830.8825 | 40.8192 | 40.8192 | 96.6057 | 0.4 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 70.3285 | 22.5078 | 535686.5766 | 44.6405 | 44.6405 | 99.0725 | 0.5 | 71.85 | 16.85 | 636930 | 53.0775 | 53.0775 | 72.2552 | 24.4345 | 581542.2708 | 48.4619 | 48.4619 | 101.5394 | 0.6 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 74.1819 | 26.3613 | 627397.9649 | 52.2832 | 52.2832 | 104.0062 | 0.7 | 70.99 | 15.99 | 604422 | 50.3685 | 50.3685 | 76.1086 | 28.288 | 673253.6591 | 56.1045 | 56.1045 | 106.473 | 0.8 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 78.0353 | 30.2147 | 719109.3532 | 59.9258 | 59.9258 | 108.9398 | 0.9 | 70.13 | 15.13 | 571914 | 47.6595 | 47.6595 | 79.962 | 32.1414 | 764965.0474 | 63.7471 | 63.7471 | 111.4066 | 1 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 81.8887 | 34.0681 | 810820.7415 | 67.5684 | 67.5684 | 113.8734 | 70 | 75 | 29.5148 | 30 | 75.4
6/25/20XX 8:00:00 AM | 0.33333 | 1 | 72.2 | 68.6 | 70.8397 | 82.8715 | 12.0318 | 60 | 72.2 |  | 72.2 | 81.187 | 0.1 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 64.4782 | 16.6575 | 396449.4407 | 33.0375 | 33.0375 | 92.3205 | 0.2 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 66.3347 | 18.5141 | 440635.0815 | 36.7196 | 36.7196 | 95.4356 | 0.3 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 68.1913 | 20.3706 | 484820.7222 | 40.4017 | 40.4017 | 98.5507 | 0.4 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 70.0478 | 22.2272 | 529006.363 | 44.0839 | 44.0839 | 101.6659 | 0.5 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 71.9043 | 24.0837 | 573192.0037 | 47.766 | 47.766 | 104.781 | 0.6 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 73.7609 | 25.9402 | 617377.6445 | 51.4481 | 51.4481 | 107.8961 | 0.7 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 75.6174 | 27.7968 | 661563.2852 | 55.1303 | 55.1303 | 111.0113 | 0.8 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 77.4739 | 29.6533 | 705748.926 | 58.8124 | 58.8124 | 114.1264 | 0.9 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 79.3305 | 31.5099 | 749934.5667 | 62.4945 | 62.4945 | 117.2415 | 1 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 81.187 | 33.3664 | 794120.2075 | 66.1767 | 66.1767 | 120.3567 | 70 | 70 | 30.0181 | 30 | 68.6
6/25/20XX 9:00:00 AM | 0.375 | 1 | 73.8 | 65 | 74.8769 | 87.6104 | 12.7335 | 60 | 73.8 |  | 73.8 | 81.2436 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 64.4838 | 16.6632 | 396584.1327 | 33.0487 | 33.0487 | 92.8357 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 66.346 | 18.5254 | 440904.4655 | 36.742 | 36.742 | 96.466 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 68.2082 | 20.3876 | 485224.7982 | 40.4354 | 40.4354 | 100.0964 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 70.0704 | 22.2498 | 529545.131 | 44.1288 | 44.1288 | 103.7268 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 71.9326 | 24.112 | 573865.4637 | 47.8221 | 47.8221 | 107.3571 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 73.7948 | 25.9742 | 618185.7965 | 51.5155 | 51.5155 | 110.9875 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 75.657 | 27.8364 | 662506.1292 | 55.2088 | 55.2088 | 114.6178 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 77.5192 | 29.6986 | 706826.462 | 58.9022 | 58.9022 | 118.2482 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 79.3814 | 31.5608 | 751146.7947 | 62.5956 | 62.5956 | 121.8786 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 81.2436 | 33.423 | 795467.1275 | 66.2889 | 66.2889 | 125.5089 | 75 | 65 | 30.4192 | 30 | 65
6/25/20XX 10:00:00 AM | 0.41667 | 1 | 76 | 61.1 | 80.7483 | 94.5029 | 13.7546 | 60 | 76 |  | 76 | 82.2613 | 0.1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 64.5856 | 16.765 | 399006.1305 | 33.2505 | 33.2505 | 93.7305 | 0.2 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 66.5496 | 18.7289 | 445748.461 | 37.1457 | 37.1457 | 98.2557 | 0.3 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 68.5135 | 20.6929 | 492490.7916 | 41.0409 | 41.0409 | 102.7809 | 0.4 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 70.4775 | 22.6569 | 539233.1221 | 44.9361 | 44.9361 | 107.3061 | 0.5 | 75 | 20 | 756000 | 63 | 63 | 72.4414 | 24.6208 | 585975.4526 | 48.8313 | 48.8313 | 111.8313 | 0.6 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 74.4054 | 26.5848 | 632717.7831 | 52.7265 | 52.7265 | 116.3565 | 0.7 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 76.3694 | 28.5487 | 679460.1136 | 56.6217 | 56.6217 | 120.8817 | 0.8 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 78.3333 | 30.5127 | 726202.4441 | 60.5169 | 60.5169 | 125.4069 | 0.9 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 80.2973 | 32.4767 | 772944.7747 | 64.4121 | 64.4121 | 129.9321 | 1 | 76 | 21 | 793800 | 66.15 | 66.15 | 82.2613 | 34.4406 | 819687.1052 | 68.3073 | 68.3073 | 134.4573 | 75 | 60 | 31.1179 | 32 | 61.1
6/25/20XX 11:00:00 AM | 0.45833 | 1 | 78.1 | 58.2 | 71.9966 | 86.7115 | 14.7149 | 50 | 78.1 |  | 78.1 | 84.0628 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 64.7657 | 16.9451 | 403293.7193 | 33.6078 | 33.6078 | 94.7493 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 66.9099 | 19.0892 | 454323.6385 | 37.8603 | 37.8603 | 100.2933 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 69.054 | 21.2333 | 505353.5578 | 42.1128 | 42.1128 | 105.8373 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 71.1981 | 23.3775 | 556383.4771 | 46.3653 | 46.3653 | 111.3813 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 73.3422 | 25.5216 | 607413.3964 | 50.6178 | 50.6178 | 116.9253 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 75.4863 | 27.6657 | 658443.3156 | 54.8703 | 54.8703 | 122.4693 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 77.6304 | 29.8098 | 709473.2349 | 59.1228 | 59.1228 | 128.0133 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 79.7745 | 31.9539 | 760503.1542 | 63.3753 | 63.3753 | 133.5573 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 81.9187 | 34.098 | 811533.0735 | 67.6278 | 67.6278 | 139.1013 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 84.0628 | 36.2421 | 862562.9927 | 71.8802 | 71.8802 | 144.6452 | 80 | 60 | 31.9151 | 32 | 58.2
6/25/20XX 12:00:00 PM | 0.5 | 1 | 80.1 | 53.2 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 82.0193 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 64.5614 | 16.7408 | 398430.1958 | 33.2025 | 33.2025 | 94.974 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 66.5012 | 18.6805 | 444596.5916 | 37.0497 | 37.0497 | 100.7427 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 68.4409 | 20.6203 | 490762.9874 | 40.8969 | 40.8969 | 106.5114 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 70.3807 | 22.5601 | 536929.3832 | 44.7441 | 44.7441 | 112.2801 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 72.3205 | 24.4998 | 583095.779 | 48.5913 | 48.5913 | 118.0488 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 74.2602 | 26.4396 | 629262.1749 | 52.4385 | 52.4385 | 123.8175 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 76.2 | 28.3794 | 675428.5707 | 56.2857 | 56.2857 | 129.5862 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 78.1397 | 30.3191 | 721594.9665 | 60.1329 | 60.1329 | 135.3549 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 80.0795 | 32.2589 | 767761.3623 | 63.9801 | 63.9801 | 141.1236 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 82.0193 | 34.1986 | 813927.7581 | 67.8273 | 67.8273 | 146.8923 | 80 | 55 | 32.0853 | 32 | 53.2
6/25/20XX 1:00:00 PM | 0.54167 | 1 | 80.8 | 50.3 | 78.7895 | 94.9151 | 16.1256 | 50 | 80.8 |  | 80.8 | 79.2733 | 0.1 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 64.2868 | 16.4662 | 391894.698 | 32.6579 | 32.6579 | 94.6499 | 0.2 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 65.952 | 18.1313 | 431525.5961 | 35.9605 | 35.9605 | 100.0945 | 0.3 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 67.6171 | 19.7965 | 471156.4941 | 39.263 | 39.263 | 105.539 | 0.4 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 69.2823 | 21.4617 | 510787.3921 | 42.5656 | 42.5656 | 110.9836 | 0.5 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 70.9475 | 23.1268 | 550418.2902 | 45.8682 | 45.8682 | 116.4282 | 0.6 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 72.6126 | 24.792 | 590049.1882 | 49.1708 | 49.1708 | 121.8728 | 0.7 | 78.76 | 23.76 | 898128 | 74.844 | 74.844 | 74.2778 | 26.4571 | 629680.0863 | 52.4733 | 52.4733 | 127.3173 | 0.8 | 79.44 | 24.44 | 923832 | 76.986 | 76.986 | 75.9429 | 28.1223 | 669310.9843 | 55.7759 | 55.7759 | 132.7619 | 0.9 | 80.12 | 25.12 | 949536 | 79.128 | 79.128 | 77.6081 | 29.7875 | 708941.8823 | 59.0785 | 59.0785 | 138.2065 | 1 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 79.2733 | 31.4526 | 748572.7804 | 62.3811 | 62.3811 | 143.6511 | 80 | 50 | 31.8263 | 32 | 50.3
6/25/20XX 2:00:00 PM | 0.58333 | 1 | 81.2 | 51.9 | 79.8394 | 96.1834 | 16.3439 | 50 | 81.2 |  | 81.2 | 82.9448 | 0.1 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 64.6539 | 16.8333 | 400632.9076 | 33.3861 | 33.3861 | 95.5041 | 0.2 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 66.6863 | 18.8656 | 449002.0152 | 37.4168 | 37.4168 | 101.8028 | 0.3 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 68.7186 | 20.8979 | 497371.1228 | 41.4476 | 41.4476 | 108.1016 | 0.4 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 70.7509 | 22.9303 | 545740.2304 | 45.4784 | 45.4784 | 114.4004 | 0.5 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 72.7832 | 24.9626 | 594109.3379 | 49.5091 | 49.5091 | 120.6991 | 0.6 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 74.8155 | 26.9949 | 642478.4455 | 53.5399 | 53.5399 | 126.9979 | 0.7 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 76.8478 | 29.0272 | 690847.5531 | 57.5706 | 57.5706 | 133.2966 | 0.8 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 78.8802 | 31.0595 | 739216.6607 | 61.6014 | 61.6014 | 139.5954 | 0.9 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 80.9125 | 33.0918 | 787585.7683 | 65.6321 | 65.6321 | 145.8941 | 1 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 82.9448 | 35.1242 | 835954.8759 | 69.6629 | 69.6629 | 152.1929 | 80 | 50 | 32.5003 | 32 | 51.9
6/25/20XX 3:00:00 PM | 0.625 | 1 | 79.9 | 53 | 76.4687 | 92.1119 | 15.6433 | 50 | 79.9 |  | 79.9 | 81.1617 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 64.4756 | 16.655 | 396389.0432 | 33.0324 | 33.0324 | 94.7409 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 66.3296 | 18.509 | 440514.2865 | 36.7095 | 36.7095 | 100.2765 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 68.1836 | 20.363 | 484639.5297 | 40.3866 | 40.3866 | 105.8121 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 70.0376 | 22.217 | 528764.7729 | 44.0637 | 44.0637 | 111.3477 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 71.8916 | 24.071 | 572890.0162 | 47.7408 | 47.7408 | 116.8833 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 73.7456 | 25.925 | 617015.2594 | 51.4179 | 51.4179 | 122.4189 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 75.5996 | 27.779 | 661140.5026 | 55.095 | 55.095 | 127.9545 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 77.4536 | 29.633 | 705265.7458 | 58.7721 | 58.7721 | 133.4901 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 79.3076 | 31.487 | 749390.9891 | 62.4492 | 62.4492 | 139.0257 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 81.1617 | 33.341 | 793516.2323 | 66.1264 | 66.1264 | 144.5614 | 80 | 55 | 31.9018 | 32 | 53
6/25/20XX 4:00:00 PM | 0.66667 | 1 | 78.3 | 56.6 | 72.4824 | 87.2982 | 14.8157 | 50 | 78.3 |  | 78.3 | 82.2608 | 0.1 | 74.43 | 19.43 | 734454 | 61.2045 | 61.2045 | 64.5856 | 16.7649 | 399005.0514 | 33.2504 | 33.2504 | 94.4549 | 0.2 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 66.5495 | 18.7288 | 445746.3027 | 37.1455 | 37.1455 | 99.7045 | 0.3 | 75.29 | 20.29 | 766962 | 63.9135 | 63.9135 | 68.5134 | 20.6928 | 492487.5541 | 41.0406 | 41.0406 | 104.9541 | 0.4 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 70.4773 | 22.6567 | 539228.8055 | 44.9357 | 44.9357 | 110.2037 | 0.5 | 76.15 | 21.15 | 799470 | 66.6225 | 66.6225 | 72.4412 | 24.6206 | 585970.0568 | 48.8308 | 48.8308 | 115.4533 | 0.6 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 74.4051 | 26.5845 | 632711.3082 | 52.7259 | 52.7259 | 120.7029 | 0.7 | 77.01 | 22.01 | 831978 | 69.3315 | 69.3315 | 76.3691 | 28.5484 | 679452.5596 | 56.621 | 56.621 | 125.9525 | 0.8 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 78.333 | 30.5123 | 726193.811 | 60.5162 | 60.5162 | 131.2022 | 0.9 | 77.87 | 22.87 | 864486 | 72.0405 | 72.0405 | 80.2969 | 32.4763 | 772935.0623 | 64.4113 | 64.4113 | 136.4518 | 1 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 82.2608 | 34.4402 | 819676.3137 | 68.3064 | 68.3064 | 141.7014 | 80 | 55 | 31.6818 | 32 | 56.6
6/25/20XX 5:00:00 PM | 0.70833 | 1 | 77.2 | 58.5 | 69.8436 | 84.112 | 14.2685 | 50 | 77.2 |  | 77.2 | 81.9717 | 0.1 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 64.5566 | 16.736 | 398317.067 | 33.1931 | 33.1931 | 94.0511 | 0.2 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 66.4917 | 18.671 | 444370.3341 | 37.0309 | 37.0309 | 98.8969 | 0.3 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 68.4267 | 20.606 | 490423.6011 | 40.8686 | 40.8686 | 103.7426 | 0.4 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 70.3617 | 22.541 | 536476.8682 | 44.7064 | 44.7064 | 108.5884 | 0.5 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 72.2967 | 24.4761 | 582530.1352 | 48.5442 | 48.5442 | 113.4342 | 0.6 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 74.2317 | 26.4111 | 628583.4023 | 52.382 | 52.382 | 118.28 | 0.7 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 76.1667 | 28.3461 | 674636.6693 | 56.2197 | 56.2197 | 123.1257 | 0.8 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 78.1017 | 30.2811 | 720689.9364 | 60.0575 | 60.0575 | 127.9715 | 0.9 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 80.0367 | 32.2161 | 766743.2034 | 63.8953 | 63.8953 | 132.8173 | 1 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 81.9717 | 34.1511 | 812796.4705 | 67.733 | 67.733 | 137.663 | 75 | 60 | 31.3668 | 32 | 58.5
6/25/20XX 6:00:00 PM | 0.75 | 1 | 76.6 | 59.1 | 68.4384 | 82.4157 | 13.9773 | 50 | 76.6 |  | 76.6 | 81.1577 | 0.1 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 64.4752 | 16.6546 | 396379.6762 | 33.0316 | 33.0316 | 93.7006 | 0.2 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 66.3288 | 18.5082 | 440495.5524 | 36.708 | 36.708 | 98.196 | 0.3 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 68.1825 | 20.3618 | 484611.4287 | 40.3843 | 40.3843 | 102.6913 | 0.4 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 70.0361 | 22.2154 | 528727.3049 | 44.0606 | 44.0606 | 107.1866 | 0.5 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 71.8897 | 24.069 | 572843.1811 | 47.7369 | 47.7369 | 111.6819 | 0.6 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 73.7433 | 25.9226 | 616959.0573 | 51.4133 | 51.4133 | 116.1773 | 0.7 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 75.5969 | 27.7763 | 661074.9335 | 55.0896 | 55.0896 | 120.6726 | 0.8 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 77.4505 | 29.6299 | 705190.8098 | 58.7659 | 58.7659 | 125.1679 | 0.9 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 79.3041 | 31.4835 | 749306.686 | 62.4422 | 62.4422 | 129.6632 | 1 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 81.1577 | 33.3371 | 793422.5622 | 66.1185 | 66.1185 | 134.1585 | 75 | 60 | 31.0922 | 32 | 59.1
6/25/20XX 7:00:00 PM | 0.79167 | 1 | 75.3 | 60.8 | 78.8391 | 92.2616 | 13.4225 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/25/20XX 8:00:00 PM | 0.83333 | 1 | 74.1 | 61.3 | 75.6554 | 88.5243 | 12.8688 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/25/20XX 9:00:00 PM | 0.875 | 1 | 73.9 | 61.3 | 75.1356 | 87.9141 | 12.7785 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/25/20XX 10:00:00 PM | 0.91667 | 1 | 73.1 | 61.9 | 73.0869 | 85.5092 | 12.4223 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/25/20XX 11:00:00 PM | 0.95833 | 1 | 72.4 | 63.5 | 71.3339 | 83.4515 | 12.1177 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/25/20XX 12:00:00 AM | 0 | 2 | 70.5 | 68.6 | 66.7576 | 78.0804 | 11.3228 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/26/20XX 1:00:00 AM | 0.041667 | 2 | 70.2 | 68.7 | 66.0589 | 77.2604 | 11.2015 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/26/20XX 2:00:00 AM | 0.083333 | 2 | 69.4 | 68.4 | 64.2269 | 75.1104 | 10.8835 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/26/20XX 3:00:00 AM | 0.125 | 2 | 68.8 | 70.7 | 73.5326 | 84.2494 | 10.7169 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/26/20XX 4:00:00 AM | 0.16667 | 2 | 67.9 | 72.3 | 71.2205 | 81.5937 | 10.3732 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/26/20XX 5:00:00 AM | 0.20833 | 2 | 67.3 | 73.4 | 69.7151 | 79.8649 | 10.1498 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/26/20XX 6:00:00 AM | 0.25 | 2 | 68.6 | 71.9 | 73.0131 | 83.6528 | 10.6396 | 70 | 68.6 |  | 68.6 | 75.0347 | 0.1 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 63.8629 | 16.0423 | 381806.8029 | 31.8172 | 31.8172 | 89.9662 | 0.2 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 65.1042 | 17.2836 | 411349.8057 | 34.2792 | 34.2792 | 90.7272 | 0.3 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 66.3455 | 18.5249 | 440892.8086 | 36.7411 | 36.7411 | 91.4881 | 0.4 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 67.5868 | 19.7662 | 470435.8115 | 39.203 | 39.203 | 92.249 | 0.5 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 68.8281 | 21.0075 | 499978.8143 | 41.6649 | 41.6649 | 93.0099 | 0.6 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 70.0694 | 22.2488 | 529521.8172 | 44.1268 | 44.1268 | 93.7708 | 0.7 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 71.3108 | 23.4901 | 559064.8201 | 46.5887 | 46.5887 | 94.5317 | 0.8 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 72.5521 | 24.7314 | 588607.8229 | 49.0507 | 49.0507 | 95.2927 | 0.9 | 69.14 | 14.14 | 534492 | 44.541 | 44.541 | 73.7934 | 25.9727 | 618150.8258 | 51.5126 | 51.5126 | 96.0536 | 1 | 68.6 | 13.6 | 514080 | 42.84 | 42.84 | 75.0347 | 27.214 | 647693.8287 | 53.9745 | 53.9745 | 96.8145 | 70 | 70 | 28.1753 | 28 | 71.9
6/26/20XX 7:00:00 AM | 0.29167 | 2 | 70.2 | 69.6 | 66.0589 | 77.2604 | 11.2015 | 60 | 70.2 |  | 70.2 | 76.8124 | 0.1 | 73.62 | 18.62 | 703836 | 58.653 | 58.653 | 64.0407 | 16.2201 | 386037.7241 | 32.1698 | 32.1698 | 90.8228 | 0.2 | 73.24 | 18.24 | 689472 | 57.456 | 57.456 | 65.4598 | 17.6391 | 419811.6482 | 34.9843 | 34.9843 | 92.4403 | 0.3 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 66.8788 | 19.0582 | 453585.5723 | 37.7988 | 37.7988 | 94.0578 | 0.4 | 72.48 | 17.48 | 660744 | 55.062 | 55.062 | 68.2979 | 20.4773 | 487359.4965 | 40.6133 | 40.6133 | 95.6753 | 0.5 | 72.1 | 17.1 | 646380 | 53.865 | 53.865 | 69.717 | 21.8964 | 521133.4206 | 43.4278 | 43.4278 | 97.2928 | 0.6 | 71.72 | 16.72 | 632016 | 52.668 | 52.668 | 71.1361 | 23.3154 | 554907.3447 | 46.2423 | 46.2423 | 98.9103 | 0.7 | 71.34 | 16.34 | 617652 | 51.471 | 51.471 | 72.5551 | 24.7345 | 588681.2688 | 49.0568 | 49.0568 | 100.5278 | 0.8 | 70.96 | 15.96 | 603288 | 50.274 | 50.274 | 73.9742 | 26.1536 | 622455.1929 | 51.8713 | 51.8713 | 102.1453 | 0.9 | 70.58 | 15.58 | 588924 | 49.077 | 49.077 | 75.3933 | 27.5727 | 656229.117 | 54.6858 | 54.6858 | 103.7628 | 1 | 70.2 | 15.2 | 574560 | 47.88 | 47.88 | 76.8124 | 28.9917 | 690003.0412 | 57.5003 | 57.5003 | 105.3803 | 70 | 70 | 28.8446 | 28 | 69.6
6/26/20XX 8:00:00 AM | 0.33333 | 2 | 71.5 | 65.5 | 69.1333 | 80.8687 | 11.7354 | 60 | 71.5 |  | 71.5 | 75.5878 | 0.1 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 63.9182 | 16.0976 | 383123.2498 | 31.9269 | 31.9269 | 90.9894 | 0.2 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 65.2149 | 17.3942 | 413982.6997 | 34.4986 | 34.4986 | 92.7736 | 0.3 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 66.5115 | 18.6908 | 444842.1495 | 37.0702 | 37.0702 | 94.5577 | 0.4 | 73 | 18 | 680400 | 56.7 | 56.7 | 67.8081 | 19.9875 | 475701.5994 | 39.6418 | 39.6418 | 96.3418 | 0.5 | 72.75 | 17.75 | 670950 | 55.9125 | 55.9125 | 69.1047 | 21.2841 | 506561.0492 | 42.2134 | 42.2134 | 98.1259 | 0.6 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 70.4013 | 22.5807 | 537420.4991 | 44.785 | 44.785 | 99.91 | 0.7 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 71.6979 | 23.8773 | 568279.9489 | 47.3567 | 47.3567 | 101.6942 | 0.8 | 72 | 17 | 642600 | 53.55 | 53.55 | 72.9946 | 25.1739 | 599139.3988 | 49.9283 | 49.9283 | 103.4783 | 0.9 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 74.2912 | 26.4705 | 629998.8486 | 52.4999 | 52.4999 | 105.2624 | 1 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 75.5878 | 27.7672 | 660858.2985 | 55.0715 | 55.0715 | 107.0465 | 70 | 65 | 28.9716 | 28 | 65.5
6/26/20XX 9:00:00 AM | 0.375 | 2 | 73.3 | 61.6 | 73.5946 | 86.1051 | 12.5105 | 60 | 73.3 |  | 73.3 | 75.5962 | 0.1 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 63.9191 | 16.0985 | 383143.3671 | 31.9286 | 31.9286 | 91.5581 | 0.2 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 65.2166 | 17.3959 | 414022.9341 | 34.5019 | 34.5019 | 93.9109 | 0.3 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 66.514 | 18.6934 | 444902.5012 | 37.0752 | 37.0752 | 96.2637 | 0.4 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 67.8115 | 19.9908 | 475782.0683 | 39.6485 | 39.6485 | 98.6165 | 0.5 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 69.1089 | 21.2883 | 506661.6353 | 42.2218 | 42.2218 | 100.9693 | 0.6 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 70.4064 | 22.5858 | 537541.2024 | 44.7951 | 44.7951 | 103.3221 | 0.7 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 71.7039 | 23.8832 | 568420.7695 | 47.3684 | 47.3684 | 105.6749 | 0.8 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 73.0013 | 25.1807 | 599300.3365 | 49.9417 | 49.9417 | 108.0277 | 0.9 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 74.2988 | 26.4781 | 630179.9036 | 52.515 | 52.515 | 110.3805 | 1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 75.5962 | 27.7756 | 661059.4707 | 55.0883 | 55.0883 | 112.7333 | 75 | 60 | 29.4135 | 30 | 61.6
6/26/20XX 10:00:00 AM | 0.41667 | 2 | 75.2 | 57.8 | 65.252 | 78.5695 | 13.3175 | 50 | 75.2 |  | 75.2 | 75.6396 | 0.1 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 63.9234 | 16.1028 | 383246.6784 | 31.9372 | 31.9372 | 92.1652 | 0.2 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 65.2252 | 17.4046 | 414229.5567 | 34.5191 | 34.5191 | 95.1251 | 0.3 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 66.527 | 18.7064 | 445212.4351 | 37.101 | 37.101 | 98.085 | 0.4 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 67.8288 | 20.0082 | 476195.3135 | 39.6829 | 39.6829 | 101.0449 | 0.5 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 69.1306 | 21.31 | 507178.1919 | 42.2648 | 42.2648 | 104.0048 | 0.6 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 70.4324 | 22.6118 | 538161.0702 | 44.8468 | 44.8468 | 106.9648 | 0.7 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 71.7342 | 23.9136 | 569143.9486 | 47.4287 | 47.4287 | 109.9247 | 0.8 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 73.036 | 25.2154 | 600126.827 | 50.0106 | 50.0106 | 112.8846 | 0.9 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 74.3378 | 26.5172 | 631109.7054 | 52.5925 | 52.5925 | 115.8445 | 1 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 75.6396 | 27.819 | 662092.5837 | 55.1744 | 55.1744 | 118.8044 | 75 | 60 | 29.8854 | 30 | 57.8
6/26/20XX 11:00:00 AM | 0.45833 | 2 | 77.6 | 53 | 70.7937 | 85.2591 | 14.4654 | 50 | 77.6 |  | 77.6 | 75.1333 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 63.8728 | 16.0522 | 382041.6397 | 31.8368 | 31.8368 | 92.8208 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 65.124 | 17.3033 | 411819.4795 | 34.3183 | 34.3183 | 96.4363 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 66.3751 | 18.5545 | 441597.3192 | 36.7998 | 36.7998 | 100.0518 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 67.6263 | 19.8057 | 471375.159 | 39.2813 | 39.2813 | 103.6673 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 68.8775 | 21.0568 | 501152.9987 | 41.7627 | 41.7627 | 107.2827 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 70.1287 | 22.308 | 530930.8384 | 44.2442 | 44.2442 | 110.8982 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 71.3798 | 23.5592 | 560708.6782 | 46.7257 | 46.7257 | 114.5137 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 72.631 | 24.8104 | 590486.5179 | 49.2072 | 49.2072 | 118.1292 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 73.8822 | 26.0615 | 620264.3577 | 51.6887 | 51.6887 | 121.7447 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 75.1333 | 27.3127 | 650042.1974 | 54.1702 | 54.1702 | 125.3602 | 80 | 55 | 30.3936 | 30 | 53
6/26/20XX 12:00:00 PM | 0.5 | 2 | 79 | 51.6 | 74.2046 | 89.3778 | 15.1731 | 50 | 79 |  | 79 | 76.6323 | 0.1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 64.0227 | 16.2021 | 385609.2745 | 32.1341 | 32.1341 | 93.5591 | 0.2 | 75 | 20 | 756000 | 63 | 63 | 65.4238 | 17.6031 | 418954.749 | 34.9129 | 34.9129 | 97.9129 | 0.3 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 66.8248 | 19.0042 | 452300.2236 | 37.6917 | 37.6917 | 102.2667 | 0.4 | 76 | 21 | 793800 | 66.15 | 66.15 | 68.2259 | 20.4053 | 485645.6981 | 40.4705 | 40.4705 | 106.6205 | 0.5 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 69.627 | 21.8064 | 518991.1726 | 43.2493 | 43.2493 | 110.9743 | 0.6 | 77 | 22 | 831600 | 69.3 | 69.3 | 71.0281 | 23.2074 | 552336.6471 | 46.0281 | 46.0281 | 115.3281 | 0.7 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 72.4291 | 24.6085 | 585682.1216 | 48.8068 | 48.8068 | 119.6818 | 0.8 | 78 | 23 | 869400 | 72.45 | 72.45 | 73.8302 | 26.0096 | 619027.5962 | 51.5856 | 51.5856 | 124.0356 | 0.9 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 75.2313 | 27.4106 | 652373.0707 | 54.3644 | 54.3644 | 128.3894 | 1 | 79 | 24 | 907200 | 75.6 | 75.6 | 76.6323 | 28.8117 | 685718.5452 | 57.1432 | 57.1432 | 132.7432 | 80 | 50 | 30.9713 | 30 | 51.6
6/26/20XX 1:00:00 PM | 0.54167 | 2 | 78.9 | 50.1 | 73.9565 | 89.0782 | 15.1216 | 50 | 78.9 |  | 78.9 | 74.1078 | 0.1 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 63.7702 | 15.9496 | 379600.7943 | 31.6334 | 31.6334 | 93.0269 | 0.2 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 64.9189 | 17.0982 | 406937.7887 | 33.9115 | 33.9115 | 96.8485 | 0.3 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 66.0675 | 18.2468 | 434274.783 | 36.1896 | 36.1896 | 100.6701 | 0.4 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 67.2161 | 19.3955 | 461611.7773 | 38.4676 | 38.4676 | 104.4916 | 0.5 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 68.3647 | 20.5441 | 488948.7717 | 40.7457 | 40.7457 | 108.3132 | 0.6 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 69.5133 | 21.6927 | 516285.766 | 43.0238 | 43.0238 | 112.1348 | 0.7 | 77.43 | 22.43 | 847854 | 70.6545 | 70.6545 | 70.6619 | 22.8413 | 543622.7603 | 45.3019 | 45.3019 | 115.9564 | 0.8 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 71.8105 | 23.9899 | 570959.7547 | 47.58 | 47.58 | 119.778 | 0.9 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 72.9592 | 25.1385 | 598296.749 | 49.8581 | 49.8581 | 123.5996 | 1 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 74.1078 | 26.2871 | 625633.7433 | 52.1361 | 52.1361 | 127.4211 | 80 | 50 | 30.5511 | 30 | 50.1
6/26/20XX 2:00:00 PM | 0.58333 | 2 | 79.3 | 50.1 | 74.9531 | 90.2816 | 15.3285 | 50 | 79.3 |  | 79.3 | 75.1063 | 0.1 | 74.53 | 19.53 | 738234 | 61.5195 | 61.5195 | 63.8701 | 16.0495 | 381977.405 | 31.8315 | 31.8315 | 93.351 | 0.2 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 65.1186 | 17.2979 | 411691.0101 | 34.3076 | 34.3076 | 97.4966 | 0.3 | 75.59 | 20.59 | 778302 | 64.8585 | 64.8585 | 66.367 | 18.5464 | 441404.6151 | 36.7837 | 36.7837 | 101.6422 | 0.4 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 67.6155 | 19.7949 | 471118.2202 | 39.2599 | 39.2599 | 105.7879 | 0.5 | 76.65 | 21.65 | 818370 | 68.1975 | 68.1975 | 68.864 | 21.0434 | 500831.8252 | 41.736 | 41.736 | 109.9335 | 0.6 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 70.1125 | 22.2918 | 530545.4302 | 44.2121 | 44.2121 | 114.0791 | 0.7 | 77.71 | 22.71 | 858438 | 71.5365 | 71.5365 | 71.3609 | 23.5403 | 560259.0353 | 46.6883 | 46.6883 | 118.2248 | 0.8 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 72.6094 | 24.7888 | 589972.6403 | 49.1644 | 49.1644 | 122.3704 | 0.9 | 78.77 | 23.77 | 898506 | 74.8755 | 74.8755 | 73.8579 | 26.0372 | 619686.2454 | 51.6405 | 51.6405 | 126.516 | 1 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 75.1063 | 27.2857 | 649399.8504 | 54.1167 | 54.1167 | 130.6617 | 80 | 50 | 30.8055 | 30 | 50.1
6/26/20XX 3:00:00 PM | 0.625 | 2 | 79.2 | 50.7 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 75.7722 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 63.9367 | 16.1161 | 383562.2677 | 31.9635 | 31.9635 | 93.4515 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 65.2518 | 17.4311 | 414860.7354 | 34.5717 | 34.5717 | 97.6977 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 66.5668 | 18.7462 | 446159.2031 | 37.1799 | 37.1799 | 101.9439 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 67.8819 | 20.0612 | 477457.6708 | 39.7881 | 39.7881 | 106.1901 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 69.1969 | 21.3763 | 508756.1385 | 42.3963 | 42.3963 | 110.4363 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 70.512 | 22.6914 | 540054.6062 | 45.0046 | 45.0046 | 114.6826 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 71.8271 | 24.0064 | 571353.0739 | 47.6128 | 47.6128 | 118.9288 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 73.1421 | 25.3215 | 602651.5416 | 50.221 | 50.221 | 123.175 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 74.4572 | 26.6366 | 633950.0093 | 52.8292 | 52.8292 | 127.4212 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 75.7722 | 27.9516 | 665248.477 | 55.4374 | 55.4374 | 131.6674 | 80 | 50 | 30.8854 | 30 | 50.7
6/26/20XX 4:00:00 PM | 0.66667 | 2 | 78.1 | 51.1 | 71.9966 | 86.7115 | 14.7149 | 50 | 78.1 |  | 78.1 | 73.6152 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 63.721 | 15.9004 | 378428.4764 | 31.5357 | 31.5357 | 92.6772 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 64.8203 | 16.9997 | 404593.1528 | 33.7161 | 33.7161 | 96.1491 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 65.9197 | 18.0991 | 430757.8292 | 35.8965 | 35.8965 | 99.621 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 67.0191 | 19.1984 | 456922.5056 | 38.0769 | 38.0769 | 103.0929 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 68.1184 | 20.2978 | 483087.182 | 40.2573 | 40.2573 | 106.5648 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 69.2178 | 21.3971 | 509251.8584 | 42.4377 | 42.4377 | 110.0367 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 70.3171 | 22.4965 | 535416.5348 | 44.618 | 44.618 | 113.5085 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 71.4165 | 23.5958 | 561581.2112 | 46.7984 | 46.7984 | 116.9804 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 72.5158 | 24.6952 | 587745.8876 | 48.9788 | 48.9788 | 120.4523 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 73.6152 | 25.7946 | 613910.564 | 51.1592 | 51.1592 | 123.9242 | 80 | 50 | 30.2782 | 30 | 51.1
6/26/20XX 5:00:00 PM | 0.70833 | 2 | 78.1 | 51.3 | 71.9966 | 86.7115 | 14.7149 | 50 | 78.1 |  | 78.1 | 73.9095 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 63.7504 | 15.9298 | 379128.9058 | 31.5941 | 31.5941 | 92.7356 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 64.8792 | 17.0586 | 405994.0116 | 33.8328 | 33.8328 | 96.2658 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 66.008 | 18.1874 | 432859.1173 | 36.0716 | 36.0716 | 99.7961 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 67.1368 | 19.3161 | 459724.2231 | 38.3104 | 38.3104 | 103.3264 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 68.2656 | 20.4449 | 486589.3289 | 40.5491 | 40.5491 | 106.8566 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 69.3943 | 21.5737 | 513454.4347 | 42.7879 | 42.7879 | 110.3869 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 70.5231 | 22.7025 | 540319.5405 | 45.0266 | 45.0266 | 113.9171 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 71.6519 | 23.8313 | 567184.6463 | 47.2654 | 47.2654 | 117.4474 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 72.7807 | 24.9601 | 594049.752 | 49.5041 | 49.5041 | 120.9776 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 73.9095 | 26.0889 | 620914.8578 | 51.7429 | 51.7429 | 124.5079 | 80 | 50 | 30.3243 | 30 | 51.3
6/26/20XX 6:00:00 PM | 0.75 | 2 | 75.3 | 57.1 | 65.4753 | 78.8391 | 13.3637 | 50 | 75.3 |  | 75.3 | 74.9636 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 63.8558 | 16.0352 | 381637.6943 | 31.8031 | 31.8031 | 92.0626 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 65.09 | 17.2694 | 411011.5887 | 34.251 | 34.251 | 94.92 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 66.3242 | 18.5036 | 440385.483 | 36.6988 | 36.6988 | 97.7773 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 67.5584 | 19.7378 | 469759.3774 | 39.1466 | 39.1466 | 100.6346 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 68.7926 | 20.972 | 499133.2717 | 41.5944 | 41.5944 | 103.4919 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 70.0268 | 22.2062 | 528507.1661 | 44.0423 | 44.0423 | 106.3493 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 71.261 | 23.4404 | 557881.0604 | 46.4901 | 46.4901 | 109.2066 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 72.4952 | 24.6746 | 587254.9547 | 48.9379 | 48.9379 | 112.0639 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 73.7294 | 25.9088 | 616628.8491 | 51.3857 | 51.3857 | 114.9212 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 74.9636 | 27.143 | 646002.7434 | 53.8336 | 53.8336 | 117.7786 | 75 | 55 | 29.8041 | 30 | 57.1
6/26/20XX 7:00:00 PM | 0.79167 | 2 | 74.5 | 59.5 | 63.7064 | 76.7042 | 12.9978 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/26/20XX 8:00:00 PM | 0.83333 | 2 | 73.5 | 59.6 | 61.5526 | 74.1052 | 12.5526 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/26/20XX 9:00:00 PM | 0.875 | 2 | 73.4 | 59.8 | 61.3407 | 73.8495 | 12.5088 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/26/20XX 10:00:00 PM | 0.91667 | 2 | 72.7 | 59 | 59.8747 | 72.0807 | 12.206 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/26/20XX 11:00:00 PM | 0.95833 | 2 | 71.2 | 63.9 | 68.413 | 80.0233 | 11.6102 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/26/20XX 12:00:00 AM | 0 | 3 | 70.6 | 66.3 | 66.992 | 78.3554 | 11.3635 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/27/20XX 1:00:00 AM | 0.041667 | 3 | 70 | 68.2 | 65.5967 | 76.7179 | 11.1212 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/27/20XX 2:00:00 AM | 0.083333 | 3 | 68.9 | 69.3 | 63.1047 | 73.7935 | 10.6888 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/27/20XX 3:00:00 AM | 0.125 | 3 | 68.5 | 69.7 | 62.2194 | 72.7546 | 10.5352 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/27/20XX 4:00:00 AM | 0.16667 | 3 | 67.6 | 75.5 | 70.4642 | 80.7252 | 10.261 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/27/20XX 5:00:00 AM | 0.20833 | 3 | 67.3 | 77 | 69.7151 | 79.8649 | 10.1498 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/27/20XX 6:00:00 AM | 0.25 | 3 | 68.1 | 77.1 | 71.7287 | 82.1774 | 10.4487 | 70 | 68.1 |  | 68.1 | 79.1473 | 0.1 | 73.41 | 18.41 | 695898 | 57.9915 | 57.9915 | 64.2742 | 16.4536 | 391594.8001 | 32.6329 | 32.6329 | 90.6244 | 0.2 | 72.82 | 17.82 | 673596 | 56.133 | 56.133 | 65.9268 | 18.1061 | 430925.8002 | 35.9105 | 35.9105 | 92.0435 | 0.3 | 72.23 | 17.23 | 651294 | 54.2745 | 54.2745 | 67.5793 | 19.7587 | 470256.8004 | 39.1881 | 39.1881 | 93.4626 | 0.4 | 71.64 | 16.64 | 628992 | 52.416 | 52.416 | 69.2319 | 21.4113 | 509587.8005 | 42.4657 | 42.4657 | 94.8817 | 0.5 | 71.05 | 16.05 | 606690 | 50.5575 | 50.5575 | 70.8844 | 23.0638 | 548918.8006 | 45.7432 | 45.7432 | 96.3007 | 0.6 | 70.46 | 15.46 | 584388 | 48.699 | 48.699 | 72.537 | 24.7164 | 588249.8007 | 49.0208 | 49.0208 | 97.7198 | 0.7 | 69.87 | 14.87 | 562086 | 46.8405 | 46.8405 | 74.1896 | 26.3689 | 627580.8009 | 52.2984 | 52.2984 | 99.1389 | 0.8 | 69.28 | 14.28 | 539784 | 44.982 | 44.982 | 75.8421 | 28.0215 | 666911.801 | 55.576 | 55.576 | 100.558 | 0.9 | 68.69 | 13.69 | 517482 | 43.1235 | 43.1235 | 77.4947 | 29.6741 | 706242.8011 | 58.8536 | 58.8536 | 101.9771 | 1 | 68.1 | 13.1 | 495180 | 41.265 | 41.265 | 79.1473 | 31.3266 | 745573.8012 | 62.1312 | 62.1312 | 103.3962 | 70 | 75 | 28.6947 | 28 | 77.1
6/27/20XX 7:00:00 AM | 0.29167 | 3 | 69.7 | 73.4 | 75.9105 | 86.9813 | 11.0709 | 70 | 69.7 |  | 69.7 | 79.6746 | 0.1 | 73.57 | 18.57 | 701946 | 58.4955 | 58.4955 | 64.3269 | 16.5063 | 392849.7607 | 32.7375 | 32.7375 | 91.233 | 0.2 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 66.0322 | 18.2116 | 433435.7215 | 36.1196 | 36.1196 | 93.2606 | 0.3 | 72.71 | 17.71 | 669438 | 55.7865 | 55.7865 | 67.7375 | 19.9169 | 474021.6822 | 39.5018 | 39.5018 | 95.2883 | 0.4 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 69.4428 | 21.6222 | 514607.6429 | 42.884 | 42.884 | 97.316 | 0.5 | 71.85 | 16.85 | 636930 | 53.0775 | 53.0775 | 71.1481 | 23.3275 | 555193.6037 | 46.2661 | 46.2661 | 99.3436 | 0.6 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 72.8534 | 25.0328 | 595779.5644 | 49.6483 | 49.6483 | 101.3713 | 0.7 | 70.99 | 15.99 | 604422 | 50.3685 | 50.3685 | 74.5587 | 26.738 | 636365.5251 | 53.0305 | 53.0305 | 103.399 | 0.8 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 76.264 | 28.4433 | 676951.4859 | 56.4126 | 56.4126 | 105.4266 | 0.9 | 70.13 | 15.13 | 571914 | 47.6595 | 47.6595 | 77.9693 | 30.1486 | 717537.4466 | 59.7948 | 59.7948 | 107.4543 | 1 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 79.6746 | 31.8539 | 758123.4073 | 63.177 | 63.177 | 109.482 | 70 | 75 | 29.1691 | 30 | 73.4
6/27/20XX 8:00:00 AM | 0.33333 | 3 | 71.3 | 70.9 | 80.3042 | 92.0306 | 11.7264 | 70 | 71.3 |  | 71.3 | 81.3596 | 0.1 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 64.4954 | 16.6748 | 396860.1693 | 33.0717 | 33.0717 | 92.0712 | 0.2 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 66.3692 | 18.5486 | 441456.5385 | 36.788 | 36.788 | 94.937 | 0.3 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 68.243 | 20.4224 | 486052.9078 | 40.5044 | 40.5044 | 97.8029 | 0.4 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 70.1168 | 22.2962 | 530649.2771 | 44.2208 | 44.2208 | 100.6688 | 0.5 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 71.9906 | 24.17 | 575245.6464 | 47.9371 | 47.9371 | 103.5346 | 0.6 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 73.8644 | 26.0438 | 619842.0156 | 51.6535 | 51.6535 | 106.4005 | 0.7 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 75.7382 | 27.9176 | 664438.3849 | 55.3699 | 55.3699 | 109.2664 | 0.8 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 77.612 | 29.7914 | 709034.7542 | 59.0862 | 59.0862 | 112.1322 | 0.9 | 71.57 | 16.57 | 626346 | 52.1955 | 52.1955 | 79.4858 | 31.6652 | 753631.1235 | 62.8026 | 62.8026 | 114.9981 | 1 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 81.3596 | 33.539 | 798227.4927 | 66.519 | 66.519 | 117.864 | 70 | 70 | 29.8244 | 30 | 70.9
6/27/20XX 9:00:00 AM | 0.375 | 3 | 73.2 | 65.7 | 73.3404 | 85.8067 | 12.4664 | 60 | 73.2 |  | 73.2 | 80.4462 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 64.4041 | 16.5835 | 394686.2396 | 32.8905 | 32.8905 | 92.4885 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 66.1865 | 18.3659 | 437108.6791 | 36.4257 | 36.4257 | 95.7717 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 67.969 | 20.1484 | 479531.1187 | 39.9609 | 39.9609 | 99.0549 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 69.7515 | 21.9308 | 521953.5583 | 43.4961 | 43.4961 | 102.3381 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 71.5339 | 23.7133 | 564375.9978 | 47.0313 | 47.0313 | 105.6213 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 73.3164 | 25.4957 | 606798.4374 | 50.5665 | 50.5665 | 108.9045 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 75.0988 | 27.2782 | 649220.877 | 54.1017 | 54.1017 | 112.1877 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 76.8813 | 29.0606 | 691643.3166 | 57.6369 | 57.6369 | 115.4709 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 78.6637 | 30.8431 | 734065.7561 | 61.1721 | 61.1721 | 118.7541 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 80.4462 | 32.6256 | 776488.1957 | 64.7073 | 64.7073 | 122.0373 | 75 | 65 | 30.1474 | 30 | 65.7
6/27/20XX 10:00:00 AM | 0.41667 | 3 | 74.4 | 61.4 | 76.4409 | 89.4463 | 13.0054 | 60 | 74.4 |  | 74.4 | 78.2616 | 0.1 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 64.1856 | 16.365 | 389487.0325 | 32.4573 | 32.4573 | 92.4333 | 0.2 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 65.7496 | 17.929 | 426710.265 | 35.5592 | 35.5592 | 95.6612 | 0.3 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 67.3136 | 19.493 | 463933.4975 | 38.6611 | 38.6611 | 98.8891 | 0.4 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 68.8776 | 21.057 | 501156.73 | 41.7631 | 41.7631 | 102.1171 | 0.5 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 70.4416 | 22.621 | 538379.9626 | 44.865 | 44.865 | 105.345 | 0.6 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 72.0056 | 24.185 | 575603.1951 | 47.9669 | 47.9669 | 108.5729 | 0.7 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 73.5696 | 25.749 | 612826.4276 | 51.0689 | 51.0689 | 111.8009 | 0.8 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 75.1336 | 27.313 | 650049.6601 | 54.1708 | 54.1708 | 115.0288 | 0.9 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 76.6976 | 28.877 | 687272.8926 | 57.2727 | 57.2727 | 118.2567 | 1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 78.2616 | 30.441 | 724496.1251 | 60.3747 | 60.3747 | 121.4847 | 75 | 60 | 30.0998 | 30 | 61.4
6/27/20XX 11:00:00 AM | 0.45833 | 3 | 76.8 | 57.7 | 68.9041 | 82.9779 | 14.0738 | 50 | 76.8 |  | 76.8 | 79.7409 | 0.1 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 64.3336 | 16.5129 | 393007.7076 | 32.7506 | 32.7506 | 93.4826 | 0.2 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 66.0455 | 18.2249 | 433751.6152 | 36.146 | 36.146 | 97.76 | 0.3 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 67.7574 | 19.9368 | 474495.5229 | 39.5413 | 39.5413 | 102.0373 | 0.4 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 69.4693 | 21.6487 | 515239.4305 | 42.9366 | 42.9366 | 106.3146 | 0.5 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 71.1813 | 23.3606 | 555983.3381 | 46.3319 | 46.3319 | 110.5919 | 0.6 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 72.8932 | 25.0726 | 596727.2457 | 49.7273 | 49.7273 | 114.8693 | 0.7 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 74.6051 | 26.7845 | 637471.1534 | 53.1226 | 53.1226 | 119.1466 | 0.8 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 76.3171 | 28.4964 | 678215.061 | 56.5179 | 56.5179 | 123.4239 | 0.9 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 78.029 | 30.2084 | 718958.9686 | 59.9132 | 59.9132 | 127.7012 | 1 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 79.7409 | 31.9203 | 759702.8762 | 63.3086 | 63.3086 | 131.9786 | 75 | 60 | 30.9194 | 30 | 57.7
6/27/20XX 12:00:00 PM | 0.5 | 3 | 78.6 | 54.5 | 73.2164 | 88.1844 | 14.968 | 50 | 78.6 |  | 78.6 | 79.952 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 64.3547 | 16.534 | 393510.1025 | 32.7925 | 32.7925 | 94.0915 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 66.0877 | 18.2671 | 434756.405 | 36.2297 | 36.2297 | 98.9777 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 67.8207 | 20.0001 | 476002.7075 | 39.6669 | 39.6669 | 103.8639 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 69.5538 | 21.7332 | 517249.01 | 43.1041 | 43.1041 | 108.7501 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 71.2868 | 23.4662 | 558495.3125 | 46.5413 | 46.5413 | 113.6363 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 73.0199 | 25.1992 | 599741.6149 | 49.9785 | 49.9785 | 118.5225 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 74.7529 | 26.9323 | 640987.9174 | 53.4157 | 53.4157 | 123.4087 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 76.4859 | 28.6653 | 682234.2199 | 56.8529 | 56.8529 | 128.2949 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 78.219 | 30.3983 | 723480.5224 | 60.29 | 60.29 | 133.181 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 79.952 | 32.1314 | 764726.8249 | 63.7272 | 63.7272 | 138.0672 | 80 | 55 | 31.3936 | 32 | 54.5
6/27/20XX 1:00:00 PM | 0.54167 | 3 | 78.9 | 53.6 | 73.9565 | 89.0782 | 15.1216 | 50 | 78.9 |  | 78.9 | 79.4003 | 0.1 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 64.2995 | 16.4789 | 392197.0986 | 32.6831 | 32.6831 | 94.0766 | 0.2 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 65.9774 | 18.1567 | 432130.3973 | 36.0109 | 36.0109 | 98.9479 | 0.3 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 67.6552 | 19.8346 | 472063.6959 | 39.3386 | 39.3386 | 103.8191 | 0.4 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 69.3331 | 21.5125 | 511996.9945 | 42.6664 | 42.6664 | 108.6904 | 0.5 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 71.011 | 23.1903 | 551930.2932 | 45.9942 | 45.9942 | 113.5617 | 0.6 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 72.6889 | 24.8682 | 591863.5918 | 49.322 | 49.322 | 118.433 | 0.7 | 77.43 | 22.43 | 847854 | 70.6545 | 70.6545 | 74.3667 | 26.5461 | 631796.8904 | 52.6497 | 52.6497 | 123.3042 | 0.8 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 76.0446 | 28.224 | 671730.1891 | 55.9775 | 55.9775 | 128.1755 | 0.9 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 77.7225 | 29.9018 | 711663.4877 | 59.3053 | 59.3053 | 133.0468 | 1 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 79.4003 | 31.5797 | 751596.7863 | 62.6331 | 62.6331 | 137.9181 | 80 | 55 | 31.3806 | 32 | 53.6
6/27/20XX 2:00:00 PM | 0.58333 | 3 | 78.6 | 54.5 | 73.2164 | 88.1844 | 14.968 | 50 | 78.6 |  | 78.6 | 79.952 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 64.3547 | 16.534 | 393510.1025 | 32.7925 | 32.7925 | 94.0915 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 66.0877 | 18.2671 | 434756.405 | 36.2297 | 36.2297 | 98.9777 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 67.8207 | 20.0001 | 476002.7075 | 39.6669 | 39.6669 | 103.8639 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 69.5538 | 21.7332 | 517249.01 | 43.1041 | 43.1041 | 108.7501 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 71.2868 | 23.4662 | 558495.3125 | 46.5413 | 46.5413 | 113.6363 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 73.0199 | 25.1992 | 599741.6149 | 49.9785 | 49.9785 | 118.5225 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 74.7529 | 26.9323 | 640987.9174 | 53.4157 | 53.4157 | 123.4087 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 76.4859 | 28.6653 | 682234.2199 | 56.8529 | 56.8529 | 128.2949 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 78.219 | 30.3983 | 723480.5224 | 60.29 | 60.29 | 133.181 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 79.952 | 32.1314 | 764726.8249 | 63.7272 | 63.7272 | 138.0672 | 80 | 55 | 31.3936 | 32 | 54.5
6/27/20XX 3:00:00 PM | 0.625 | 3 | 77.7 | 55.9 | 71.0329 | 85.548 | 14.515 | 50 | 77.7 |  | 77.7 | 79.5968 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 64.3191 | 16.4985 | 392664.6784 | 32.7221 | 32.7221 | 93.7376 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 66.0167 | 18.196 | 433065.5567 | 36.0888 | 36.0888 | 98.2698 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 67.7142 | 19.8935 | 473466.4351 | 39.4555 | 39.4555 | 102.802 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 69.4117 | 21.5911 | 513867.3135 | 42.8223 | 42.8223 | 107.3343 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 71.1092 | 23.2886 | 554268.1918 | 46.189 | 46.189 | 111.8665 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 72.8067 | 24.9861 | 594669.0702 | 49.5558 | 49.5558 | 116.3988 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 74.5042 | 26.6836 | 635069.9485 | 52.9225 | 52.9225 | 120.931 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 76.2018 | 28.3811 | 675470.8269 | 56.2892 | 56.2892 | 125.4632 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 77.8993 | 30.0786 | 715871.7053 | 59.656 | 59.656 | 129.9955 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 79.5968 | 31.7762 | 756272.5836 | 63.0227 | 63.0227 | 134.5277 | 80 | 55 | 31.1173 | 32 | 55.9
6/27/20XX 4:00:00 PM | 0.66667 | 3 | 77.2 | 57.7 | 69.8436 | 84.112 | 14.2685 | 50 | 77.2 |  | 77.2 | 80.8303 | 0.1 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 64.4425 | 16.6219 | 395600.3526 | 32.9667 | 32.9667 | 93.8247 | 0.2 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 66.2634 | 18.4427 | 438936.9052 | 36.5781 | 36.5781 | 98.4441 | 0.3 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 68.0842 | 20.2636 | 482273.4577 | 40.1895 | 40.1895 | 103.0635 | 0.4 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 69.9051 | 22.0845 | 525610.0103 | 43.8008 | 43.8008 | 107.6828 | 0.5 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 71.726 | 23.9053 | 568946.5629 | 47.4122 | 47.4122 | 112.3022 | 0.6 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 73.5468 | 25.7262 | 612283.1155 | 51.0236 | 51.0236 | 116.9216 | 0.7 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 75.3677 | 27.547 | 655619.6681 | 54.635 | 54.635 | 121.541 | 0.8 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 77.1885 | 29.3679 | 698956.2206 | 58.2464 | 58.2464 | 126.1604 | 0.9 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 79.0094 | 31.1888 | 742292.7732 | 61.8577 | 61.8577 | 130.7797 | 1 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 80.8303 | 33.0096 | 785629.3258 | 65.4691 | 65.4691 | 135.3991 | 75 | 60 | 31.188 | 32 | 57.7
6/27/20XX 5:00:00 PM | 0.70833 | 3 | 76 | 58.8 | 67.0571 | 80.7483 | 13.6912 | 50 | 76 |  | 76 | 79.1053 | 0.1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 64.27 | 16.4494 | 391494.9658 | 32.6246 | 32.6246 | 93.1046 | 0.2 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 65.9184 | 18.0977 | 430726.1317 | 35.8938 | 35.8938 | 97.0038 | 0.3 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 67.5667 | 19.7461 | 469957.2975 | 39.1631 | 39.1631 | 100.9031 | 0.4 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 69.2151 | 21.3945 | 509188.4634 | 42.4324 | 42.4324 | 104.8024 | 0.5 | 75 | 20 | 756000 | 63 | 63 | 70.8635 | 23.0428 | 548419.6292 | 45.7016 | 45.7016 | 108.7016 | 0.6 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 72.5118 | 24.6912 | 587650.7951 | 48.9709 | 48.9709 | 112.6009 | 0.7 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 74.1602 | 26.3396 | 626881.9609 | 52.2402 | 52.2402 | 116.5002 | 0.8 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 75.8086 | 27.9879 | 666113.1268 | 55.5094 | 55.5094 | 120.3994 | 0.9 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 77.4569 | 29.6363 | 705344.2926 | 58.7787 | 58.7787 | 124.2987 | 1 | 76 | 21 | 793800 | 66.15 | 66.15 | 79.1053 | 31.2847 | 744575.4584 | 62.048 | 62.048 | 128.198 | 75 | 60 | 30.6238 | 30 | 58.8
6/27/20XX 6:00:00 PM | 0.75 | 3 | 74.6 | 62.4 | 76.9684 | 90.0655 | 13.0971 | 60 | 74.6 |  | 74.6 | 80.1117 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 64.3706 | 16.55 | 393890.1517 | 32.8242 | 32.8242 | 92.8632 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 66.1196 | 18.299 | 435516.5035 | 36.293 | 36.293 | 96.521 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 67.8687 | 20.048 | 477142.8552 | 39.7619 | 39.7619 | 100.1789 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 69.6177 | 21.797 | 518769.207 | 43.2308 | 43.2308 | 103.8368 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 71.3667 | 23.546 | 560395.5587 | 46.6996 | 46.6996 | 107.4946 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 73.1157 | 25.295 | 602021.9104 | 50.1685 | 50.1685 | 111.1525 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 74.8647 | 27.044 | 643648.2622 | 53.6374 | 53.6374 | 114.8104 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 76.6137 | 28.7931 | 685274.6139 | 57.1062 | 57.1062 | 118.4682 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 78.3627 | 30.5421 | 726900.9656 | 60.5751 | 60.5751 | 122.1261 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 80.1117 | 32.2911 | 768527.3174 | 64.0439 | 64.0439 | 125.7839 | 75 | 60 | 30.4382 | 30 | 62.4
6/27/20XX 7:00:00 PM | 0.79167 | 3 | 73.6 | 64.5 | 74.3617 | 87.0056 | 12.6439 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/27/20XX 8:00:00 PM | 0.83333 | 3 | 73.1 | 65.1 | 73.0869 | 85.5092 | 12.4223 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/27/20XX 9:00:00 PM | 0.875 | 3 | 71.8 | 71.3 | 81.7218 | 93.6601 | 11.9383 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/27/20XX 10:00:00 PM | 0.91667 | 3 | 71.2 | 73.5 | 80.0233 | 91.7077 | 11.6844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/27/20XX 11:00:00 PM | 0.95833 | 3 | 70.7 | 74.6 | 78.6313 | 90.1079 | 11.4766 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/27/20XX 12:00:00 AM | 0 | 4 | 70.8 | 73.5 | 78.908 | 90.4259 | 11.5179 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/28/20XX 1:00:00 AM | 0.041667 | 4 | 70.9 | 75 | 79.1855 | 90.7449 | 11.5593 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/28/20XX 2:00:00 AM | 0.083333 | 4 | 70.1 | 76.4 | 76.9888 | 88.2203 | 11.2316 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/28/20XX 3:00:00 AM | 0.125 | 4 | 70 | 76.9 | 76.7179 | 87.9091 | 11.1912 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/28/20XX 4:00:00 AM | 0.16667 | 4 | 69.6 | 78.4 | 75.643 | 86.674 | 11.031 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/28/20XX 5:00:00 AM | 0.20833 | 4 | 69.6 | 78.5 | 75.643 | 86.674 | 11.031 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/28/20XX 6:00:00 AM | 0.25 | 4 | 69.9 | 77.5 | 76.4479 | 87.5989 | 11.151 | 70 | 69.9 |  | 69.9 | 84.8112 | 0.1 | 73.59 | 18.59 | 702702 | 58.5585 | 58.5585 | 64.8406 | 17.02 | 405074.8952 | 33.7562 | 33.7562 | 92.3147 | 0.2 | 73.18 | 18.18 | 687204 | 57.267 | 57.267 | 67.0595 | 19.2389 | 457885.9904 | 38.1572 | 38.1572 | 95.4242 | 0.3 | 72.77 | 17.77 | 671706 | 55.9755 | 55.9755 | 69.2785 | 21.4579 | 510697.0856 | 42.5581 | 42.5581 | 98.5336 | 0.4 | 72.36 | 17.36 | 656208 | 54.684 | 54.684 | 71.4974 | 23.6768 | 563508.1808 | 46.959 | 46.959 | 101.643 | 0.5 | 71.95 | 16.95 | 640710 | 53.3925 | 53.3925 | 73.7164 | 25.8958 | 616319.2759 | 51.3599 | 51.3599 | 104.7524 | 0.6 | 71.54 | 16.54 | 625212 | 52.101 | 52.101 | 75.9354 | 28.1147 | 669130.3711 | 55.7609 | 55.7609 | 107.8619 | 0.7 | 71.13 | 16.13 | 609714 | 50.8095 | 50.8095 | 78.1543 | 30.3337 | 721941.4663 | 60.1618 | 60.1618 | 110.9713 | 0.8 | 70.72 | 15.72 | 594216 | 49.518 | 49.518 | 80.3733 | 32.5526 | 774752.5615 | 64.5627 | 64.5627 | 114.0807 | 0.9 | 70.31 | 15.31 | 578718 | 48.2265 | 48.2265 | 82.5922 | 34.7716 | 827563.6567 | 68.9636 | 68.9636 | 117.1901 | 1 | 69.9 | 14.9 | 563220 | 46.935 | 46.935 | 84.8112 | 36.9905 | 880374.7519 | 73.3646 | 73.3646 | 120.2996 | 70 | 75 | 30.0202 | 30 | 77.5
6/28/20XX 7:00:00 AM | 0.29167 | 4 | 70.9 | 75.9 | 79.1855 | 90.7449 | 11.5593 | 70 | 70.9 |  | 70.9 | 86.0055 | 0.1 | 73.69 | 18.69 | 706482 | 58.8735 | 58.8735 | 64.96 | 17.1394 | 407917.4917 | 33.9931 | 33.9931 | 92.8666 | 0.2 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 67.2984 | 19.4778 | 463571.1833 | 38.6309 | 38.6309 | 96.5279 | 0.3 | 73.07 | 18.07 | 683046 | 56.9205 | 56.9205 | 69.6368 | 21.8162 | 519224.875 | 43.2687 | 43.2687 | 100.1892 | 0.4 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 71.9752 | 24.1546 | 574878.5666 | 47.9065 | 47.9065 | 103.8505 | 0.5 | 72.45 | 17.45 | 659610 | 54.9675 | 54.9675 | 74.3136 | 26.493 | 630532.2583 | 52.5444 | 52.5444 | 107.5119 | 0.6 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 76.652 | 28.8313 | 686185.9499 | 57.1822 | 57.1822 | 111.1732 | 0.7 | 71.83 | 16.83 | 636174 | 53.0145 | 53.0145 | 78.9904 | 31.1697 | 741839.6416 | 61.82 | 61.82 | 114.8345 | 0.8 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 81.3288 | 33.5081 | 797493.3332 | 66.4578 | 66.4578 | 118.4958 | 0.9 | 71.21 | 16.21 | 612738 | 51.0615 | 51.0615 | 83.6671 | 35.8465 | 853147.0249 | 71.0956 | 71.0956 | 122.1571 | 1 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 86.0055 | 38.1849 | 908800.7165 | 75.7334 | 75.7334 | 125.8184 | 70 | 75 | 30.4522 | 30 | 75.9
6/28/20XX 8:00:00 AM | 0.33333 | 4 | 72.4 | 72.5 | 83.4515 | 95.6486 | 12.1971 | 70 | 72.4 |  | 72.4 | 86.5008 | 0.1 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 65.0095 | 17.1889 | 409096.1638 | 34.0913 | 34.0913 | 93.4373 | 0.2 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 67.3975 | 19.5768 | 465928.5277 | 38.8274 | 38.8274 | 97.6694 | 0.3 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 69.7854 | 21.9647 | 522760.8915 | 43.5634 | 43.5634 | 101.9014 | 0.4 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 72.1733 | 24.3527 | 579593.2553 | 48.2994 | 48.2994 | 106.1334 | 0.5 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 74.5612 | 26.7406 | 636425.6192 | 53.0355 | 53.0355 | 110.3655 | 0.6 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 76.9491 | 29.1285 | 693257.983 | 57.7715 | 57.7715 | 114.5975 | 0.7 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 79.337 | 31.5164 | 750090.3468 | 62.5075 | 62.5075 | 118.8295 | 0.8 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 81.7249 | 33.9043 | 806922.7107 | 67.2436 | 67.2436 | 123.0616 | 0.9 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 84.1129 | 36.2922 | 863755.0745 | 71.9796 | 71.9796 | 127.2936 | 1 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 86.5008 | 38.6801 | 920587.4383 | 76.7156 | 76.7156 | 131.5256 | 70 | 70 | 30.8978 | 30 | 72.5
6/28/20XX 9:00:00 AM | 0.375 | 4 | 74 | 69.8 | 75.3952 | 88.2187 | 12.8236 | 60 | 74 |  | 74 | 87.9623 | 0.1 | 74 | 19 | 718200 | 59.85 | 59.85 | 65.1557 | 17.3351 | 412574.486 | 34.3812 | 34.3812 | 94.2312 | 0.2 | 74 | 19 | 718200 | 59.85 | 59.85 | 67.6898 | 19.8691 | 472885.1721 | 39.4071 | 39.4071 | 99.2571 | 0.3 | 74 | 19 | 718200 | 59.85 | 59.85 | 70.2238 | 22.4032 | 533195.8581 | 44.433 | 44.433 | 104.283 | 0.4 | 74 | 19 | 718200 | 59.85 | 59.85 | 72.7579 | 24.9372 | 593506.5441 | 49.4589 | 49.4589 | 109.3089 | 0.5 | 74 | 19 | 718200 | 59.85 | 59.85 | 75.2919 | 27.4713 | 653817.2301 | 54.4848 | 54.4848 | 114.3348 | 0.6 | 74 | 19 | 718200 | 59.85 | 59.85 | 77.826 | 30.0054 | 714127.9162 | 59.5107 | 59.5107 | 119.3607 | 0.7 | 74 | 19 | 718200 | 59.85 | 59.85 | 80.3601 | 32.5394 | 774438.6022 | 64.5366 | 64.5366 | 124.3866 | 0.8 | 74 | 19 | 718200 | 59.85 | 59.85 | 82.8941 | 35.0735 | 834749.2882 | 69.5624 | 69.5624 | 129.4124 | 0.9 | 74 | 19 | 718200 | 59.85 | 59.85 | 85.4282 | 37.6076 | 895059.9743 | 74.5883 | 74.5883 | 134.4383 | 1 | 74 | 19 | 718200 | 59.85 | 59.85 | 87.9623 | 40.1416 | 955370.6603 | 79.6142 | 79.6142 | 139.4642 | 75 | 70 | 31.5192 | 32 | 69.8
6/28/20XX 10:00:00 AM | 0.41667 | 4 | 75.9 | 66 | 80.4731 | 94.1799 | 13.7068 | 60 | 75.9 |  | 75.9 | 88.6972 | 0.1 | 74.19 | 19.19 | 725382 | 60.4485 | 60.4485 | 65.2292 | 17.4086 | 414323.6817 | 34.527 | 34.527 | 94.9755 | 0.2 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 67.8367 | 20.0161 | 476383.5633 | 39.6986 | 39.6986 | 100.7456 | 0.3 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 70.4443 | 22.6237 | 538443.445 | 44.8703 | 44.8703 | 106.5158 | 0.4 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 73.0519 | 25.2312 | 600503.3266 | 50.0419 | 50.0419 | 112.2859 | 0.5 | 74.95 | 19.95 | 754110 | 62.8425 | 62.8425 | 75.6594 | 27.8388 | 662563.2083 | 55.2136 | 55.2136 | 118.0561 | 0.6 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 78.267 | 30.4463 | 724623.0899 | 60.3853 | 60.3853 | 123.8263 | 0.7 | 75.33 | 20.33 | 768474 | 64.0395 | 64.0395 | 80.8745 | 33.0539 | 786682.9716 | 65.5569 | 65.5569 | 129.5964 | 0.8 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 83.4821 | 35.6615 | 848742.8533 | 70.7286 | 70.7286 | 135.3666 | 0.9 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 86.0897 | 38.269 | 910802.7349 | 75.9002 | 75.9002 | 141.1367 | 1 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 88.6972 | 40.8766 | 972862.6166 | 81.0719 | 81.0719 | 146.9069 | 75 | 65 | 32.1008 | 32 | 66
6/28/20XX 11:00:00 AM | 0.45833 | 4 | 77.8 | 62.4 | 85.8376 | 100.478 | 14.6404 | 60 | 77.8 |  | 77.8 | 89.3513 | 0.1 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 65.2946 | 17.474 | 415880.3939 | 34.6567 | 34.6567 | 95.7037 | 0.2 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 67.9676 | 20.1469 | 479496.9879 | 39.9581 | 39.9581 | 102.2021 | 0.3 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 70.6405 | 22.8199 | 543113.5818 | 45.2595 | 45.2595 | 108.7005 | 0.4 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 73.3135 | 25.4929 | 606730.1757 | 50.5608 | 50.5608 | 115.1988 | 0.5 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 75.9865 | 28.1658 | 670346.7696 | 55.8622 | 55.8622 | 121.6972 | 0.6 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 78.6594 | 30.8388 | 733963.3636 | 61.1636 | 61.1636 | 128.1956 | 0.7 | 76.66 | 21.66 | 818748 | 68.229 | 68.229 | 81.3324 | 33.5118 | 797579.9575 | 66.465 | 66.465 | 134.694 | 0.8 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 84.0054 | 36.1847 | 861196.5514 | 71.7664 | 71.7664 | 141.1924 | 0.9 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 86.6783 | 38.8577 | 924813.1454 | 77.0678 | 77.0678 | 147.6908 | 1 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 89.3513 | 41.5307 | 988429.7393 | 82.3691 | 82.3691 | 154.1891 | 80 | 60 | 32.67 | 32 | 62.4
6/28/20XX 12:00:00 PM | 0.5 | 4 | 79.1 | 59.5 | 74.4534 | 89.6782 | 15.2248 | 50 | 79.1 |  | 79.1 | 88.9169 | 0.1 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 65.2512 | 17.4305 | 414846.632 | 34.5706 | 34.5706 | 96.0271 | 0.2 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 67.8807 | 20.0601 | 477429.464 | 39.7858 | 39.7858 | 102.8488 | 0.3 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 70.5102 | 22.6896 | 540012.296 | 45.001 | 45.001 | 109.6705 | 0.4 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 73.1398 | 25.3191 | 602595.1281 | 50.2163 | 50.2163 | 116.4923 | 0.5 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 75.7693 | 27.9487 | 665177.9601 | 55.4315 | 55.4315 | 123.314 | 0.6 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 78.3988 | 30.5782 | 727760.7921 | 60.6467 | 60.6467 | 130.1357 | 0.7 | 77.57 | 22.57 | 853146 | 71.0955 | 71.0955 | 81.0283 | 33.2077 | 790343.6241 | 65.862 | 65.862 | 136.9575 | 0.8 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 83.6579 | 35.8372 | 852926.4561 | 71.0772 | 71.0772 | 143.7792 | 0.9 | 78.59 | 23.59 | 891702 | 74.3085 | 74.3085 | 86.2874 | 38.4668 | 915509.2881 | 76.2924 | 76.2924 | 150.6009 | 1 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 88.9169 | 41.0963 | 978092.1201 | 81.5077 | 81.5077 | 157.4227 | 80 | 60 | 32.9213 | 32 | 59.5
6/28/20XX 1:00:00 PM | 0.54167 | 4 | 80 | 58 | 76.7237 | 92.42 | 15.6963 | 50 | 80 |  | 80 | 89.2807 | 0.1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 65.2875 | 17.4669 | 415712.4518 | 34.6427 | 34.6427 | 96.3827 | 0.2 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 67.9535 | 20.1328 | 479161.1036 | 39.9301 | 39.9301 | 103.5601 | 0.3 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 70.6194 | 22.7987 | 542609.7554 | 45.2175 | 45.2175 | 110.7375 | 0.4 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 73.2853 | 25.4646 | 606058.4072 | 50.5049 | 50.5049 | 117.9149 | 0.5 | 77 | 22 | 831600 | 69.3 | 69.3 | 75.9512 | 28.1305 | 669507.0591 | 55.7923 | 55.7923 | 125.0923 | 0.6 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 78.6171 | 30.7965 | 732955.7109 | 61.0796 | 61.0796 | 132.2696 | 0.7 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 81.283 | 33.4624 | 796404.3627 | 66.367 | 66.367 | 139.447 | 0.8 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 83.9489 | 36.1283 | 859853.0145 | 71.6544 | 71.6544 | 146.6244 | 0.9 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 86.6148 | 38.7942 | 923301.6663 | 76.9418 | 76.9418 | 153.8018 | 1 | 80 | 25 | 945000 | 78.75 | 78.75 | 89.2807 | 41.4601 | 986750.3181 | 82.2292 | 82.2292 | 160.9792 | 80 | 60 | 33.1994 | 34 | 58
6/28/20XX 2:00:00 PM | 0.58333 | 4 | 80.6 | 56.7 | 78.2688 | 94.2862 | 16.0174 | 50 | 80.6 |  | 80.6 | 89.0004 | 0.1 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 65.2595 | 17.4389 | 415045.3499 | 34.5871 | 34.5871 | 96.5161 | 0.2 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 67.8974 | 20.0768 | 477826.8998 | 39.8189 | 39.8189 | 103.8269 | 0.3 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 70.5353 | 22.7146 | 540608.4496 | 45.0507 | 45.0507 | 111.1377 | 0.4 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 73.1732 | 25.3525 | 603389.9995 | 50.2825 | 50.2825 | 118.4485 | 0.5 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 75.811 | 27.9904 | 666171.5494 | 55.5143 | 55.5143 | 125.7593 | 0.6 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 78.4489 | 30.6283 | 728953.0993 | 60.7461 | 60.7461 | 133.0701 | 0.7 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 81.0868 | 33.2662 | 791734.6491 | 65.9779 | 65.9779 | 140.3809 | 0.8 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 83.7247 | 35.904 | 854516.199 | 71.2097 | 71.2097 | 147.6917 | 0.9 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 86.3626 | 38.5419 | 917297.7489 | 76.4415 | 76.4415 | 155.0025 | 1 | 80.6 | 25.6 | 967680 | 80.64 | 80.64 | 89.0004 | 41.1798 | 980079.2988 | 81.6733 | 81.6733 | 162.3133 | 80 | 55 | 33.3029 | 34 | 56.7
6/28/20XX 3:00:00 PM | 0.625 | 4 | 80.1 | 57 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 88.0041 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 65.1599 | 17.3392 | 412673.9571 | 34.3895 | 34.3895 | 96.161 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 67.6981 | 19.8775 | 473084.1142 | 39.4237 | 39.4237 | 103.1167 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 70.2364 | 22.4157 | 533494.2714 | 44.4579 | 44.4579 | 110.0724 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 72.7746 | 24.954 | 593904.4285 | 49.492 | 49.492 | 117.028 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 75.3128 | 27.4922 | 654314.5856 | 54.5262 | 54.5262 | 123.9837 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 77.8511 | 30.0305 | 714724.7427 | 59.5604 | 59.5604 | 130.9394 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 80.3893 | 32.5687 | 775134.8999 | 64.5946 | 64.5946 | 137.8951 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 82.9276 | 35.1069 | 835545.057 | 69.6288 | 69.6288 | 144.8508 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 85.4658 | 37.6452 | 895955.2141 | 74.6629 | 74.6629 | 151.8064 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 88.0041 | 40.1834 | 956365.3712 | 79.6971 | 79.6971 | 158.7621 | 80 | 55 | 33.0238 | 34 | 57
6/28/20XX 4:00:00 PM | 0.66667 | 4 | 79.2 | 59.6 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 89.3684 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 65.2963 | 17.4757 | 415921.0654 | 34.6601 | 34.6601 | 96.1481 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 67.971 | 20.1504 | 479578.3309 | 39.9649 | 39.9649 | 103.0909 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 70.6457 | 22.825 | 543235.5963 | 45.2696 | 45.2696 | 110.0336 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 73.3203 | 25.4997 | 606892.8617 | 50.5744 | 50.5744 | 116.9764 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 75.995 | 28.1744 | 670550.1272 | 55.8792 | 55.8792 | 123.9192 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 78.6697 | 30.8491 | 734207.3926 | 61.1839 | 61.1839 | 130.8619 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 81.3444 | 33.5237 | 797864.658 | 66.4887 | 66.4887 | 137.8047 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 84.019 | 36.1984 | 861521.9235 | 71.7935 | 71.7935 | 144.7475 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 86.6937 | 38.8731 | 925179.1889 | 77.0983 | 77.0983 | 151.6903 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 89.3684 | 41.5478 | 988836.4543 | 82.403 | 82.403 | 158.633 | 80 | 60 | 33.0166 | 34 | 59.6
6/28/20XX 5:00:00 PM | 0.70833 | 4 | 77.6 | 65.7 | 85.2591 | 99.7988 | 14.5397 | 60 | 77.6 |  | 77.6 | 93.5468 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 65.7141 | 17.8935 | 425865.6018 | 35.4888 | 35.4888 | 96.4728 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 68.8067 | 20.986 | 499467.4037 | 41.6223 | 41.6223 | 103.7403 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 71.8992 | 24.0785 | 573069.2055 | 47.7558 | 47.7558 | 111.0078 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 74.9917 | 27.1711 | 646671.0073 | 53.8893 | 53.8893 | 118.2753 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 78.0842 | 30.2636 | 720272.8092 | 60.0227 | 60.0227 | 125.5427 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 81.1767 | 33.3561 | 793874.611 | 66.1562 | 66.1562 | 132.8102 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 84.2692 | 36.4486 | 867476.4128 | 72.2897 | 72.2897 | 140.0777 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 87.3617 | 39.5411 | 941078.2147 | 78.4232 | 78.4232 | 147.3452 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 90.4542 | 42.6336 | 1014680.0165 | 84.5567 | 84.5567 | 154.6127 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 93.5468 | 45.7261 | 1088281.8183 | 90.6902 | 90.6902 | 161.8802 | 80 | 65 | 33.2781 | 34 | 65.7
6/28/20XX 6:00:00 PM | 0.75 | 4 | 77.1 | 65.5 | 83.8273 | 98.1177 | 14.2905 | 60 | 77.1 |  | 77.1 | 91.687 | 0.1 | 74.31 | 19.31 | 729918 | 60.8265 | 60.8265 | 65.5282 | 17.7075 | 421439.4155 | 35.12 | 35.12 | 95.9465 | 0.2 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 68.4347 | 20.6141 | 490615.0309 | 40.8846 | 40.8846 | 102.6876 | 0.3 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 71.3412 | 23.5206 | 559790.6464 | 46.6492 | 46.6492 | 109.4287 | 0.4 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 74.2478 | 26.4272 | 628966.2618 | 52.4139 | 52.4139 | 116.1699 | 0.5 | 75.55 | 20.55 | 776790 | 64.7325 | 64.7325 | 77.1543 | 29.3337 | 698141.8773 | 58.1785 | 58.1785 | 122.911 | 0.6 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 80.0609 | 32.2402 | 767317.4928 | 63.9431 | 63.9431 | 129.6521 | 0.7 | 76.17 | 21.17 | 800226 | 66.6855 | 66.6855 | 82.9674 | 35.1468 | 836493.1082 | 69.7078 | 69.7078 | 136.3933 | 0.8 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 85.8739 | 38.0533 | 905668.7237 | 75.4724 | 75.4724 | 143.1344 | 0.9 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 88.7805 | 40.9598 | 974844.3391 | 81.237 | 81.237 | 149.8755 | 1 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 91.687 | 43.8664 | 1044019.9546 | 87.0017 | 87.0017 | 156.6167 | 75 | 65 | 32.8639 | 32 | 65.5
6/28/20XX 7:00:00 PM | 0.79167 | 4 | 76.3 | 65.9 | 81.5784 | 95.4774 | 13.8991 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/28/20XX 8:00:00 PM | 0.83333 | 4 | 75.6 | 67.2 | 79.6526 | 93.2166 | 13.564 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/28/20XX 9:00:00 PM | 0.875 | 4 | 74.8 | 68.5 | 77.499 | 90.6884 | 13.1894 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/28/20XX 10:00:00 PM | 0.91667 | 4 | 74.5 | 69.7 | 76.7042 | 89.7555 | 13.0512 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/28/20XX 11:00:00 PM | 0.95833 | 4 | 74.4 | 68.2 | 76.4409 | 89.4463 | 13.0054 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/28/20XX 12:00:00 AM | 0 | 5 | 73.8 | 67.4 | 74.8769 | 87.6104 | 12.7335 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/29/20XX 1:00:00 AM | 0.041667 | 5 | 72.7 | 69.9 | 72.0807 | 84.3281 | 12.2474 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/29/20XX 2:00:00 AM | 0.083333 | 5 | 71.8 | 72.9 | 81.7218 | 93.6601 | 11.9383 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/29/20XX 3:00:00 AM | 0.125 | 5 | 71 | 73.8 | 79.4639 | 91.0648 | 11.6009 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/29/20XX 4:00:00 AM | 0.16667 | 5 | 70.4 | 76.1 | 77.8062 | 89.1597 | 11.3535 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/29/20XX 5:00:00 AM | 0.20833 | 5 | 69 | 81.9 | 84.8499 | 95.6435 | 10.7936 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/29/20XX 6:00:00 AM | 0.25 | 5 | 69.9 | 79.8 | 76.4479 | 87.5989 | 11.151 | 70 | 69.9 |  | 69.9 | 87.3759 | 0.1 | 73.59 | 18.59 | 702702 | 58.5585 | 58.5585 | 65.0971 | 17.2764 | 411178.9312 | 34.2649 | 34.2649 | 92.8234 | 0.2 | 73.18 | 18.18 | 687204 | 57.267 | 57.267 | 67.5725 | 19.7519 | 470094.0623 | 39.1745 | 39.1745 | 96.4415 | 0.3 | 72.77 | 17.77 | 671706 | 55.9755 | 55.9755 | 70.0479 | 22.2273 | 529009.1935 | 44.0841 | 44.0841 | 100.0596 | 0.4 | 72.36 | 17.36 | 656208 | 54.684 | 54.684 | 72.5233 | 24.7027 | 587924.3247 | 48.9937 | 48.9937 | 103.6777 | 0.5 | 71.95 | 16.95 | 640710 | 53.3925 | 53.3925 | 74.9988 | 27.1781 | 646839.4558 | 53.9033 | 53.9033 | 107.2958 | 0.6 | 71.54 | 16.54 | 625212 | 52.101 | 52.101 | 77.4742 | 29.6536 | 705754.587 | 58.8129 | 58.8129 | 110.9139 | 0.7 | 71.13 | 16.13 | 609714 | 50.8095 | 50.8095 | 79.9496 | 32.129 | 764669.7182 | 63.7225 | 63.7225 | 114.532 | 0.8 | 70.72 | 15.72 | 594216 | 49.518 | 49.518 | 82.425 | 34.6044 | 823584.8493 | 68.6321 | 68.6321 | 118.1501 | 0.9 | 70.31 | 15.31 | 578718 | 48.2265 | 48.2265 | 84.9005 | 37.0798 | 882499.9805 | 73.5417 | 73.5417 | 121.7682 | 1 | 69.9 | 14.9 | 563220 | 46.935 | 46.935 | 87.3759 | 39.5553 | 941415.1117 | 78.4513 | 78.4513 | 125.3863 | 70 | 80 | 30.4207 | 30 | 79.8
6/29/20XX 7:00:00 AM | 0.29167 | 5 | 71.1 | 77.2 | 79.7432 | 91.3858 | 11.6426 | 70 | 71.1 |  | 71.1 | 88.1258 | 0.1 | 73.71 | 18.71 | 707238 | 58.9365 | 58.9365 | 65.1721 | 17.3514 | 412963.8316 | 34.4137 | 34.4137 | 93.3502 | 0.2 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 67.7225 | 19.9018 | 473663.8632 | 39.472 | 39.472 | 97.495 | 0.3 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 70.2729 | 22.4523 | 534363.8948 | 44.5303 | 44.5303 | 101.6398 | 0.4 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 72.8233 | 25.0027 | 595063.9264 | 49.5887 | 49.5887 | 105.7847 | 0.5 | 72.55 | 17.55 | 663390 | 55.2825 | 55.2825 | 75.3737 | 27.5531 | 655763.958 | 54.647 | 54.647 | 109.9295 | 0.6 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 77.9242 | 30.1035 | 716463.9896 | 59.7053 | 59.7053 | 114.0743 | 0.7 | 71.97 | 16.97 | 641466 | 53.4555 | 53.4555 | 80.4746 | 32.654 | 777164.0211 | 64.7637 | 64.7637 | 118.2192 | 0.8 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 83.025 | 35.2044 | 837864.0527 | 69.822 | 69.822 | 122.364 | 0.9 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 85.5754 | 37.7548 | 898564.0843 | 74.8803 | 74.8803 | 126.5088 | 1 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 88.1258 | 40.3052 | 959264.1159 | 79.9387 | 79.9387 | 130.6537 | 70 | 75 | 30.8325 | 30 | 77.2
6/29/20XX 8:00:00 AM | 0.33333 | 5 | 73 | 70.2 | 85.2126 | 97.6734 | 12.4608 | 70 | 73 |  | 73 | 85.4618 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.9057 | 17.085 | 406623.5075 | 33.8853 | 33.8853 | 93.4203 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 67.1897 | 19.369 | 460983.215 | 38.4153 | 38.4153 | 97.6353 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 69.4737 | 21.6531 | 515342.9225 | 42.9452 | 42.9452 | 101.8502 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 71.7577 | 23.9371 | 569702.63 | 47.4752 | 47.4752 | 106.0652 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 74.0417 | 26.2211 | 624062.3375 | 52.0052 | 52.0052 | 110.2802 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 76.3258 | 28.5051 | 678422.045 | 56.5352 | 56.5352 | 114.4952 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 78.6098 | 30.7891 | 732781.7524 | 61.0651 | 61.0651 | 118.7101 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 80.8938 | 33.0732 | 787141.4599 | 65.5951 | 65.5951 | 122.9251 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 83.1778 | 35.3572 | 841501.1674 | 70.1251 | 70.1251 | 127.1401 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 85.4618 | 37.6412 | 895860.8749 | 74.6551 | 74.6551 | 131.3551 | 75 | 70 | 30.8826 | 30 | 70.2
6/29/20XX 9:00:00 AM | 0.375 | 5 | 75.3 | 65 | 78.8391 | 92.2616 | 13.4225 | 60 | 75.3 |  | 75.3 | 85.5503 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 64.9145 | 17.0939 | 406834.136 | 33.9028 | 33.9028 | 94.1623 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 67.2074 | 19.3867 | 461404.4721 | 38.4504 | 38.4504 | 99.1194 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 69.5002 | 21.6796 | 515974.8081 | 42.9979 | 42.9979 | 104.0764 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 71.7931 | 23.9725 | 570545.1441 | 47.5454 | 47.5454 | 109.0334 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 74.086 | 26.2654 | 625115.4802 | 52.093 | 52.093 | 113.9905 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 76.3789 | 28.5582 | 679685.8162 | 56.6405 | 56.6405 | 118.9475 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 78.6717 | 30.8511 | 734256.1522 | 61.188 | 61.188 | 123.9045 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 80.9646 | 33.144 | 788826.4883 | 65.7355 | 65.7355 | 128.8615 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 83.2575 | 35.4368 | 843396.8243 | 70.2831 | 70.2831 | 133.8186 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 85.5503 | 37.7297 | 897967.1603 | 74.8306 | 74.8306 | 138.7756 | 75 | 65 | 31.461 | 32 | 65
6/29/20XX 10:00:00 AM | 0.41667 | 5 | 77.8 | 60.1 | 85.8376 | 100.478 | 14.6404 | 60 | 77.8 |  | 77.8 | 85.984 | 0.1 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 64.9579 | 17.1372 | 407866.2451 | 33.9889 | 33.9889 | 95.0359 | 0.2 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 67.2941 | 19.4735 | 463468.6901 | 38.6224 | 38.6224 | 100.8664 | 0.3 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 69.6303 | 21.8097 | 519071.1352 | 43.2559 | 43.2559 | 106.6969 | 0.4 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 71.9666 | 24.1459 | 574673.5803 | 47.8895 | 47.8895 | 112.5275 | 0.5 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 74.3028 | 26.4822 | 630276.0253 | 52.523 | 52.523 | 118.358 | 0.6 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 76.6391 | 28.8184 | 685878.4704 | 57.1565 | 57.1565 | 124.1885 | 0.7 | 76.66 | 21.66 | 818748 | 68.229 | 68.229 | 78.9753 | 31.1547 | 741480.9154 | 61.7901 | 61.7901 | 130.0191 | 0.8 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 81.3115 | 33.4909 | 797083.3605 | 66.4236 | 66.4236 | 135.8496 | 0.9 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 83.6478 | 35.8271 | 852685.8056 | 71.0572 | 71.0572 | 141.6802 | 1 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 85.984 | 38.1634 | 908288.2506 | 75.6907 | 75.6907 | 147.5107 | 80 | 60 | 32.1425 | 32 | 60.1
6/29/20XX 11:00:00 AM | 0.45833 | 5 | 80.1 | 54.5 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 84.0667 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 64.7661 | 16.9455 | 403303.0615 | 33.6086 | 33.6086 | 95.3801 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 66.9106 | 19.09 | 454342.323 | 37.8619 | 37.8619 | 101.5549 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 69.0552 | 21.2345 | 505381.5846 | 42.1151 | 42.1151 | 107.7296 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 71.1997 | 23.379 | 556420.8461 | 46.3684 | 46.3684 | 113.9044 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 73.3442 | 25.5235 | 607460.1076 | 50.6217 | 50.6217 | 120.0792 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 75.4887 | 27.668 | 658499.3691 | 54.8749 | 54.8749 | 126.2539 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 77.6332 | 29.8125 | 709538.6307 | 59.1282 | 59.1282 | 132.4287 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 79.7777 | 31.9571 | 760577.8922 | 63.3815 | 63.3815 | 138.6035 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 81.9222 | 34.1016 | 811617.1537 | 67.6348 | 67.6348 | 144.7783 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 84.0667 | 36.2461 | 862656.4152 | 71.888 | 71.888 | 150.953 | 80 | 55 | 32.4064 | 32 | 54.5
6/29/20XX 12:00:00 PM | 0.5 | 5 | 82.3 | 52.1 | 82.7861 | 99.7431 | 16.957 | 50 | 82.3 |  | 82.3 | 86.3471 | 0.1 | 74.83 | 19.83 | 749574 | 62.4645 | 62.4645 | 64.9942 | 17.1735 | 408730.421 | 34.0609 | 34.0609 | 96.5254 | 0.2 | 75.66 | 20.66 | 780948 | 65.079 | 65.079 | 67.3667 | 19.5461 | 465197.042 | 38.7664 | 38.7664 | 103.8454 | 0.3 | 76.49 | 21.49 | 812322 | 67.6935 | 67.6935 | 69.7393 | 21.9186 | 521663.6631 | 43.472 | 43.472 | 111.1655 | 0.4 | 77.32 | 22.32 | 843696 | 70.308 | 70.308 | 72.1118 | 24.2912 | 578130.2841 | 48.1775 | 48.1775 | 118.4855 | 0.5 | 78.15 | 23.15 | 875070 | 72.9225 | 72.9225 | 74.4844 | 26.6637 | 634596.9051 | 52.8831 | 52.8831 | 125.8056 | 0.6 | 78.98 | 23.98 | 906444 | 75.537 | 75.537 | 76.8569 | 29.0363 | 691063.5261 | 57.5886 | 57.5886 | 133.1256 | 0.7 | 79.81 | 24.81 | 937818 | 78.1515 | 78.1515 | 79.2295 | 31.4088 | 747530.1471 | 62.2942 | 62.2942 | 140.4457 | 0.8 | 80.64 | 25.64 | 969192 | 80.766 | 80.766 | 81.602 | 33.7814 | 803996.7682 | 66.9997 | 66.9997 | 147.7657 | 0.9 | 81.47 | 26.47 | 1000566 | 83.3805 | 83.3805 | 83.9746 | 36.1539 | 860463.3892 | 71.7053 | 71.7053 | 155.0858 | 1 | 82.3 | 27.3 | 1031940 | 85.995 | 85.995 | 86.3471 | 38.5265 | 916930.0102 | 76.4108 | 76.4108 | 162.4058 | 80 | 50 | 33.304 | 34 | 52.1
6/29/20XX 1:00:00 PM | 0.54167 | 5 | 82.5 | 49.3 | 66.3809 | 83.3313 | 16.9504 | 40 | 82.5 |  | 82.5 | 82.1448 | 0.1 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 64.574 | 16.7533 | 398728.968 | 33.2274 | 33.2274 | 95.7549 | 0.2 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 66.5263 | 18.7056 | 445194.136 | 37.0995 | 37.0995 | 102.3045 | 0.3 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 68.4786 | 20.658 | 491659.3039 | 40.9716 | 40.9716 | 108.8541 | 0.4 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 70.4309 | 22.6103 | 538124.4719 | 44.8437 | 44.8437 | 115.4037 | 0.5 | 78.25 | 23.25 | 878850 | 73.2375 | 73.2375 | 72.3832 | 24.5626 | 584589.6399 | 48.7158 | 48.7158 | 121.9533 | 0.6 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 74.3355 | 26.5149 | 631054.8079 | 52.5879 | 52.5879 | 128.5029 | 0.7 | 79.95 | 24.95 | 943110 | 78.5925 | 78.5925 | 76.2879 | 28.4672 | 677519.9758 | 56.46 | 56.46 | 135.0525 | 0.8 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 78.2402 | 30.4195 | 723985.1438 | 60.3321 | 60.3321 | 141.6021 | 0.9 | 81.65 | 26.65 | 1007370 | 83.9475 | 83.9475 | 80.1925 | 32.3719 | 770450.3118 | 64.2042 | 64.2042 | 148.1517 | 1 | 82.5 | 27.5 | 1039500 | 86.625 | 86.625 | 82.1448 | 34.3242 | 816915.4798 | 68.0763 | 68.0763 | 154.7013 | 80 | 50 | 32.6935 | 32 | 49.3
6/29/20XX 2:00:00 PM | 0.58333 | 5 | 81.7 | 50.7 | 81.168 | 97.7883 | 16.6202 | 50 | 81.7 |  | 81.7 | 82.3314 | 0.1 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 64.5926 | 16.772 | 399173.1048 | 33.2644 | 33.2644 | 95.5399 | 0.2 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 66.5636 | 18.743 | 446082.4096 | 37.1735 | 37.1735 | 101.8745 | 0.3 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 68.5346 | 20.7139 | 492991.7143 | 41.0826 | 41.0826 | 108.2091 | 0.4 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 70.5055 | 22.6849 | 539901.0191 | 44.9918 | 44.9918 | 114.5438 | 0.5 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 72.4765 | 24.6559 | 586810.3239 | 48.9009 | 48.9009 | 120.8784 | 0.6 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 74.4475 | 26.6269 | 633719.6287 | 52.81 | 52.81 | 127.213 | 0.7 | 79.39 | 24.39 | 921942 | 76.8285 | 76.8285 | 76.4185 | 28.5979 | 680628.9335 | 56.7191 | 56.7191 | 133.5476 | 0.8 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 78.3895 | 30.5688 | 727538.2383 | 60.6282 | 60.6282 | 139.8822 | 0.9 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 80.3604 | 32.5398 | 774447.543 | 64.5373 | 64.5373 | 146.2168 | 1 | 81.7 | 26.7 | 1009260 | 84.105 | 84.105 | 82.3314 | 34.5108 | 821356.8478 | 68.4464 | 68.4464 | 152.5514 | 80 | 50 | 32.5266 | 32 | 50.7
6/29/20XX 3:00:00 PM | 0.625 | 5 | 82.4 | 48.5 | 66.1648 | 83.0584 | 16.8936 | 40 | 82.4 |  | 82.4 | 80.5243 | 0.1 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 64.4119 | 16.5913 | 394872.2293 | 32.906 | 32.906 | 95.402 | 0.2 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 66.2022 | 18.3815 | 437480.6587 | 36.4567 | 36.4567 | 101.5987 | 0.3 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 67.9924 | 20.1718 | 480089.088 | 40.0074 | 40.0074 | 107.7954 | 0.4 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 69.7827 | 21.9621 | 522697.5174 | 43.5581 | 43.5581 | 113.9921 | 0.5 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 71.573 | 23.7524 | 565305.9467 | 47.1088 | 47.1088 | 120.1888 | 0.6 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 73.3633 | 25.5426 | 607914.3761 | 50.6595 | 50.6595 | 126.3855 | 0.7 | 79.88 | 24.88 | 940464 | 78.372 | 78.372 | 75.1535 | 27.3329 | 650522.8054 | 54.2102 | 54.2102 | 132.5822 | 0.8 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 76.9438 | 29.1232 | 693131.2348 | 57.7609 | 57.7609 | 138.7789 | 0.9 | 81.56 | 26.56 | 1003968 | 83.664 | 83.664 | 78.7341 | 30.9134 | 735739.6641 | 61.3116 | 61.3116 | 144.9756 | 1 | 82.4 | 27.4 | 1035720 | 86.31 | 86.31 | 80.5243 | 32.7037 | 778348.0935 | 64.8623 | 64.8623 | 151.1723 | 80 | 50 | 32.4147 | 32 | 48.5
6/29/20XX 4:00:00 PM | 0.66667 | 5 | 82.2 | 47.7 | 65.7342 | 82.5146 | 16.7804 | 40 | 82.2 |  | 82.2 | 78.6551 | 0.1 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 64.225 | 16.4044 | 390423.5311 | 32.5353 | 32.5353 | 94.9683 | 0.2 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 65.8283 | 18.0077 | 428583.2621 | 35.7153 | 35.7153 | 100.7313 | 0.3 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 67.4317 | 19.6111 | 466742.9932 | 38.8952 | 38.8952 | 106.4942 | 0.4 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 69.035 | 21.2144 | 504902.7243 | 42.0752 | 42.0752 | 112.2572 | 0.5 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 70.6384 | 22.8178 | 543062.4553 | 45.2552 | 45.2552 | 118.0202 | 0.6 | 78.92 | 23.92 | 904176 | 75.348 | 75.348 | 72.2417 | 24.4211 | 581222.1864 | 48.4352 | 48.4352 | 123.7832 | 0.7 | 79.74 | 24.74 | 935172 | 77.931 | 77.931 | 73.8451 | 26.0245 | 619381.9175 | 51.6152 | 51.6152 | 129.5462 | 0.8 | 80.56 | 25.56 | 966168 | 80.514 | 80.514 | 75.4484 | 27.6278 | 657541.6485 | 54.7951 | 54.7951 | 135.3091 | 0.9 | 81.38 | 26.38 | 997164 | 83.097 | 83.097 | 77.0518 | 29.2312 | 695701.3796 | 57.9751 | 57.9751 | 141.0721 | 1 | 82.2 | 27.2 | 1028160 | 85.68 | 85.68 | 78.6551 | 30.8345 | 733861.1107 | 61.1551 | 61.1551 | 146.8351 | 80 | 50 | 32.0723 | 32 | 47.7
6/29/20XX 5:00:00 PM | 0.70833 | 5 | 81.1 | 50.6 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 80.5532 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 64.4148 | 16.5942 | 394941.0094 | 32.9118 | 32.9118 | 94.9983 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 66.208 | 18.3873 | 437618.2187 | 36.4682 | 36.4682 | 100.7912 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 68.0011 | 20.1805 | 480295.4281 | 40.0246 | 40.0246 | 106.5841 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 69.7943 | 21.9736 | 522972.6375 | 43.5811 | 43.5811 | 112.3771 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 71.5874 | 23.7668 | 565649.8468 | 47.1375 | 47.1375 | 118.17 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 73.3806 | 25.56 | 608327.0562 | 50.6939 | 50.6939 | 123.9629 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 75.1738 | 27.3531 | 651004.2656 | 54.2504 | 54.2504 | 129.7559 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 76.9669 | 29.1463 | 693681.4749 | 57.8068 | 57.8068 | 135.5488 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 78.7601 | 30.9394 | 736358.6843 | 61.3632 | 61.3632 | 141.3417 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 80.5532 | 32.7326 | 779035.8937 | 64.9197 | 64.9197 | 147.1347 | 80 | 50 | 32.1006 | 32 | 50.6
6/29/20XX 6:00:00 PM | 0.75 | 5 | 80.1 | 51.2 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 78.8694 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 64.2464 | 16.4258 | 390933.4793 | 32.5778 | 32.5778 | 94.3493 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 65.8712 | 18.0506 | 429603.1587 | 35.8003 | 35.8003 | 99.4933 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 67.496 | 19.6753 | 468272.838 | 39.0227 | 39.0227 | 104.6372 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 69.1207 | 21.3001 | 506942.5173 | 42.2452 | 42.2452 | 109.7812 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 70.7455 | 22.9249 | 545612.1966 | 45.4677 | 45.4677 | 114.9252 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 72.3703 | 24.5497 | 584281.876 | 48.6902 | 48.6902 | 120.0692 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 73.9951 | 26.1744 | 622951.5553 | 51.9126 | 51.9126 | 125.2131 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 75.6198 | 27.7992 | 661621.2346 | 55.1351 | 55.1351 | 130.3571 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 77.2446 | 29.424 | 700290.914 | 58.3576 | 58.3576 | 135.5011 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 78.8694 | 31.0488 | 738960.5933 | 61.58 | 61.58 | 140.645 | 80 | 50 | 31.5914 | 32 | 51.2
6/29/20XX 7:00:00 PM | 0.79167 | 5 | 79.4 | 50 | 75.2039 | 90.5845 | 15.3806 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/29/20XX 8:00:00 PM | 0.83333 | 5 | 78 | 51.6 | 71.7546 | 86.4193 | 14.6647 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/29/20XX 9:00:00 PM | 0.875 | 5 | 76.9 | 53.5 | 69.138 | 83.2602 | 14.1222 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/29/20XX 10:00:00 PM | 0.91667 | 5 | 76.6 | 53.8 | 68.4384 | 82.4157 | 13.9773 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/29/20XX 11:00:00 PM | 0.95833 | 5 | 75.1 | 56.5 | 65.0293 | 78.3007 | 13.2714 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/29/20XX 12:00:00 AM | 0 | 6 | 74 | 57.1 | 62.6216 | 75.3952 | 12.7735 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/30/20XX 1:00:00 AM | 0.041667 | 6 | 73.5 | 57.6 | 61.5526 | 74.1052 | 12.5526 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/30/20XX 2:00:00 AM | 0.083333 | 6 | 72.5 | 60.7 | 71.5821 | 83.7428 | 12.1608 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/30/20XX 3:00:00 AM | 0.125 | 6 | 71.6 | 62 | 69.3749 | 81.1522 | 11.7773 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/30/20XX 4:00:00 AM | 0.16667 | 6 | 70.6 | 66.4 | 66.992 | 78.3554 | 11.3635 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/30/20XX 5:00:00 AM | 0.20833 | 6 | 70.1 | 69.4 | 65.8275 | 76.9888 | 11.1613 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/30/20XX 6:00:00 AM | 0.25 | 6 | 70.7 | 69.3 | 67.227 | 78.6313 | 11.4043 | 60 | 70.7 |  | 70.7 | 77.833 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 64.1428 | 16.3221 | 388466.815 | 32.3722 | 32.3722 | 91.1827 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 65.6639 | 17.8433 | 424669.8299 | 35.3892 | 35.3892 | 93.1602 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 67.185 | 19.3644 | 460872.8449 | 38.4061 | 38.4061 | 95.1376 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 68.7062 | 20.8855 | 497075.8598 | 41.423 | 41.423 | 97.115 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 70.2273 | 22.4067 | 533278.8748 | 44.4399 | 44.4399 | 99.0924 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 71.7484 | 23.9278 | 569481.8897 | 47.4568 | 47.4568 | 101.0698 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 73.2696 | 25.4489 | 605684.9047 | 50.4737 | 50.4737 | 103.0472 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 74.7907 | 26.9701 | 641887.9196 | 53.4907 | 53.4907 | 105.0247 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 76.3118 | 28.4912 | 678090.9346 | 56.5076 | 56.5076 | 107.0021 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 77.833 | 30.0124 | 714293.9496 | 59.5245 | 59.5245 | 108.9795 | 70 | 70 | 29.1264 | 30 | 69.3
6/30/20XX 7:00:00 AM | 0.29167 | 6 | 72.6 | 65.1 | 71.831 | 84.035 | 12.204 | 60 | 72.6 |  | 72.6 | 78.0551 | 0.1 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 64.165 | 16.3443 | 388995.3495 | 32.4163 | 32.4163 | 91.8253 | 0.2 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 65.7083 | 17.8877 | 425726.8989 | 35.4772 | 35.4772 | 94.4452 | 0.3 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 67.2517 | 19.431 | 462458.4484 | 38.5382 | 38.5382 | 97.0652 | 0.4 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 68.795 | 20.9744 | 499189.9979 | 41.5992 | 41.5992 | 99.6852 | 0.5 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 70.3383 | 22.5177 | 535921.5474 | 44.6601 | 44.6601 | 102.3051 | 0.6 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 71.8817 | 24.0611 | 572653.0968 | 47.7211 | 47.7211 | 104.9251 | 0.7 | 73.02 | 18.02 | 681156 | 56.763 | 56.763 | 73.425 | 25.6044 | 609384.6463 | 50.7821 | 50.7821 | 107.5451 | 0.8 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 74.9684 | 27.1477 | 646116.1958 | 53.843 | 53.843 | 110.165 | 0.9 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 76.5117 | 28.6911 | 682847.7453 | 56.904 | 56.904 | 112.785 | 1 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 78.0551 | 30.2344 | 719579.2947 | 59.9649 | 59.9649 | 115.4049 | 75 | 65 | 29.6265 | 30 | 65.1
6/30/20XX 8:00:00 AM | 0.33333 | 6 | 74.6 | 60.7 | 76.9684 | 90.0655 | 13.0971 | 60 | 74.6 |  | 74.6 | 77.8852 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 64.148 | 16.3274 | 388591.0481 | 32.3826 | 32.3826 | 92.4216 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.6743 | 17.8537 | 424918.2962 | 35.4099 | 35.4099 | 95.6379 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 67.2007 | 19.3801 | 461245.5444 | 38.4371 | 38.4371 | 98.8541 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 68.7271 | 20.9064 | 497572.7925 | 41.4644 | 41.4644 | 102.0704 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 70.2534 | 22.4328 | 533900.0406 | 44.4917 | 44.4917 | 105.2867 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 71.7798 | 23.9591 | 570227.2887 | 47.5189 | 47.5189 | 108.5029 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 73.3061 | 25.4855 | 606554.5368 | 50.5462 | 50.5462 | 111.7192 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 74.8325 | 27.0118 | 642881.7849 | 53.5735 | 53.5735 | 114.9355 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 76.3588 | 28.5382 | 679209.0331 | 56.6008 | 56.6008 | 118.1518 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 77.8852 | 30.0645 | 715536.2812 | 59.628 | 59.628 | 121.368 | 75 | 60 | 30.0899 | 30 | 60.7
6/30/20XX 9:00:00 AM | 0.375 | 6 | 76.8 | 54.5 | 68.9041 | 82.9779 | 14.0738 | 50 | 76.8 |  | 76.8 | 75.2373 | 0.1 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 63.8832 | 16.0626 | 382289.1281 | 31.8574 | 31.8574 | 92.5894 | 0.2 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.1448 | 17.3241 | 412314.4562 | 34.3595 | 34.3595 | 95.9735 | 0.3 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 66.4063 | 18.5857 | 442339.7843 | 36.8616 | 36.8616 | 99.3576 | 0.4 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 67.6679 | 19.8473 | 472365.1123 | 39.3638 | 39.3638 | 102.7418 | 0.5 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 68.9295 | 21.1088 | 502390.4404 | 41.8659 | 41.8659 | 106.1259 | 0.6 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 70.191 | 22.3704 | 532415.7685 | 44.368 | 44.368 | 109.51 | 0.7 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 71.4526 | 23.632 | 562441.0966 | 46.8701 | 46.8701 | 112.8941 | 0.8 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 72.7142 | 24.8935 | 592466.4247 | 49.3722 | 49.3722 | 116.2782 | 0.9 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 73.9757 | 26.1551 | 622491.7528 | 51.8743 | 51.8743 | 119.6623 | 1 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 75.2373 | 27.4167 | 652517.0809 | 54.3764 | 54.3764 | 123.0464 | 75 | 55 | 30.2141 | 30 | 54.5
6/30/20XX 10:00:00 AM | 0.41667 | 6 | 79.6 | 49.7 | 60.3422 | 75.7077 | 15.3655 | 40 | 79.6 |  | 79.6 | 75.2468 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 63.8841 | 16.0635 | 382311.5919 | 31.8593 | 31.8593 | 93.4733 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 65.1467 | 17.326 | 412359.3838 | 34.3633 | 34.3633 | 97.7413 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 66.4092 | 18.5885 | 442407.1757 | 36.8673 | 36.8673 | 102.0093 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 67.6717 | 19.851 | 472454.9677 | 39.3712 | 39.3712 | 106.2772 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 68.9342 | 21.1136 | 502502.7596 | 41.8752 | 41.8752 | 110.5452 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 70.1967 | 22.3761 | 532550.5515 | 44.3792 | 44.3792 | 114.8132 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 71.4592 | 23.6386 | 562598.3434 | 46.8832 | 46.8832 | 119.0812 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 72.7217 | 24.9011 | 592646.1353 | 49.3872 | 49.3872 | 123.3492 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 73.9842 | 26.1636 | 622693.9272 | 51.8912 | 51.8912 | 127.6172 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 75.2468 | 27.4261 | 652741.7192 | 54.3951 | 54.3951 | 131.8851 | 80 | 50 | 30.901 | 30 | 49.7
6/30/20XX 11:00:00 AM | 0.45833 | 6 | 81.8 | 47.9 | 64.8799 | 81.4359 | 16.556 | 40 | 81.8 |  | 81.8 | 77.9591 | 0.1 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 64.1554 | 16.3347 | 388767.0413 | 32.3973 | 32.3973 | 94.7043 | 0.2 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 65.6891 | 17.8685 | 425270.2826 | 35.4392 | 35.4392 | 100.2032 | 0.3 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 67.2229 | 19.4022 | 461773.524 | 38.4811 | 38.4811 | 105.7021 | 0.4 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 68.7566 | 20.936 | 498276.7653 | 41.5231 | 41.5231 | 111.2011 | 0.5 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 70.2904 | 22.4697 | 534780.0066 | 44.565 | 44.565 | 116.7 | 0.6 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 71.8241 | 24.0035 | 571283.2479 | 47.6069 | 47.6069 | 122.1989 | 0.7 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 73.3579 | 25.5372 | 607786.4893 | 50.6489 | 50.6489 | 127.6979 | 0.8 | 80.24 | 25.24 | 954072 | 79.506 | 79.506 | 74.8916 | 27.071 | 644289.7306 | 53.6908 | 53.6908 | 133.1968 | 0.9 | 81.02 | 26.02 | 983556 | 81.963 | 81.963 | 76.4254 | 28.6047 | 680792.9719 | 56.7327 | 56.7327 | 138.6957 | 1 | 81.8 | 26.8 | 1013040 | 84.42 | 84.42 | 77.9591 | 30.1385 | 717296.2132 | 59.7747 | 59.7747 | 144.1947 | 80 | 50 | 31.8651 | 32 | 47.9
6/30/20XX 12:00:00 PM | 0.5 | 6 | 83.4 | 44.1 | 68.3521 | 85.8211 | 17.469 | 40 | 83.4 |  | 83.4 | 75.5144 | 0.1 | 74.94 | 19.94 | 753732 | 62.811 | 62.811 | 63.9109 | 16.0903 | 382948.6426 | 31.9124 | 31.9124 | 94.7234 | 0.2 | 75.88 | 20.88 | 789264 | 65.772 | 65.772 | 65.2002 | 17.3796 | 413633.4851 | 34.4695 | 34.4695 | 100.2415 | 0.3 | 76.82 | 21.82 | 824796 | 68.733 | 68.733 | 66.4895 | 18.6688 | 444318.3277 | 37.0265 | 37.0265 | 105.7595 | 0.4 | 77.76 | 22.76 | 860328 | 71.694 | 71.694 | 67.7787 | 19.9581 | 475003.1702 | 39.5836 | 39.5836 | 111.2776 | 0.5 | 78.7 | 23.7 | 895860 | 74.655 | 74.655 | 69.068 | 21.2474 | 505688.0128 | 42.1407 | 42.1407 | 116.7957 | 0.6 | 79.64 | 24.64 | 931392 | 77.616 | 77.616 | 70.3573 | 22.5367 | 536372.8553 | 44.6977 | 44.6977 | 122.3137 | 0.7 | 80.58 | 25.58 | 966924 | 80.577 | 80.577 | 71.6466 | 23.826 | 567057.6979 | 47.2548 | 47.2548 | 127.8318 | 0.8 | 81.52 | 26.52 | 1002456 | 83.538 | 83.538 | 72.9359 | 25.1152 | 597742.5404 | 49.8119 | 49.8119 | 133.3499 | 0.9 | 82.46 | 27.46 | 1037988 | 86.499 | 86.499 | 74.2251 | 26.4045 | 628427.383 | 52.3689 | 52.3689 | 138.8679 | 1 | 83.4 | 28.4 | 1073520 | 89.46 | 89.46 | 75.5144 | 27.6938 | 659112.2255 | 54.926 | 54.926 | 144.386 | 85 | 45 | 31.8731 | 32 | 44.1
6/30/20XX 1:00:00 PM | 0.54167 | 6 | 84 | 44.6 | 69.6925 | 87.5144 | 17.8219 | 40 | 84 |  | 84 | 77.8905 | 0.1 | 75 | 20 | 756000 | 63 | 63 | 64.1485 | 16.3279 | 388603.785 | 32.3836 | 32.3836 | 95.3836 | 0.2 | 76 | 21 | 793800 | 66.15 | 66.15 | 65.6754 | 17.8548 | 424943.77 | 35.412 | 35.412 | 101.562 | 0.3 | 77 | 22 | 831600 | 69.3 | 69.3 | 67.2023 | 19.3817 | 461283.755 | 38.4403 | 38.4403 | 107.7403 | 0.4 | 78 | 23 | 869400 | 72.45 | 72.45 | 68.7292 | 20.9086 | 497623.74 | 41.4686 | 41.4686 | 113.9186 | 0.5 | 79 | 24 | 907200 | 75.6 | 75.6 | 70.2561 | 22.4355 | 533963.725 | 44.497 | 44.497 | 120.097 | 0.6 | 80 | 25 | 945000 | 78.75 | 78.75 | 71.783 | 23.9623 | 570303.71 | 47.5253 | 47.5253 | 126.2753 | 0.7 | 81 | 26 | 982800 | 81.9 | 81.9 | 73.3099 | 25.4892 | 606643.6951 | 50.5536 | 50.5536 | 132.4536 | 0.8 | 82 | 27 | 1020600 | 85.05 | 85.05 | 74.8368 | 27.0161 | 642983.6801 | 53.582 | 53.582 | 138.632 | 0.9 | 83 | 28 | 1058400 | 88.2 | 88.2 | 76.3636 | 28.543 | 679323.6651 | 56.6103 | 56.6103 | 144.8103 | 1 | 84 | 29 | 1096200 | 91.35 | 91.35 | 77.8905 | 30.0699 | 715663.6501 | 59.6386 | 59.6386 | 150.9886 | 85 | 45 | 32.3932 | 32 | 44.6
6/30/20XX 2:00:00 PM | 0.58333 | 6 | 83.2 | 47.2 | 67.91 | 85.2627 | 17.3526 | 40 | 83.2 |  | 83.2 | 80.4039 | 0.1 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 64.3999 | 16.5792 | 394585.6781 | 32.8821 | 32.8821 | 95.6301 | 0.2 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 66.1781 | 18.3575 | 436907.5561 | 36.409 | 36.409 | 102.055 | 0.3 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 67.9563 | 20.1357 | 479229.4342 | 39.9358 | 39.9358 | 108.4798 | 0.4 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 69.7346 | 21.9139 | 521551.3122 | 43.4626 | 43.4626 | 114.9046 | 0.5 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 71.5128 | 23.6922 | 563873.1903 | 46.9894 | 46.9894 | 121.3294 | 0.6 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 73.291 | 25.4704 | 606195.0683 | 50.5163 | 50.5163 | 127.7543 | 0.7 | 80.44 | 25.44 | 961632 | 80.136 | 80.136 | 75.0692 | 27.2486 | 648516.9464 | 54.0431 | 54.0431 | 134.1791 | 0.8 | 81.36 | 26.36 | 996408 | 83.034 | 83.034 | 76.8475 | 29.0268 | 690838.8245 | 57.5699 | 57.5699 | 140.6039 | 0.9 | 82.28 | 27.28 | 1031184 | 85.932 | 85.932 | 78.6257 | 30.8051 | 733160.7025 | 61.0967 | 61.0967 | 147.0287 | 1 | 83.2 | 28.2 | 1065960 | 88.83 | 88.83 | 80.4039 | 32.5833 | 775482.5806 | 64.6235 | 64.6235 | 153.4535 | 85 | 45 | 32.5919 | 32 | 47.2
6/30/20XX 3:00:00 PM | 0.625 | 6 | 82.9 | 48.3 | 67.2512 | 84.4305 | 17.1793 | 40 | 82.9 |  | 82.9 | 81.5101 | 0.1 | 74.89 | 19.89 | 751842 | 62.6535 | 62.6535 | 64.5105 | 16.6898 | 397218.2541 | 33.1015 | 33.1015 | 95.755 | 0.2 | 75.78 | 20.78 | 785484 | 65.457 | 65.457 | 66.3993 | 18.5787 | 442172.7082 | 36.8477 | 36.8477 | 102.3047 | 0.3 | 76.67 | 21.67 | 819126 | 68.2605 | 68.2605 | 68.2882 | 20.4675 | 487127.1623 | 40.5939 | 40.5939 | 108.8544 | 0.4 | 77.56 | 22.56 | 852768 | 71.064 | 71.064 | 70.177 | 22.3564 | 532081.6163 | 44.3401 | 44.3401 | 115.4041 | 0.5 | 78.45 | 23.45 | 886410 | 73.8675 | 73.8675 | 72.0658 | 24.2452 | 577036.0704 | 48.0863 | 48.0863 | 121.9538 | 0.6 | 79.34 | 24.34 | 920052 | 76.671 | 76.671 | 73.9547 | 26.1341 | 621990.5245 | 51.8325 | 51.8325 | 128.5035 | 0.7 | 80.23 | 25.23 | 953694 | 79.4745 | 79.4745 | 75.8435 | 28.0229 | 666944.9786 | 55.5787 | 55.5787 | 135.0532 | 0.8 | 81.12 | 26.12 | 987336 | 82.278 | 82.278 | 77.7324 | 29.9117 | 711899.4327 | 59.325 | 59.325 | 141.603 | 0.9 | 82.01 | 27.01 | 1020978 | 85.0815 | 85.0815 | 79.6212 | 31.8006 | 756853.8868 | 63.0712 | 63.0712 | 148.1527 | 1 | 82.9 | 27.9 | 1054620 | 87.885 | 87.885 | 81.5101 | 33.6894 | 801808.3408 | 66.8174 | 66.8174 | 154.7024 | 85 | 50 | 32.692 | 32 | 48.3
6/30/20XX 4:00:00 PM | 0.66667 | 6 | 81.9 | 49.5 | 65.0926 | 81.7045 | 16.6119 | 40 | 81.9 |  | 81.9 | 80.8739 | 0.1 | 74.79 | 19.79 | 748062 | 62.3385 | 62.3385 | 64.4469 | 16.6262 | 395704.1709 | 32.9753 | 32.9753 | 95.3138 | 0.2 | 75.58 | 20.58 | 777924 | 64.827 | 64.827 | 66.2721 | 18.4515 | 439144.5419 | 36.5954 | 36.5954 | 101.4224 | 0.3 | 76.37 | 21.37 | 807786 | 67.3155 | 67.3155 | 68.0973 | 20.2767 | 482584.9128 | 40.2154 | 40.2154 | 107.5309 | 0.4 | 77.16 | 22.16 | 837648 | 69.804 | 69.804 | 69.9225 | 22.1019 | 526025.2837 | 43.8354 | 43.8354 | 113.6394 | 0.5 | 77.95 | 22.95 | 867510 | 72.2925 | 72.2925 | 71.7478 | 23.9271 | 569465.6547 | 47.4555 | 47.4555 | 119.748 | 0.6 | 78.74 | 23.74 | 897372 | 74.781 | 74.781 | 73.573 | 25.7524 | 612906.0256 | 51.0755 | 51.0755 | 125.8565 | 0.7 | 79.53 | 24.53 | 927234 | 77.2695 | 77.2695 | 75.3982 | 27.5776 | 656346.3966 | 54.6955 | 54.6955 | 131.965 | 0.8 | 80.32 | 25.32 | 957096 | 79.758 | 79.758 | 77.2234 | 29.4028 | 699786.7675 | 58.3156 | 58.3156 | 138.0736 | 0.9 | 81.11 | 26.11 | 986958 | 82.2465 | 82.2465 | 79.0487 | 31.228 | 743227.1384 | 61.9356 | 61.9356 | 144.1821 | 1 | 81.9 | 26.9 | 1016820 | 84.735 | 84.735 | 80.8739 | 33.0533 | 786667.5094 | 65.5556 | 65.5556 | 150.2906 | 80 | 50 | 32.347 | 32 | 49.5
6/30/20XX 5:00:00 PM | 0.70833 | 6 | 80.1 | 54.6 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 84.2242 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 64.7819 | 16.9613 | 403677.8973 | 33.6398 | 33.6398 | 95.4113 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 66.9421 | 19.1215 | 455091.9947 | 37.9243 | 37.9243 | 101.6173 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 69.1024 | 21.2818 | 506506.092 | 42.2088 | 42.2088 | 107.8233 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 71.2627 | 23.442 | 557920.1894 | 46.4933 | 46.4933 | 114.0293 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 73.4229 | 25.6023 | 609334.2867 | 50.7779 | 50.7779 | 120.2354 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 75.5832 | 27.7625 | 660748.3841 | 55.0624 | 55.0624 | 126.4414 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 77.7434 | 29.9228 | 712162.4814 | 59.3469 | 59.3469 | 132.6474 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 79.9037 | 32.083 | 763576.5788 | 63.6314 | 63.6314 | 138.8534 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 82.0639 | 34.2433 | 814990.6761 | 67.9159 | 67.9159 | 145.0594 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 84.2242 | 36.4036 | 866404.7735 | 72.2004 | 72.2004 | 151.2654 | 80 | 55 | 32.4311 | 32 | 54.6
6/30/20XX 6:00:00 PM | 0.75 | 6 | 79 | 56.9 | 74.2046 | 89.3778 | 15.1731 | 50 | 79 |  | 79 | 84.6741 | 0.1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 64.8269 | 17.0062 | 404748.6393 | 33.7291 | 33.7291 | 95.1541 | 0.2 | 75 | 20 | 756000 | 63 | 63 | 67.0321 | 19.2115 | 457233.4785 | 38.1028 | 38.1028 | 101.1028 | 0.3 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 69.2374 | 21.4167 | 509718.3178 | 42.4765 | 42.4765 | 107.0515 | 0.4 | 76 | 21 | 793800 | 66.15 | 66.15 | 71.4426 | 23.622 | 562203.157 | 46.8503 | 46.8503 | 113.0003 | 0.5 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 73.6479 | 25.8272 | 614687.9963 | 51.224 | 51.224 | 118.949 | 0.6 | 77 | 22 | 831600 | 69.3 | 69.3 | 75.8531 | 28.0325 | 667172.8356 | 55.5977 | 55.5977 | 124.8977 | 0.7 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 78.0583 | 30.2377 | 719657.6748 | 59.9715 | 59.9715 | 130.8465 | 0.8 | 78 | 23 | 869400 | 72.45 | 72.45 | 80.2636 | 32.443 | 772142.5141 | 64.3452 | 64.3452 | 136.7952 | 0.9 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 82.4688 | 34.6482 | 824627.3533 | 68.7189 | 68.7189 | 142.7439 | 1 | 79 | 24 | 907200 | 75.6 | 75.6 | 84.6741 | 36.8535 | 877112.1926 | 73.0927 | 73.0927 | 148.6927 | 80 | 55 | 32.2317 | 32 | 56.9
6/30/20XX 7:00:00 PM | 0.79167 | 6 | 78 | 59.8 | 71.7546 | 86.4193 | 14.6647 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/30/20XX 8:00:00 PM | 0.83333 | 6 | 76.8 | 62.1 | 82.9779 | 97.1205 | 14.1426 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/30/20XX 9:00:00 PM | 0.875 | 6 | 75.9 | 64.9 | 80.4731 | 94.1799 | 13.7068 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/30/20XX 10:00:00 PM | 0.91667 | 6 | 75.4 | 66.1 | 79.1095 | 92.579 | 13.4695 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/30/20XX 11:00:00 PM | 0.95833 | 6 | 74.9 | 65.8 | 77.7654 | 91.0012 | 13.2358 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6/30/20XX 12:00:00 AM | 0 | 7 | 74.1 | 67.2 | 75.6554 | 88.5243 | 12.8688 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/1/20XX 1:00:00 AM | 0.041667 | 7 | 73.9 | 66.7 | 75.1356 | 87.9141 | 12.7785 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/1/20XX 2:00:00 AM | 0.083333 | 7 | 73.1 | 68.3 | 73.0869 | 85.5092 | 12.4223 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/1/20XX 3:00:00 AM | 0.125 | 7 | 72.4 | 70.5 | 83.4515 | 95.6486 | 12.1971 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/1/20XX 4:00:00 AM | 0.16667 | 7 | 71.7 | 71.3 | 81.4366 | 93.3322 | 11.8956 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/1/20XX 5:00:00 AM | 0.20833 | 7 | 71 | 73.6 | 79.4639 | 91.0648 | 11.6009 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/1/20XX 6:00:00 AM | 0.25 | 7 | 71.6 | 74.6 | 81.1522 | 93.0054 | 11.8531 | 70 | 71.6 |  | 71.6 | 86.6047 | 0.1 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 65.0199 | 17.1993 | 409343.4079 | 34.112 | 34.112 | 93.206 | 0.2 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 67.4182 | 19.5976 | 466423.0158 | 38.8686 | 38.8686 | 97.2066 | 0.3 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 69.8165 | 21.9959 | 523502.6238 | 43.6252 | 43.6252 | 101.2072 | 0.4 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 72.2148 | 24.3942 | 580582.2317 | 48.3819 | 48.3819 | 105.2079 | 0.5 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 74.6131 | 26.7925 | 637661.8396 | 53.1385 | 53.1385 | 109.2085 | 0.6 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 77.0114 | 29.1908 | 694741.4475 | 57.8951 | 57.8951 | 113.2091 | 0.7 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 79.4098 | 31.5891 | 751821.0554 | 62.6518 | 62.6518 | 117.2098 | 0.8 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 81.8081 | 33.9874 | 808900.6634 | 67.4084 | 67.4084 | 121.2104 | 0.9 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 84.2064 | 36.3857 | 865980.2713 | 72.165 | 72.165 | 125.211 | 1 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 86.6047 | 38.784 | 923059.8792 | 76.9217 | 76.9217 | 129.2117 | 70 | 75 | 30.7176 | 30 | 74.6
7/1/20XX 7:00:00 AM | 0.29167 | 7 | 73 | 72 | 85.2126 | 97.6734 | 12.4608 | 70 | 73 |  | 73 | 87.7048 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 65.1299 | 17.3093 | 411961.7213 | 34.3301 | 34.3301 | 93.8651 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 67.6383 | 19.8176 | 471659.6426 | 39.305 | 39.305 | 98.525 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 70.1466 | 22.3259 | 531357.564 | 44.2798 | 44.2798 | 103.1848 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 72.6549 | 24.8343 | 591055.4853 | 49.2546 | 49.2546 | 107.8446 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 75.1632 | 27.3426 | 650753.4066 | 54.2295 | 54.2295 | 112.5045 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 77.6715 | 29.8509 | 710451.3279 | 59.2043 | 59.2043 | 117.1643 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 80.1798 | 32.3592 | 770149.2493 | 64.1791 | 64.1791 | 121.8241 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 82.6882 | 34.8675 | 829847.1706 | 69.1539 | 69.1539 | 126.4839 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 85.1965 | 37.3758 | 889545.0919 | 74.1288 | 74.1288 | 131.1438 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 87.7048 | 39.8842 | 949243.0132 | 79.1036 | 79.1036 | 135.8036 | 75 | 70 | 31.2333 | 32 | 72
7/1/20XX 8:00:00 AM | 0.33333 | 7 | 74.9 | 69.6 | 77.7654 | 91.0012 | 13.2358 | 60 | 74.9 |  | 74.9 | 90.4718 | 0.1 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 65.4066 | 17.586 | 418547.1238 | 34.8789 | 34.8789 | 95.0124 | 0.2 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 68.1917 | 20.371 | 484830.4475 | 40.4025 | 40.4025 | 100.8195 | 0.3 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 70.9767 | 23.156 | 551113.7713 | 45.9261 | 45.9261 | 106.6266 | 0.4 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 73.7617 | 25.9411 | 617397.0951 | 51.4498 | 51.4498 | 112.4338 | 0.5 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 76.5467 | 28.7261 | 683680.4189 | 56.9734 | 56.9734 | 118.2409 | 0.6 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 79.3317 | 31.5111 | 749963.7426 | 62.497 | 62.497 | 124.048 | 0.7 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 82.1167 | 34.2961 | 816247.0664 | 68.0206 | 68.0206 | 129.8551 | 0.8 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 84.9017 | 37.0811 | 882530.3902 | 73.5442 | 73.5442 | 135.6622 | 0.9 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 87.6868 | 39.8661 | 948813.714 | 79.0678 | 79.0678 | 141.4693 | 1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 90.4718 | 42.6511 | 1015097.0377 | 84.5914 | 84.5914 | 147.2764 | 75 | 70 | 32.1329 | 32 | 69.6
7/1/20XX 9:00:00 AM | 0.375 | 7 | 76.4 | 66.4 | 81.8567 | 95.8042 | 13.9475 | 60 | 76.4 |  | 76.4 | 90.7831 | 0.1 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 65.4378 | 17.6171 | 419288.026 | 34.9407 | 34.9407 | 95.5467 | 0.2 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 68.2539 | 20.4333 | 486312.252 | 40.526 | 40.526 | 101.888 | 0.3 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 71.0701 | 23.2494 | 553336.478 | 46.1114 | 46.1114 | 108.2294 | 0.4 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 73.8862 | 26.0656 | 620360.7039 | 51.6967 | 51.6967 | 114.5707 | 0.5 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 76.7024 | 28.8817 | 687384.9299 | 57.2821 | 57.2821 | 120.9121 | 0.6 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 79.5185 | 31.6979 | 754409.1559 | 62.8674 | 62.8674 | 127.2534 | 0.7 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 82.3346 | 34.514 | 821433.3819 | 68.4528 | 68.4528 | 133.5948 | 0.8 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 85.1508 | 37.3302 | 888457.6079 | 74.0381 | 74.0381 | 139.9361 | 0.9 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 87.9669 | 40.1463 | 955481.8339 | 79.6235 | 79.6235 | 146.2775 | 1 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 90.7831 | 42.9624 | 1022506.0599 | 85.2088 | 85.2088 | 152.6188 | 75 | 65 | 32.5502 | 32 | 66.4
7/1/20XX 10:00:00 AM | 0.41667 | 7 | 78.2 | 64.8 | 87.0044 | 101.8479 | 14.8435 | 60 | 78.2 |  | 78.2 | 94.1293 | 0.1 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 65.7724 | 17.9518 | 427252.0076 | 35.6043 | 35.6043 | 96.7773 | 0.2 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 68.9232 | 21.1025 | 502240.2152 | 41.8534 | 41.8534 | 104.3494 | 0.3 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 72.0739 | 24.2533 | 577228.4228 | 48.1024 | 48.1024 | 111.9214 | 0.4 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 75.2247 | 27.4041 | 652216.6304 | 54.3514 | 54.3514 | 119.4934 | 0.5 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 78.3755 | 30.5548 | 727204.8381 | 60.6004 | 60.6004 | 127.0654 | 0.6 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 81.5262 | 33.7056 | 802193.0457 | 66.8494 | 66.8494 | 134.6374 | 0.7 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 84.677 | 36.8564 | 877181.2533 | 73.0984 | 73.0984 | 142.2094 | 0.8 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 87.8278 | 40.0071 | 952169.4609 | 79.3475 | 79.3475 | 149.7815 | 0.9 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 90.9785 | 43.1579 | 1027157.6685 | 85.5965 | 85.5965 | 157.3535 | 1 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 94.1293 | 46.3087 | 1102145.8761 | 91.8455 | 91.8455 | 164.9255 | 80 | 65 | 33.5169 | 34 | 64.8
7/1/20XX 11:00:00 AM | 0.45833 | 7 | 80.6 | 59 | 78.2688 | 94.2862 | 16.0174 | 50 | 80.6 |  | 80.6 | 92.6844 | 0.1 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 65.6279 | 17.8073 | 423813.2494 | 35.3178 | 35.3178 | 97.2468 | 0.2 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 68.6342 | 20.8136 | 495362.6989 | 41.2802 | 41.2802 | 105.2882 | 0.3 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 71.6405 | 23.8198 | 566912.1483 | 47.2427 | 47.2427 | 113.3297 | 0.4 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 74.6467 | 26.8261 | 638461.5977 | 53.2051 | 53.2051 | 121.3711 | 0.5 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 77.653 | 29.8324 | 710011.0471 | 59.1676 | 59.1676 | 129.4126 | 0.6 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 80.6593 | 32.8387 | 781560.4966 | 65.13 | 65.13 | 137.454 | 0.7 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 83.6656 | 35.845 | 853109.946 | 71.0925 | 71.0925 | 145.4955 | 0.8 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 86.6719 | 38.8512 | 924659.3954 | 77.0549 | 77.0549 | 153.5369 | 0.9 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 89.6781 | 41.8575 | 996208.8448 | 83.0174 | 83.0174 | 161.5784 | 1 | 80.6 | 25.6 | 967680 | 80.64 | 80.64 | 92.6844 | 44.8638 | 1067758.2943 | 88.9799 | 88.9799 | 169.6199 | 80 | 60 | 33.8807 | 34 | 59
7/1/20XX 12:00:00 PM | 0.5 | 7 | 81.9 | 57.8 | 81.7045 | 98.4363 | 16.7319 | 50 | 81.9 |  | 81.9 | 94.7553 | 0.1 | 74.79 | 19.79 | 748062 | 62.3385 | 62.3385 | 65.835 | 18.0144 | 428742.0181 | 35.7285 | 35.7285 | 98.067 | 0.2 | 75.58 | 20.58 | 777924 | 64.827 | 64.827 | 69.0484 | 21.2277 | 505220.2362 | 42.1017 | 42.1017 | 106.9287 | 0.3 | 76.37 | 21.37 | 807786 | 67.3155 | 67.3155 | 72.2617 | 24.4411 | 581698.4543 | 48.4749 | 48.4749 | 115.7904 | 0.4 | 77.16 | 22.16 | 837648 | 69.804 | 69.804 | 75.4751 | 27.6545 | 658176.6724 | 54.8481 | 54.8481 | 124.6521 | 0.5 | 77.95 | 22.95 | 867510 | 72.2925 | 72.2925 | 78.6885 | 30.8679 | 734654.8904 | 61.2212 | 61.2212 | 133.5137 | 0.6 | 78.74 | 23.74 | 897372 | 74.781 | 74.781 | 81.9019 | 34.0812 | 811133.1085 | 67.5944 | 67.5944 | 142.3754 | 0.7 | 79.53 | 24.53 | 927234 | 77.2695 | 77.2695 | 85.1152 | 37.2946 | 887611.3266 | 73.9676 | 73.9676 | 151.2371 | 0.8 | 80.32 | 25.32 | 957096 | 79.758 | 79.758 | 88.3286 | 40.508 | 964089.5447 | 80.3408 | 80.3408 | 160.0988 | 0.9 | 81.11 | 26.11 | 986958 | 82.2465 | 82.2465 | 91.542 | 43.7213 | 1040567.7628 | 86.714 | 86.714 | 168.9605 | 1 | 81.9 | 26.9 | 1016820 | 84.735 | 84.735 | 94.7553 | 46.9347 | 1117045.9809 | 93.0872 | 93.0872 | 177.8222 | 80 | 60 | 34.5253 | 34 | 57.8
7/1/20XX 1:00:00 PM | 0.54167 | 7 | 82.4 | 57.9 | 83.0584 | 100.072 | 17.0136 | 50 | 82.4 |  | 82.4 | 96.4991 | 0.1 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 66.0094 | 18.1888 | 432892.2815 | 36.0744 | 36.0744 | 98.5704 | 0.2 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 69.3971 | 21.5765 | 513520.7631 | 42.7934 | 42.7934 | 107.9354 | 0.3 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 72.7849 | 24.9643 | 594149.2446 | 49.5124 | 49.5124 | 117.3004 | 0.4 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 76.1726 | 28.352 | 674777.7262 | 56.2315 | 56.2315 | 126.6655 | 0.5 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 79.5604 | 31.7398 | 755406.2077 | 62.9505 | 62.9505 | 136.0305 | 0.6 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 82.9481 | 35.1275 | 836034.6892 | 69.6696 | 69.6696 | 145.3956 | 0.7 | 79.88 | 24.88 | 940464 | 78.372 | 78.372 | 86.3359 | 38.5153 | 916663.1708 | 76.3886 | 76.3886 | 154.7606 | 0.8 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 89.7236 | 41.903 | 997291.6523 | 83.1076 | 83.1076 | 164.1256 | 0.9 | 81.56 | 26.56 | 1003968 | 83.664 | 83.664 | 93.1114 | 45.2908 | 1077920.1339 | 89.8267 | 89.8267 | 173.4907 | 1 | 82.4 | 27.4 | 1035720 | 86.31 | 86.31 | 96.4991 | 48.6785 | 1158548.6154 | 96.5457 | 96.5457 | 182.8557 | 80 | 60 | 34.922 | 34 | 57.9
7/1/20XX 2:00:00 PM | 0.58333 | 7 | 82 | 59 | 81.9738 | 98.7617 | 16.7879 | 50 | 82 |  | 82 | 97.0829 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 66.0678 | 18.2471 | 434281.6721 | 36.1901 | 36.1901 | 98.5601 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 69.5139 | 21.6933 | 516299.5442 | 43.025 | 43.025 | 107.915 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 72.96 | 25.1394 | 598317.4163 | 49.8598 | 49.8598 | 117.2698 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 76.4061 | 28.5855 | 680335.2884 | 56.6946 | 56.6946 | 126.6246 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 79.8523 | 32.0316 | 762353.1605 | 63.5294 | 63.5294 | 135.9794 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 83.2984 | 35.4778 | 844371.0326 | 70.3643 | 70.3643 | 145.3343 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 86.7445 | 38.9239 | 926388.9047 | 77.1991 | 77.1991 | 154.6891 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 90.1907 | 42.37 | 1008406.7768 | 84.0339 | 84.0339 | 164.0439 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 93.6368 | 45.8162 | 1090424.6489 | 90.8687 | 90.8687 | 173.3987 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 97.0829 | 49.2623 | 1172442.521 | 97.7035 | 97.7035 | 182.7535 | 80 | 60 | 34.9152 | 34 | 59
7/1/20XX 3:00:00 PM | 0.625 | 7 | 81.9 | 59.8 | 81.7045 | 98.4363 | 16.7319 | 50 | 81.9 |  | 81.9 | 98.1017 | 0.1 | 74.79 | 19.79 | 748062 | 62.3385 | 62.3385 | 66.1696 | 18.349 | 436706.3865 | 36.3922 | 36.3922 | 98.7307 | 0.2 | 75.58 | 20.58 | 777924 | 64.827 | 64.827 | 69.7176 | 21.897 | 521148.9729 | 43.4291 | 43.4291 | 108.2561 | 0.3 | 76.37 | 21.37 | 807786 | 67.3155 | 67.3155 | 73.2657 | 25.445 | 605591.5594 | 50.466 | 50.466 | 117.7815 | 0.4 | 77.16 | 22.16 | 837648 | 69.804 | 69.804 | 76.8137 | 28.993 | 690034.1458 | 57.5028 | 57.5028 | 127.3068 | 0.5 | 77.95 | 22.95 | 867510 | 72.2925 | 72.2925 | 80.3617 | 32.541 | 774476.7323 | 64.5397 | 64.5397 | 136.8322 | 0.6 | 78.74 | 23.74 | 897372 | 74.781 | 74.781 | 83.9097 | 36.089 | 858919.3188 | 71.5766 | 71.5766 | 146.3576 | 0.7 | 79.53 | 24.53 | 927234 | 77.2695 | 77.2695 | 87.4577 | 39.6371 | 943361.9052 | 78.6135 | 78.6135 | 155.883 | 0.8 | 80.32 | 25.32 | 957096 | 79.758 | 79.758 | 91.0057 | 43.1851 | 1027804.4917 | 85.6504 | 85.6504 | 165.4084 | 0.9 | 81.11 | 26.11 | 986958 | 82.2465 | 82.2465 | 94.5537 | 46.7331 | 1112247.0781 | 92.6873 | 92.6873 | 174.9338 | 1 | 81.9 | 26.9 | 1016820 | 84.735 | 84.735 | 98.1017 | 50.2811 | 1196689.6646 | 99.7241 | 99.7241 | 184.4591 | 80 | 60 | 35.0504 | 36 | 59.8
7/1/20XX 4:00:00 PM | 0.66667 | 7 | 80.3 | 62.8 | 93.3492 | 109.2977 | 15.9485 | 60 | 80.3 |  | 80.3 | 97.8148 | 0.1 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 66.1409 | 18.3203 | 436023.5398 | 36.3353 | 36.3353 | 98.1698 | 0.2 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 69.6603 | 21.8396 | 519783.2796 | 43.3153 | 43.3153 | 107.1343 | 0.3 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 73.1796 | 25.359 | 603543.0194 | 50.2953 | 50.2953 | 116.0988 | 0.4 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 76.6989 | 28.8783 | 687302.7591 | 57.2752 | 57.2752 | 125.0632 | 0.5 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 80.2182 | 32.3976 | 771062.4989 | 64.2552 | 64.2552 | 134.0277 | 0.6 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 83.7375 | 35.9169 | 854822.2387 | 71.2352 | 71.2352 | 142.9922 | 0.7 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 87.2568 | 39.4362 | 938581.9785 | 78.2152 | 78.2152 | 151.9567 | 0.8 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 90.7762 | 42.9555 | 1022341.7183 | 85.1951 | 85.1951 | 160.9211 | 0.9 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 94.2955 | 46.4749 | 1106101.4581 | 92.1751 | 92.1751 | 169.8856 | 1 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 97.8148 | 49.9942 | 1189861.1978 | 99.1551 | 99.1551 | 178.8501 | 80 | 65 | 34.6115 | 34 | 62.8
7/1/20XX 5:00:00 PM | 0.70833 | 7 | 79.5 | 61.9 | 90.8883 | 106.4082 | 15.5199 | 60 | 79.5 |  | 79.5 | 93.8371 | 0.1 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 65.7432 | 17.9225 | 426556.5439 | 35.5464 | 35.5464 | 97.1289 | 0.2 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 68.8647 | 21.0441 | 500849.2877 | 41.7374 | 41.7374 | 105.0524 | 0.3 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 71.9863 | 24.1656 | 575142.0316 | 47.9285 | 47.9285 | 112.976 | 0.4 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 75.1078 | 27.2872 | 649434.7754 | 54.1196 | 54.1196 | 120.8996 | 0.5 | 76.75 | 21.75 | 822150 | 68.5125 | 68.5125 | 78.2294 | 30.4087 | 723727.5193 | 60.3106 | 60.3106 | 128.8231 | 0.6 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 81.3509 | 33.5303 | 798020.2631 | 66.5017 | 66.5017 | 136.7467 | 0.7 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 84.4724 | 36.6518 | 872313.007 | 72.6928 | 72.6928 | 144.6703 | 0.8 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 87.594 | 39.7734 | 946605.7508 | 78.8838 | 78.8838 | 152.5938 | 0.9 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 90.7155 | 42.8949 | 1020898.4947 | 85.0749 | 85.0749 | 160.5174 | 1 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 93.8371 | 46.0164 | 1095191.2386 | 91.2659 | 91.2659 | 168.4409 | 80 | 60 | 33.7909 | 34 | 61.9
7/1/20XX 6:00:00 PM | 0.75 | 7 | 79.2 | 61.5 | 89.9794 | 105.341 | 15.3616 | 60 | 79.2 |  | 79.2 | 92.2837 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 65.5878 | 17.7672 | 422859.474 | 35.2383 | 35.2383 | 96.7263 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 68.554 | 20.7334 | 493455.148 | 41.1213 | 41.1213 | 104.2473 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 71.5202 | 23.6996 | 564050.822 | 47.0042 | 47.0042 | 111.7682 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 74.4865 | 26.6658 | 634646.496 | 52.8872 | 52.8872 | 119.2892 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 77.4527 | 29.632 | 705242.17 | 58.7702 | 58.7702 | 126.8102 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 80.4189 | 32.5982 | 775837.844 | 64.6532 | 64.6532 | 134.3312 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 83.3851 | 35.5644 | 846433.518 | 70.5361 | 70.5361 | 141.8521 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 86.3513 | 38.5306 | 917029.192 | 76.4191 | 76.4191 | 149.3731 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 89.3175 | 41.4968 | 987624.866 | 82.3021 | 82.3021 | 156.8941 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 92.2837 | 44.463 | 1058220.54 | 88.185 | 88.185 | 164.415 | 80 | 60 | 33.4736 | 34 | 61.5
7/1/20XX 7:00:00 PM | 0.79167 | 7 | 77.9 | 63.9 | 86.1281 | 100.819 | 14.691 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/1/20XX 8:00:00 PM | 0.83333 | 7 | 76.7 | 64.2 | 82.6964 | 96.79 | 14.0936 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/1/20XX 9:00:00 PM | 0.875 | 7 | 75.7 | 66.5 | 79.9253 | 93.5368 | 13.6115 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/1/20XX 10:00:00 PM | 0.91667 | 7 | 74.7 | 68.5 | 77.2333 | 90.3765 | 13.1432 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/1/20XX 11:00:00 PM | 0.95833 | 7 | 74.3 | 69 | 76.1783 | 89.138 | 12.9597 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/1/20XX 12:00:00 AM | 0 | 1 | 73.6 | 69.6 | 74.3617 | 87.0056 | 12.6439 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/2/20XX 1:00:00 AM | 0.041667 | 1 | 73.1 | 70.6 | 85.5092 | 98.0145 | 12.5053 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/2/20XX 2:00:00 AM | 0.083333 | 1 | 72.1 | 72.7 | 82.5828 | 94.6498 | 12.0671 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/2/20XX 3:00:00 AM | 0.125 | 1 | 71.6 | 73.2 | 81.1522 | 93.0054 | 11.8531 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/2/20XX 4:00:00 AM | 0.16667 | 1 | 70.7 | 74.9 | 78.6313 | 90.1079 | 11.4766 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/2/20XX 5:00:00 AM | 0.20833 | 1 | 70.4 | 76.2 | 77.8062 | 89.1597 | 11.3535 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/2/20XX 6:00:00 AM | 0.25 | 1 | 71.2 | 74.7 | 80.0233 | 91.7077 | 11.6844 | 70 | 71.2 |  | 71.2 | 85.515 | 0.1 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 64.911 | 17.0903 | 406749.9178 | 33.8958 | 33.8958 | 92.8638 | 0.2 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 67.2003 | 19.3797 | 461236.0357 | 38.4363 | 38.4363 | 96.5223 | 0.3 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 69.4896 | 21.669 | 515722.1535 | 42.9768 | 42.9768 | 100.1808 | 0.4 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 71.779 | 23.9583 | 570208.2714 | 47.5174 | 47.5174 | 103.8394 | 0.5 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 74.0683 | 26.2477 | 624694.3892 | 52.0579 | 52.0579 | 107.4979 | 0.6 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 76.3576 | 28.537 | 679180.5071 | 56.5984 | 56.5984 | 111.1564 | 0.7 | 72.04 | 17.04 | 644112 | 53.676 | 53.676 | 78.647 | 30.8263 | 733666.6249 | 61.1389 | 61.1389 | 114.8149 | 0.8 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 80.9363 | 33.1157 | 788152.7428 | 65.6794 | 65.6794 | 118.4734 | 0.9 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 83.2256 | 35.405 | 842638.8606 | 70.2199 | 70.2199 | 122.1319 | 1 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 85.515 | 37.6943 | 897124.9784 | 74.7604 | 74.7604 | 125.7904 | 70 | 75 | 30.4492 | 30 | 74.7
7/2/20XX 7:00:00 AM | 0.29167 | 1 | 72.4 | 71.9 | 83.4515 | 95.6486 | 12.1971 | 70 | 72.4 |  | 72.4 | 85.769 | 0.1 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 64.9364 | 17.1157 | 407354.4222 | 33.9462 | 33.9462 | 93.2922 | 0.2 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 67.2511 | 19.4305 | 462445.0445 | 38.5371 | 38.5371 | 97.3791 | 0.3 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 69.5658 | 21.7452 | 517535.6667 | 43.128 | 43.128 | 101.466 | 0.4 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 71.8806 | 24.0599 | 572626.2889 | 47.7189 | 47.7189 | 105.5529 | 0.5 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 74.1953 | 26.3747 | 627716.9112 | 52.3097 | 52.3097 | 109.6397 | 0.6 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 76.51 | 28.6894 | 682807.5334 | 56.9006 | 56.9006 | 113.7266 | 0.7 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 78.8248 | 31.0041 | 737898.1556 | 61.4915 | 61.4915 | 117.8135 | 0.8 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 81.1395 | 33.3189 | 792988.7779 | 66.0824 | 66.0824 | 121.9004 | 0.9 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 83.4542 | 35.6336 | 848079.4001 | 70.6733 | 70.6733 | 125.9873 | 1 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 85.769 | 37.9483 | 903170.0223 | 75.2642 | 75.2642 | 130.0742 | 70 | 70 | 30.7834 | 30 | 71.9
7/2/20XX 8:00:00 AM | 0.33333 | 1 | 74.5 | 66.3 | 76.7042 | 89.7555 | 13.0512 | 60 | 74.5 |  | 74.5 | 84.9265 | 0.1 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 64.8521 | 17.0315 | 405349.4083 | 33.7791 | 33.7791 | 93.7866 | 0.2 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 67.0826 | 19.262 | 458435.0166 | 38.2029 | 38.2029 | 98.3679 | 0.3 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 69.3131 | 21.4925 | 511520.6248 | 42.6267 | 42.6267 | 102.9492 | 0.4 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 71.5436 | 23.723 | 564606.2331 | 47.0505 | 47.0505 | 107.5305 | 0.5 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 73.7741 | 25.9534 | 617691.8414 | 51.4743 | 51.4743 | 112.1118 | 0.6 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 76.0046 | 28.1839 | 670777.4497 | 55.8981 | 55.8981 | 116.6931 | 0.7 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 78.235 | 30.4144 | 723863.058 | 60.3219 | 60.3219 | 121.2744 | 0.8 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 80.4655 | 32.6449 | 776948.6663 | 64.7457 | 64.7457 | 125.8557 | 0.9 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 82.696 | 34.8754 | 830034.2745 | 69.1695 | 69.1695 | 130.437 | 1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 84.9265 | 37.1059 | 883119.8828 | 73.5933 | 73.5933 | 135.0183 | 75 | 65 | 31.167 | 32 | 66.3
7/2/20XX 9:00:00 AM | 0.375 | 1 | 76.3 | 62.8 | 81.5784 | 95.4774 | 13.8991 | 60 | 76.3 |  | 76.3 | 85.4701 | 0.1 | 74.23 | 19.23 | 726894 | 60.5745 | 60.5745 | 64.9065 | 17.0858 | 406643.1743 | 33.8869 | 33.8869 | 94.4614 | 0.2 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 67.1913 | 19.3707 | 461022.5487 | 38.4185 | 38.4185 | 99.7175 | 0.3 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 69.4762 | 21.6555 | 515401.923 | 42.9502 | 42.9502 | 104.9737 | 0.4 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 71.761 | 23.9404 | 569781.2973 | 47.4818 | 47.4818 | 110.2298 | 0.5 | 75.15 | 20.15 | 761670 | 63.4725 | 63.4725 | 74.0459 | 26.2252 | 624160.6717 | 52.0134 | 52.0134 | 115.4859 | 0.6 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 76.3307 | 28.5101 | 678540.046 | 56.545 | 56.545 | 120.742 | 0.7 | 75.61 | 20.61 | 779058 | 64.9215 | 64.9215 | 78.6156 | 30.7949 | 732919.4203 | 61.0766 | 61.0766 | 125.9981 | 0.8 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 80.9004 | 33.0798 | 787298.7947 | 65.6082 | 65.6082 | 131.2542 | 0.9 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 83.1853 | 35.3646 | 841678.169 | 70.1398 | 70.1398 | 136.5103 | 1 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 85.4701 | 37.6495 | 896057.5433 | 74.6715 | 74.6715 | 141.7665 | 75 | 65 | 31.6938 | 32 | 62.8
7/2/20XX 10:00:00 AM | 0.41667 | 1 | 78.6 | 57.8 | 73.2164 | 88.1844 | 14.968 | 50 | 78.6 |  | 78.6 | 84.8915 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 64.8486 | 17.028 | 405265.9691 | 33.7722 | 33.7722 | 95.0712 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 67.0756 | 19.255 | 458268.1382 | 38.189 | 38.189 | 100.937 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 69.3026 | 21.4819 | 511270.3074 | 42.6059 | 42.6059 | 106.8029 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 71.5296 | 23.7089 | 564272.4765 | 47.0227 | 47.0227 | 112.6687 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 73.7565 | 25.9359 | 617274.6456 | 51.4396 | 51.4396 | 118.5346 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 75.9835 | 28.1629 | 670276.8147 | 55.8564 | 55.8564 | 124.4004 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 78.2105 | 30.3899 | 723278.9839 | 60.2732 | 60.2732 | 130.2662 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 80.4375 | 32.6169 | 776281.153 | 64.6901 | 64.6901 | 136.1321 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 82.6645 | 34.8438 | 829283.3221 | 69.1069 | 69.1069 | 141.9979 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 84.8915 | 37.0708 | 882285.4912 | 73.5238 | 73.5238 | 147.8638 | 80 | 60 | 32.1676 | 32 | 57.8
7/2/20XX 11:00:00 AM | 0.45833 | 1 | 80.3 | 55.4 | 77.4931 | 93.3492 | 15.8561 | 50 | 80.3 |  | 80.3 | 86.0554 | 0.1 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 64.965 | 17.1444 | 408036.156 | 34.003 | 34.003 | 95.8375 | 0.2 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 67.3084 | 19.4878 | 463808.5119 | 38.6507 | 38.6507 | 102.4697 | 0.3 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 69.6518 | 21.8311 | 519580.8679 | 43.2984 | 43.2984 | 109.1019 | 0.4 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 71.9951 | 24.1745 | 575353.2238 | 47.9461 | 47.9461 | 115.7341 | 0.5 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 74.3385 | 26.5179 | 631125.5798 | 52.5938 | 52.5938 | 122.3663 | 0.6 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 76.6819 | 28.8613 | 686897.9358 | 57.2415 | 57.2415 | 128.9985 | 0.7 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 79.0253 | 31.2046 | 742670.2917 | 61.8892 | 61.8892 | 135.6307 | 0.8 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 81.3686 | 33.548 | 798442.6477 | 66.5369 | 66.5369 | 142.2629 | 0.9 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 83.712 | 35.8914 | 854215.0036 | 71.1846 | 71.1846 | 148.8951 | 1 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 86.0554 | 38.2348 | 909987.3596 | 75.8323 | 75.8323 | 155.5273 | 80 | 55 | 32.7673 | 32 | 55.4
7/2/20XX 12:00:00 PM | 0.5 | 1 | 81.6 | 53 | 80.9009 | 97.4655 | 16.5647 | 50 | 81.6 |  | 81.6 | 85.8703 | 0.1 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 64.9465 | 17.1259 | 407595.523 | 33.9663 | 33.9663 | 96.2103 | 0.2 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 67.2714 | 19.4507 | 462927.2459 | 38.5773 | 38.5773 | 103.2153 | 0.3 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 69.5962 | 21.7756 | 518258.9689 | 43.1882 | 43.1882 | 110.2202 | 0.4 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 71.9211 | 24.1004 | 573590.6918 | 47.7992 | 47.7992 | 117.2252 | 0.5 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 74.2459 | 26.4253 | 628922.4148 | 52.4102 | 52.4102 | 124.2302 | 0.6 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 76.5708 | 28.7502 | 684254.1378 | 57.0212 | 57.0212 | 131.2352 | 0.7 | 79.32 | 24.32 | 919296 | 76.608 | 76.608 | 78.8957 | 31.075 | 739585.8607 | 61.6322 | 61.6322 | 138.2402 | 0.8 | 80.08 | 25.08 | 948024 | 79.002 | 79.002 | 81.2205 | 33.3999 | 794917.5837 | 66.2431 | 66.2431 | 145.2451 | 0.9 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 83.5454 | 35.7248 | 850249.3067 | 70.8541 | 70.8541 | 152.2501 | 1 | 81.6 | 26.6 | 1005480 | 83.79 | 83.79 | 85.8703 | 38.0496 | 905581.0296 | 75.4651 | 75.4651 | 159.2551 | 80 | 55 | 33.0574 | 34 | 53
7/2/20XX 1:00:00 PM | 0.54167 | 1 | 83.1 | 50.6 | 84.9846 | 102.3992 | 17.4147 | 50 | 83.1 |  | 83.1 | 86.0294 | 0.1 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 64.9624 | 17.1418 | 407974.3809 | 33.9979 | 33.9979 | 96.7144 | 0.2 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 67.3032 | 19.4826 | 463684.9618 | 38.6404 | 38.6404 | 104.2234 | 0.3 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 69.644 | 21.8233 | 519395.5427 | 43.283 | 43.283 | 111.7325 | 0.4 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 71.9848 | 24.1641 | 575106.1235 | 47.9255 | 47.9255 | 119.2415 | 0.5 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 74.3255 | 26.5049 | 630816.7044 | 52.5681 | 52.5681 | 126.7506 | 0.6 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 76.6663 | 28.8457 | 686527.2853 | 57.2106 | 57.2106 | 134.2596 | 0.7 | 80.37 | 25.37 | 958986 | 79.9155 | 79.9155 | 79.0071 | 31.1865 | 742237.8662 | 61.8532 | 61.8532 | 141.7687 | 0.8 | 81.28 | 26.28 | 993384 | 82.782 | 82.782 | 81.3479 | 33.5272 | 797948.4471 | 66.4957 | 66.4957 | 149.2777 | 0.9 | 82.19 | 27.19 | 1027782 | 85.6485 | 85.6485 | 83.6887 | 35.868 | 853659.028 | 71.1383 | 71.1383 | 156.7868 | 1 | 83.1 | 28.1 | 1062180 | 88.515 | 88.515 | 86.0294 | 38.2088 | 909369.6089 | 75.7808 | 75.7808 | 164.2958 | 85 | 50 | 33.4506 | 34 | 50.6
7/2/20XX 2:00:00 PM | 0.58333 | 1 | 81.7 | 53.9 | 81.168 | 97.7883 | 16.6202 | 50 | 81.7 |  | 81.7 | 87.6499 | 0.1 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 65.1245 | 17.3038 | 411831.0859 | 34.3193 | 34.3193 | 96.5948 | 0.2 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 67.6273 | 19.8067 | 471398.3719 | 39.2832 | 39.2832 | 103.9842 | 0.3 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 70.1301 | 22.3095 | 530965.6578 | 44.2471 | 44.2471 | 111.3736 | 0.4 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 72.6329 | 24.8123 | 590532.9438 | 49.2111 | 49.2111 | 118.7631 | 0.5 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 75.1358 | 27.3151 | 650100.2297 | 54.175 | 54.175 | 126.1525 | 0.6 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 77.6386 | 29.818 | 709667.5156 | 59.139 | 59.139 | 133.542 | 0.7 | 79.39 | 24.39 | 921942 | 76.8285 | 76.8285 | 80.1414 | 32.3208 | 769234.8016 | 64.1029 | 64.1029 | 140.9314 | 0.8 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 82.6442 | 34.8236 | 828802.0875 | 69.0668 | 69.0668 | 148.3208 | 0.9 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 85.1471 | 37.3264 | 888369.3735 | 74.0308 | 74.0308 | 155.7103 | 1 | 81.7 | 26.7 | 1009260 | 84.105 | 84.105 | 87.6499 | 39.8293 | 947936.6594 | 78.9947 | 78.9947 | 163.0997 | 80 | 55 | 33.3612 | 34 | 53.9
7/2/20XX 3:00:00 PM | 0.625 | 1 | 81.7 | 51.7 | 81.168 | 97.7883 | 16.6202 | 50 | 81.7 |  | 81.7 | 83.9934 | 0.1 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 64.7588 | 16.9382 | 403128.7239 | 33.5941 | 33.5941 | 95.8696 | 0.2 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 66.896 | 19.0754 | 453993.6478 | 37.8328 | 37.8328 | 102.5338 | 0.3 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 69.0332 | 21.2125 | 504858.5717 | 42.0715 | 42.0715 | 109.198 | 0.4 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 71.1704 | 23.3497 | 555723.4956 | 46.3103 | 46.3103 | 115.8623 | 0.5 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 73.3075 | 25.4869 | 606588.4195 | 50.549 | 50.549 | 122.5265 | 0.6 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 75.4447 | 27.6241 | 657453.3434 | 54.7878 | 54.7878 | 129.1908 | 0.7 | 79.39 | 24.39 | 921942 | 76.8285 | 76.8285 | 77.5819 | 29.7613 | 708318.2673 | 59.0265 | 59.0265 | 135.855 | 0.8 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 79.7191 | 31.8985 | 759183.1911 | 63.2653 | 63.2653 | 142.5193 | 0.9 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 81.8563 | 34.0356 | 810048.115 | 67.504 | 67.504 | 149.1835 | 1 | 81.7 | 26.7 | 1009260 | 84.105 | 84.105 | 83.9934 | 36.1728 | 860913.0389 | 71.7428 | 71.7428 | 155.8478 | 80 | 50 | 32.7874 | 32 | 51.7
7/2/20XX 4:00:00 PM | 0.66667 | 1 | 80.7 | 55.5 | 78.5288 | 94.6002 | 16.0714 | 50 | 80.7 |  | 80.7 | 87.3681 | 0.1 | 74.67 | 19.67 | 743526 | 61.9605 | 61.9605 | 65.0963 | 17.2756 | 411160.3184 | 34.2634 | 34.2634 | 96.2239 | 0.2 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 67.5709 | 19.7503 | 470056.8368 | 39.1714 | 39.1714 | 103.2424 | 0.3 | 76.01 | 21.01 | 794178 | 66.1815 | 66.1815 | 70.0456 | 22.2249 | 528953.3552 | 44.0794 | 44.0794 | 110.2609 | 0.4 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 72.5202 | 24.6996 | 587849.8736 | 48.9875 | 48.9875 | 117.2795 | 0.5 | 77.35 | 22.35 | 844830 | 70.4025 | 70.4025 | 74.9949 | 27.1742 | 646746.392 | 53.8955 | 53.8955 | 124.298 | 0.6 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 77.4695 | 29.6489 | 705642.9104 | 58.8036 | 58.8036 | 131.3166 | 0.7 | 78.69 | 23.69 | 895482 | 74.6235 | 74.6235 | 79.9441 | 32.1235 | 764539.4288 | 63.7116 | 63.7116 | 138.3351 | 0.8 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 82.4188 | 34.5981 | 823435.9472 | 68.6197 | 68.6197 | 145.3537 | 0.9 | 80.03 | 25.03 | 946134 | 78.8445 | 78.8445 | 84.8934 | 37.0728 | 882332.4656 | 73.5277 | 73.5277 | 152.3722 | 1 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 87.3681 | 39.5474 | 941228.984 | 78.4357 | 78.4357 | 159.3907 | 80 | 55 | 33.0714 | 34 | 55.5
7/2/20XX 5:00:00 PM | 0.70833 | 1 | 79.7 | 57.4 | 75.9607 | 91.4984 | 15.5378 | 50 | 79.7 |  | 79.7 | 87.4586 | 0.1 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 65.1053 | 17.2847 | 411375.8045 | 34.2813 | 34.2813 | 95.9268 | 0.2 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 67.589 | 19.7684 | 470487.809 | 39.2073 | 39.2073 | 102.6483 | 0.3 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 70.0727 | 22.2521 | 529599.8135 | 44.1333 | 44.1333 | 109.3698 | 0.4 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 72.5564 | 24.7358 | 588711.818 | 49.0593 | 49.0593 | 116.0913 | 0.5 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 75.0401 | 27.2195 | 647823.8226 | 53.9853 | 53.9853 | 122.8128 | 0.6 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 77.5238 | 29.7032 | 706935.8271 | 58.9113 | 58.9113 | 129.5343 | 0.7 | 77.99 | 22.99 | 869022 | 72.4185 | 72.4185 | 80.0075 | 32.1869 | 766047.8316 | 63.8373 | 63.8373 | 136.2558 | 0.8 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 82.4912 | 34.6706 | 825159.8361 | 68.7633 | 68.7633 | 142.9773 | 0.9 | 79.13 | 24.13 | 912114 | 76.0095 | 76.0095 | 84.9749 | 37.1543 | 884271.8406 | 73.6893 | 73.6893 | 149.6988 | 1 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 87.4586 | 39.638 | 943383.8451 | 78.6153 | 78.6153 | 156.4203 | 80 | 55 | 32.8401 | 32 | 57.4
7/2/20XX 6:00:00 PM | 0.75 | 1 | 78.3 | 59.7 | 72.4824 | 87.2982 | 14.8157 | 50 | 78.3 |  | 78.3 | 86.8537 | 0.1 | 74.43 | 19.43 | 734454 | 61.2045 | 61.2045 | 65.0448 | 17.2242 | 409936.0777 | 34.1613 | 34.1613 | 95.3658 | 0.2 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 67.468 | 19.6474 | 467608.3553 | 38.9674 | 38.9674 | 101.5264 | 0.3 | 75.29 | 20.29 | 766962 | 63.9135 | 63.9135 | 69.8912 | 22.0706 | 525280.633 | 43.7734 | 43.7734 | 107.6869 | 0.4 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 72.3145 | 24.4938 | 582952.9106 | 48.5794 | 48.5794 | 113.8474 | 0.5 | 76.15 | 21.15 | 799470 | 66.6225 | 66.6225 | 74.7377 | 26.917 | 640625.1883 | 53.3854 | 53.3854 | 120.0079 | 0.6 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 77.1609 | 29.3402 | 698297.4659 | 58.1915 | 58.1915 | 126.1685 | 0.7 | 77.01 | 22.01 | 831978 | 69.3315 | 69.3315 | 79.5841 | 31.7634 | 755969.7436 | 62.9975 | 62.9975 | 132.329 | 0.8 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 82.0073 | 34.1866 | 813642.0213 | 67.8035 | 67.8035 | 138.4895 | 0.9 | 77.87 | 22.87 | 864486 | 72.0405 | 72.0405 | 84.4305 | 36.6098 | 871314.2989 | 72.6095 | 72.6095 | 144.65 | 1 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 86.8537 | 39.033 | 928986.5766 | 77.4155 | 77.4155 | 150.8105 | 80 | 60 | 32.4015 | 32 | 59.7
7/2/20XX 7:00:00 PM | 0.79167 | 1 | 77.1 | 61.7 | 83.8273 | 98.1177 | 14.2905 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/2/20XX 8:00:00 PM | 0.83333 | 1 | 76.1 | 63.1 | 81.0242 | 94.8268 | 13.8027 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/2/20XX 9:00:00 PM | 0.875 | 1 | 75.5 | 63.9 | 79.3806 | 92.8973 | 13.5167 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/2/20XX 10:00:00 PM | 0.91667 | 1 | 74.8 | 66.5 | 77.499 | 90.6884 | 13.1894 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/2/20XX 11:00:00 PM | 0.95833 | 1 | 74.4 | 67.3 | 76.4409 | 89.4463 | 13.0054 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/2/20XX 12:00:00 AM | 0 | 2 | 73.4 | 69.4 | 73.8495 | 86.4044 | 12.5549 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/3/20XX 1:00:00 AM | 0.041667 | 2 | 72.8 | 70.8 | 84.6221 | 96.9944 | 12.3723 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/3/20XX 2:00:00 AM | 0.083333 | 2 | 71.8 | 71.8 | 81.7218 | 93.6601 | 11.9383 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/3/20XX 3:00:00 AM | 0.125 | 2 | 71.7 | 72.2 | 81.4366 | 93.3322 | 11.8956 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/3/20XX 4:00:00 AM | 0.16667 | 2 | 71.1 | 72.9 | 79.7432 | 91.3858 | 11.6426 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/3/20XX 5:00:00 AM | 0.20833 | 2 | 70.5 | 74.5 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/3/20XX 6:00:00 AM | 0.25 | 2 | 71.7 | 73.2 | 81.4366 | 93.3322 | 11.8956 | 70 | 71.7 |  | 71.7 | 85.2432 | 0.1 | 73.77 | 18.77 | 709506 | 59.1255 | 59.1255 | 64.8838 | 17.0632 | 406103.1525 | 33.8419 | 33.8419 | 92.9674 | 0.2 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 67.1459 | 19.3253 | 459942.5049 | 38.3285 | 38.3285 | 96.7295 | 0.3 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 69.4081 | 21.5875 | 513781.8574 | 42.8152 | 42.8152 | 100.4917 | 0.4 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 71.6703 | 23.8496 | 567621.2099 | 47.3018 | 47.3018 | 104.2538 | 0.5 | 72.85 | 17.85 | 674730 | 56.2275 | 56.2275 | 73.9324 | 26.1118 | 621460.5624 | 51.7884 | 51.7884 | 108.0159 | 0.6 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 76.1946 | 28.3739 | 675299.9148 | 56.275 | 56.275 | 111.778 | 0.7 | 72.39 | 17.39 | 657342 | 54.7785 | 54.7785 | 78.4567 | 30.6361 | 729139.2673 | 60.7616 | 60.7616 | 115.5401 | 0.8 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 80.7189 | 32.8983 | 782978.6198 | 65.2482 | 65.2482 | 119.3022 | 0.9 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 82.9811 | 35.1604 | 836817.9722 | 69.7348 | 69.7348 | 123.0643 | 1 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 85.2432 | 37.4226 | 890657.3247 | 74.2214 | 74.2214 | 126.8264 | 70 | 75 | 30.5294 | 30 | 73.2
7/3/20XX 7:00:00 AM | 0.29167 | 2 | 72.9 | 69.8 | 72.5823 | 84.9169 | 12.3346 | 60 | 72.9 |  | 72.9 | 84.6702 | 0.1 | 73.89 | 18.89 | 714042 | 59.5035 | 59.5035 | 64.8265 | 17.0059 | 404739.4316 | 33.7283 | 33.7283 | 93.2318 | 0.2 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 67.0313 | 19.2107 | 457215.0632 | 38.1013 | 38.1013 | 97.2583 | 0.3 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 69.2362 | 21.4156 | 509690.6949 | 42.4742 | 42.4742 | 101.2847 | 0.4 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 71.4411 | 23.6204 | 562166.3265 | 46.8472 | 46.8472 | 105.3112 | 0.5 | 73.45 | 18.45 | 697410 | 58.1175 | 58.1175 | 73.6459 | 25.8253 | 614641.9581 | 51.2202 | 51.2202 | 109.3377 | 0.6 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 75.8508 | 28.0302 | 667117.5897 | 55.5931 | 55.5931 | 113.3641 | 0.7 | 73.23 | 18.23 | 689094 | 57.4245 | 57.4245 | 78.0556 | 30.235 | 719593.2213 | 59.9661 | 59.9661 | 117.3906 | 0.8 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 80.2605 | 32.4399 | 772068.853 | 64.3391 | 64.3391 | 121.4171 | 0.9 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 82.4654 | 34.6447 | 824544.4846 | 68.712 | 68.712 | 125.4435 | 1 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 84.6702 | 36.8496 | 877020.1162 | 73.085 | 73.085 | 129.47 | 75 | 70 | 30.7343 | 30 | 69.8
7/3/20XX 8:00:00 AM | 0.33333 | 2 | 74.1 | 69.4 | 75.6554 | 88.5243 | 12.8688 | 60 | 74.1 |  | 74.1 | 87.7521 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 65.1347 | 17.3141 | 412074.3973 | 34.3395 | 34.3395 | 94.221 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 67.6477 | 19.8271 | 471884.9946 | 39.3237 | 39.3237 | 99.2367 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 70.1608 | 22.3402 | 531695.5919 | 44.308 | 44.308 | 104.2525 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 72.6738 | 24.8532 | 591506.1891 | 49.2922 | 49.2922 | 109.2682 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 75.1869 | 27.3663 | 651316.7864 | 54.2764 | 54.2764 | 114.2839 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 77.6999 | 29.8793 | 711127.3837 | 59.2606 | 59.2606 | 119.2996 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 80.213 | 32.3924 | 770937.981 | 64.2448 | 64.2448 | 124.3153 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 82.726 | 34.9054 | 830748.5783 | 69.229 | 69.229 | 129.331 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 85.2391 | 37.4185 | 890559.1756 | 74.2133 | 74.2133 | 134.3468 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 87.7521 | 39.9315 | 950369.7728 | 79.1975 | 79.1975 | 139.3625 | 75 | 70 | 31.5109 | 32 | 69.4
7/3/20XX 9:00:00 AM | 0.375 | 2 | 76 | 65.5 | 80.7483 | 94.5029 | 13.7546 | 60 | 76 |  | 76 | 88.3133 | 0.1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 65.1908 | 17.3702 | 413409.9959 | 34.4508 | 34.4508 | 94.9308 | 0.2 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 67.76 | 19.9393 | 474556.1918 | 39.5463 | 39.5463 | 100.6563 | 0.3 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 70.3291 | 22.5085 | 535702.3877 | 44.6419 | 44.6419 | 106.3819 | 0.4 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 72.8983 | 25.0777 | 596848.5837 | 49.7374 | 49.7374 | 112.1074 | 0.5 | 75 | 20 | 756000 | 63 | 63 | 75.4675 | 27.6468 | 657994.7796 | 54.8329 | 54.8329 | 117.8329 | 0.6 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 78.0366 | 30.216 | 719140.9755 | 59.9284 | 59.9284 | 123.5584 | 0.7 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 80.6058 | 32.7852 | 780287.1714 | 65.0239 | 65.0239 | 129.2839 | 0.8 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 83.175 | 35.3543 | 841433.3673 | 70.1194 | 70.1194 | 135.0094 | 0.9 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 85.7441 | 37.9235 | 902579.5632 | 75.215 | 75.215 | 140.735 | 1 | 76 | 21 | 793800 | 66.15 | 66.15 | 88.3133 | 40.4927 | 963725.7591 | 80.3105 | 80.3105 | 146.4605 | 75 | 65 | 32.0653 | 32 | 65.5
7/3/20XX 10:00:00 AM | 0.41667 | 2 | 78.3 | 60.7 | 87.2982 | 102.1928 | 14.8947 | 60 | 78.3 |  | 78.3 | 88.3408 | 0.1 | 74.43 | 19.43 | 734454 | 61.2045 | 61.2045 | 65.1935 | 17.3729 | 413475.3707 | 34.4563 | 34.4563 | 95.6608 | 0.2 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 67.7655 | 19.9448 | 474686.9415 | 39.5572 | 39.5572 | 102.1162 | 0.3 | 75.29 | 20.29 | 766962 | 63.9135 | 63.9135 | 70.3374 | 22.5167 | 535898.5122 | 44.6582 | 44.6582 | 108.5717 | 0.4 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 72.9093 | 25.0887 | 597110.083 | 49.7592 | 49.7592 | 115.0272 | 0.5 | 76.15 | 21.15 | 799470 | 66.6225 | 66.6225 | 75.4812 | 27.6606 | 658321.6537 | 54.8601 | 54.8601 | 121.4826 | 0.6 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 78.0531 | 30.2325 | 719533.2244 | 59.9611 | 59.9611 | 127.9381 | 0.7 | 77.01 | 22.01 | 831978 | 69.3315 | 69.3315 | 80.625 | 32.8044 | 780744.7952 | 65.0621 | 65.0621 | 134.3936 | 0.8 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 83.197 | 35.3763 | 841956.3659 | 70.163 | 70.163 | 140.849 | 0.9 | 77.87 | 22.87 | 864486 | 72.0405 | 72.0405 | 85.7689 | 37.9482 | 903167.9367 | 75.264 | 75.264 | 147.3045 | 1 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 88.3408 | 40.5201 | 964379.5074 | 80.365 | 80.365 | 153.76 | 80 | 60 | 32.6345 | 32 | 60.7
7/3/20XX 11:00:00 AM | 0.45833 | 2 | 80.4 | 57.6 | 77.751 | 93.6607 | 15.9097 | 50 | 80.4 |  | 80.4 | 89.8423 | 0.1 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 65.3437 | 17.5231 | 417049.0818 | 34.7541 | 34.7541 | 96.6201 | 0.2 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 68.0658 | 20.2451 | 481834.3636 | 40.1529 | 40.1529 | 104.0349 | 0.3 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 70.7878 | 22.9672 | 546619.6454 | 45.5516 | 45.5516 | 111.4496 | 0.4 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 73.5099 | 25.6893 | 611404.9272 | 50.9504 | 50.9504 | 118.8644 | 0.5 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 76.232 | 28.4114 | 676190.209 | 56.3492 | 56.3492 | 126.2792 | 0.6 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 78.9541 | 31.1334 | 740975.4908 | 61.748 | 61.748 | 133.694 | 0.7 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 81.6761 | 33.8555 | 805760.7726 | 67.1467 | 67.1467 | 141.1087 | 0.8 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 84.3982 | 36.5776 | 870546.0544 | 72.5455 | 72.5455 | 148.5235 | 0.9 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 87.1203 | 39.2996 | 935331.3362 | 77.9443 | 77.9443 | 155.9383 | 1 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 89.8423 | 42.0217 | 1000116.618 | 83.3431 | 83.3431 | 163.3531 | 80 | 60 | 33.3858 | 34 | 57.6
7/3/20XX 12:00:00 PM | 0.5 | 2 | 82 | 55.7 | 81.9738 | 98.7617 | 16.7879 | 50 | 82 |  | 82 | 91.5429 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 65.5138 | 17.6931 | 421096.4492 | 35.0914 | 35.0914 | 97.4614 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 68.4059 | 20.5853 | 489929.0983 | 40.8274 | 40.8274 | 105.7174 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 71.298 | 23.4774 | 558761.7475 | 46.5635 | 46.5635 | 113.9735 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 74.1901 | 26.3695 | 627594.3966 | 52.2995 | 52.2995 | 122.2295 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 77.0823 | 29.2616 | 696427.0458 | 58.0356 | 58.0356 | 130.4856 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 79.9744 | 32.1538 | 765259.695 | 63.7716 | 63.7716 | 138.7416 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 82.8665 | 35.0459 | 834092.3441 | 69.5077 | 69.5077 | 146.9977 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 85.7587 | 37.938 | 902924.9933 | 75.2437 | 75.2437 | 155.2537 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 88.6508 | 40.8302 | 971757.6424 | 80.9798 | 80.9798 | 163.5098 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 91.5429 | 43.7223 | 1040590.2916 | 86.7159 | 86.7159 | 171.7659 | 80 | 55 | 34.0458 | 34 | 55.7
7/3/20XX 1:00:00 PM | 0.54167 | 2 | 81.6 | 56.3 | 80.9009 | 97.4655 | 16.5647 | 50 | 81.6 |  | 81.6 | 91.3366 | 0.1 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 65.4931 | 17.6725 | 420605.416 | 35.0505 | 35.0505 | 97.2945 | 0.2 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 68.3646 | 20.544 | 488947.032 | 40.7456 | 40.7456 | 105.3836 | 0.3 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 71.2361 | 23.4155 | 557288.648 | 46.4407 | 46.4407 | 113.4727 | 0.4 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 74.1076 | 26.287 | 625630.264 | 52.1359 | 52.1359 | 121.5619 | 0.5 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 76.9791 | 29.1585 | 693971.88 | 57.831 | 57.831 | 129.651 | 0.6 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 79.8506 | 32.03 | 762313.496 | 63.5261 | 63.5261 | 137.7401 | 0.7 | 79.32 | 24.32 | 919296 | 76.608 | 76.608 | 82.7221 | 34.9015 | 830655.112 | 69.2213 | 69.2213 | 145.8293 | 0.8 | 80.08 | 25.08 | 948024 | 79.002 | 79.002 | 85.5936 | 37.773 | 898996.7281 | 74.9164 | 74.9164 | 153.9184 | 0.9 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 88.4651 | 40.6445 | 967338.3441 | 80.6115 | 80.6115 | 162.0075 | 1 | 81.6 | 26.6 | 1005480 | 83.79 | 83.79 | 91.3366 | 43.516 | 1035679.9601 | 86.3067 | 86.3067 | 170.0967 | 80 | 55 | 33.9151 | 34 | 56.3
7/3/20XX 2:00:00 PM | 0.58333 | 2 | 81.2 | 57.4 | 79.8394 | 96.1834 | 16.3439 | 50 | 81.2 |  | 81.2 | 91.9339 | 0.1 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 65.5529 | 17.7322 | 422027.0806 | 35.1689 | 35.1689 | 97.2869 | 0.2 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 68.4841 | 20.6635 | 491790.3612 | 40.9825 | 40.9825 | 105.3685 | 0.3 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 71.4153 | 23.5947 | 561553.6417 | 46.7961 | 46.7961 | 113.4501 | 0.4 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 74.3466 | 26.5259 | 631316.9223 | 52.6097 | 52.6097 | 121.5317 | 0.5 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 77.2778 | 29.4572 | 701080.2029 | 58.4234 | 58.4234 | 129.6134 | 0.6 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 80.209 | 32.3884 | 770843.4835 | 64.237 | 64.237 | 137.695 | 0.7 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 83.1402 | 35.3196 | 840606.764 | 70.0506 | 70.0506 | 145.7766 | 0.8 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 86.0715 | 38.2508 | 910370.0446 | 75.8642 | 75.8642 | 153.8582 | 0.9 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 89.0027 | 41.1821 | 980133.3252 | 81.6778 | 81.6778 | 161.9398 | 1 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 91.9339 | 44.1133 | 1049896.6058 | 87.4914 | 87.4914 | 170.0214 | 80 | 55 | 33.9105 | 34 | 57.4
7/3/20XX 3:00:00 PM | 0.625 | 2 | 81.3 | 57.2 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 91.9109 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 65.5506 | 17.7299 | 421972.2642 | 35.1644 | 35.1644 | 97.3139 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 68.4795 | 20.6589 | 491680.7283 | 40.9734 | 40.9734 | 105.4224 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 71.4084 | 23.5878 | 561389.1925 | 46.7824 | 46.7824 | 113.5309 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 74.3373 | 26.5167 | 631097.6567 | 52.5915 | 52.5915 | 121.6395 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 77.2663 | 29.4456 | 700806.1208 | 58.4005 | 58.4005 | 129.748 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 80.1952 | 32.3746 | 770514.585 | 64.2095 | 64.2095 | 137.8565 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 83.1241 | 35.3035 | 840223.0491 | 70.0186 | 70.0186 | 145.9651 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 86.053 | 38.2324 | 909931.5133 | 75.8276 | 75.8276 | 154.0736 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 88.982 | 41.1613 | 979639.9775 | 81.6367 | 81.6367 | 162.1822 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 91.9109 | 44.0903 | 1049348.4416 | 87.4457 | 87.4457 | 170.2907 | 80 | 55 | 33.9314 | 34 | 57.2
7/3/20XX 4:00:00 PM | 0.66667 | 2 | 79.2 | 63.2 | 89.9794 | 105.341 | 15.3616 | 60 | 79.2 |  | 79.2 | 94.8951 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 65.849 | 18.0284 | 429074.7653 | 35.7562 | 35.7562 | 97.2442 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 69.0763 | 21.2557 | 505885.7306 | 42.1571 | 42.1571 | 105.2831 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 72.3037 | 24.4831 | 582696.696 | 48.5581 | 48.5581 | 113.3221 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 75.531 | 27.7104 | 659507.6613 | 54.959 | 54.959 | 121.361 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 78.7584 | 30.9378 | 736318.6266 | 61.3599 | 61.3599 | 129.3999 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 81.9857 | 34.1651 | 813129.5919 | 67.7608 | 67.7608 | 137.4388 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 85.2131 | 37.3925 | 889940.5572 | 74.1617 | 74.1617 | 145.4777 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 88.4404 | 40.6198 | 966751.5226 | 80.5626 | 80.5626 | 153.5166 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 91.6678 | 43.8472 | 1043562.4879 | 86.9635 | 86.9635 | 161.5555 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 94.8951 | 47.0745 | 1120373.4532 | 93.3645 | 93.3645 | 169.5945 | 80 | 65 | 33.883 | 34 | 63.2
7/3/20XX 5:00:00 PM | 0.70833 | 2 | 79 | 64.8 | 89.3778 | 104.6345 | 15.2568 | 60 | 79 |  | 79 | 96.701 | 0.1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 66.0296 | 18.2089 | 433372.7137 | 36.1144 | 36.1144 | 97.5394 | 0.2 | 75 | 20 | 756000 | 63 | 63 | 69.4375 | 21.6169 | 514481.6273 | 42.8735 | 42.8735 | 105.8735 | 0.3 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 72.8454 | 25.0248 | 595590.541 | 49.6325 | 49.6325 | 114.2075 | 0.4 | 76 | 21 | 793800 | 66.15 | 66.15 | 76.2534 | 28.4328 | 676699.4547 | 56.3916 | 56.3916 | 122.5416 | 0.5 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 79.6613 | 31.8407 | 757808.3684 | 63.1507 | 63.1507 | 130.8757 | 0.6 | 77 | 22 | 831600 | 69.3 | 69.3 | 83.0693 | 35.2486 | 838917.282 | 69.9098 | 69.9098 | 139.2098 | 0.7 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 86.4772 | 38.6566 | 920026.1957 | 76.6688 | 76.6688 | 147.5438 | 0.8 | 78 | 23 | 869400 | 72.45 | 72.45 | 89.8851 | 42.0645 | 1001135.1094 | 83.4279 | 83.4279 | 155.8779 | 0.9 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 93.2931 | 45.4724 | 1082244.023 | 90.187 | 90.187 | 164.212 | 1 | 79 | 24 | 907200 | 75.6 | 75.6 | 96.701 | 48.8804 | 1163352.9367 | 96.9461 | 96.9461 | 172.5461 | 80 | 65 | 34.1168 | 34 | 64.8
7/3/20XX 6:00:00 PM | 0.75 | 2 | 78.1 | 66.4 | 86.7115 | 101.504 | 14.7925 | 60 | 78.1 |  | 78.1 | 96.1787 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 65.9773 | 18.1567 | 432129.5526 | 36.0108 | 36.0108 | 97.1523 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 69.333 | 21.5124 | 511995.3053 | 42.6663 | 42.6663 | 105.0993 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 72.6887 | 24.8681 | 591861.0579 | 49.3218 | 49.3218 | 113.0463 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 76.0444 | 28.2238 | 671726.8105 | 55.9772 | 55.9772 | 120.9932 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 79.4002 | 31.5795 | 751592.5631 | 62.6327 | 62.6327 | 128.9402 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 82.7559 | 34.9352 | 831458.3158 | 69.2882 | 69.2882 | 136.8872 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 86.1116 | 38.2909 | 911324.0684 | 75.9437 | 75.9437 | 144.8342 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 89.4673 | 41.6466 | 991189.821 | 82.5992 | 82.5992 | 152.7812 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 92.823 | 45.0023 | 1071055.5737 | 89.2546 | 89.2546 | 160.7281 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 96.1787 | 48.358 | 1150921.3263 | 95.9101 | 95.9101 | 168.6751 | 80 | 65 | 33.8134 | 34 | 66.4
7/3/20XX 7:00:00 PM | 0.79167 | 2 | 76.7 | 68.8 | 82.6964 | 96.79 | 14.0936 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/3/20XX 8:00:00 PM | 0.83333 | 2 | 75.5 | 69.9 | 79.3806 | 92.8973 | 13.5167 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/3/20XX 9:00:00 PM | 0.875 | 2 | 75.3 | 70.9 | 92.2616 | 105.7806 | 13.519 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/3/20XX 10:00:00 PM | 0.91667 | 2 | 75.4 | 70.2 | 92.579 | 106.1458 | 13.5668 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/3/20XX 11:00:00 PM | 0.95833 | 2 | 74 | 74.6 | 88.2187 | 101.1303 | 12.9116 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/3/20XX 12:00:00 AM | 0 | 3 | 74 | 74.3 | 88.2187 | 101.1303 | 12.9116 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/4/20XX 1:00:00 AM | 0.041667 | 3 | 73.5 | 75.5 | 86.7045 | 99.389 | 12.6844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/4/20XX 2:00:00 AM | 0.083333 | 3 | 73.3 | 76.1 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/4/20XX 3:00:00 AM | 0.125 | 3 | 72.8 | 74.9 | 84.6221 | 96.9944 | 12.3723 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/4/20XX 4:00:00 AM | 0.16667 | 3 | 72.4 | 75.1 | 83.4515 | 95.6486 | 12.1971 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/4/20XX 5:00:00 AM | 0.20833 | 3 | 71.5 | 76.2 | 80.8687 | 92.6795 | 11.8108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/4/20XX 6:00:00 AM | 0.25 | 3 | 71.7 | 78.2 | 81.4366 | 93.3322 | 11.8956 | 70 | 71.7 |  | 71.7 | 91.191 | 0.1 | 73.77 | 18.77 | 709506 | 59.1255 | 59.1255 | 65.4786 | 17.6579 | 420258.9732 | 35.0216 | 35.0216 | 94.1471 | 0.2 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 68.3355 | 20.5149 | 488254.1464 | 40.6878 | 40.6878 | 99.0888 | 0.3 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 71.1925 | 23.3718 | 556249.3195 | 46.3541 | 46.3541 | 104.0306 | 0.4 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 74.0494 | 26.2288 | 624244.4927 | 52.0204 | 52.0204 | 108.9724 | 0.5 | 72.85 | 17.85 | 674730 | 56.2275 | 56.2275 | 76.9063 | 29.0857 | 692239.6659 | 57.6866 | 57.6866 | 113.9141 | 0.6 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 79.7633 | 31.9426 | 760234.8391 | 63.3529 | 63.3529 | 118.8559 | 0.7 | 72.39 | 17.39 | 657342 | 54.7785 | 54.7785 | 82.6202 | 34.7996 | 828230.0122 | 69.0192 | 69.0192 | 123.7977 | 0.8 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 85.4772 | 37.6565 | 896225.1854 | 74.6854 | 74.6854 | 128.7394 | 0.9 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 88.3341 | 40.5135 | 964220.3586 | 80.3517 | 80.3517 | 133.6812 | 1 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 91.191 | 43.3704 | 1032215.5318 | 86.018 | 86.018 | 138.623 | 70 | 80 | 31.4589 | 32 | 78.2
7/4/20XX 7:00:00 AM | 0.29167 | 3 | 72.7 | 75.2 | 84.3281 | 96.6564 | 12.3283 | 70 | 72.7 |  | 72.7 | 90.7388 | 0.1 | 73.87 | 18.87 | 713286 | 59.4405 | 59.4405 | 65.4334 | 17.6127 | 419182.753 | 34.9319 | 34.9319 | 94.3724 | 0.2 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 68.2451 | 20.4244 | 486101.706 | 40.5085 | 40.5085 | 99.5395 | 0.3 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 71.0568 | 23.2362 | 553020.659 | 46.0851 | 46.0851 | 104.7066 | 0.4 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 73.8685 | 26.0479 | 619939.6119 | 51.6616 | 51.6616 | 109.8736 | 0.5 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 76.6802 | 28.8596 | 686858.5649 | 57.2382 | 57.2382 | 115.0407 | 0.6 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 79.492 | 31.6713 | 753777.5179 | 62.8148 | 62.8148 | 120.2078 | 0.7 | 73.09 | 18.09 | 683802 | 56.9835 | 56.9835 | 82.3037 | 34.483 | 820696.4709 | 68.3914 | 68.3914 | 125.3749 | 0.8 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 85.1154 | 37.2948 | 887615.4239 | 73.968 | 73.968 | 130.542 | 0.9 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 87.9271 | 40.1065 | 954534.3769 | 79.5445 | 79.5445 | 135.709 | 1 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 90.7388 | 42.9182 | 1021453.3299 | 85.1211 | 85.1211 | 140.8761 | 75 | 75 | 31.634 | 32 | 75.2
7/4/20XX 8:00:00 AM | 0.33333 | 3 | 74 | 71.5 | 88.2187 | 101.1303 | 12.9116 | 70 | 74 |  | 74 | 90.1555 | 0.1 | 74 | 19 | 718200 | 59.85 | 59.85 | 65.375 | 17.5544 | 417794.3348 | 34.8162 | 34.8162 | 94.6662 | 0.2 | 74 | 19 | 718200 | 59.85 | 59.85 | 68.1284 | 20.3078 | 483324.8696 | 40.2771 | 40.2771 | 100.1271 | 0.3 | 74 | 19 | 718200 | 59.85 | 59.85 | 70.8818 | 23.0612 | 548855.4044 | 45.738 | 45.738 | 105.588 | 0.4 | 74 | 19 | 718200 | 59.85 | 59.85 | 73.6352 | 25.8145 | 614385.9392 | 51.1988 | 51.1988 | 111.0488 | 0.5 | 74 | 19 | 718200 | 59.85 | 59.85 | 76.3886 | 28.5679 | 679916.474 | 56.6597 | 56.6597 | 116.5097 | 0.6 | 74 | 19 | 718200 | 59.85 | 59.85 | 79.1419 | 31.3213 | 745447.0088 | 62.1206 | 62.1206 | 121.9706 | 0.7 | 74 | 19 | 718200 | 59.85 | 59.85 | 81.8953 | 34.0747 | 810977.5436 | 67.5815 | 67.5815 | 127.4315 | 0.8 | 74 | 19 | 718200 | 59.85 | 59.85 | 84.6487 | 36.8281 | 876508.0784 | 73.0423 | 73.0423 | 132.8923 | 0.9 | 74 | 19 | 718200 | 59.85 | 59.85 | 87.4021 | 39.5815 | 942038.6132 | 78.5032 | 78.5032 | 138.3532 | 1 | 74 | 19 | 718200 | 59.85 | 59.85 | 90.1555 | 42.3348 | 1007569.148 | 83.9641 | 83.9641 | 143.8141 | 75 | 70 | 31.8622 | 32 | 71.5
7/4/20XX 9:00:00 AM | 0.375 | 3 | 75.7 | 67.7 | 79.9253 | 93.5368 | 13.6115 | 60 | 75.7 |  | 75.7 | 90.4061 | 0.1 | 74.17 | 19.17 | 724626 | 60.3855 | 60.3855 | 65.4001 | 17.5794 | 418390.9074 | 34.8659 | 34.8659 | 95.2514 | 0.2 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 68.1785 | 20.3579 | 484518.0149 | 40.3765 | 40.3765 | 101.2975 | 0.3 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 70.957 | 23.1363 | 550645.1223 | 45.8871 | 45.8871 | 107.3436 | 0.4 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 73.7354 | 25.9148 | 616772.2297 | 51.3977 | 51.3977 | 113.3897 | 0.5 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 76.5139 | 28.6932 | 682899.3372 | 56.9083 | 56.9083 | 119.4358 | 0.6 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 79.2923 | 31.4717 | 749026.4446 | 62.4189 | 62.4189 | 125.4819 | 0.7 | 75.19 | 20.19 | 763182 | 63.5985 | 63.5985 | 82.0708 | 34.2501 | 815153.552 | 67.9295 | 67.9295 | 131.528 | 0.8 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 84.8492 | 37.0286 | 881280.6595 | 73.4401 | 73.4401 | 137.5741 | 0.9 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 87.6277 | 39.807 | 947407.7669 | 78.9506 | 78.9506 | 143.6201 | 1 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 90.4061 | 42.5855 | 1013534.8744 | 84.4612 | 84.4612 | 149.6662 | 75 | 70 | 32.3192 | 32 | 67.7
7/4/20XX 10:00:00 AM | 0.41667 | 3 | 78.4 | 62.3 | 87.5927 | 102.5387 | 14.946 | 60 | 78.4 |  | 78.4 | 91.0303 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 65.4625 | 17.6419 | 419876.4604 | 34.9897 | 34.9897 | 96.2257 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 68.3034 | 20.4827 | 487489.1208 | 40.6241 | 40.6241 | 103.2461 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 71.1442 | 23.3236 | 555101.7812 | 46.2585 | 46.2585 | 110.2665 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 73.9851 | 26.1645 | 622714.4416 | 51.8929 | 51.8929 | 117.2869 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 76.826 | 29.0053 | 690327.102 | 57.5273 | 57.5273 | 124.3073 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 79.6668 | 31.8462 | 757939.7623 | 63.1616 | 63.1616 | 131.3276 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 82.5077 | 34.6871 | 825552.4227 | 68.796 | 68.796 | 138.348 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 85.3486 | 37.5279 | 893165.0831 | 74.4304 | 74.4304 | 145.3684 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 88.1894 | 40.3688 | 960777.7435 | 80.0648 | 80.0648 | 152.3888 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 91.0303 | 43.2097 | 1028390.4039 | 85.6992 | 85.6992 | 159.4092 | 80 | 60 | 33.0805 | 34 | 62.3
7/4/20XX 11:00:00 AM | 0.45833 | 3 | 80.6 | 55.9 | 78.2688 | 94.2862 | 16.0174 | 50 | 80.6 |  | 80.6 | 87.719 | 0.1 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 65.1314 | 17.3107 | 411995.6457 | 34.333 | 34.333 | 96.262 | 0.2 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 67.6411 | 19.8205 | 471727.4914 | 39.3106 | 39.3106 | 103.3186 | 0.3 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 70.1509 | 22.3302 | 531459.3371 | 44.2883 | 44.2883 | 110.3753 | 0.4 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 72.6606 | 24.84 | 591191.1827 | 49.2659 | 49.2659 | 117.4319 | 0.5 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 75.1703 | 27.3497 | 650923.0284 | 54.2436 | 54.2436 | 124.4886 | 0.6 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 77.6801 | 29.8594 | 710654.8741 | 59.2212 | 59.2212 | 131.5452 | 0.7 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 80.1898 | 32.3692 | 770386.7198 | 64.1989 | 64.1989 | 138.6019 | 0.8 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 82.6996 | 34.8789 | 830118.5655 | 69.1765 | 69.1765 | 145.6585 | 0.9 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 85.2093 | 37.3887 | 889850.4112 | 74.1542 | 74.1542 | 152.7152 | 1 | 80.6 | 25.6 | 967680 | 80.64 | 80.64 | 87.719 | 39.8984 | 949582.2568 | 79.1319 | 79.1319 | 159.7719 | 80 | 55 | 33.1019 | 34 | 55.9
7/4/20XX 12:00:00 PM | 0.5 | 3 | 81.8 | 55 | 81.4359 | 98.1119 | 16.676 | 50 | 81.8 |  | 81.8 | 89.7739 | 0.1 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 65.3369 | 17.5162 | 416886.1312 | 34.7405 | 34.7405 | 97.0475 | 0.2 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 68.0521 | 20.2314 | 481508.4623 | 40.1257 | 40.1257 | 104.8897 | 0.3 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 70.7673 | 22.9467 | 546130.7935 | 45.5109 | 45.5109 | 112.7319 | 0.4 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 73.4825 | 25.6619 | 610753.1247 | 50.8961 | 50.8961 | 120.5741 | 0.5 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 76.1978 | 28.3771 | 675375.4558 | 56.2813 | 56.2813 | 128.4163 | 0.6 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 78.913 | 31.0923 | 739997.787 | 61.6665 | 61.6665 | 136.2585 | 0.7 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 81.6282 | 33.8076 | 804620.1182 | 67.0517 | 67.0517 | 144.1007 | 0.8 | 80.24 | 25.24 | 954072 | 79.506 | 79.506 | 84.3434 | 36.5228 | 869242.4494 | 72.4369 | 72.4369 | 151.9429 | 0.9 | 81.02 | 26.02 | 983556 | 81.963 | 81.963 | 87.0586 | 39.238 | 933864.7805 | 77.8221 | 77.8221 | 159.7851 | 1 | 81.8 | 26.8 | 1013040 | 84.42 | 84.42 | 89.7739 | 41.9532 | 998487.1117 | 83.2073 | 83.2073 | 167.6273 | 80 | 55 | 33.719 | 34 | 55
7/4/20XX 1:00:00 PM | 0.54167 | 3 | 81.8 | 55.1 | 81.4359 | 98.1119 | 16.676 | 50 | 81.8 |  | 81.8 | 89.9406 | 0.1 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 65.3535 | 17.5329 | 417283.0195 | 34.7736 | 34.7736 | 97.0806 | 0.2 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 68.0854 | 20.2648 | 482302.239 | 40.1919 | 40.1919 | 104.9559 | 0.3 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 70.8173 | 22.9967 | 547321.4585 | 45.6101 | 45.6101 | 112.8311 | 0.4 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 73.5492 | 25.7286 | 612340.678 | 51.0284 | 51.0284 | 120.7064 | 0.5 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 76.2811 | 28.4605 | 677359.8975 | 56.4467 | 56.4467 | 128.5817 | 0.6 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 79.013 | 31.1924 | 742379.1169 | 61.8649 | 61.8649 | 136.4569 | 0.7 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 81.7449 | 33.9243 | 807398.3364 | 67.2832 | 67.2832 | 144.3322 | 0.8 | 80.24 | 25.24 | 954072 | 79.506 | 79.506 | 84.4768 | 36.6562 | 872417.5559 | 72.7015 | 72.7015 | 152.2075 | 0.9 | 81.02 | 26.02 | 983556 | 81.963 | 81.963 | 87.2087 | 39.3881 | 937436.7754 | 78.1197 | 78.1197 | 160.0827 | 1 | 81.8 | 26.8 | 1013040 | 84.42 | 84.42 | 89.9406 | 42.12 | 1002455.9949 | 83.538 | 83.538 | 167.958 | 80 | 55 | 33.7452 | 34 | 55.1
7/4/20XX 2:00:00 PM | 0.58333 | 3 | 81.9 | 54.3 | 81.7045 | 98.4363 | 16.7319 | 50 | 81.9 |  | 81.9 | 88.8992 | 0.1 | 74.79 | 19.79 | 748062 | 62.3385 | 62.3385 | 65.2494 | 17.4288 | 414804.3734 | 34.567 | 34.567 | 96.9055 | 0.2 | 75.58 | 20.58 | 777924 | 64.827 | 64.827 | 67.8771 | 20.0565 | 477344.9469 | 39.7787 | 39.7787 | 104.6057 | 0.3 | 76.37 | 21.37 | 807786 | 67.3155 | 67.3155 | 70.5049 | 22.6843 | 539885.5203 | 44.9905 | 44.9905 | 112.306 | 0.4 | 77.16 | 22.16 | 837648 | 69.804 | 69.804 | 73.1327 | 25.312 | 602426.0938 | 50.2022 | 50.2022 | 120.0062 | 0.5 | 77.95 | 22.95 | 867510 | 72.2925 | 72.2925 | 75.7604 | 27.9398 | 664966.6672 | 55.4139 | 55.4139 | 127.7064 | 0.6 | 78.74 | 23.74 | 897372 | 74.781 | 74.781 | 78.3882 | 30.5675 | 727507.2406 | 60.6256 | 60.6256 | 135.4066 | 0.7 | 79.53 | 24.53 | 927234 | 77.2695 | 77.2695 | 81.0159 | 33.1953 | 790047.8141 | 65.8373 | 65.8373 | 143.1068 | 0.8 | 80.32 | 25.32 | 957096 | 79.758 | 79.758 | 83.6437 | 35.823 | 852588.3875 | 71.049 | 71.049 | 150.807 | 0.9 | 81.11 | 26.11 | 986958 | 82.2465 | 82.2465 | 86.2714 | 38.4508 | 915128.961 | 76.2607 | 76.2607 | 158.5072 | 1 | 81.9 | 26.9 | 1016820 | 84.735 | 84.735 | 88.8992 | 41.0786 | 977669.5344 | 81.4725 | 81.4725 | 166.2075 | 80 | 55 | 33.6063 | 34 | 54.3
7/4/20XX 3:00:00 PM | 0.625 | 3 | 81.8 | 52.5 | 81.4359 | 98.1119 | 16.676 | 50 | 81.8 |  | 81.8 | 85.6049 | 0.1 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 64.92 | 17.0993 | 406963.9231 | 33.9137 | 33.9137 | 96.2207 | 0.2 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 67.2183 | 19.3976 | 461664.0463 | 38.472 | 38.472 | 103.236 | 0.3 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 69.5166 | 21.696 | 516364.1694 | 43.0303 | 43.0303 | 110.2513 | 0.4 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 71.8149 | 23.9943 | 571064.2926 | 47.5887 | 47.5887 | 117.2667 | 0.5 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 74.1133 | 26.2926 | 625764.4157 | 52.147 | 52.147 | 124.282 | 0.6 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 76.4116 | 28.5909 | 680464.5389 | 56.7054 | 56.7054 | 131.2974 | 0.7 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 78.7099 | 30.8893 | 735164.662 | 61.2637 | 61.2637 | 138.3127 | 0.8 | 80.24 | 25.24 | 954072 | 79.506 | 79.506 | 81.0082 | 33.1876 | 789864.7852 | 65.8221 | 65.8221 | 145.3281 | 0.9 | 81.02 | 26.02 | 983556 | 81.963 | 81.963 | 83.3066 | 35.4859 | 844564.9083 | 70.3804 | 70.3804 | 152.3434 | 1 | 81.8 | 26.8 | 1013040 | 84.42 | 84.42 | 85.6049 | 37.7842 | 899265.0315 | 74.9388 | 74.9388 | 159.3588 | 80 | 50 | 33.0648 | 34 | 52.5
7/4/20XX 4:00:00 PM | 0.66667 | 3 | 81.3 | 54.8 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 87.9752 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 65.157 | 17.3364 | 412605.2315 | 34.3838 | 34.3838 | 96.5333 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 67.6923 | 19.8717 | 472946.663 | 39.4122 | 39.4122 | 103.8612 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 70.2277 | 22.4071 | 533288.0945 | 44.4407 | 44.4407 | 111.1892 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 72.763 | 24.9424 | 593629.5261 | 49.4691 | 49.4691 | 118.5171 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 75.2984 | 27.4778 | 653970.9576 | 54.4976 | 54.4976 | 125.8451 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 77.8338 | 30.0131 | 714312.3891 | 59.526 | 59.526 | 133.173 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 80.3691 | 32.5485 | 774653.8206 | 64.5545 | 64.5545 | 140.501 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 82.9045 | 35.0838 | 834995.2521 | 69.5829 | 69.5829 | 147.8289 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 85.4398 | 37.6192 | 895336.6836 | 74.6114 | 74.6114 | 155.1569 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 87.9752 | 40.1545 | 955678.1152 | 79.6398 | 79.6398 | 162.4848 | 80 | 55 | 33.314 | 34 | 54.8
7/4/20XX 5:00:00 PM | 0.70833 | 3 | 81.1 | 54 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 86.0915 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 64.9686 | 17.148 | 408122.1481 | 34.0102 | 34.0102 | 96.0967 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 67.3156 | 19.495 | 463980.4962 | 38.665 | 38.665 | 102.988 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 69.6626 | 21.842 | 519838.8442 | 43.3199 | 43.3199 | 109.8794 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 72.0096 | 24.189 | 575697.1923 | 47.9748 | 47.9748 | 116.7708 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 74.3566 | 26.5359 | 631555.5404 | 52.6296 | 52.6296 | 123.6621 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 76.7036 | 28.8829 | 687413.8885 | 57.2845 | 57.2845 | 130.5535 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 79.0506 | 31.2299 | 743272.2365 | 61.9394 | 61.9394 | 137.4449 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 81.3975 | 33.5769 | 799130.5846 | 66.5942 | 66.5942 | 144.3362 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 83.7445 | 35.9239 | 854988.9327 | 71.2491 | 71.2491 | 151.2276 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 86.0915 | 38.2709 | 910847.2808 | 75.9039 | 75.9039 | 158.1189 | 80 | 55 | 32.9694 | 32 | 54
7/4/20XX 6:00:00 PM | 0.75 | 3 | 80.3 | 52.7 | 77.4931 | 93.3492 | 15.8561 | 50 | 80.3 |  | 80.3 | 81.7742 | 0.1 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 64.5369 | 16.7163 | 397847.0063 | 33.1539 | 33.1539 | 94.9884 | 0.2 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 66.4522 | 18.6315 | 443430.2125 | 36.9525 | 36.9525 | 100.7715 | 0.3 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 68.3674 | 20.5468 | 489013.4188 | 40.7511 | 40.7511 | 106.5546 | 0.4 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 70.2827 | 22.462 | 534596.625 | 44.5497 | 44.5497 | 112.3377 | 0.5 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 72.1979 | 24.3773 | 580179.8313 | 48.3483 | 48.3483 | 118.1208 | 0.6 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 74.1132 | 26.2926 | 625763.0376 | 52.1469 | 52.1469 | 123.9039 | 0.7 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 76.0285 | 28.2078 | 671346.2438 | 55.9455 | 55.9455 | 129.687 | 0.8 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 77.9437 | 30.1231 | 716929.4501 | 59.7441 | 59.7441 | 135.4701 | 0.9 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 79.859 | 32.0383 | 762512.6563 | 63.5427 | 63.5427 | 141.2532 | 1 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 81.7742 | 33.9536 | 808095.8626 | 67.3413 | 67.3413 | 147.0363 | 80 | 55 | 32.096 | 32 | 52.7
7/4/20XX 7:00:00 PM | 0.79167 | 3 | 79.7 | 51.6 | 75.9607 | 91.4984 | 15.5378 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/4/20XX 8:00:00 PM | 0.83333 | 3 | 78.4 | 53.5 | 72.7264 | 87.5927 | 14.8663 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/4/20XX 9:00:00 PM | 0.875 | 3 | 77 | 56.7 | 69.3725 | 83.5433 | 14.1708 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/4/20XX 10:00:00 PM | 0.91667 | 3 | 76.6 | 58.4 | 68.4384 | 82.4157 | 13.9773 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/4/20XX 11:00:00 PM | 0.95833 | 3 | 75.1 | 59.8 | 65.0293 | 78.3007 | 13.2714 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/4/20XX 12:00:00 AM | 0 | 4 | 74.1 | 64.5 | 75.6554 | 88.5243 | 12.8688 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/5/20XX 1:00:00 AM | 0.041667 | 4 | 73.8 | 65.3 | 74.8769 | 87.6104 | 12.7335 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/5/20XX 2:00:00 AM | 0.083333 | 4 | 73.4 | 66.2 | 73.8495 | 86.4044 | 12.5549 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/5/20XX 3:00:00 AM | 0.125 | 4 | 72.5 | 68.7 | 71.5821 | 83.7428 | 12.1608 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/5/20XX 4:00:00 AM | 0.16667 | 4 | 72.3 | 68.3 | 71.0864 | 83.1611 | 12.0747 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/5/20XX 5:00:00 AM | 0.20833 | 4 | 71.9 | 69.2 | 70.104 | 82.008 | 11.904 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/5/20XX 6:00:00 AM | 0.25 | 4 | 72 | 69.9 | 70.3485 | 82.2949 | 11.9464 | 60 | 72 |  | 72 | 82.1755 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.577 | 16.7564 | 398801.9184 | 33.2335 | 33.2335 | 92.4535 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 66.5324 | 18.7118 | 445340.0368 | 37.1117 | 37.1117 | 95.7017 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 68.4878 | 20.6671 | 491878.1552 | 40.9898 | 40.9898 | 98.9498 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 70.4432 | 22.6225 | 538416.2736 | 44.868 | 44.868 | 102.198 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 72.3985 | 24.5779 | 584954.392 | 48.7462 | 48.7462 | 105.4462 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 74.3539 | 26.5333 | 631492.5104 | 52.6244 | 52.6244 | 108.6944 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 76.3093 | 28.4887 | 678030.6288 | 56.5026 | 56.5026 | 111.9426 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 78.2647 | 30.4441 | 724568.7472 | 60.3807 | 60.3807 | 115.1907 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 80.2201 | 32.3994 | 771106.8656 | 64.2589 | 64.2589 | 118.4389 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 82.1755 | 34.3548 | 817644.984 | 68.1371 | 68.1371 | 121.6871 | 70 | 70 | 30.1236 | 30 | 69.9
7/5/20XX 7:00:00 AM | 0.29167 | 4 | 73.3 | 66.8 | 73.5946 | 86.1051 | 12.5105 | 60 | 73.3 |  | 73.3 | 82.1017 | 0.1 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 64.5696 | 16.749 | 398626.4203 | 33.2189 | 33.2189 | 92.8484 | 0.2 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 66.5177 | 18.697 | 444989.0406 | 37.0824 | 37.0824 | 96.4914 | 0.3 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 68.4657 | 20.645 | 491351.6609 | 40.946 | 40.946 | 100.1345 | 0.4 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 70.4137 | 22.593 | 537714.2813 | 44.8095 | 44.8095 | 103.7775 | 0.5 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 72.3617 | 24.541 | 584076.9016 | 48.6731 | 48.6731 | 107.4206 | 0.6 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 74.3097 | 26.4891 | 630439.5219 | 52.5366 | 52.5366 | 111.0636 | 0.7 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 76.2577 | 28.4371 | 676802.1422 | 56.4002 | 56.4002 | 114.7067 | 0.8 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 78.2057 | 30.3851 | 723164.7625 | 60.2637 | 60.2637 | 118.3497 | 0.9 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 80.1537 | 32.3331 | 769527.3828 | 64.1273 | 64.1273 | 121.9928 | 1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 82.1017 | 34.2811 | 815890.0031 | 67.9908 | 67.9908 | 125.6358 | 75 | 65 | 30.4308 | 30 | 66.8
7/5/20XX 8:00:00 AM | 0.33333 | 4 | 74.7 | 64.6 | 77.2333 | 90.3765 | 13.1432 | 60 | 74.7 |  | 74.7 | 83.2792 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 64.6874 | 16.8668 | 401428.7342 | 33.4524 | 33.4524 | 93.5229 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 66.7531 | 18.9325 | 450593.6685 | 37.5495 | 37.5495 | 97.8405 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 68.8189 | 20.9983 | 499758.6027 | 41.6466 | 41.6466 | 102.1581 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 70.8846 | 23.064 | 548923.5369 | 45.7436 | 45.7436 | 106.4756 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 72.9504 | 25.1298 | 598088.4711 | 49.8407 | 49.8407 | 110.7932 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 75.0162 | 27.1955 | 647253.4054 | 53.9378 | 53.9378 | 115.1108 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 77.0819 | 29.2613 | 696418.3396 | 58.0349 | 58.0349 | 119.4284 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 79.1477 | 31.327 | 745583.2738 | 62.1319 | 62.1319 | 123.7459 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 81.2134 | 33.3928 | 794748.208 | 66.229 | 66.229 | 128.0635 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 83.2792 | 35.4585 | 843913.1423 | 70.3261 | 70.3261 | 132.3811 | 75 | 65 | 30.9583 | 30 | 64.6
7/5/20XX 9:00:00 AM | 0.375 | 4 | 77.2 | 60.4 | 84.112 | 98.452 | 14.34 | 60 | 77.2 |  | 77.2 | 84.6856 | 0.1 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 64.828 | 17.0074 | 404776.0761 | 33.7313 | 33.7313 | 94.5893 | 0.2 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 67.0344 | 19.2138 | 457288.3523 | 38.1074 | 38.1074 | 99.9734 | 0.3 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 69.2408 | 21.4202 | 509800.6284 | 42.4834 | 42.4834 | 105.3574 | 0.4 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 71.4472 | 23.6266 | 562312.9045 | 46.8594 | 46.8594 | 110.7414 | 0.5 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 73.6536 | 25.833 | 614825.1806 | 51.2354 | 51.2354 | 116.1254 | 0.6 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 75.86 | 28.0394 | 667337.4568 | 55.6115 | 55.6115 | 121.5095 | 0.7 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 78.0664 | 30.2458 | 719849.7329 | 59.9875 | 59.9875 | 126.8935 | 0.8 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 80.2728 | 32.4522 | 772362.009 | 64.3635 | 64.3635 | 132.2775 | 0.9 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 82.4792 | 34.6586 | 824874.2851 | 68.7395 | 68.7395 | 137.6615 | 1 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 84.6856 | 36.865 | 877386.5613 | 73.1155 | 73.1155 | 143.0455 | 75 | 60 | 31.7918 | 32 | 60.4
7/5/20XX 10:00:00 AM | 0.41667 | 4 | 79.7 | 55.5 | 75.9607 | 91.4984 | 15.5378 | 50 | 79.7 |  | 79.7 | 84.5064 | 0.1 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 64.8101 | 16.9895 | 404349.6316 | 33.6958 | 33.6958 | 95.3413 | 0.2 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 66.9986 | 19.178 | 456435.4632 | 38.0363 | 38.0363 | 101.4773 | 0.3 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 69.1871 | 21.3664 | 508521.2948 | 42.3768 | 42.3768 | 107.6133 | 0.4 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 71.3756 | 23.5549 | 560607.1263 | 46.7173 | 46.7173 | 113.7493 | 0.5 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 73.564 | 25.7434 | 612692.9579 | 51.0577 | 51.0577 | 119.8852 | 0.6 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 75.7525 | 27.9319 | 664778.7895 | 55.3982 | 55.3982 | 126.0212 | 0.7 | 77.99 | 22.99 | 869022 | 72.4185 | 72.4185 | 77.941 | 30.1204 | 716864.6211 | 59.7387 | 59.7387 | 132.1572 | 0.8 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 80.1295 | 32.3088 | 768950.4527 | 64.0792 | 64.0792 | 138.2932 | 0.9 | 79.13 | 24.13 | 912114 | 76.0095 | 76.0095 | 82.318 | 34.4973 | 821036.2843 | 68.4197 | 68.4197 | 144.4292 | 1 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 84.5064 | 36.6858 | 873122.1159 | 72.7602 | 72.7602 | 150.5652 | 80 | 55 | 32.3772 | 32 | 55.5
7/5/20XX 11:00:00 AM | 0.45833 | 4 | 82.8 | 50.2 | 84.1546 | 101.3965 | 17.2419 | 50 | 82.8 |  | 82.8 | 84.4995 | 0.1 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 64.8094 | 16.9888 | 404333.0719 | 33.6944 | 33.6944 | 96.3164 | 0.2 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 66.9972 | 19.1766 | 456402.3438 | 38.0335 | 38.0335 | 103.4275 | 0.3 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 69.185 | 21.3644 | 508471.6156 | 42.3726 | 42.3726 | 110.5386 | 0.4 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 71.3728 | 23.5521 | 560540.8875 | 46.7117 | 46.7117 | 117.6497 | 0.5 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 73.5606 | 25.7399 | 612610.1594 | 51.0508 | 51.0508 | 124.7608 | 0.6 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 75.7483 | 27.9277 | 664679.4313 | 55.39 | 55.39 | 131.872 | 0.7 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 77.9361 | 30.1155 | 716748.7031 | 59.7291 | 59.7291 | 138.9831 | 0.8 | 81.04 | 26.04 | 984312 | 82.026 | 82.026 | 80.1239 | 32.3033 | 768817.975 | 64.0682 | 64.0682 | 146.0942 | 0.9 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 82.3117 | 34.4911 | 820887.2469 | 68.4073 | 68.4073 | 153.2053 | 1 | 82.8 | 27.8 | 1050840 | 87.57 | 87.57 | 84.4995 | 36.6788 | 872956.5188 | 72.7464 | 72.7464 | 160.3164 | 85 | 50 | 33.1367 | 34 | 50.2
7/5/20XX 12:00:00 PM | 0.5 | 4 | 84.8 | 45.9 | 71.5125 | 89.814 | 18.3015 | 40 | 84.8 |  | 84.8 | 82.3104 | 0.1 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 64.5905 | 16.7699 | 399123.0895 | 33.2603 | 33.2603 | 96.5123 | 0.2 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 66.5594 | 18.7388 | 445982.3789 | 37.1652 | 37.1652 | 103.8192 | 0.3 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 68.5283 | 20.7076 | 492841.6684 | 41.0701 | 41.0701 | 111.1261 | 0.4 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 70.4971 | 22.6765 | 539700.9578 | 44.9751 | 44.9751 | 118.4331 | 0.5 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 72.466 | 24.6454 | 586560.2473 | 48.88 | 48.88 | 125.74 | 0.6 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 74.4349 | 26.6143 | 633419.5368 | 52.785 | 52.785 | 133.047 | 0.7 | 81.56 | 26.56 | 1003968 | 83.664 | 83.664 | 76.4038 | 28.5831 | 680278.8262 | 56.6899 | 56.6899 | 140.3539 | 0.8 | 82.64 | 27.64 | 1044792 | 87.066 | 87.066 | 78.3727 | 30.552 | 727138.1157 | 60.5948 | 60.5948 | 147.6608 | 0.9 | 83.72 | 28.72 | 1085616 | 90.468 | 90.468 | 80.3415 | 32.5209 | 773997.4051 | 64.4998 | 64.4998 | 154.9678 | 1 | 84.8 | 29.8 | 1126440 | 93.87 | 93.87 | 82.3104 | 34.4898 | 820856.6946 | 68.4047 | 68.4047 | 162.2747 | 85 | 45 | 33.2836 | 34 | 45.9
7/5/20XX 1:00:00 PM | 0.54167 | 4 | 85.7 | 44.3 | 73.6057 | 92.4593 | 18.8536 | 40 | 85.7 |  | 85.7 | 81.7127 | 0.1 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 64.5307 | 16.7101 | 397700.5787 | 33.1417 | 33.1417 | 96.6772 | 0.2 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 66.4398 | 18.6192 | 443137.3574 | 36.9281 | 36.9281 | 104.1491 | 0.3 | 77.51 | 22.51 | 850878 | 70.9065 | 70.9065 | 68.349 | 20.5283 | 488574.1361 | 40.7145 | 40.7145 | 111.621 | 0.4 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 70.2581 | 22.4374 | 534010.9148 | 44.5009 | 44.5009 | 119.0929 | 0.5 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 72.1672 | 24.3465 | 579447.6936 | 48.2873 | 48.2873 | 126.5648 | 0.6 | 81.02 | 26.02 | 983556 | 81.963 | 81.963 | 74.0763 | 26.2557 | 624884.4723 | 52.0737 | 52.0737 | 134.0367 | 0.7 | 82.19 | 27.19 | 1027782 | 85.6485 | 85.6485 | 75.9854 | 28.1648 | 670321.251 | 55.8601 | 55.8601 | 141.5086 | 0.8 | 83.36 | 28.36 | 1072008 | 89.334 | 89.334 | 77.8945 | 30.0739 | 715758.0297 | 59.6465 | 59.6465 | 148.9805 | 0.9 | 84.53 | 29.53 | 1116234 | 93.0195 | 93.0195 | 79.8036 | 31.983 | 761194.8084 | 63.4329 | 63.4329 | 156.4524 | 1 | 85.7 | 30.7 | 1160460 | 96.705 | 96.705 | 81.7127 | 33.8921 | 806631.5871 | 67.2193 | 67.2193 | 163.9243 | 85 | 45 | 33.4103 | 34 | 44.3
7/5/20XX 2:00:00 PM | 0.58333 | 4 | 86.2 | 42.3 | 74.7896 | 93.9557 | 19.1661 | 40 | 86.2 |  | 86.2 | 79.1978 | 0.1 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 64.2793 | 16.4586 | 391715.1356 | 32.6429 | 32.6429 | 96.3359 | 0.2 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 65.9369 | 18.1162 | 431166.4713 | 35.9305 | 35.9305 | 103.4665 | 0.3 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 67.5945 | 19.7739 | 470617.8069 | 39.2182 | 39.2182 | 110.5972 | 0.4 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 69.2521 | 21.4315 | 510069.1425 | 42.5058 | 42.5058 | 117.7278 | 0.5 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 70.9097 | 23.0891 | 549520.4782 | 45.7934 | 45.7934 | 124.8584 | 0.6 | 81.32 | 26.32 | 994896 | 82.908 | 82.908 | 72.5673 | 24.7467 | 588971.8138 | 49.081 | 49.081 | 131.989 | 0.7 | 82.54 | 27.54 | 1041012 | 86.751 | 86.751 | 74.225 | 26.4043 | 628423.1494 | 52.3686 | 52.3686 | 139.1196 | 0.8 | 83.76 | 28.76 | 1087128 | 90.594 | 90.594 | 75.8826 | 28.062 | 667874.4851 | 55.6562 | 55.6562 | 146.2502 | 0.9 | 84.98 | 29.98 | 1133244 | 94.437 | 94.437 | 77.5402 | 29.7196 | 707325.8207 | 58.9438 | 58.9438 | 153.3808 | 1 | 86.2 | 31.2 | 1179360 | 98.28 | 98.28 | 79.1978 | 31.3772 | 746777.1563 | 62.2314 | 62.2314 | 160.5114 | 85 | 40 | 33.1376 | 34 | 42.3
7/5/20XX 3:00:00 PM | 0.625 | 4 | 85.4 | 43.4 | 72.9026 | 91.5706 | 18.6681 | 40 | 85.4 |  | 85.4 | 79.2497 | 0.1 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 64.2844 | 16.4638 | 391838.6095 | 32.6532 | 32.6532 | 96.0942 | 0.2 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 65.9472 | 18.1266 | 431413.4191 | 35.9511 | 35.9511 | 102.9831 | 0.3 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 67.6101 | 19.7894 | 470988.2286 | 39.249 | 39.249 | 109.872 | 0.4 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 69.2729 | 21.4522 | 510563.0381 | 42.5469 | 42.5469 | 116.7609 | 0.5 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 70.9357 | 23.115 | 550137.8476 | 45.8448 | 45.8448 | 123.6498 | 0.6 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 72.5985 | 24.7778 | 589712.6572 | 49.1427 | 49.1427 | 130.5387 | 0.7 | 81.98 | 26.98 | 1019844 | 84.987 | 84.987 | 74.2613 | 26.4406 | 629287.4667 | 52.4406 | 52.4406 | 137.4276 | 0.8 | 83.12 | 28.12 | 1062936 | 88.578 | 88.578 | 75.9241 | 28.1035 | 668862.2762 | 55.7385 | 55.7385 | 144.3165 | 0.9 | 84.26 | 29.26 | 1106028 | 92.169 | 92.169 | 77.5869 | 29.7663 | 708437.0857 | 59.0364 | 59.0364 | 151.2054 | 1 | 85.4 | 30.4 | 1149120 | 95.76 | 95.76 | 79.2497 | 31.4291 | 748011.8953 | 62.3343 | 62.3343 | 158.0943 | 85 | 45 | 32.9497 | 32 | 43.4
7/5/20XX 4:00:00 PM | 0.66667 | 4 | 85.2 | 42.6 | 72.4368 | 90.982 | 18.5452 | 40 | 85.2 |  | 85.2 | 77.2586 | 0.1 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 64.0853 | 16.2647 | 387099.7368 | 32.2583 | 32.2583 | 95.6363 | 0.2 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 65.549 | 17.7284 | 421935.6735 | 35.1613 | 35.1613 | 102.0673 | 0.3 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 67.0127 | 19.1921 | 456771.6103 | 38.0643 | 38.0643 | 108.4983 | 0.4 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 68.4764 | 20.6558 | 491607.547 | 40.9673 | 40.9673 | 114.9293 | 0.5 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 69.9401 | 22.1195 | 526443.4838 | 43.8703 | 43.8703 | 121.3603 | 0.6 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 71.4038 | 23.5832 | 561279.4206 | 46.7733 | 46.7733 | 127.7913 | 0.7 | 81.84 | 26.84 | 1014552 | 84.546 | 84.546 | 72.8675 | 25.0469 | 596115.3573 | 49.6763 | 49.6763 | 134.2223 | 0.8 | 82.96 | 27.96 | 1056888 | 88.074 | 88.074 | 74.3312 | 26.5106 | 630951.2941 | 52.5793 | 52.5793 | 140.6533 | 0.9 | 84.08 | 29.08 | 1099224 | 91.602 | 91.602 | 75.7949 | 27.9743 | 665787.2308 | 55.4823 | 55.4823 | 147.0843 | 1 | 85.2 | 30.2 | 1141560 | 95.13 | 95.13 | 77.2586 | 29.4379 | 700623.1676 | 58.3853 | 58.3853 | 153.5153 | 85 | 45 | 32.5878 | 32 | 42.6
7/5/20XX 5:00:00 PM | 0.70833 | 4 | 84.7 | 43.7 | 71.283 | 89.5239 | 18.241 | 40 | 84.7 |  | 84.7 | 78.0321 | 0.1 | 75.07 | 20.07 | 758646 | 63.2205 | 63.2205 | 64.1627 | 16.342 | 388940.7306 | 32.4117 | 32.4117 | 95.6322 | 0.2 | 76.14 | 21.14 | 799092 | 66.591 | 66.591 | 65.7037 | 17.8831 | 425617.6611 | 35.4681 | 35.4681 | 102.0591 | 0.3 | 77.21 | 22.21 | 839538 | 69.9615 | 69.9615 | 67.2448 | 19.4241 | 462294.5917 | 38.5245 | 38.5245 | 108.486 | 0.4 | 78.28 | 23.28 | 879984 | 73.332 | 73.332 | 68.7858 | 20.9652 | 498971.5222 | 41.581 | 41.581 | 114.913 | 0.5 | 79.35 | 24.35 | 920430 | 76.7025 | 76.7025 | 70.3269 | 22.5062 | 535648.4528 | 44.6374 | 44.6374 | 121.3399 | 0.6 | 80.42 | 25.42 | 960876 | 80.073 | 80.073 | 71.8679 | 24.0473 | 572325.3833 | 47.6938 | 47.6938 | 127.7668 | 0.7 | 81.49 | 26.49 | 1001322 | 83.4435 | 83.4435 | 73.409 | 25.5883 | 609002.3139 | 50.7502 | 50.7502 | 134.1937 | 0.8 | 82.56 | 27.56 | 1041768 | 86.814 | 86.814 | 74.95 | 27.1294 | 645679.2444 | 53.8066 | 53.8066 | 140.6206 | 0.9 | 83.63 | 28.63 | 1082214 | 90.1845 | 90.1845 | 76.4911 | 28.6704 | 682356.175 | 56.863 | 56.863 | 147.0475 | 1 | 84.7 | 29.7 | 1122660 | 93.555 | 93.555 | 78.0321 | 30.2115 | 719033.1055 | 59.9194 | 59.9194 | 153.4744 | 85 | 45 | 32.5869 | 32 | 43.7
7/5/20XX 6:00:00 PM | 0.75 | 4 | 83.6 | 45.8 | 68.7966 | 86.3826 | 17.586 | 40 | 83.6 |  | 83.6 | 78.9964 | 0.1 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 64.2591 | 16.4385 | 391235.846 | 32.603 | 32.603 | 95.477 | 0.2 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 65.8966 | 18.076 | 430207.892 | 35.8507 | 35.8507 | 101.7487 | 0.3 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 67.5341 | 19.7134 | 469179.938 | 39.0983 | 39.0983 | 108.0203 | 0.4 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 69.1716 | 21.3509 | 508151.984 | 42.346 | 42.346 | 114.292 | 0.5 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 70.809 | 22.9884 | 547124.03 | 45.5937 | 45.5937 | 120.5637 | 0.6 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 72.4465 | 24.6259 | 586096.076 | 48.8413 | 48.8413 | 126.8353 | 0.7 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 74.084 | 26.2634 | 625068.122 | 52.089 | 52.089 | 133.107 | 0.8 | 81.68 | 26.68 | 1008504 | 84.042 | 84.042 | 75.7215 | 27.9008 | 664040.168 | 55.3367 | 55.3367 | 139.3787 | 0.9 | 82.64 | 27.64 | 1044792 | 87.066 | 87.066 | 77.359 | 29.5383 | 703012.214 | 58.5844 | 58.5844 | 145.6504 | 1 | 83.6 | 28.6 | 1081080 | 90.09 | 90.09 | 78.9964 | 31.1758 | 741984.2601 | 61.832 | 61.832 | 151.922 | 85 | 45 | 32.4689 | 32 | 45.8
7/5/20XX 7:00:00 PM | 0.79167 | 4 | 81.7 | 48.5 | 64.6678 | 81.168 | 16.5002 | 40 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/5/20XX 8:00:00 PM | 0.83333 | 4 | 80.1 | 50.6 | 76.9795 | 92.7289 | 15.7494 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/5/20XX 9:00:00 PM | 0.875 | 4 | 79.2 | 54.4 | 74.7029 | 89.9794 | 15.2766 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/5/20XX 10:00:00 PM | 0.91667 | 4 | 78.4 | 57.6 | 72.7264 | 87.5927 | 14.8663 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/5/20XX 11:00:00 PM | 0.95833 | 4 | 78 | 59 | 71.7546 | 86.4193 | 14.6647 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/5/20XX 12:00:00 AM | 0 | 5 | 77.1 | 61.8 | 83.8273 | 98.1177 | 14.2905 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/6/20XX 1:00:00 AM | 0.041667 | 5 | 76.3 | 65.8 | 81.5784 | 95.4774 | 13.8991 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/6/20XX 2:00:00 AM | 0.083333 | 5 | 75.4 | 67.9 | 79.1095 | 92.579 | 13.4695 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/6/20XX 3:00:00 AM | 0.125 | 5 | 74.5 | 70.4 | 89.7555 | 102.8978 | 13.1423 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/6/20XX 4:00:00 AM | 0.16667 | 5 | 74.4 | 70 | 89.4463 | 102.5422 | 13.0959 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/6/20XX 5:00:00 AM | 0.20833 | 5 | 74.1 | 71.5 | 88.5243 | 101.4817 | 12.9575 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/6/20XX 6:00:00 AM | 0.25 | 5 | 74.1 | 74 | 88.5243 | 101.4817 | 12.9575 | 70 | 74.1 |  | 74.1 | 93.7073 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 65.7302 | 17.9096 | 426247.5828 | 35.5206 | 35.5206 | 95.4021 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 68.8388 | 21.0181 | 500231.3656 | 41.6859 | 41.6859 | 101.5989 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 71.9473 | 24.1267 | 574215.1485 | 47.8513 | 47.8513 | 107.7958 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 75.0559 | 27.2352 | 648198.9313 | 54.0166 | 54.0166 | 113.9926 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 78.1644 | 30.3438 | 722182.7141 | 60.1819 | 60.1819 | 120.1894 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 81.273 | 33.4524 | 796166.4969 | 66.3472 | 66.3472 | 126.3862 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 84.3816 | 36.5609 | 870150.2798 | 72.5125 | 72.5125 | 132.583 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 87.4901 | 39.6695 | 944134.0626 | 78.6778 | 78.6778 | 138.7798 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 90.5987 | 42.7781 | 1018117.8454 | 84.8432 | 84.8432 | 144.9767 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 93.7073 | 45.8866 | 1092101.6282 | 91.0085 | 91.0085 | 151.1735 | 75 | 75 | 32.4424 | 32 | 74
7/6/20XX 7:00:00 AM | 0.29167 | 5 | 75.7 | 70.2 | 93.5368 | 107.2477 | 13.7109 | 70 | 75.7 |  | 75.7 | 93.811 | 0.1 | 74.17 | 19.17 | 724626 | 60.3855 | 60.3855 | 65.7406 | 17.9199 | 426494.4631 | 35.5412 | 35.5412 | 95.9267 | 0.2 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 68.8595 | 21.0389 | 500725.1262 | 41.7271 | 41.7271 | 102.6481 | 0.3 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 71.9784 | 24.1578 | 574955.7892 | 47.913 | 47.913 | 109.3695 | 0.4 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 75.0974 | 27.2767 | 649186.4523 | 54.0989 | 54.0989 | 116.0909 | 0.5 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 78.2163 | 30.3957 | 723417.1154 | 60.2848 | 60.2848 | 122.8123 | 0.6 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 81.3352 | 33.5146 | 797647.7785 | 66.4706 | 66.4706 | 129.5336 | 0.7 | 75.19 | 20.19 | 763182 | 63.5985 | 63.5985 | 84.4542 | 36.6335 | 871878.4415 | 72.6565 | 72.6565 | 136.255 | 0.8 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 87.5731 | 39.7525 | 946109.1046 | 78.8424 | 78.8424 | 142.9764 | 0.9 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 90.6921 | 42.8714 | 1020339.7677 | 85.0283 | 85.0283 | 149.6978 | 1 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 93.811 | 45.9904 | 1094570.4308 | 91.2142 | 91.2142 | 156.4192 | 75 | 70 | 32.8522 | 32 | 70.2
7/6/20XX 8:00:00 AM | 0.33333 | 5 | 77.6 | 65.9 | 85.2591 | 99.7988 | 14.5397 | 60 | 77.6 |  | 77.6 | 93.8376 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 65.7432 | 17.9226 | 426557.6911 | 35.5465 | 35.5465 | 96.5305 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 68.8648 | 21.0442 | 500851.5821 | 41.7376 | 41.7376 | 103.8556 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 71.9864 | 24.1658 | 575145.4732 | 47.9288 | 47.9288 | 111.1808 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 75.108 | 27.2874 | 649439.3642 | 54.1199 | 54.1199 | 118.5059 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 78.2296 | 30.409 | 723733.2553 | 60.3111 | 60.3111 | 125.8311 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 81.3512 | 33.5306 | 798027.1463 | 66.5023 | 66.5023 | 133.1563 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 84.4728 | 36.6521 | 872321.0374 | 72.6934 | 72.6934 | 140.4814 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 87.5944 | 39.7737 | 946614.9284 | 78.8846 | 78.8846 | 147.8066 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 90.716 | 42.8953 | 1020908.8195 | 85.0757 | 85.0757 | 155.1317 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 93.8376 | 46.0169 | 1095202.7105 | 91.2669 | 91.2669 | 162.4569 | 80 | 65 | 33.3237 | 34 | 65.9
7/6/20XX 9:00:00 AM | 0.375 | 5 | 79.6 | 62.2 | 91.1929 | 106.7659 | 15.5729 | 60 | 79.6 |  | 79.6 | 94.619 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.8214 | 18.0007 | 428417.4873 | 35.7015 | 35.7015 | 97.3155 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 69.0211 | 21.2005 | 504571.1746 | 42.0476 | 42.0476 | 105.4256 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 72.2208 | 24.4002 | 580724.8619 | 48.3937 | 48.3937 | 113.5357 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 75.4206 | 27.5999 | 656878.5493 | 54.7399 | 54.7399 | 121.6459 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 78.6203 | 30.7997 | 733032.2366 | 61.086 | 61.086 | 129.756 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 81.82 | 33.9994 | 809185.9239 | 67.4322 | 67.4322 | 137.8662 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 85.0198 | 37.1991 | 885339.6112 | 73.7783 | 73.7783 | 145.9763 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 88.2195 | 40.3989 | 961493.2985 | 80.1244 | 80.1244 | 154.0864 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 91.4192 | 43.5986 | 1037646.9858 | 86.4706 | 86.4706 | 162.1966 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 94.619 | 46.7983 | 1113800.6731 | 92.8167 | 92.8167 | 170.3067 | 80 | 60 | 33.9381 | 34 | 62.2
7/6/20XX 10:00:00 AM | 0.41667 | 5 | 81.3 | 57.7 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 92.7308 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 65.6326 | 17.8119 | 423923.7293 | 35.327 | 35.327 | 97.4765 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 68.6435 | 20.8228 | 495583.6586 | 41.2986 | 41.2986 | 105.7476 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 71.6544 | 23.8338 | 567243.5879 | 47.2703 | 47.2703 | 114.0188 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 74.6653 | 26.8447 | 638903.5172 | 53.242 | 53.242 | 122.29 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 77.6762 | 29.8556 | 710563.4465 | 59.2136 | 59.2136 | 130.5611 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 80.6872 | 32.8665 | 782223.3758 | 65.1853 | 65.1853 | 138.8323 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 83.6981 | 35.8774 | 853883.3051 | 71.1569 | 71.1569 | 147.1034 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 86.709 | 38.8884 | 925543.2344 | 77.1286 | 77.1286 | 155.3746 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 89.7199 | 41.8993 | 997203.1637 | 83.1003 | 83.1003 | 163.6458 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 92.7308 | 44.9102 | 1068863.093 | 89.0719 | 89.0719 | 171.9169 | 80 | 60 | 34.0601 | 34 | 57.7
7/6/20XX 11:00:00 AM | 0.45833 | 5 | 83.9 | 51.2 | 87.2303 | 105.1128 | 17.8825 | 50 | 83.9 |  | 83.9 | 89.3762 | 0.1 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 65.2971 | 17.4765 | 415939.6387 | 34.6616 | 34.6616 | 97.6301 | 0.2 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 67.9725 | 20.1519 | 479615.4774 | 39.968 | 39.968 | 106.055 | 0.3 | 76.97 | 21.97 | 830466 | 69.2055 | 69.2055 | 70.648 | 22.8274 | 543291.3161 | 45.2743 | 45.2743 | 114.4798 | 0.4 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 73.3235 | 25.5028 | 606967.1548 | 50.5806 | 50.5806 | 122.9046 | 0.5 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 75.9989 | 28.1783 | 670642.9935 | 55.8869 | 55.8869 | 131.3294 | 0.6 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 78.6744 | 30.8537 | 734318.8322 | 61.1932 | 61.1932 | 139.7542 | 0.7 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 81.3498 | 33.5292 | 797994.6709 | 66.4996 | 66.4996 | 148.1791 | 0.8 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 84.0253 | 36.2046 | 861670.5096 | 71.8059 | 71.8059 | 156.6039 | 0.9 | 82.91 | 27.91 | 1054998 | 87.9165 | 87.9165 | 86.7007 | 38.8801 | 925346.3483 | 77.1122 | 77.1122 | 165.0287 | 1 | 83.9 | 28.9 | 1092420 | 91.035 | 91.035 | 89.3762 | 41.5556 | 989022.187 | 82.4185 | 82.4185 | 173.4535 | 85 | 50 | 34.1725 | 34 | 51.2
7/6/20XX 12:00:00 PM | 0.5 | 5 | 85.4 | 49.6 | 72.9026 | 91.5706 | 18.6681 | 40 | 85.4 |  | 85.4 | 90.8239 | 0.1 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 65.4419 | 17.6212 | 419385.1973 | 34.9488 | 34.9488 | 98.3898 | 0.2 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 68.2621 | 20.4415 | 486506.5946 | 40.5422 | 40.5422 | 107.5742 | 0.3 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 71.0823 | 23.2617 | 553627.992 | 46.1357 | 46.1357 | 116.7587 | 0.4 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 73.9025 | 26.0819 | 620749.3893 | 51.7291 | 51.7291 | 125.9431 | 0.5 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 76.7228 | 28.9021 | 687870.7866 | 57.3226 | 57.3226 | 135.1276 | 0.6 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 79.543 | 31.7224 | 754992.1839 | 62.916 | 62.916 | 144.312 | 0.7 | 81.98 | 26.98 | 1019844 | 84.987 | 84.987 | 82.3632 | 34.5426 | 822113.5812 | 68.5095 | 68.5095 | 153.4965 | 0.8 | 83.12 | 28.12 | 1062936 | 88.578 | 88.578 | 85.1834 | 37.3628 | 889234.9786 | 74.1029 | 74.1029 | 162.6809 | 0.9 | 84.26 | 29.26 | 1106028 | 92.169 | 92.169 | 88.0037 | 40.183 | 956356.3759 | 79.6964 | 79.6964 | 171.8654 | 1 | 85.4 | 30.4 | 1149120 | 95.76 | 95.76 | 90.8239 | 43.0033 | 1023477.7732 | 85.2898 | 85.2898 | 181.0498 | 85 | 50 | 34.7685 | 34 | 49.6
7/6/20XX 1:00:00 PM | 0.54167 | 5 | 86.2 | 48.4 | 74.7896 | 93.9557 | 19.1661 | 40 | 86.2 |  | 86.2 | 90.8891 | 0.1 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 65.4484 | 17.6278 | 419540.4777 | 34.9617 | 34.9617 | 98.6547 | 0.2 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 68.2751 | 20.4545 | 486817.1553 | 40.5681 | 40.5681 | 108.1041 | 0.3 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 71.1019 | 23.2813 | 554093.833 | 46.1745 | 46.1745 | 117.5535 | 0.4 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 73.9286 | 26.108 | 621370.5106 | 51.7809 | 51.7809 | 127.0029 | 0.5 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 76.7554 | 28.9348 | 688647.1883 | 57.3873 | 57.3873 | 136.4523 | 0.6 | 81.32 | 26.32 | 994896 | 82.908 | 82.908 | 79.5821 | 31.7615 | 755923.8659 | 62.9937 | 62.9937 | 145.9017 | 0.7 | 82.54 | 27.54 | 1041012 | 86.751 | 86.751 | 82.4089 | 34.5883 | 823200.5436 | 68.6 | 68.6 | 155.351 | 0.8 | 83.76 | 28.76 | 1087128 | 90.594 | 90.594 | 85.2356 | 37.415 | 890477.2212 | 74.2064 | 74.2064 | 164.8004 | 0.9 | 84.98 | 29.98 | 1133244 | 94.437 | 94.437 | 88.0624 | 40.2418 | 957753.8989 | 79.8128 | 79.8128 | 174.2498 | 1 | 86.2 | 31.2 | 1179360 | 98.28 | 98.28 | 90.8891 | 43.0685 | 1025030.5765 | 85.4192 | 85.4192 | 183.6992 | 85 | 50 | 34.9754 | 34 | 48.4
7/6/20XX 2:00:00 PM | 0.58333 | 5 | 85.8 | 47.9 | 73.8413 | 92.757 | 18.9157 | 40 | 85.8 |  | 85.8 | 88.7847 | 0.1 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 65.2379 | 17.4173 | 414531.8911 | 34.5443 | 34.5443 | 98.1113 | 0.2 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 67.8542 | 20.0336 | 476799.9822 | 39.7333 | 39.7333 | 107.0173 | 0.3 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 70.4706 | 22.6499 | 539068.0733 | 44.9223 | 44.9223 | 115.9233 | 0.4 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 73.0869 | 25.2662 | 601336.1644 | 50.1113 | 50.1113 | 124.8293 | 0.5 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 75.7032 | 27.8825 | 663604.2555 | 55.3004 | 55.3004 | 133.7354 | 0.6 | 81.08 | 26.08 | 985824 | 82.152 | 82.152 | 78.3195 | 30.4988 | 725872.3465 | 60.4894 | 60.4894 | 142.6414 | 0.7 | 82.26 | 27.26 | 1030428 | 85.869 | 85.869 | 80.9358 | 33.1151 | 788140.4376 | 65.6784 | 65.6784 | 151.5474 | 0.8 | 83.44 | 28.44 | 1075032 | 89.586 | 89.586 | 83.5521 | 35.7315 | 850408.5287 | 70.8674 | 70.8674 | 160.4534 | 0.9 | 84.62 | 29.62 | 1119636 | 93.303 | 93.303 | 86.1684 | 38.3478 | 912676.6198 | 76.0564 | 76.0564 | 169.3594 | 1 | 85.8 | 30.8 | 1164240 | 97.02 | 97.02 | 88.7847 | 40.9641 | 974944.7109 | 81.2454 | 81.2454 | 178.2654 | 85 | 50 | 34.5463 | 34 | 47.9
7/6/20XX 3:00:00 PM | 0.625 | 5 | 84.9 | 49.6 | 71.7427 | 90.1049 | 18.3622 | 40 | 84.9 |  | 84.9 | 89.3704 | 0.1 | 75.09 | 20.09 | 759402 | 63.2835 | 63.2835 | 65.2965 | 17.4759 | 415925.853 | 34.6605 | 34.6605 | 97.944 | 0.2 | 76.18 | 21.18 | 800604 | 66.717 | 66.717 | 67.9714 | 20.1508 | 479587.9059 | 39.9657 | 39.9657 | 106.6827 | 0.3 | 77.27 | 22.27 | 841806 | 70.1505 | 70.1505 | 70.6463 | 22.8256 | 543249.9589 | 45.2708 | 45.2708 | 115.4213 | 0.4 | 78.36 | 23.36 | 883008 | 73.584 | 73.584 | 73.3211 | 25.5005 | 606912.0119 | 50.576 | 50.576 | 124.16 | 0.5 | 79.45 | 24.45 | 924210 | 77.0175 | 77.0175 | 75.996 | 28.1754 | 670574.0649 | 55.8812 | 55.8812 | 132.8987 | 0.6 | 80.54 | 25.54 | 965412 | 80.451 | 80.451 | 78.6709 | 30.8503 | 734236.1178 | 61.1863 | 61.1863 | 141.6373 | 0.7 | 81.63 | 26.63 | 1006614 | 83.8845 | 83.8845 | 81.3458 | 33.5251 | 797898.1708 | 66.4915 | 66.4915 | 150.376 | 0.8 | 82.72 | 27.72 | 1047816 | 87.318 | 87.318 | 84.0206 | 36.2 | 861560.2238 | 71.7967 | 71.7967 | 159.1147 | 0.9 | 83.81 | 28.81 | 1089018 | 90.7515 | 90.7515 | 86.6955 | 38.8749 | 925222.2768 | 77.1019 | 77.1019 | 167.8534 | 1 | 84.9 | 29.9 | 1130220 | 94.185 | 94.185 | 89.3704 | 41.5498 | 988884.3297 | 82.407 | 82.407 | 176.592 | 85 | 50 | 34.4173 | 34 | 49.6
7/6/20XX 4:00:00 PM | 0.66667 | 5 | 84.7 | 47.7 | 71.283 | 89.5239 | 18.241 | 40 | 84.7 |  | 84.7 | 85.3285 | 0.1 | 75.07 | 20.07 | 758646 | 63.2205 | 63.2205 | 64.8923 | 17.0717 | 406306.1295 | 33.8588 | 33.8588 | 97.0793 | 0.2 | 76.14 | 21.14 | 799092 | 66.591 | 66.591 | 67.163 | 19.3424 | 460348.459 | 38.3624 | 38.3624 | 104.9534 | 0.3 | 77.21 | 22.21 | 839538 | 69.9615 | 69.9615 | 69.4337 | 21.6131 | 514390.7885 | 42.8659 | 42.8659 | 112.8274 | 0.4 | 78.28 | 23.28 | 879984 | 73.332 | 73.332 | 71.7044 | 23.8837 | 568433.118 | 47.3694 | 47.3694 | 120.7014 | 0.5 | 79.35 | 24.35 | 920430 | 76.7025 | 76.7025 | 73.9751 | 26.1544 | 622475.4475 | 51.873 | 51.873 | 128.5755 | 0.6 | 80.42 | 25.42 | 960876 | 80.073 | 80.073 | 76.2457 | 28.4251 | 676517.777 | 56.3765 | 56.3765 | 136.4495 | 0.7 | 81.49 | 26.49 | 1001322 | 83.4435 | 83.4435 | 78.5164 | 30.6958 | 730560.1065 | 60.88 | 60.88 | 144.3235 | 0.8 | 82.56 | 27.56 | 1041768 | 86.814 | 86.814 | 80.7871 | 32.9665 | 784602.436 | 65.3835 | 65.3835 | 152.1975 | 0.9 | 83.63 | 28.63 | 1082214 | 90.1845 | 90.1845 | 83.0578 | 35.2372 | 838644.7655 | 69.8871 | 69.8871 | 160.0716 | 1 | 84.7 | 29.7 | 1122660 | 93.555 | 93.555 | 85.3285 | 37.5079 | 892687.095 | 74.3906 | 74.3906 | 167.9456 | 85 | 50 | 33.7332 | 34 | 47.7
7/6/20XX 5:00:00 PM | 0.70833 | 5 | 84.2 | 47.8 | 70.1439 | 88.0847 | 17.9408 | 40 | 84.2 |  | 84.2 | 84.1378 | 0.1 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 64.7732 | 16.9526 | 403472.2045 | 33.6227 | 33.6227 | 96.6857 | 0.2 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 66.9249 | 19.1042 | 454680.609 | 37.8901 | 37.8901 | 104.1661 | 0.3 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 69.0765 | 21.2558 | 505889.0135 | 42.1574 | 42.1574 | 111.6464 | 0.4 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 71.2281 | 23.4075 | 557097.418 | 46.4248 | 46.4248 | 119.1268 | 0.5 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 73.3797 | 25.5591 | 608305.8225 | 50.6922 | 50.6922 | 126.6072 | 0.6 | 80.12 | 25.12 | 949536 | 79.128 | 79.128 | 75.5313 | 27.7107 | 659514.227 | 54.9595 | 54.9595 | 134.0875 | 0.7 | 81.14 | 26.14 | 988092 | 82.341 | 82.341 | 77.6829 | 29.8623 | 710722.6316 | 59.2269 | 59.2269 | 141.5679 | 0.8 | 82.16 | 27.16 | 1026648 | 85.554 | 85.554 | 79.8345 | 32.0139 | 761931.0361 | 63.4943 | 63.4943 | 149.0483 | 0.9 | 83.18 | 28.18 | 1065204 | 88.767 | 88.767 | 81.9862 | 34.1655 | 813139.4406 | 67.7616 | 67.7616 | 156.5286 | 1 | 84.2 | 29.2 | 1103760 | 91.98 | 91.98 | 84.1378 | 36.3171 | 864347.8451 | 72.029 | 72.029 | 164.009 | 85 | 50 | 33.4234 | 34 | 47.8
7/6/20XX 6:00:00 PM | 0.75 | 5 | 82.7 | 51 | 83.8795 | 101.064 | 17.1846 | 50 | 82.7 |  | 82.7 | 85.5979 | 0.1 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 64.9193 | 17.0986 | 406947.3902 | 33.9123 | 33.9123 | 96.5028 | 0.2 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 67.2169 | 19.3963 | 461630.9804 | 38.4692 | 38.4692 | 103.8002 | 0.3 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 69.5145 | 21.6939 | 516314.5705 | 43.0262 | 43.0262 | 111.0977 | 0.4 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 71.8122 | 23.9915 | 570998.1607 | 47.5832 | 47.5832 | 118.3952 | 0.5 | 78.35 | 23.35 | 882630 | 73.5525 | 73.5525 | 74.1098 | 26.2891 | 625681.7509 | 52.1401 | 52.1401 | 125.6926 | 0.6 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 76.4074 | 28.5868 | 680365.3411 | 56.6971 | 56.6971 | 132.9901 | 0.7 | 80.09 | 25.09 | 948402 | 79.0335 | 79.0335 | 78.705 | 30.8844 | 735048.9312 | 61.2541 | 61.2541 | 140.2876 | 0.8 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 81.0027 | 33.182 | 789732.5214 | 65.811 | 65.811 | 147.585 | 0.9 | 81.83 | 26.83 | 1014174 | 84.5145 | 84.5145 | 83.3003 | 35.4797 | 844416.1116 | 70.368 | 70.368 | 154.8825 | 1 | 82.7 | 27.7 | 1047060 | 87.255 | 87.255 | 85.5979 | 37.7773 | 899099.7018 | 74.925 | 74.925 | 162.18 | 85 | 50 | 33.2846 | 34 | 51
7/6/20XX 7:00:00 PM | 0.79167 | 5 | 81.3 | 52.4 | 80.1037 | 96.5026 | 16.3989 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/6/20XX 8:00:00 PM | 0.83333 | 5 | 80.2 | 54.9 | 77.2359 | 93.0386 | 15.8027 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/6/20XX 9:00:00 PM | 0.875 | 5 | 79.5 | 56.6 | 75.4555 | 90.8883 | 15.4328 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/6/20XX 10:00:00 PM | 0.91667 | 5 | 78.8 | 59.2 | 73.7091 | 88.7794 | 15.0703 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/6/20XX 11:00:00 PM | 0.95833 | 5 | 78 | 62.4 | 86.4193 | 101.161 | 14.7417 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/6/20XX 12:00:00 AM | 0 | 6 | 77.3 | 64.6 | 84.3976 | 98.7873 | 14.3897 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/7/20XX 1:00:00 AM | 0.041667 | 6 | 76.4 | 67.2 | 81.8567 | 95.8042 | 13.9475 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/7/20XX 2:00:00 AM | 0.083333 | 6 | 75.7 | 69 | 79.9253 | 93.5368 | 13.6115 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/7/20XX 3:00:00 AM | 0.125 | 6 | 75.5 | 70.4 | 92.8973 | 106.512 | 13.6147 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/7/20XX 4:00:00 AM | 0.16667 | 6 | 74.6 | 74 | 90.0655 | 103.2545 | 13.1889 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/7/20XX 5:00:00 AM | 0.20833 | 6 | 74.1 | 74.2 | 88.5243 | 101.4817 | 12.9575 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/7/20XX 6:00:00 AM | 0.25 | 6 | 74.9 | 73.2 | 91.0012 | 104.3307 | 13.3295 | 70 | 74.9 |  | 74.9 | 95.2666 | 0.1 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 65.8861 | 18.0655 | 429958.9381 | 35.8299 | 35.8299 | 95.9634 | 0.2 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 69.1506 | 21.33 | 507654.0763 | 42.3045 | 42.3045 | 102.7215 | 0.3 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 72.4151 | 24.5945 | 585349.2144 | 48.7791 | 48.7791 | 109.4796 | 0.4 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 75.6796 | 27.859 | 663044.3526 | 55.2537 | 55.2537 | 116.2377 | 0.5 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 78.9441 | 31.1235 | 740739.4907 | 61.7283 | 61.7283 | 122.9958 | 0.6 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 82.2086 | 34.388 | 818434.6289 | 68.2029 | 68.2029 | 129.7539 | 0.7 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 85.4731 | 37.6525 | 896129.767 | 74.6775 | 74.6775 | 136.512 | 0.8 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 88.7376 | 40.917 | 973824.9052 | 81.1521 | 81.1521 | 143.2701 | 0.9 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 92.0021 | 44.1815 | 1051520.0433 | 87.6267 | 87.6267 | 150.0282 | 1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 95.2666 | 47.446 | 1129215.1815 | 94.1013 | 94.1013 | 156.7863 | 75 | 75 | 32.8832 | 32 | 73.2
7/7/20XX 7:00:00 AM | 0.29167 | 6 | 75.7 | 71.7 | 93.5368 | 107.2477 | 13.7109 | 70 | 75.7 |  | 75.7 | 95.8676 | 0.1 | 74.17 | 19.17 | 724626 | 60.3855 | 60.3855 | 65.9462 | 18.1256 | 431389.2488 | 35.9491 | 35.9491 | 96.3346 | 0.2 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 69.2708 | 21.4502 | 510514.6976 | 42.5429 | 42.5429 | 103.4639 | 0.3 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 72.5954 | 24.7748 | 589640.1464 | 49.1367 | 49.1367 | 110.5932 | 0.4 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 75.92 | 28.0994 | 668765.5952 | 55.7305 | 55.7305 | 117.7225 | 0.5 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 79.2446 | 31.424 | 747891.044 | 62.3243 | 62.3243 | 124.8518 | 0.6 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 82.5692 | 34.7486 | 827016.4928 | 68.918 | 68.918 | 131.981 | 0.7 | 75.19 | 20.19 | 763182 | 63.5985 | 63.5985 | 85.8938 | 38.0732 | 906141.9416 | 75.5118 | 75.5118 | 139.1103 | 0.8 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 89.2184 | 41.3978 | 985267.3904 | 82.1056 | 82.1056 | 146.2396 | 0.9 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 92.543 | 44.7224 | 1064392.8392 | 88.6994 | 88.6994 | 153.3689 | 1 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 95.8676 | 48.047 | 1143518.288 | 95.2932 | 95.2932 | 160.4982 | 75 | 70 | 33.1741 | 34 | 71.7
7/7/20XX 8:00:00 AM | 0.33333 | 6 | 78.1 | 65.9 | 86.7115 | 101.504 | 14.7925 | 60 | 78.1 |  | 78.1 | 95.439 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 65.9034 | 18.0827 | 430369.2426 | 35.8641 | 35.8641 | 97.0056 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 69.1851 | 21.3645 | 508474.6851 | 42.3729 | 42.3729 | 104.8059 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 72.4669 | 24.6462 | 586580.1277 | 48.8817 | 48.8817 | 112.6062 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 75.7486 | 27.928 | 664685.5702 | 55.3905 | 55.3905 | 120.4065 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 79.0303 | 31.2097 | 742791.0128 | 61.8993 | 61.8993 | 128.2068 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 82.3121 | 34.4914 | 820896.4553 | 68.408 | 68.408 | 136.007 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 85.5938 | 37.7732 | 899001.8979 | 74.9168 | 74.9168 | 143.8073 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 88.8756 | 41.0549 | 977107.3404 | 81.4256 | 81.4256 | 151.6076 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 92.1573 | 44.3367 | 1055212.783 | 87.9344 | 87.9344 | 159.4079 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 95.439 | 47.6184 | 1133318.2255 | 94.4432 | 94.4432 | 167.2082 | 80 | 65 | 33.6976 | 34 | 65.9
7/7/20XX 9:00:00 AM | 0.375 | 6 | 79.9 | 61.1 | 92.1119 | 107.8449 | 15.733 | 60 | 79.9 |  | 79.9 | 93.8426 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 65.7437 | 17.9231 | 426569.6442 | 35.5475 | 35.5475 | 97.256 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 68.8658 | 21.0452 | 500875.4885 | 41.7396 | 41.7396 | 105.3066 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 71.9879 | 24.1673 | 575181.3327 | 47.9318 | 47.9318 | 113.3573 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 75.11 | 27.2894 | 649487.1769 | 54.1239 | 54.1239 | 121.4079 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 78.2321 | 30.4115 | 723793.0211 | 60.3161 | 60.3161 | 129.4586 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 81.3542 | 33.5336 | 798098.8654 | 66.5082 | 66.5082 | 137.5092 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 84.4763 | 36.6557 | 872404.7096 | 72.7004 | 72.7004 | 145.5599 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 87.5984 | 39.7778 | 946710.5538 | 78.8925 | 78.8925 | 153.6105 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 90.7205 | 42.8998 | 1021016.3981 | 85.0847 | 85.0847 | 161.6612 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 93.8426 | 46.0219 | 1095322.2423 | 91.2769 | 91.2769 | 169.7119 | 80 | 60 | 33.8901 | 34 | 61.1
7/7/20XX 10:00:00 AM | 0.41667 | 6 | 81.7 | 57.1 | 81.168 | 97.7883 | 16.6202 | 50 | 81.7 |  | 81.7 | 92.9684 | 0.1 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 65.6563 | 17.8357 | 424489.0671 | 35.3741 | 35.3741 | 97.6496 | 0.2 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 68.691 | 20.8704 | 496714.3342 | 41.3929 | 41.3929 | 106.0939 | 0.3 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 71.7257 | 23.905 | 568939.6013 | 47.4116 | 47.4116 | 114.5381 | 0.4 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 74.7603 | 26.9397 | 641164.8684 | 53.4304 | 53.4304 | 122.9824 | 0.5 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 77.795 | 29.9744 | 713390.1355 | 59.4492 | 59.4492 | 131.4267 | 0.6 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 80.8297 | 33.0091 | 785615.4026 | 65.468 | 65.468 | 139.871 | 0.7 | 79.39 | 24.39 | 921942 | 76.8285 | 76.8285 | 83.8644 | 36.0437 | 857840.6697 | 71.4867 | 71.4867 | 148.3152 | 0.8 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 86.899 | 39.0784 | 930065.9368 | 77.5055 | 77.5055 | 156.7595 | 0.9 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 89.9337 | 42.1131 | 1002291.2039 | 83.5243 | 83.5243 | 165.2038 | 1 | 81.7 | 26.7 | 1009260 | 84.105 | 84.105 | 92.9684 | 45.1478 | 1074516.471 | 89.543 | 89.543 | 173.648 | 80 | 55 | 34.1957 | 34 | 57.1
7/7/20XX 11:00:00 AM | 0.45833 | 6 | 83.7 | 54.3 | 86.6644 | 104.429 | 17.7646 | 50 | 83.7 |  | 83.7 | 94.3032 | 0.1 | 74.97 | 19.97 | 754866 | 62.9055 | 62.9055 | 65.7898 | 17.9692 | 427665.8571 | 35.6388 | 35.6388 | 98.5443 | 0.2 | 75.94 | 20.94 | 791532 | 65.961 | 65.961 | 68.9579 | 21.1373 | 503067.9141 | 41.9223 | 41.9223 | 107.8833 | 0.3 | 76.91 | 21.91 | 828198 | 69.0165 | 69.0165 | 72.1261 | 24.3055 | 578469.9712 | 48.2058 | 48.2058 | 117.2223 | 0.4 | 77.88 | 22.88 | 864864 | 72.072 | 72.072 | 75.2942 | 27.4736 | 653872.0283 | 54.4893 | 54.4893 | 126.5613 | 0.5 | 78.85 | 23.85 | 901530 | 75.1275 | 75.1275 | 78.4624 | 30.6418 | 729274.0853 | 60.7728 | 60.7728 | 135.9003 | 0.6 | 79.82 | 24.82 | 938196 | 78.183 | 78.183 | 81.6306 | 33.8099 | 804676.1424 | 67.0563 | 67.0563 | 145.2393 | 0.7 | 80.79 | 25.79 | 974862 | 81.2385 | 81.2385 | 84.7987 | 36.9781 | 880078.1995 | 73.3398 | 73.3398 | 154.5783 | 0.8 | 81.76 | 26.76 | 1011528 | 84.294 | 84.294 | 87.9669 | 40.1462 | 955480.2566 | 79.6234 | 79.6234 | 163.9174 | 0.9 | 82.73 | 27.73 | 1048194 | 87.3495 | 87.3495 | 91.135 | 43.3144 | 1030882.3136 | 85.9069 | 85.9069 | 173.2564 | 1 | 83.7 | 28.7 | 1084860 | 90.405 | 90.405 | 94.3032 | 46.4825 | 1106284.3707 | 92.1904 | 92.1904 | 182.5954 | 85 | 55 | 34.8971 | 34 | 54.3
7/7/20XX 12:00:00 PM | 0.5 | 6 | 84.9 | 52.4 | 90.1049 | 108.5867 | 18.4818 | 50 | 84.9 |  | 84.9 | 94.5405 | 0.1 | 75.09 | 20.09 | 759402 | 63.2835 | 63.2835 | 65.8135 | 17.9929 | 428230.7442 | 35.6859 | 35.6859 | 98.9694 | 0.2 | 76.18 | 21.18 | 800604 | 66.717 | 66.717 | 69.0054 | 21.1848 | 504197.6884 | 42.0165 | 42.0165 | 108.7335 | 0.3 | 77.27 | 22.27 | 841806 | 70.1505 | 70.1505 | 72.1973 | 24.3767 | 580164.6326 | 48.3471 | 48.3471 | 118.4976 | 0.4 | 78.36 | 23.36 | 883008 | 73.584 | 73.584 | 75.3892 | 27.5686 | 656131.5769 | 54.6776 | 54.6776 | 128.2616 | 0.5 | 79.45 | 24.45 | 924210 | 77.0175 | 77.0175 | 78.5811 | 30.7604 | 732098.5211 | 61.0082 | 61.0082 | 138.0257 | 0.6 | 80.54 | 25.54 | 965412 | 80.451 | 80.451 | 81.773 | 33.9523 | 808065.4653 | 67.3388 | 67.3388 | 147.7898 | 0.7 | 81.63 | 26.63 | 1006614 | 83.8845 | 83.8845 | 84.9649 | 37.1442 | 884032.4095 | 73.6694 | 73.6694 | 157.5539 | 0.8 | 82.72 | 27.72 | 1047816 | 87.318 | 87.318 | 88.1567 | 40.3361 | 959999.3537 | 79.9999 | 79.9999 | 167.3179 | 0.9 | 83.81 | 28.81 | 1089018 | 90.7515 | 90.7515 | 91.3486 | 43.528 | 1035966.2979 | 86.3305 | 86.3305 | 177.082 | 1 | 84.9 | 29.9 | 1130220 | 94.185 | 94.185 | 94.5405 | 46.7199 | 1111933.2421 | 92.6611 | 92.6611 | 186.8461 | 85 | 50 | 35.2296 | 36 | 52.4
7/7/20XX 1:00:00 PM | 0.54167 | 6 | 85.2 | 52.9 | 90.982 | 109.6468 | 18.6648 | 50 | 85.2 |  | 85.2 | 96.3948 | 0.1 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 65.999 | 18.1783 | 432643.9798 | 36.0537 | 36.0537 | 99.4317 | 0.2 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 69.3763 | 21.5556 | 513024.1596 | 42.752 | 42.752 | 109.658 | 0.3 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 72.7536 | 24.933 | 593404.3394 | 49.4504 | 49.4504 | 119.8844 | 0.4 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 76.1309 | 28.3103 | 673784.5193 | 56.1487 | 56.1487 | 130.1107 | 0.5 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 79.5082 | 31.6876 | 754164.6991 | 62.8471 | 62.8471 | 140.3371 | 0.6 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 82.8855 | 35.0649 | 834544.8789 | 69.5454 | 69.5454 | 150.5634 | 0.7 | 81.84 | 26.84 | 1014552 | 84.546 | 84.546 | 86.2629 | 38.4422 | 914925.0587 | 76.2438 | 76.2438 | 160.7898 | 0.8 | 82.96 | 27.96 | 1056888 | 88.074 | 88.074 | 89.6402 | 41.8195 | 995305.2385 | 82.9421 | 82.9421 | 171.0161 | 0.9 | 84.08 | 29.08 | 1099224 | 91.602 | 91.602 | 93.0175 | 45.1969 | 1075685.4183 | 89.6405 | 89.6405 | 181.2425 | 1 | 85.2 | 30.2 | 1141560 | 95.13 | 95.13 | 96.3948 | 48.5742 | 1156065.5982 | 96.3388 | 96.3388 | 191.4688 | 85 | 55 | 35.5948 | 36 | 52.9
7/7/20XX 2:00:00 PM | 0.58333 | 6 | 84.8 | 53.4 | 89.814 | 108.2352 | 18.4212 | 50 | 84.8 |  | 84.8 | 96.0772 | 0.1 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 65.9672 | 18.1466 | 431888.0801 | 35.9907 | 35.9907 | 99.2427 | 0.2 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 69.3127 | 21.4921 | 511512.3603 | 42.626 | 42.626 | 109.28 | 0.3 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 72.6583 | 24.8377 | 591136.6404 | 49.2614 | 49.2614 | 119.3174 | 0.4 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 76.0039 | 28.1832 | 670760.9206 | 55.8967 | 55.8967 | 129.3547 | 0.5 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 79.3494 | 31.5288 | 750385.2007 | 62.5321 | 62.5321 | 139.3921 | 0.6 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 82.695 | 34.8743 | 830009.4809 | 69.1675 | 69.1675 | 149.4295 | 0.7 | 81.56 | 26.56 | 1003968 | 83.664 | 83.664 | 86.0405 | 38.2199 | 909633.761 | 75.8028 | 75.8028 | 159.4668 | 0.8 | 82.64 | 27.64 | 1044792 | 87.066 | 87.066 | 89.3861 | 41.5655 | 989258.0411 | 82.4382 | 82.4382 | 169.5042 | 0.9 | 83.72 | 28.72 | 1085616 | 90.468 | 90.468 | 92.7317 | 44.911 | 1068882.3213 | 89.0735 | 89.0735 | 179.5415 | 1 | 84.8 | 29.8 | 1126440 | 93.87 | 93.87 | 96.0772 | 48.2566 | 1148506.6014 | 95.7089 | 95.7089 | 189.5789 | 85 | 55 | 35.4464 | 36 | 53.4
7/7/20XX 3:00:00 PM | 0.625 | 6 | 84.2 | 56.8 | 88.0847 | 106.1454 | 18.0606 | 50 | 84.2 |  | 84.2 | 100.366 | 0.1 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 66.3961 | 18.5754 | 442095.3301 | 36.8413 | 36.8413 | 99.9043 | 0.2 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 70.1705 | 22.3499 | 531926.8602 | 44.3272 | 44.3272 | 110.6032 | 0.3 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 73.9449 | 26.1243 | 621758.3903 | 51.8132 | 51.8132 | 121.3022 | 0.4 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 77.7194 | 29.8987 | 711589.9205 | 59.2992 | 59.2992 | 132.0012 | 0.5 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 81.4938 | 33.6732 | 801421.4506 | 66.7851 | 66.7851 | 142.7001 | 0.6 | 80.12 | 25.12 | 949536 | 79.128 | 79.128 | 85.2682 | 37.4476 | 891252.9807 | 74.2711 | 74.2711 | 153.3991 | 0.7 | 81.14 | 26.14 | 988092 | 82.341 | 82.341 | 89.0427 | 41.222 | 981084.5108 | 81.757 | 81.757 | 164.098 | 0.8 | 82.16 | 27.16 | 1026648 | 85.554 | 85.554 | 92.8171 | 44.9965 | 1070916.0409 | 89.243 | 89.243 | 174.797 | 0.9 | 83.18 | 28.18 | 1065204 | 88.767 | 88.767 | 96.5915 | 48.7709 | 1160747.571 | 96.729 | 96.729 | 185.496 | 1 | 84.2 | 29.2 | 1103760 | 91.98 | 91.98 | 100.366 | 52.5453 | 1250579.1011 | 104.2149 | 104.2149 | 196.1949 | 85 | 55 | 35.9724 | 36 | 56.8
7/7/20XX 4:00:00 PM | 0.66667 | 6 | 82.7 | 58.4 | 83.8795 | 101.064 | 17.1846 | 50 | 82.7 |  | 82.7 | 98.3145 | 0.1 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 66.1909 | 18.3703 | 437212.8511 | 36.4344 | 36.4344 | 99.0249 | 0.2 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 69.7602 | 21.9396 | 522161.9021 | 43.5135 | 43.5135 | 108.8445 | 0.3 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 73.3295 | 25.5089 | 607110.9532 | 50.5926 | 50.5926 | 118.6641 | 0.4 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 76.8988 | 29.0782 | 692060.0042 | 57.6717 | 57.6717 | 128.4837 | 0.5 | 78.35 | 23.35 | 882630 | 73.5525 | 73.5525 | 80.4681 | 32.6474 | 777009.0553 | 64.7508 | 64.7508 | 138.3033 | 0.6 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 84.0374 | 36.2167 | 861958.1063 | 71.8298 | 71.8298 | 148.1228 | 0.7 | 80.09 | 25.09 | 948402 | 79.0335 | 79.0335 | 87.6066 | 39.786 | 946907.1574 | 78.9089 | 78.9089 | 157.9424 | 0.8 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 91.1759 | 43.3553 | 1031856.2084 | 85.988 | 85.988 | 167.762 | 0.9 | 81.83 | 26.83 | 1014174 | 84.5145 | 84.5145 | 94.7452 | 46.9246 | 1116805.2595 | 93.0671 | 93.0671 | 177.5816 | 1 | 82.7 | 27.7 | 1047060 | 87.255 | 87.255 | 98.3145 | 50.4939 | 1201754.3105 | 100.1462 | 100.1462 | 187.4012 | 85 | 60 | 35.2808 | 36 | 58.4
7/7/20XX 5:00:00 PM | 0.70833 | 6 | 82.2 | 59.9 | 82.5146 | 99.4151 | 16.9005 | 50 | 82.2 |  | 82.2 | 99.2461 | 0.1 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 66.2841 | 18.4634 | 439430.0034 | 36.6192 | 36.6192 | 99.0522 | 0.2 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 69.9465 | 22.1259 | 526596.2067 | 43.883 | 43.883 | 108.899 | 0.3 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 73.609 | 25.7883 | 613762.4101 | 51.1469 | 51.1469 | 118.7459 | 0.4 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 77.2714 | 29.4508 | 700928.6134 | 58.4107 | 58.4107 | 128.5927 | 0.5 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 80.9339 | 33.1132 | 788094.8168 | 65.6746 | 65.6746 | 138.4396 | 0.6 | 78.92 | 23.92 | 904176 | 75.348 | 75.348 | 84.5963 | 36.7757 | 875261.0202 | 72.9384 | 72.9384 | 148.2864 | 0.7 | 79.74 | 24.74 | 935172 | 77.931 | 77.931 | 88.2588 | 40.4381 | 962427.2235 | 80.2023 | 80.2023 | 158.1333 | 0.8 | 80.56 | 25.56 | 966168 | 80.514 | 80.514 | 91.9212 | 44.1006 | 1049593.4269 | 87.4661 | 87.4661 | 167.9801 | 0.9 | 81.38 | 26.38 | 997164 | 83.097 | 83.097 | 95.5836 | 47.763 | 1136759.6302 | 94.73 | 94.73 | 177.827 | 1 | 82.2 | 27.2 | 1028160 | 85.68 | 85.68 | 99.2461 | 51.4255 | 1223925.8336 | 101.9938 | 101.9938 | 187.6738 | 80 | 60 | 35.3039 | 36 | 59.9
7/7/20XX 6:00:00 PM | 0.75 | 6 | 81.2 | 60.3 | 96.1834 | 112.6256 | 16.4423 | 60 | 81.2 |  | 81.2 | 96.6766 | 0.1 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 66.0271 | 18.2065 | 433314.6693 | 36.1096 | 36.1096 | 98.2276 | 0.2 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 69.4326 | 21.612 | 514365.5386 | 42.8638 | 42.8638 | 107.2498 | 0.3 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 72.8381 | 25.0175 | 595416.408 | 49.618 | 49.618 | 116.272 | 0.4 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 76.2436 | 28.423 | 676467.2773 | 56.3723 | 56.3723 | 125.2943 | 0.5 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 79.6491 | 31.8285 | 757518.1466 | 63.1265 | 63.1265 | 134.3165 | 0.6 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 83.0546 | 35.234 | 838569.0159 | 69.8808 | 69.8808 | 143.3388 | 0.7 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 86.4601 | 38.6395 | 919619.8853 | 76.635 | 76.635 | 152.361 | 0.8 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 89.8656 | 42.045 | 1000670.7546 | 83.3892 | 83.3892 | 161.3832 | 0.9 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 93.2711 | 45.4505 | 1081721.6239 | 90.1435 | 90.1435 | 170.4055 | 1 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 96.6766 | 48.856 | 1162772.4932 | 96.8977 | 96.8977 | 179.4277 | 80 | 60 | 34.6545 | 34 | 60.3
7/7/20XX 7:00:00 PM | 0.79167 | 6 | 79.9 | 61.7 | 92.1119 | 107.8449 | 15.733 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/7/20XX 8:00:00 PM | 0.83333 | 6 | 78.8 | 64.6 | 88.7794 | 103.932 | 15.1526 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/7/20XX 9:00:00 PM | 0.875 | 6 | 77.5 | 67.1 | 84.9711 | 99.4607 | 14.4896 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/7/20XX 10:00:00 PM | 0.91667 | 6 | 77.1 | 68.4 | 83.8273 | 98.1177 | 14.2905 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/7/20XX 11:00:00 PM | 0.95833 | 6 | 75.1 | 73.7 | 91.6296 | 105.0536 | 13.424 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/7/20XX 12:00:00 AM | 0 | 7 | 74.5 | 75.4 | 89.7555 | 102.8978 | 13.1423 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/8/20XX 1:00:00 AM | 0.041667 | 7 | 72.8 | 81.4 | 96.9944 | 109.3866 | 12.3922 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/8/20XX 2:00:00 AM | 0.083333 | 7 | 72.7 | 81.3 | 96.6564 | 109.004 | 12.3476 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/8/20XX 3:00:00 AM | 0.125 | 7 | 72.5 | 81.9 | 95.9835 | 108.2423 | 12.2588 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/8/20XX 4:00:00 AM | 0.16667 | 7 | 72.2 | 82.7 | 94.9817 | 107.1084 | 12.1266 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/8/20XX 5:00:00 AM | 0.20833 | 7 | 71.8 | 81.8 | 93.6601 | 105.6125 | 11.9523 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/8/20XX 6:00:00 AM | 0.25 | 7 | 73 | 80 | 97.6734 | 110.1553 | 12.4819 | 80 | 73 |  | 73 | 97.6734 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 66.1268 | 18.3062 | 435687.1161 | 36.3073 | 36.3073 | 95.8423 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 69.632 | 21.8114 | 519110.4323 | 43.2592 | 43.2592 | 102.4792 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 73.1372 | 25.3165 | 602533.7484 | 50.2111 | 50.2111 | 109.1161 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 76.6424 | 28.8217 | 685957.0645 | 57.1631 | 57.1631 | 115.7531 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 80.1475 | 32.3269 | 769380.3807 | 64.115 | 64.115 | 122.39 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 83.6527 | 35.8321 | 852803.6968 | 71.067 | 71.067 | 129.027 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 87.1579 | 39.3373 | 936227.0129 | 78.0189 | 78.0189 | 135.6639 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 90.6631 | 42.8425 | 1019650.329 | 84.9709 | 84.9709 | 142.3009 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 94.1683 | 46.3476 | 1103073.6452 | 91.9228 | 91.9228 | 148.9378 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 97.6734 | 49.8528 | 1186496.9613 | 98.8747 | 98.8747 | 155.5747 | 75 | 80 | 32.792 | 32 | 80
7/8/20XX 7:00:00 AM | 0.29167 | 7 | 74.2 | 76.5 | 88.8307 | 101.8342 | 13.0035 | 70 | 74.2 |  | 74.2 | 97.283 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 66.0878 | 18.2671 | 434757.774 | 36.2298 | 36.2298 | 96.1428 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 69.5539 | 21.7333 | 517251.748 | 43.1043 | 43.1043 | 103.0803 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 73.02 | 25.1994 | 599745.722 | 49.9788 | 49.9788 | 110.0178 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 76.4862 | 28.6655 | 682239.696 | 56.8533 | 56.8533 | 116.9553 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 79.9523 | 32.1317 | 764733.67 | 63.7278 | 63.7278 | 123.8928 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 83.4184 | 35.5978 | 847227.6439 | 70.6023 | 70.6023 | 130.8303 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 86.8846 | 39.0639 | 929721.6179 | 77.4768 | 77.4768 | 137.7678 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 90.3507 | 42.5301 | 1012215.5919 | 84.3513 | 84.3513 | 144.7053 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 93.8168 | 45.9962 | 1094709.5659 | 91.2258 | 91.2258 | 151.6428 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 97.283 | 49.4623 | 1177203.5399 | 98.1003 | 98.1003 | 158.5803 | 75 | 75 | 33.0264 | 34 | 76.5
7/8/20XX 8:00:00 AM | 0.33333 | 7 | 75.6 | 73.8 | 93.2166 | 106.8793 | 13.6627 | 70 | 75.6 |  | 75.6 | 98.4084 | 0.1 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 66.2003 | 18.3797 | 437436.3375 | 36.453 | 36.453 | 96.807 | 0.2 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 69.779 | 21.9584 | 522608.8751 | 43.5507 | 43.5507 | 104.4087 | 0.3 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 73.3577 | 25.537 | 607781.4126 | 50.6485 | 50.6485 | 112.0105 | 0.4 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 76.9363 | 29.1157 | 692953.9502 | 57.7462 | 57.7462 | 119.6122 | 0.5 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 80.515 | 32.6944 | 778126.4877 | 64.8439 | 64.8439 | 127.2139 | 0.6 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 84.0937 | 36.2731 | 863299.0253 | 71.9416 | 71.9416 | 134.8156 | 0.7 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 87.6724 | 39.8517 | 948471.5628 | 79.0393 | 79.0393 | 142.4173 | 0.8 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 91.2511 | 43.4304 | 1033644.1004 | 86.137 | 86.137 | 150.019 | 0.9 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 94.8297 | 47.0091 | 1118816.6379 | 93.2347 | 93.2347 | 157.6207 | 1 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 98.4084 | 50.5878 | 1203989.1754 | 100.3324 | 100.3324 | 165.2224 | 75 | 75 | 33.5472 | 34 | 73.8
7/8/20XX 9:00:00 AM | 0.375 | 7 | 77.5 | 68.4 | 84.9711 | 99.4607 | 14.4896 | 60 | 77.5 |  | 77.5 | 97.1424 | 0.1 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 66.0737 | 18.2531 | 434423.1288 | 36.2019 | 36.2019 | 97.1544 | 0.2 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 69.5258 | 21.7051 | 516582.4576 | 43.0485 | 43.0485 | 105.1035 | 0.3 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 72.9779 | 25.1572 | 598741.7864 | 49.8951 | 49.8951 | 113.0526 | 0.4 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 76.4299 | 28.6093 | 680901.1152 | 56.7418 | 56.7418 | 121.0018 | 0.5 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 79.882 | 32.0614 | 763060.444 | 63.5884 | 63.5884 | 128.9509 | 0.6 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 83.3341 | 35.5134 | 845219.7728 | 70.435 | 70.435 | 136.9 | 0.7 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 86.7861 | 38.9655 | 927379.1017 | 77.2816 | 77.2816 | 144.8491 | 0.8 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 90.2382 | 42.4176 | 1009538.4305 | 84.1282 | 84.1282 | 152.7982 | 0.9 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 93.6903 | 45.8697 | 1091697.7593 | 90.9748 | 90.9748 | 160.7473 | 1 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 97.1424 | 49.3217 | 1173857.0881 | 97.8214 | 97.8214 | 168.6964 | 75 | 70 | 33.8167 | 34 | 68.4
7/8/20XX 10:00:00 AM | 0.41667 | 7 | 79.6 | 62.8 | 91.1929 | 106.7659 | 15.5729 | 60 | 79.6 |  | 79.6 | 95.5534 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.9148 | 18.0942 | 430641.2999 | 35.8868 | 35.8868 | 97.5008 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 69.208 | 21.3873 | 509018.7997 | 42.4182 | 42.4182 | 105.7962 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 72.5011 | 24.6805 | 587396.2996 | 48.9497 | 48.9497 | 114.0917 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 75.7943 | 27.9737 | 665773.7994 | 55.4811 | 55.4811 | 122.3871 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 79.0875 | 31.2669 | 744151.2993 | 62.0126 | 62.0126 | 130.6826 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 82.3807 | 34.56 | 822528.7991 | 68.5441 | 68.5441 | 138.9781 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 85.6738 | 37.8532 | 900906.299 | 75.0755 | 75.0755 | 147.2735 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 88.967 | 41.1464 | 979283.7989 | 81.607 | 81.607 | 155.569 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 92.2602 | 44.4396 | 1057661.2987 | 88.1384 | 88.1384 | 163.8644 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 95.5534 | 47.7327 | 1136038.7986 | 94.6699 | 94.6699 | 172.1599 | 80 | 65 | 34.0846 | 34 | 62.8
7/8/20XX 11:00:00 AM | 0.45833 | 7 | 82.3 | 55.7 | 82.7861 | 99.7431 | 16.957 | 50 | 82.3 |  | 82.3 | 92.4516 | 0.1 | 74.83 | 19.83 | 749574 | 62.4645 | 62.4645 | 65.6046 | 17.784 | 423259.1503 | 35.2716 | 35.2716 | 97.7361 | 0.2 | 75.66 | 20.66 | 780948 | 65.079 | 65.079 | 68.5876 | 20.767 | 494254.5006 | 41.1879 | 41.1879 | 106.2669 | 0.3 | 76.49 | 21.49 | 812322 | 67.6935 | 67.6935 | 71.5706 | 23.75 | 565249.8509 | 47.1042 | 47.1042 | 114.7977 | 0.4 | 77.32 | 22.32 | 843696 | 70.308 | 70.308 | 74.5536 | 26.733 | 636245.2012 | 53.0204 | 53.0204 | 123.3284 | 0.5 | 78.15 | 23.15 | 875070 | 72.9225 | 72.9225 | 77.5366 | 29.716 | 707240.5515 | 58.9367 | 58.9367 | 131.8592 | 0.6 | 78.98 | 23.98 | 906444 | 75.537 | 75.537 | 80.5196 | 32.699 | 778235.9018 | 64.853 | 64.853 | 140.39 | 0.7 | 79.81 | 24.81 | 937818 | 78.1515 | 78.1515 | 83.5026 | 35.682 | 849231.2521 | 70.7693 | 70.7693 | 148.9208 | 0.8 | 80.64 | 25.64 | 969192 | 80.766 | 80.766 | 86.4856 | 38.665 | 920226.6024 | 76.6856 | 76.6856 | 157.4516 | 0.9 | 81.47 | 26.47 | 1000566 | 83.3805 | 83.3805 | 89.4686 | 41.648 | 991221.9527 | 82.6018 | 82.6018 | 165.9823 | 1 | 82.3 | 27.3 | 1031940 | 85.995 | 85.995 | 92.4516 | 44.631 | 1062217.303 | 88.5181 | 88.5181 | 174.5131 | 80 | 55 | 34.2621 | 34 | 55.7
7/8/20XX 12:00:00 PM | 0.5 | 7 | 83.7 | 53.4 | 86.6644 | 104.429 | 17.7646 | 50 | 83.7 |  | 83.7 | 92.7044 | 0.1 | 74.97 | 19.97 | 754866 | 62.9055 | 62.9055 | 65.6299 | 17.8093 | 423860.6757 | 35.3217 | 35.3217 | 98.2272 | 0.2 | 75.94 | 20.94 | 791532 | 65.961 | 65.961 | 68.6382 | 20.8175 | 495457.5514 | 41.2881 | 41.2881 | 107.2491 | 0.3 | 76.91 | 21.91 | 828198 | 69.0165 | 69.0165 | 71.6464 | 23.8258 | 567054.4271 | 47.2545 | 47.2545 | 116.271 | 0.4 | 77.88 | 22.88 | 864864 | 72.072 | 72.072 | 74.6547 | 26.8341 | 638651.3028 | 53.2209 | 53.2209 | 125.2929 | 0.5 | 78.85 | 23.85 | 901530 | 75.1275 | 75.1275 | 77.663 | 29.8424 | 710248.1786 | 59.1873 | 59.1873 | 134.3148 | 0.6 | 79.82 | 24.82 | 938196 | 78.183 | 78.183 | 80.6713 | 32.8506 | 781845.0543 | 65.1538 | 65.1538 | 143.3368 | 0.7 | 80.79 | 25.79 | 974862 | 81.2385 | 81.2385 | 83.6795 | 35.8589 | 853441.93 | 71.1202 | 71.1202 | 152.3587 | 0.8 | 81.76 | 26.76 | 1011528 | 84.294 | 84.294 | 86.6878 | 38.8672 | 925038.8057 | 77.0866 | 77.0866 | 161.3806 | 0.9 | 82.73 | 27.73 | 1048194 | 87.3495 | 87.3495 | 89.6961 | 41.8754 | 996635.6814 | 83.053 | 83.053 | 170.4025 | 1 | 83.7 | 28.7 | 1084860 | 90.405 | 90.405 | 92.7044 | 44.8837 | 1068232.5571 | 89.0194 | 89.0194 | 179.4244 | 85 | 55 | 34.646 | 34 | 53.4
7/8/20XX 1:00:00 PM | 0.54167 | 7 | 83.8 | 52.4 | 86.947 | 104.7705 | 17.8235 | 50 | 83.8 |  | 83.8 | 91.2246 | 0.1 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 65.4819 | 17.6613 | 420338.8591 | 35.0282 | 35.0282 | 97.9652 | 0.2 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 68.3422 | 20.5216 | 488413.9182 | 40.7012 | 40.7012 | 106.7252 | 0.3 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 71.2025 | 23.3819 | 556488.9772 | 46.3741 | 46.3741 | 115.4851 | 0.4 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 74.0628 | 26.2422 | 624564.0363 | 52.047 | 52.047 | 124.245 | 0.5 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 76.9231 | 29.1025 | 692639.0954 | 57.7199 | 57.7199 | 133.0049 | 0.6 | 79.88 | 24.88 | 940464 | 78.372 | 78.372 | 79.7834 | 31.9628 | 760714.1545 | 63.3928 | 63.3928 | 141.7648 | 0.7 | 80.86 | 25.86 | 977508 | 81.459 | 81.459 | 82.6437 | 34.8231 | 828789.2135 | 69.0658 | 69.0658 | 150.5248 | 0.8 | 81.84 | 26.84 | 1014552 | 84.546 | 84.546 | 85.504 | 37.6834 | 896864.2726 | 74.7387 | 74.7387 | 159.2847 | 0.9 | 82.82 | 27.82 | 1051596 | 87.633 | 87.633 | 88.3643 | 40.5437 | 964939.3317 | 80.4116 | 80.4116 | 168.0446 | 1 | 83.8 | 28.8 | 1088640 | 90.72 | 90.72 | 91.2246 | 43.404 | 1033014.3908 | 86.0845 | 86.0845 | 176.8045 | 85 | 50 | 34.4382 | 34 | 52.4
7/8/20XX 2:00:00 PM | 0.58333 | 7 | 84.6 | 51 | 89.2346 | 107.5349 | 18.3003 | 50 | 84.6 |  | 84.6 | 91.0646 | 0.1 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 65.4659 | 17.6453 | 419958.0717 | 34.9965 | 34.9965 | 98.1855 | 0.2 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 68.3102 | 20.4896 | 487652.3435 | 40.6377 | 40.6377 | 107.1657 | 0.3 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 71.1545 | 23.3339 | 555346.6152 | 46.2789 | 46.2789 | 116.1459 | 0.4 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 73.9988 | 26.1782 | 623040.8869 | 51.9201 | 51.9201 | 125.1261 | 0.5 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 76.8431 | 29.0225 | 690735.1587 | 57.5613 | 57.5613 | 134.1063 | 0.6 | 80.36 | 25.36 | 958608 | 79.884 | 79.884 | 79.6874 | 31.8668 | 758429.4304 | 63.2025 | 63.2025 | 143.0865 | 0.7 | 81.42 | 26.42 | 998676 | 83.223 | 83.223 | 82.5317 | 34.7111 | 826123.7021 | 68.8436 | 68.8436 | 152.0666 | 0.8 | 82.48 | 27.48 | 1038744 | 86.562 | 86.562 | 85.376 | 37.5554 | 893817.9739 | 74.4848 | 74.4848 | 161.0468 | 0.9 | 83.54 | 28.54 | 1078812 | 89.901 | 89.901 | 88.2203 | 40.3997 | 961512.2456 | 80.126 | 80.126 | 170.027 | 1 | 84.6 | 29.6 | 1118880 | 93.24 | 93.24 | 91.0646 | 43.244 | 1029206.5173 | 85.7672 | 85.7672 | 179.0072 | 85 | 50 | 34.6097 | 34 | 51
7/8/20XX 3:00:00 PM | 0.625 | 7 | 82.8 | 54.2 | 84.1546 | 101.3965 | 17.2419 | 50 | 82.8 |  | 82.8 | 91.3962 | 0.1 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 65.4991 | 17.6785 | 420747.3233 | 35.0623 | 35.0623 | 97.6843 | 0.2 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 68.3766 | 20.5559 | 489230.8465 | 40.7692 | 40.7692 | 106.1632 | 0.3 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 71.254 | 23.4334 | 557714.3698 | 46.4762 | 46.4762 | 114.6422 | 0.4 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 74.1315 | 26.3108 | 626197.893 | 52.1832 | 52.1832 | 123.1212 | 0.5 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 77.0089 | 29.1883 | 694681.4163 | 57.8901 | 57.8901 | 131.6001 | 0.6 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 79.8864 | 32.0658 | 763164.9395 | 63.5971 | 63.5971 | 140.0791 | 0.7 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 82.7638 | 34.9432 | 831648.4628 | 69.304 | 69.304 | 148.558 | 0.8 | 81.04 | 26.04 | 984312 | 82.026 | 82.026 | 85.6413 | 37.8207 | 900131.9861 | 75.011 | 75.011 | 157.037 | 0.9 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 88.5188 | 40.6981 | 968615.5093 | 80.718 | 80.718 | 165.516 | 1 | 82.8 | 27.8 | 1050840 | 87.57 | 87.57 | 91.3962 | 43.5756 | 1037099.0326 | 86.4249 | 86.4249 | 173.9949 | 85 | 55 | 34.2194 | 34 | 54.2
7/8/20XX 4:00:00 PM | 0.66667 | 7 | 82 | 56.7 | 81.9738 | 98.7617 | 16.7879 | 50 | 82 |  | 82 | 93.2217 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 65.6816 | 17.861 | 425091.9713 | 35.4243 | 35.4243 | 97.7943 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 68.7416 | 20.921 | 497920.1425 | 41.4933 | 41.4933 | 106.3833 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 71.8017 | 23.981 | 570748.3138 | 47.5624 | 47.5624 | 114.9724 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 74.8617 | 27.041 | 643576.4851 | 53.6314 | 53.6314 | 123.5614 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 77.9217 | 30.101 | 716404.6563 | 59.7004 | 59.7004 | 132.1504 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 80.9817 | 33.161 | 789232.8276 | 65.7694 | 65.7694 | 140.7394 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 84.0417 | 36.2211 | 862060.9989 | 71.8384 | 71.8384 | 149.3284 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 87.1017 | 39.2811 | 934889.1701 | 77.9074 | 77.9074 | 157.9174 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 90.1617 | 42.3411 | 1007717.3414 | 83.9764 | 83.9764 | 166.5064 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 93.2217 | 45.4011 | 1080545.5126 | 90.0455 | 90.0455 | 175.0955 | 80 | 55 | 34.3092 | 34 | 56.7
7/8/20XX 5:00:00 PM | 0.70833 | 7 | 80.2 | 59.4 | 77.2359 | 93.0386 | 15.8027 | 50 | 80.2 |  | 80.2 | 92.0905 | 0.1 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 65.5685 | 17.7479 | 422399.5973 | 35.2 | 35.2 | 97.003 | 0.2 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 68.5154 | 20.6948 | 492535.3946 | 41.0446 | 41.0446 | 104.8006 | 0.3 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 71.4623 | 23.6416 | 562671.1919 | 46.8893 | 46.8893 | 112.5983 | 0.4 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 74.4092 | 26.5885 | 632806.9892 | 52.7339 | 52.7339 | 120.3959 | 0.5 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 77.356 | 29.5354 | 702942.7865 | 58.5786 | 58.5786 | 128.1936 | 0.6 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 80.3029 | 32.4823 | 773078.5837 | 64.4232 | 64.4232 | 135.9912 | 0.7 | 78.34 | 23.34 | 882252 | 73.521 | 73.521 | 83.2498 | 35.4292 | 843214.381 | 70.2679 | 70.2679 | 143.7889 | 0.8 | 78.96 | 23.96 | 905688 | 75.474 | 75.474 | 86.1967 | 38.3761 | 913350.1783 | 76.1125 | 76.1125 | 151.5865 | 0.9 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 89.1436 | 41.3229 | 983485.9756 | 81.9572 | 81.9572 | 159.3842 | 1 | 80.2 | 25.2 | 952560 | 79.38 | 79.38 | 92.0905 | 44.2698 | 1053621.7729 | 87.8018 | 87.8018 | 167.1818 | 80 | 60 | 33.6892 | 34 | 59.4
7/8/20XX 6:00:00 PM | 0.75 | 7 | 78.6 | 63.3 | 88.1844 | 103.2334 | 15.049 | 60 | 78.6 |  | 78.6 | 93.1506 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 65.6745 | 17.8539 | 424922.6845 | 35.4102 | 35.4102 | 96.7092 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 68.7274 | 20.9068 | 497581.5691 | 41.4651 | 41.4651 | 104.2131 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 71.7803 | 23.9597 | 570240.4536 | 47.52 | 47.52 | 111.717 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 74.8332 | 27.0126 | 642899.3382 | 53.5749 | 53.5749 | 119.2209 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 77.8861 | 30.0655 | 715558.2227 | 59.6299 | 59.6299 | 126.7249 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 80.939 | 33.1184 | 788217.1073 | 65.6848 | 65.6848 | 134.2288 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 83.9919 | 36.1713 | 860875.9918 | 71.7397 | 71.7397 | 141.7327 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 87.0448 | 39.2242 | 933534.8764 | 77.7946 | 77.7946 | 149.2366 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 90.0977 | 42.277 | 1006193.7609 | 83.8495 | 83.8495 | 156.7405 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 93.1506 | 45.3299 | 1078852.6454 | 89.9044 | 89.9044 | 164.2444 | 80 | 65 | 33.462 | 34 | 63.3
7/8/20XX 7:00:00 PM | 0.79167 | 7 | 77.9 | 65.6 | 86.1281 | 100.819 | 14.691 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/8/20XX 8:00:00 PM | 0.83333 | 7 | 76.2 | 68.6 | 81.3009 | 95.1517 | 13.8508 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/8/20XX 9:00:00 PM | 0.875 | 7 | 75.5 | 70.1 | 92.8973 | 106.512 | 13.6147 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/8/20XX 10:00:00 PM | 0.91667 | 7 | 74.2 | 71.8 | 88.8307 | 101.8342 | 13.0035 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/8/20XX 11:00:00 PM | 0.95833 | 7 | 73.6 | 69.8 | 74.3617 | 87.0056 | 12.6439 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/8/20XX 12:00:00 AM | 0 | 1 | 73.1 | 70.9 | 85.5092 | 98.0145 | 12.5053 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/9/20XX 1:00:00 AM | 0.041667 | 1 | 72.3 | 71.9 | 83.1611 | 95.3147 | 12.1536 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/9/20XX 2:00:00 AM | 0.083333 | 1 | 71.8 | 71.1 | 81.7218 | 93.6601 | 11.9383 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/9/20XX 3:00:00 AM | 0.125 | 1 | 71.6 | 70.1 | 81.1522 | 93.0054 | 11.8531 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/9/20XX 4:00:00 AM | 0.16667 | 1 | 70.8 | 71.2 | 78.908 | 90.4259 | 11.5179 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/9/20XX 5:00:00 AM | 0.20833 | 1 | 70 | 73.5 | 76.7179 | 87.9091 | 11.1912 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/9/20XX 6:00:00 AM | 0.25 | 1 | 70.6 | 72.4 | 78.3554 | 89.7909 | 11.4354 | 70 | 70.6 |  | 70.6 | 81.0999 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 64.4695 | 16.6488 | 396242.1447 | 33.0202 | 33.0202 | 91.7992 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 66.3173 | 18.4967 | 440220.4893 | 36.685 | 36.685 | 94.393 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 68.1651 | 20.3445 | 484198.834 | 40.3499 | 40.3499 | 96.9869 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 70.013 | 22.1923 | 528177.1787 | 44.0148 | 44.0148 | 99.5808 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 71.8608 | 24.0401 | 572155.5233 | 47.6796 | 47.6796 | 102.1746 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 73.7086 | 25.888 | 616133.868 | 51.3445 | 51.3445 | 104.7685 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 75.5564 | 27.7358 | 660112.2127 | 55.0094 | 55.0094 | 107.3624 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 77.4043 | 29.5836 | 704090.5573 | 58.6742 | 58.6742 | 109.9562 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 79.2521 | 31.4315 | 748068.902 | 62.3391 | 62.3391 | 112.5501 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 81.0999 | 33.2793 | 792047.2467 | 66.0039 | 66.0039 | 115.1439 | 70 | 70 | 29.6123 | 30 | 72.4
7/9/20XX 7:00:00 AM | 0.29167 | 1 | 71.1 | 71 | 79.7432 | 91.3858 | 11.6426 | 70 | 71.1 |  | 71.1 | 80.9074 | 0.1 | 73.71 | 18.71 | 707238 | 58.9365 | 58.9365 | 64.4502 | 16.6296 | 395784.0118 | 32.982 | 32.982 | 91.9185 | 0.2 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 66.2788 | 18.4582 | 439304.2236 | 36.6087 | 36.6087 | 94.6317 | 0.3 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 68.1074 | 20.2867 | 482824.4354 | 40.2354 | 40.2354 | 97.3449 | 0.4 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 69.936 | 22.1153 | 526344.6472 | 43.8621 | 43.8621 | 100.0581 | 0.5 | 72.55 | 17.55 | 663390 | 55.2825 | 55.2825 | 71.7645 | 23.9439 | 569864.859 | 47.4887 | 47.4887 | 102.7712 | 0.6 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 73.5931 | 25.7725 | 613385.0708 | 51.1154 | 51.1154 | 105.4844 | 0.7 | 71.97 | 16.97 | 641466 | 53.4555 | 53.4555 | 75.4217 | 27.6011 | 656905.2825 | 54.7421 | 54.7421 | 108.1976 | 0.8 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 77.2503 | 29.4296 | 700425.4943 | 58.3688 | 58.3688 | 110.9108 | 0.9 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 79.0789 | 31.2582 | 743945.7061 | 61.9955 | 61.9955 | 113.624 | 1 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 80.9074 | 33.0868 | 787465.9179 | 65.6222 | 65.6222 | 116.3372 | 70 | 70 | 29.7048 | 30 | 71
7/9/20XX 8:00:00 AM | 0.33333 | 1 | 72.3 | 69.1 | 71.0864 | 83.1611 | 12.0747 | 60 | 72.3 |  | 72.3 | 82.0743 | 0.1 | 73.83 | 18.83 | 711774 | 59.3145 | 59.3145 | 64.5669 | 16.7463 | 398561.241 | 33.2134 | 33.2134 | 92.5279 | 0.2 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 66.5122 | 18.6915 | 444858.6819 | 37.0716 | 37.0716 | 95.8506 | 0.3 | 73.49 | 18.49 | 698922 | 58.2435 | 58.2435 | 68.4574 | 20.6368 | 491156.1229 | 40.9297 | 40.9297 | 99.1732 | 0.4 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 70.4027 | 22.5821 | 537453.5638 | 44.7878 | 44.7878 | 102.4958 | 0.5 | 73.15 | 18.15 | 686070 | 57.1725 | 57.1725 | 72.348 | 24.5274 | 583751.0048 | 48.6459 | 48.6459 | 105.8184 | 0.6 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 74.2933 | 26.4726 | 630048.4458 | 52.504 | 52.504 | 109.141 | 0.7 | 72.81 | 17.81 | 673218 | 56.1015 | 56.1015 | 76.2385 | 28.4179 | 676345.8867 | 56.3622 | 56.3622 | 112.4637 | 0.8 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 78.1838 | 30.3632 | 722643.3277 | 60.2203 | 60.2203 | 115.7863 | 0.9 | 72.47 | 17.47 | 660366 | 55.0305 | 55.0305 | 80.1291 | 32.3084 | 768940.7687 | 64.0784 | 64.0784 | 119.1089 | 1 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 82.0743 | 34.2537 | 815238.2096 | 67.9365 | 67.9365 | 122.4315 | 70 | 70 | 30.1813 | 30 | 69.1
7/9/20XX 9:00:00 AM | 0.375 | 1 | 74.2 | 64 | 75.9165 | 88.8307 | 12.9142 | 60 | 74.2 |  | 74.2 | 81.0822 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 64.4677 | 16.6471 | 396199.8832 | 33.0167 | 33.0167 | 92.9297 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 66.3137 | 18.4931 | 440135.9663 | 36.678 | 36.678 | 96.654 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 68.1598 | 20.3392 | 484072.0495 | 40.3393 | 40.3393 | 100.3783 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 70.0058 | 22.1852 | 528008.1327 | 44.0007 | 44.0007 | 104.1027 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 71.8519 | 24.0313 | 571944.2158 | 47.662 | 47.662 | 107.827 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 73.698 | 25.8773 | 615880.299 | 51.3234 | 51.3234 | 111.5514 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 75.544 | 27.7234 | 659816.3821 | 54.9847 | 54.9847 | 115.2757 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 77.3901 | 29.5694 | 703752.4653 | 58.646 | 58.646 | 119 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 79.2361 | 31.4155 | 747688.5485 | 62.3074 | 62.3074 | 122.7244 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 81.0822 | 33.2615 | 791624.6316 | 65.9687 | 65.9687 | 126.4487 | 75 | 65 | 30.492 | 30 | 64
7/9/20XX 10:00:00 AM | 0.41667 | 1 | 76.2 | 61 | 81.3009 | 95.1517 | 13.8508 | 60 | 76.2 |  | 76.2 | 82.6859 | 0.1 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 64.6281 | 16.8074 | 400016.8636 | 33.3347 | 33.3347 | 93.8777 | 0.2 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 66.6345 | 18.8139 | 447769.9271 | 37.3142 | 37.3142 | 98.5502 | 0.3 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 68.6409 | 20.8203 | 495522.9907 | 41.2936 | 41.2936 | 103.2226 | 0.4 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 70.6474 | 22.8267 | 543276.0543 | 45.273 | 45.273 | 107.895 | 0.5 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 72.6538 | 24.8332 | 591029.1179 | 49.2524 | 49.2524 | 112.5674 | 0.6 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 74.6602 | 26.8396 | 638782.1814 | 53.2318 | 53.2318 | 117.2398 | 0.7 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 76.6667 | 28.846 | 686535.245 | 57.2113 | 57.2113 | 121.9123 | 0.8 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 78.6731 | 30.8524 | 734288.3086 | 61.1907 | 61.1907 | 126.5847 | 0.9 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 80.6795 | 32.8589 | 782041.3722 | 65.1701 | 65.1701 | 131.2571 | 1 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 82.6859 | 34.8653 | 829794.4357 | 69.1495 | 69.1495 | 135.9295 | 75 | 60 | 31.2334 | 32 | 61
7/9/20XX 11:00:00 AM | 0.45833 | 1 | 78.4 | 56.3 | 72.7264 | 87.5927 | 14.8663 | 50 | 78.4 |  | 78.4 | 82.0922 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 64.5687 | 16.7481 | 398603.7575 | 33.217 | 33.217 | 94.453 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 66.5157 | 18.6951 | 444943.7151 | 37.0786 | 37.0786 | 99.7006 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 68.4628 | 20.6422 | 491283.6726 | 40.9403 | 40.9403 | 104.9483 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 70.4099 | 22.5892 | 537623.6302 | 44.802 | 44.802 | 110.196 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 72.3569 | 24.5363 | 583963.5877 | 48.6636 | 48.6636 | 115.4436 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 74.304 | 26.4833 | 630303.5453 | 52.5253 | 52.5253 | 120.6913 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 76.251 | 28.4304 | 676643.5028 | 56.387 | 56.387 | 125.939 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 78.1981 | 30.3775 | 722983.4604 | 60.2486 | 60.2486 | 131.1866 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 80.1451 | 32.3245 | 769323.4179 | 64.1103 | 64.1103 | 136.4343 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 82.0922 | 34.2716 | 815663.3755 | 67.9719 | 67.9719 | 141.6819 | 80 | 55 | 31.6799 | 32 | 56.3
7/9/20XX 12:00:00 PM | 0.5 | 1 | 80.9 | 52.2 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 82.6105 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 64.6205 | 16.7999 | 399837.3158 | 33.3198 | 33.3198 | 95.3433 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 66.6194 | 18.7988 | 447410.8317 | 37.2842 | 37.2842 | 101.4812 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 68.6183 | 20.7977 | 494984.3475 | 41.2487 | 41.2487 | 107.6192 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 70.6172 | 22.7965 | 542557.8634 | 45.2132 | 45.2132 | 113.7572 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 72.6161 | 24.7954 | 590131.3792 | 49.1776 | 49.1776 | 119.8951 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 74.615 | 26.7943 | 637704.895 | 53.1421 | 53.1421 | 126.0331 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 76.6138 | 28.7932 | 685278.4109 | 57.1065 | 57.1065 | 132.171 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 78.6127 | 30.7921 | 732851.9267 | 61.071 | 61.071 | 138.309 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 80.6116 | 32.791 | 780425.4426 | 65.0355 | 65.0355 | 144.447 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 82.6105 | 34.7899 | 827998.9584 | 68.9999 | 68.9999 | 150.5849 | 80 | 50 | 32.3742 | 32 | 52.2
7/9/20XX 1:00:00 PM | 0.54167 | 1 | 80.9 | 52.9 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 83.7431 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 64.7338 | 16.9131 | 402532.8944 | 33.5444 | 33.5444 | 95.5679 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 66.8459 | 19.0253 | 452801.9888 | 37.7335 | 37.7335 | 101.9305 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 68.9581 | 21.1374 | 503071.0832 | 41.9226 | 41.9226 | 108.2931 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 71.0702 | 23.2496 | 553340.1776 | 46.1117 | 46.1117 | 114.6557 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 73.1824 | 25.3617 | 603609.272 | 50.3008 | 50.3008 | 121.0183 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 75.2945 | 27.4739 | 653878.3664 | 54.4899 | 54.4899 | 127.3809 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 77.4067 | 29.586 | 704147.4608 | 58.679 | 58.679 | 133.7435 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 79.5188 | 31.6982 | 754416.5552 | 62.868 | 62.868 | 140.106 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 81.631 | 33.8103 | 804685.6496 | 67.0571 | 67.0571 | 146.4686 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 83.7431 | 35.9225 | 854954.744 | 71.2462 | 71.2462 | 152.8312 | 80 | 55 | 32.5519 | 32 | 52.9
7/9/20XX 2:00:00 PM | 0.58333 | 1 | 81 | 52.3 | 79.313 | 95.5475 | 16.2344 | 50 | 81 |  | 81 | 83.047 | 0.1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 64.6642 | 16.8435 | 400876.0967 | 33.4063 | 33.4063 | 95.4613 | 0.2 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 66.7067 | 18.8861 | 449488.3934 | 37.4574 | 37.4574 | 101.7174 | 0.3 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 68.7492 | 20.9286 | 498100.6902 | 41.5084 | 41.5084 | 107.9734 | 0.4 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 70.7918 | 22.9711 | 546712.9869 | 45.5594 | 45.5594 | 114.2294 | 0.5 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 72.8343 | 25.0137 | 595325.2836 | 49.6104 | 49.6104 | 120.4854 | 0.6 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 74.8768 | 27.0562 | 643937.5803 | 53.6615 | 53.6615 | 126.7415 | 0.7 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 76.9194 | 29.0987 | 692549.8771 | 57.7125 | 57.7125 | 132.9975 | 0.8 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 78.9619 | 31.1413 | 741162.1738 | 61.7635 | 61.7635 | 139.2535 | 0.9 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 81.0044 | 33.1838 | 789774.4705 | 65.8145 | 65.8145 | 145.5095 | 1 | 81 | 26 | 982800 | 81.9 | 81.9 | 83.047 | 35.2263 | 838386.7672 | 69.8656 | 69.8656 | 151.7656 | 80 | 50 | 32.4672 | 32 | 52.3
7/9/20XX 3:00:00 PM | 0.625 | 1 | 80.9 | 52.6 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 83.2577 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 64.6852 | 16.8646 | 401377.6464 | 33.4481 | 33.4481 | 95.4716 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 66.7488 | 18.9282 | 450491.4929 | 37.541 | 37.541 | 101.738 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 68.8125 | 20.9918 | 499605.3393 | 41.6338 | 41.6338 | 108.0043 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 70.8761 | 23.0554 | 548719.1858 | 45.7266 | 45.7266 | 114.2706 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 72.9397 | 25.119 | 597833.0322 | 49.8194 | 49.8194 | 120.5369 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 75.0033 | 27.1826 | 646946.8787 | 53.9122 | 53.9122 | 126.8032 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 77.0669 | 29.2462 | 696060.7251 | 58.0051 | 58.0051 | 133.0696 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 79.1305 | 31.3099 | 745174.5716 | 62.0979 | 62.0979 | 139.3359 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 81.1941 | 33.3735 | 794288.418 | 66.1907 | 66.1907 | 145.6022 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 83.2577 | 35.4371 | 843402.2644 | 70.2835 | 70.2835 | 151.8685 | 80 | 55 | 32.4758 | 32 | 52.6
7/9/20XX 4:00:00 PM | 0.66667 | 1 | 79.7 | 57.5 | 75.9607 | 91.4984 | 15.5378 | 50 | 79.7 |  | 79.7 | 87.614 | 0.1 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 65.1209 | 17.3002 | 411745.6031 | 34.3121 | 34.3121 | 95.9576 | 0.2 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 67.6201 | 19.7995 | 471227.4062 | 39.269 | 39.269 | 102.71 | 0.3 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 70.1193 | 22.2987 | 530709.2093 | 44.2258 | 44.2258 | 109.4623 | 0.4 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 72.6186 | 24.7979 | 590191.0123 | 49.1826 | 49.1826 | 116.2146 | 0.5 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 75.1178 | 27.2972 | 649672.8154 | 54.1394 | 54.1394 | 122.9669 | 0.6 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 77.617 | 29.7964 | 709154.6185 | 59.0962 | 59.0962 | 129.7192 | 0.7 | 77.99 | 22.99 | 869022 | 72.4185 | 72.4185 | 80.1163 | 32.2956 | 768636.4216 | 64.053 | 64.053 | 136.4715 | 0.8 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 82.6155 | 34.7949 | 828118.2247 | 69.0099 | 69.0099 | 143.2239 | 0.9 | 79.13 | 24.13 | 912114 | 76.0095 | 76.0095 | 85.1148 | 37.2941 | 887600.0278 | 73.9667 | 73.9667 | 149.9762 | 1 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 87.614 | 39.7934 | 947081.8309 | 78.9235 | 78.9235 | 156.7285 | 80 | 55 | 32.8644 | 32 | 57.5
7/9/20XX 5:00:00 PM | 0.70833 | 1 | 78.5 | 58.5 | 72.9711 | 87.8882 | 14.9171 | 50 | 78.5 |  | 78.5 | 85.6506 | 0.1 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 64.9245 | 17.1039 | 407072.7381 | 33.9227 | 33.9227 | 95.1902 | 0.2 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 67.2274 | 19.4068 | 461881.6763 | 38.4901 | 38.4901 | 101.1751 | 0.3 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 69.5303 | 21.7097 | 516690.6144 | 43.0576 | 43.0576 | 107.1601 | 0.4 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 71.8332 | 24.0126 | 571499.5525 | 47.625 | 47.625 | 113.145 | 0.5 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 74.1361 | 26.3155 | 626308.4906 | 52.1924 | 52.1924 | 119.1299 | 0.6 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 76.439 | 28.6184 | 681117.4288 | 56.7598 | 56.7598 | 125.1148 | 0.7 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 78.7419 | 30.9213 | 735926.3669 | 61.3272 | 61.3272 | 131.0997 | 0.8 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 81.0448 | 33.2242 | 790735.305 | 65.8946 | 65.8946 | 137.0846 | 0.9 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 83.3477 | 35.5271 | 845544.2432 | 70.462 | 70.462 | 143.0695 | 1 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 85.6506 | 37.83 | 900353.1813 | 75.0294 | 75.0294 | 149.0544 | 80 | 60 | 32.2621 | 32 | 58.5
7/9/20XX 6:00:00 PM | 0.75 | 1 | 77.5 | 59.5 | 70.5552 | 84.9711 | 14.416 | 50 | 77.5 |  | 77.5 | 84.2503 | 0.1 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 64.7845 | 16.9639 | 403740.1077 | 33.645 | 33.645 | 94.5975 | 0.2 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 66.9474 | 19.1267 | 455216.4155 | 37.9347 | 37.9347 | 99.9897 | 0.3 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 69.1102 | 21.2896 | 506692.7232 | 42.2244 | 42.2244 | 105.3819 | 0.4 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 71.2731 | 23.4525 | 558169.0309 | 46.5141 | 46.5141 | 110.7741 | 0.5 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 73.436 | 25.6154 | 609645.3387 | 50.8038 | 50.8038 | 116.1663 | 0.6 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 75.5989 | 27.7782 | 661121.6464 | 55.0935 | 55.0935 | 121.5585 | 0.7 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 77.7617 | 29.9411 | 712597.9541 | 59.3832 | 59.3832 | 126.9507 | 0.8 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 79.9246 | 32.104 | 764074.2619 | 63.6729 | 63.6729 | 132.3429 | 0.9 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 82.0875 | 34.2668 | 815550.5696 | 67.9625 | 67.9625 | 137.735 | 1 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 84.2503 | 36.4297 | 867026.8773 | 72.2522 | 72.2522 | 143.1272 | 75 | 60 | 31.7973 | 32 | 59.5
7/9/20XX 7:00:00 PM | 0.79167 | 1 | 77 | 59.6 | 69.3725 | 83.5433 | 14.1708 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/9/20XX 8:00:00 PM | 0.83333 | 1 | 74.2 | 67.9 | 75.9165 | 88.8307 | 12.9142 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/9/20XX 9:00:00 PM | 0.875 | 1 | 73.2 | 69.7 | 73.3404 | 85.8067 | 12.4664 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/9/20XX 10:00:00 PM | 0.91667 | 1 | 73.2 | 69.7 | 73.3404 | 85.8067 | 12.4664 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/9/20XX 11:00:00 PM | 0.95833 | 1 | 73.2 | 68.3 | 73.3404 | 85.8067 | 12.4664 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/9/20XX 12:00:00 AM | 0 | 2 | 72.6 | 69.8 | 71.831 | 84.035 | 12.204 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/10/20XX 1:00:00 AM | 0.041667 | 2 | 72.2 | 71.9 | 82.8715 | 94.9817 | 12.1103 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/10/20XX 2:00:00 AM | 0.083333 | 2 | 71.8 | 71.9 | 81.7218 | 93.6601 | 11.9383 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/10/20XX 3:00:00 AM | 0.125 | 2 | 71.3 | 73 | 80.3042 | 92.0306 | 11.7264 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/10/20XX 4:00:00 AM | 0.16667 | 2 | 70.4 | 73.8 | 77.8062 | 89.1597 | 11.3535 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/10/20XX 5:00:00 AM | 0.20833 | 2 | 70.2 | 73.8 | 77.2604 | 88.5325 | 11.2721 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/10/20XX 6:00:00 AM | 0.25 | 2 | 71.1 | 73.6 | 79.7432 | 91.3858 | 11.6426 | 70 | 71.1 |  | 71.1 | 83.9345 | 0.1 | 73.71 | 18.71 | 707238 | 58.9365 | 58.9365 | 64.7529 | 16.9323 | 402988.4524 | 33.5824 | 33.5824 | 92.5189 | 0.2 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 66.8842 | 19.0636 | 453713.1047 | 37.8094 | 37.8094 | 95.8324 | 0.3 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 69.0155 | 21.1949 | 504437.7571 | 42.0365 | 42.0365 | 99.146 | 0.4 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 71.1468 | 23.3262 | 555162.4094 | 46.2635 | 46.2635 | 102.4595 | 0.5 | 72.55 | 17.55 | 663390 | 55.2825 | 55.2825 | 73.2781 | 25.4574 | 605887.0618 | 50.4906 | 50.4906 | 105.7731 | 0.6 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 75.4094 | 27.5887 | 656611.7141 | 54.7176 | 54.7176 | 109.0866 | 0.7 | 71.97 | 16.97 | 641466 | 53.4555 | 53.4555 | 77.5406 | 29.72 | 707336.3665 | 58.9447 | 58.9447 | 112.4002 | 0.8 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 79.6719 | 31.8513 | 758061.0188 | 63.1718 | 63.1718 | 115.7138 | 0.9 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 81.8032 | 33.9826 | 808785.6712 | 67.3988 | 67.3988 | 119.0273 | 1 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 83.9345 | 36.1139 | 859510.3235 | 71.6259 | 71.6259 | 122.3409 | 70 | 75 | 30.1777 | 30 | 73.6
7/10/20XX 7:00:00 AM | 0.29167 | 2 | 72.7 | 68 | 72.0807 | 84.3281 | 12.2474 | 60 | 72.7 |  | 72.7 | 81.8786 | 0.1 | 73.87 | 18.87 | 713286 | 59.4405 | 59.4405 | 64.5473 | 16.7267 | 398095.45 | 33.1746 | 33.1746 | 92.6151 | 0.2 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 66.473 | 18.6524 | 443927.1 | 36.9939 | 36.9939 | 96.0249 | 0.3 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 68.3987 | 20.5781 | 489758.7501 | 40.8132 | 40.8132 | 99.4347 | 0.4 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 70.3244 | 22.5038 | 535590.4001 | 44.6325 | 44.6325 | 102.8445 | 0.5 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 72.2501 | 24.4295 | 581422.0501 | 48.4518 | 48.4518 | 106.2543 | 0.6 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 74.1758 | 26.3552 | 627253.7001 | 52.2711 | 52.2711 | 109.6641 | 0.7 | 73.09 | 18.09 | 683802 | 56.9835 | 56.9835 | 76.1015 | 28.2809 | 673085.3502 | 56.0904 | 56.0904 | 113.0739 | 0.8 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 78.0272 | 30.2066 | 718917.0002 | 59.9098 | 59.9098 | 116.4838 | 0.9 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 79.9529 | 32.1323 | 764748.6502 | 63.7291 | 63.7291 | 119.8936 | 1 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 81.8786 | 34.058 | 810580.3002 | 67.5484 | 67.5484 | 123.3034 | 75 | 70 | 30.2488 | 30 | 68
7/10/20XX 8:00:00 AM | 0.33333 | 2 | 73.9 | 65.2 | 75.1356 | 87.9141 | 12.7785 | 60 | 73.9 |  | 73.9 | 81.7804 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 64.5375 | 16.7169 | 397861.7473 | 33.1551 | 33.1551 | 92.9736 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 66.4534 | 18.6328 | 443459.6946 | 36.955 | 36.955 | 96.742 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 68.3693 | 20.5486 | 489057.6418 | 40.7548 | 40.7548 | 100.5103 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 70.2852 | 22.4645 | 534655.5891 | 44.5546 | 44.5546 | 104.2786 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 72.201 | 24.3804 | 580253.5364 | 48.3545 | 48.3545 | 108.047 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 74.1169 | 26.2963 | 625851.4837 | 52.1543 | 52.1543 | 111.8153 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 76.0328 | 28.2122 | 671449.431 | 55.9541 | 55.9541 | 115.5836 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 77.9487 | 30.128 | 717047.3782 | 59.7539 | 59.7539 | 119.3519 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 79.8646 | 32.0439 | 762645.3255 | 63.5538 | 63.5538 | 123.1203 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 81.7804 | 33.9598 | 808243.2728 | 67.3536 | 67.3536 | 126.8886 | 75 | 65 | 30.5277 | 30 | 65.2
7/10/20XX 9:00:00 AM | 0.375 | 2 | 75.6 | 61.7 | 79.6526 | 93.2166 | 13.564 | 60 | 75.6 |  | 75.6 | 81.9584 | 0.1 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 64.5553 | 16.7347 | 398285.4244 | 33.1905 | 33.1905 | 93.5445 | 0.2 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 66.489 | 18.6684 | 444307.0488 | 37.0256 | 37.0256 | 97.8836 | 0.3 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 68.4227 | 20.602 | 490328.6731 | 40.8607 | 40.8607 | 102.2227 | 0.4 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 70.3564 | 22.5357 | 536350.2975 | 44.6959 | 44.6959 | 106.5619 | 0.5 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 72.29 | 24.4694 | 582371.9219 | 48.531 | 48.531 | 110.901 | 0.6 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 74.2237 | 26.4031 | 628393.5463 | 52.3661 | 52.3661 | 115.2401 | 0.7 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 76.1574 | 28.3368 | 674415.1707 | 56.2013 | 56.2013 | 119.5793 | 0.8 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 78.0911 | 30.2705 | 720436.7951 | 60.0364 | 60.0364 | 123.9184 | 0.9 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 80.0248 | 32.2041 | 766458.4194 | 63.8715 | 63.8715 | 128.2575 | 1 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 81.9584 | 34.1378 | 812480.0438 | 67.7067 | 67.7067 | 132.5967 | 75 | 60 | 30.9724 | 30 | 61.7
7/10/20XX 10:00:00 AM | 0.41667 | 2 | 77.5 | 59.4 | 70.5552 | 84.9711 | 14.416 | 50 | 77.5 |  | 77.5 | 84.1062 | 0.1 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 64.7701 | 16.9495 | 403397.0075 | 33.6164 | 33.6164 | 94.5689 | 0.2 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 66.9185 | 19.0979 | 454530.2149 | 37.8775 | 37.8775 | 99.9325 | 0.3 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 69.067 | 21.2464 | 505663.4224 | 42.1386 | 42.1386 | 105.2961 | 0.4 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 71.2154 | 23.3948 | 556796.6299 | 46.3997 | 46.3997 | 110.6597 | 0.5 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 73.3639 | 25.5433 | 607929.8373 | 50.6608 | 50.6608 | 116.0233 | 0.6 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 75.5124 | 27.6917 | 659063.0448 | 54.9219 | 54.9219 | 121.3869 | 0.7 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 77.6608 | 29.8402 | 710196.2522 | 59.183 | 59.183 | 126.7505 | 0.8 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 79.8093 | 31.9886 | 761329.4597 | 63.4441 | 63.4441 | 132.1141 | 0.9 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 81.9577 | 34.1371 | 812462.6672 | 67.7052 | 67.7052 | 137.4777 | 1 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 84.1062 | 36.2855 | 863595.8746 | 71.9663 | 71.9663 | 142.8413 | 75 | 60 | 31.7747 | 32 | 59.4
7/10/20XX 11:00:00 AM | 0.45833 | 2 | 79.8 | 52.3 | 76.2143 | 91.8048 | 15.5904 | 50 | 79.8 |  | 79.8 | 79.8001 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 64.3395 | 16.5188 | 393148.6009 | 32.7624 | 32.7624 | 94.4394 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 66.0573 | 18.2367 | 434033.4017 | 36.1695 | 36.1695 | 99.6735 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 67.7752 | 19.9545 | 474918.2026 | 39.5765 | 39.5765 | 104.9075 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 69.493 | 21.6724 | 515803.0034 | 42.9836 | 42.9836 | 110.1416 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 71.2109 | 23.3902 | 556687.8043 | 46.3907 | 46.3907 | 115.3757 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 72.9287 | 25.1081 | 597572.6051 | 49.7977 | 49.7977 | 120.6097 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 74.6466 | 26.8259 | 638457.406 | 53.2048 | 53.2048 | 125.8438 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 76.3644 | 28.5438 | 679342.2068 | 56.6119 | 56.6119 | 131.0779 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 78.0823 | 30.2616 | 720227.0077 | 60.0189 | 60.0189 | 136.3119 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 79.8001 | 31.9795 | 761111.8085 | 63.426 | 63.426 | 141.546 | 80 | 50 | 31.6638 | 32 | 52.3
7/10/20XX 12:00:00 PM | 0.5 | 2 | 81.4 | 50.2 | 80.3687 | 96.8227 | 16.454 | 50 | 81.4 |  | 81.4 | 80.6978 | 0.1 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 64.4292 | 16.6086 | 395285.0572 | 32.9404 | 32.9404 | 95.1214 | 0.2 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 66.2369 | 18.4162 | 438306.3144 | 36.5255 | 36.5255 | 101.0375 | 0.3 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 68.0445 | 20.2238 | 481327.5715 | 40.1106 | 40.1106 | 106.9536 | 0.4 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 69.8521 | 22.0315 | 524348.8287 | 43.6957 | 43.6957 | 112.8697 | 0.5 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 71.6597 | 23.8391 | 567370.0859 | 47.2808 | 47.2808 | 118.7858 | 0.6 | 78.44 | 23.44 | 886032 | 73.836 | 73.836 | 73.4673 | 25.6467 | 610391.3431 | 50.8659 | 50.8659 | 124.7019 | 0.7 | 79.18 | 24.18 | 914004 | 76.167 | 76.167 | 75.2749 | 27.4543 | 653412.6003 | 54.4511 | 54.4511 | 130.6181 | 0.8 | 79.92 | 24.92 | 941976 | 78.498 | 78.498 | 77.0826 | 29.2619 | 696433.8575 | 58.0362 | 58.0362 | 136.5342 | 0.9 | 80.66 | 25.66 | 969948 | 80.829 | 80.829 | 78.8902 | 31.0695 | 739455.1146 | 61.6213 | 61.6213 | 142.4503 | 1 | 81.4 | 26.4 | 997920 | 83.16 | 83.16 | 80.6978 | 32.8772 | 782476.3718 | 65.2064 | 65.2064 | 148.3664 | 80 | 50 | 32.1968 | 32 | 50.2
7/10/20XX 1:00:00 PM | 0.54167 | 2 | 82.3 | 50 | 82.7861 | 99.7431 | 16.957 | 50 | 82.3 |  | 82.3 | 82.7861 | 0.1 | 74.83 | 19.83 | 749574 | 62.4645 | 62.4645 | 64.6381 | 16.8175 | 400255.3289 | 33.3546 | 33.3546 | 95.8191 | 0.2 | 75.66 | 20.66 | 780948 | 65.079 | 65.079 | 66.6545 | 18.8339 | 448246.8579 | 37.3539 | 37.3539 | 102.4329 | 0.3 | 76.49 | 21.49 | 812322 | 67.6935 | 67.6935 | 68.671 | 20.8504 | 496238.3868 | 41.3532 | 41.3532 | 109.0467 | 0.4 | 77.32 | 22.32 | 843696 | 70.308 | 70.308 | 70.6874 | 22.8668 | 544229.9158 | 45.3525 | 45.3525 | 115.6605 | 0.5 | 78.15 | 23.15 | 875070 | 72.9225 | 72.9225 | 72.7039 | 24.8833 | 592221.4447 | 49.3518 | 49.3518 | 122.2743 | 0.6 | 78.98 | 23.98 | 906444 | 75.537 | 75.537 | 74.7203 | 26.8997 | 640212.9736 | 53.3511 | 53.3511 | 128.8881 | 0.7 | 79.81 | 24.81 | 937818 | 78.1515 | 78.1515 | 76.7368 | 28.9162 | 688204.5026 | 57.3504 | 57.3504 | 135.5019 | 0.8 | 80.64 | 25.64 | 969192 | 80.766 | 80.766 | 78.7532 | 30.9326 | 736196.0315 | 61.3497 | 61.3497 | 142.1157 | 0.9 | 81.47 | 26.47 | 1000566 | 83.3805 | 83.3805 | 80.7697 | 32.9491 | 784187.5604 | 65.349 | 65.349 | 148.7295 | 1 | 82.3 | 27.3 | 1031940 | 85.995 | 85.995 | 82.7861 | 34.9655 | 832179.0894 | 69.3483 | 69.3483 | 155.3433 | 80 | 50 | 32.7452 | 32 | 50
7/10/20XX 2:00:00 PM | 0.58333 | 2 | 82.3 | 50.8 | 82.7861 | 99.7431 | 16.957 | 50 | 82.3 |  | 82.3 | 84.1427 | 0.1 | 74.83 | 19.83 | 749574 | 62.4645 | 62.4645 | 64.7737 | 16.9531 | 403483.9354 | 33.6237 | 33.6237 | 96.0882 | 0.2 | 75.66 | 20.66 | 780948 | 65.079 | 65.079 | 66.9258 | 19.1052 | 454704.0709 | 37.892 | 37.892 | 102.971 | 0.3 | 76.49 | 21.49 | 812322 | 67.6935 | 67.6935 | 69.078 | 21.2573 | 505924.2063 | 42.1604 | 42.1604 | 109.8539 | 0.4 | 77.32 | 22.32 | 843696 | 70.308 | 70.308 | 71.2301 | 23.4094 | 557144.3418 | 46.4287 | 46.4287 | 116.7367 | 0.5 | 78.15 | 23.15 | 875070 | 72.9225 | 72.9225 | 73.3822 | 25.5615 | 608364.4772 | 50.697 | 50.697 | 123.6195 | 0.6 | 78.98 | 23.98 | 906444 | 75.537 | 75.537 | 75.5343 | 27.7136 | 659584.6127 | 54.9654 | 54.9654 | 130.5024 | 0.7 | 79.81 | 24.81 | 937818 | 78.1515 | 78.1515 | 77.6864 | 29.8657 | 710804.7481 | 59.2337 | 59.2337 | 137.3852 | 0.8 | 80.64 | 25.64 | 969192 | 80.766 | 80.766 | 79.8385 | 32.0179 | 762024.8836 | 63.5021 | 63.5021 | 144.2681 | 0.9 | 81.47 | 26.47 | 1000566 | 83.3805 | 83.3805 | 81.9906 | 34.17 | 813245.019 | 67.7704 | 67.7704 | 151.1509 | 1 | 82.3 | 27.3 | 1031940 | 85.995 | 85.995 | 84.1427 | 36.3221 | 864465.1544 | 72.0388 | 72.0388 | 158.0338 | 80 | 50 | 32.9581 | 32 | 50.8
7/10/20XX 3:00:00 PM | 0.625 | 2 | 82 | 51.1 | 81.9738 | 98.7617 | 16.7879 | 50 | 82 |  | 82 | 83.8205 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 64.7415 | 16.9209 | 402717.0475 | 33.5598 | 33.5598 | 95.9298 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 66.8614 | 19.0408 | 453170.295 | 37.7642 | 37.7642 | 102.6542 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 68.9813 | 21.1607 | 503623.5424 | 41.9686 | 41.9686 | 109.3786 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 71.1012 | 23.2805 | 554076.7899 | 46.1731 | 46.1731 | 116.1031 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 73.2211 | 25.4004 | 604530.0374 | 50.3775 | 50.3775 | 122.8275 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 75.3409 | 27.5203 | 654983.2849 | 54.5819 | 54.5819 | 129.5519 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 77.4608 | 29.6402 | 705436.5324 | 58.7864 | 58.7864 | 136.2764 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 79.5807 | 31.7601 | 755889.7799 | 62.9908 | 62.9908 | 143.0008 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 81.7006 | 33.88 | 806343.0273 | 67.1953 | 67.1953 | 149.7253 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 83.8205 | 35.9998 | 856796.2748 | 71.3997 | 71.3997 | 156.4497 | 80 | 50 | 32.8339 | 32 | 51.1
7/10/20XX 4:00:00 PM | 0.66667 | 2 | 81.2 | 53.8 | 79.8394 | 96.1834 | 16.3439 | 50 | 81.2 |  | 81.2 | 86.0501 | 0.1 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 64.9645 | 17.1438 | 408023.6219 | 34.002 | 34.002 | 96.12 | 0.2 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 67.3073 | 19.4867 | 463783.4438 | 38.6486 | 38.6486 | 103.0346 | 0.3 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 69.6502 | 21.8295 | 519543.2657 | 43.2953 | 43.2953 | 109.9493 | 0.4 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 71.993 | 24.1724 | 575303.0876 | 47.9419 | 47.9419 | 116.8639 | 0.5 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 74.3359 | 26.5152 | 631062.9095 | 52.5886 | 52.5886 | 123.7786 | 0.6 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 76.6787 | 28.8581 | 686822.7314 | 57.2352 | 57.2352 | 130.6932 | 0.7 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 79.0216 | 31.2009 | 742582.5533 | 61.8819 | 61.8819 | 137.6079 | 0.8 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 81.3644 | 33.5438 | 798342.3751 | 66.5285 | 66.5285 | 144.5225 | 0.9 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 83.7073 | 35.8866 | 854102.197 | 71.1752 | 71.1752 | 151.4372 | 1 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 86.0501 | 38.2295 | 909862.0189 | 75.8218 | 75.8218 | 158.3518 | 80 | 55 | 32.9874 | 32 | 53.8
7/10/20XX 5:00:00 PM | 0.70833 | 2 | 81.1 | 53.3 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 84.9513 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 64.8546 | 17.034 | 405408.3842 | 33.784 | 33.784 | 95.8705 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 67.0876 | 19.2669 | 458552.9684 | 38.2127 | 38.2127 | 102.5357 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 69.3205 | 21.4999 | 511697.5527 | 42.6415 | 42.6415 | 109.201 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 71.5535 | 23.7329 | 564842.1369 | 47.0702 | 47.0702 | 115.8662 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 73.7865 | 25.9658 | 617986.7211 | 51.4989 | 51.4989 | 122.5314 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 76.0194 | 28.1988 | 671131.3053 | 55.9276 | 55.9276 | 129.1966 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 78.2524 | 30.4318 | 724275.8896 | 60.3563 | 60.3563 | 135.8618 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 80.4854 | 32.6647 | 777420.4738 | 64.785 | 64.785 | 142.527 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 82.7183 | 34.8977 | 830565.058 | 69.2138 | 69.2138 | 149.1923 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 84.9513 | 37.1307 | 883709.6422 | 73.6425 | 73.6425 | 155.8575 | 80 | 55 | 32.7905 | 32 | 53.3
7/10/20XX 6:00:00 PM | 0.75 | 2 | 80 | 53.1 | 76.7237 | 92.42 | 15.6963 | 50 | 80 |  | 80 | 81.5896 | 0.1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 64.5184 | 16.6978 | 397407.4652 | 33.1173 | 33.1173 | 94.8573 | 0.2 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 66.4152 | 18.5946 | 442551.1305 | 36.8793 | 36.8793 | 100.5093 | 0.3 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 68.312 | 20.4914 | 487694.7957 | 40.6412 | 40.6412 | 106.1612 | 0.4 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 70.2088 | 22.3882 | 532838.4609 | 44.4032 | 44.4032 | 111.8132 | 0.5 | 77 | 22 | 831600 | 69.3 | 69.3 | 72.1056 | 24.285 | 577982.1262 | 48.1652 | 48.1652 | 117.4652 | 0.6 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 74.0024 | 26.1818 | 623125.7914 | 51.9271 | 51.9271 | 123.1171 | 0.7 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 75.8992 | 28.0785 | 668269.4567 | 55.6891 | 55.6891 | 128.7691 | 0.8 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 77.796 | 29.9753 | 713413.1219 | 59.4511 | 59.4511 | 134.4211 | 0.9 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 79.6928 | 31.8721 | 758556.7871 | 63.2131 | 63.2131 | 140.0731 | 1 | 80 | 25 | 945000 | 78.75 | 78.75 | 81.5896 | 33.7689 | 803700.4524 | 66.975 | 66.975 | 145.725 | 80 | 55 | 31.9934 | 32 | 53.1
7/10/20XX 7:00:00 PM | 0.79167 | 2 | 78.5 | 57.1 | 72.9711 | 87.8882 | 14.9171 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/10/20XX 8:00:00 PM | 0.83333 | 2 | 77.5 | 58.8 | 70.5552 | 84.9711 | 14.416 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/10/20XX 9:00:00 PM | 0.875 | 2 | 77 | 60.2 | 83.5433 | 97.7844 | 14.241 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/10/20XX 10:00:00 PM | 0.91667 | 2 | 76.1 | 61.4 | 81.0242 | 94.8268 | 13.8027 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/10/20XX 11:00:00 PM | 0.95833 | 2 | 75 | 65.4 | 78.0327 | 91.3149 | 13.2822 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/10/20XX 12:00:00 AM | 0 | 3 | 74.5 | 68.1 | 76.7042 | 89.7555 | 13.0512 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/11/20XX 1:00:00 AM | 0.041667 | 3 | 73.8 | 68.5 | 74.8769 | 87.6104 | 12.7335 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/11/20XX 2:00:00 AM | 0.083333 | 3 | 73.3 | 70.4 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/11/20XX 3:00:00 AM | 0.125 | 3 | 73.3 | 70.1 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/11/20XX 4:00:00 AM | 0.16667 | 3 | 72.7 | 71.2 | 84.3281 | 96.6564 | 12.3283 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/11/20XX 5:00:00 AM | 0.20833 | 3 | 71.9 | 71.6 | 82.008 | 93.989 | 11.9811 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/11/20XX 6:00:00 AM | 0.25 | 3 | 72 | 72.4 | 82.2949 | 94.3189 | 12.024 | 70 | 72 |  | 72 | 85.1807 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.8775 | 17.0569 | 405954.356 | 33.8295 | 33.8295 | 93.0495 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 67.1334 | 19.3128 | 459644.912 | 38.3037 | 38.3037 | 96.8937 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 69.3893 | 21.5687 | 513335.468 | 42.778 | 42.778 | 100.738 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 71.6453 | 23.8246 | 567026.024 | 47.2522 | 47.2522 | 104.5822 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 73.9012 | 26.0805 | 620716.58 | 51.7264 | 51.7264 | 108.4264 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 76.1571 | 28.3364 | 674407.136 | 56.2006 | 56.2006 | 112.2706 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 78.413 | 30.5923 | 728097.692 | 60.6748 | 60.6748 | 116.1148 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 80.6689 | 32.8482 | 781788.2479 | 65.149 | 65.149 | 119.959 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 82.9248 | 35.1042 | 835478.8039 | 69.6232 | 69.6232 | 123.8032 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 85.1807 | 37.3601 | 889169.3599 | 74.0974 | 74.0974 | 127.6474 | 70 | 70 | 30.5933 | 30 | 72.4
7/11/20XX 7:00:00 AM | 0.29167 | 3 | 73.5 | 69.3 | 74.1052 | 86.7045 | 12.5993 | 60 | 73.5 |  | 73.5 | 85.8226 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 64.9417 | 17.1211 | 407482.034 | 33.9568 | 33.9568 | 93.6493 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 67.2618 | 19.4412 | 462700.268 | 38.5584 | 38.5584 | 98.0934 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 69.5819 | 21.7613 | 517918.5021 | 43.1599 | 43.1599 | 102.5374 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 71.902 | 24.0814 | 573136.7361 | 47.7614 | 47.7614 | 106.9814 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 74.2221 | 26.4015 | 628354.9701 | 52.3629 | 52.3629 | 111.4254 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 76.5422 | 28.7216 | 683573.2041 | 56.9644 | 56.9644 | 115.8694 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 78.8623 | 31.0417 | 738791.4382 | 61.566 | 61.566 | 120.3135 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 81.1824 | 33.3618 | 794009.6722 | 66.1675 | 66.1675 | 124.7575 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 83.5025 | 35.6818 | 849227.9062 | 70.769 | 70.769 | 129.2015 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 85.8226 | 38.0019 | 904446.1402 | 75.3705 | 75.3705 | 133.6455 | 75 | 70 | 31.0618 | 32 | 69.3
7/11/20XX 8:00:00 AM | 0.33333 | 3 | 75.2 | 66 | 78.5695 | 91.9451 | 13.3756 | 60 | 75.2 |  | 75.2 | 86.5949 | 0.1 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.019 | 17.1983 | 409320.1124 | 34.11 | 34.11 | 94.338 | 0.2 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 67.4163 | 19.5956 | 466376.4249 | 38.8647 | 38.8647 | 99.4707 | 0.3 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 69.8136 | 21.993 | 523432.7373 | 43.6194 | 43.6194 | 104.6034 | 0.4 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 72.2109 | 24.3903 | 580489.0498 | 48.3741 | 48.3741 | 109.7361 | 0.5 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 74.6083 | 26.7876 | 637545.3622 | 53.1288 | 53.1288 | 114.8688 | 0.6 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 77.0056 | 29.1849 | 694601.6747 | 57.8835 | 57.8835 | 120.0015 | 0.7 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 79.4029 | 31.5823 | 751657.9871 | 62.6382 | 62.6382 | 125.1342 | 0.8 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 81.8002 | 33.9796 | 808714.2996 | 67.3929 | 67.3929 | 130.2669 | 0.9 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 84.1975 | 36.3769 | 865770.612 | 72.1476 | 72.1476 | 135.3996 | 1 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 86.5949 | 38.7742 | 922826.9244 | 76.9022 | 76.9022 | 140.5322 | 75 | 65 | 31.5999 | 32 | 66
7/11/20XX 9:00:00 AM | 0.375 | 3 | 76.9 | 61.8 | 83.2602 | 97.452 | 14.1918 | 60 | 76.9 |  | 76.9 | 85.8147 | 0.1 | 74.29 | 19.29 | 729162 | 60.7635 | 60.7635 | 64.9409 | 17.1203 | 407463.3542 | 33.9553 | 33.9553 | 94.7188 | 0.2 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 67.2603 | 19.4396 | 462662.9083 | 38.5552 | 38.5552 | 100.2322 | 0.3 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 69.5796 | 21.7589 | 517862.4625 | 43.1552 | 43.1552 | 105.7457 | 0.4 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 71.8989 | 24.0782 | 573062.0167 | 47.7552 | 47.7552 | 111.2592 | 0.5 | 75.45 | 20.45 | 773010 | 64.4175 | 64.4175 | 74.2182 | 26.3975 | 628261.5709 | 52.3551 | 52.3551 | 116.7726 | 0.6 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 76.5375 | 28.7169 | 683461.125 | 56.9551 | 56.9551 | 122.2861 | 0.7 | 76.03 | 21.03 | 794934 | 66.2445 | 66.2445 | 78.8568 | 31.0362 | 738660.6792 | 61.5551 | 61.5551 | 127.7996 | 0.8 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 81.1761 | 33.3555 | 793860.2334 | 66.155 | 66.155 | 133.313 | 0.9 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 83.4954 | 35.6748 | 849059.7875 | 70.755 | 70.755 | 138.8265 | 1 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 85.8147 | 37.9941 | 904259.3417 | 75.3549 | 75.3549 | 144.3399 | 75 | 60 | 31.8951 | 32 | 61.8
7/11/20XX 10:00:00 AM | 0.41667 | 3 | 78.6 | 59.2 | 73.2164 | 88.1844 | 14.968 | 50 | 78.6 |  | 78.6 | 86.987 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 65.0582 | 17.2375 | 410253.3065 | 34.1878 | 34.1878 | 95.4868 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 67.4947 | 19.6741 | 468242.813 | 39.0202 | 39.0202 | 101.7682 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 69.9312 | 22.1106 | 526232.3194 | 43.8527 | 43.8527 | 108.0497 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 72.3678 | 24.5471 | 584221.8259 | 48.6852 | 48.6852 | 114.3312 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 74.8043 | 26.9837 | 642211.3324 | 53.5176 | 53.5176 | 120.6126 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 77.2408 | 29.4202 | 700200.8389 | 58.3501 | 58.3501 | 126.8941 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 79.6774 | 31.8567 | 758190.3454 | 63.1825 | 63.1825 | 133.1755 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 82.1139 | 34.2933 | 816179.8518 | 68.015 | 68.015 | 139.457 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 84.5504 | 36.7298 | 874169.3583 | 72.8474 | 72.8474 | 145.7384 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 86.987 | 39.1663 | 932158.8648 | 77.6799 | 77.6799 | 152.0199 | 80 | 60 | 32.496 | 32 | 59.2
7/11/20XX 11:00:00 AM | 0.45833 | 3 | 81.2 | 52.5 | 79.8394 | 96.1834 | 16.3439 | 50 | 81.2 |  | 81.2 | 83.9254 | 0.1 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 64.752 | 16.9314 | 402966.8174 | 33.5806 | 33.5806 | 95.6986 | 0.2 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 66.8824 | 19.0618 | 453669.8347 | 37.8058 | 37.8058 | 102.1918 | 0.3 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 69.0128 | 21.1921 | 504372.8521 | 42.0311 | 42.0311 | 108.6851 | 0.4 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 71.1431 | 23.3225 | 555075.8695 | 46.2563 | 46.2563 | 115.1783 | 0.5 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 73.2735 | 25.4529 | 605778.8868 | 50.4816 | 50.4816 | 121.6716 | 0.6 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 75.4039 | 27.5833 | 656481.9042 | 54.7068 | 54.7068 | 128.1648 | 0.7 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 77.5343 | 29.7137 | 707184.9216 | 58.9321 | 58.9321 | 134.6581 | 0.8 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 79.6647 | 31.844 | 757887.939 | 63.1573 | 63.1573 | 141.1513 | 0.9 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 81.795 | 33.9744 | 808590.9563 | 67.3826 | 67.3826 | 147.6446 | 1 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 83.9254 | 36.1048 | 859293.9737 | 71.6078 | 71.6078 | 154.1378 | 80 | 50 | 32.6541 | 32 | 52.5
7/11/20XX 12:00:00 PM | 0.5 | 3 | 82.9 | 49.8 | 67.2512 | 84.4305 | 17.1793 | 40 | 82.9 |  | 82.9 | 84.087 | 0.1 | 74.89 | 19.89 | 751842 | 62.6535 | 62.6535 | 64.7682 | 16.9475 | 403351.2708 | 33.6126 | 33.6126 | 96.2661 | 0.2 | 75.78 | 20.78 | 785484 | 65.457 | 65.457 | 66.9147 | 19.0941 | 454438.7415 | 37.8699 | 37.8699 | 103.3269 | 0.3 | 76.67 | 21.67 | 819126 | 68.2605 | 68.2605 | 69.0612 | 21.2406 | 505526.2123 | 42.1272 | 42.1272 | 110.3877 | 0.4 | 77.56 | 22.56 | 852768 | 71.064 | 71.064 | 71.2078 | 23.3871 | 556613.683 | 46.3845 | 46.3845 | 117.4485 | 0.5 | 78.45 | 23.45 | 886410 | 73.8675 | 73.8675 | 73.3543 | 25.5337 | 607701.1538 | 50.6418 | 50.6418 | 124.5093 | 0.6 | 79.34 | 24.34 | 920052 | 76.671 | 76.671 | 75.5008 | 27.6802 | 658788.6245 | 54.8991 | 54.8991 | 131.5701 | 0.7 | 80.23 | 25.23 | 953694 | 79.4745 | 79.4745 | 77.6474 | 29.8267 | 709876.0953 | 59.1563 | 59.1563 | 138.6308 | 0.8 | 81.12 | 26.12 | 987336 | 82.278 | 82.278 | 79.7939 | 31.9733 | 760963.566 | 63.4136 | 63.4136 | 145.6916 | 0.9 | 82.01 | 27.01 | 1020978 | 85.0815 | 85.0815 | 81.9404 | 34.1198 | 812051.0368 | 67.6709 | 67.6709 | 152.7524 | 1 | 82.9 | 27.9 | 1054620 | 87.885 | 87.885 | 84.087 | 36.2663 | 863138.5076 | 71.9282 | 71.9282 | 159.8132 | 85 | 50 | 33.0965 | 34 | 49.8
7/11/20XX 1:00:00 PM | 0.54167 | 3 | 84.1 | 47.6 | 69.9179 | 87.7992 | 17.8813 | 40 | 84.1 |  | 84.1 | 83.5077 | 0.1 | 75.01 | 20.01 | 756378 | 63.0315 | 63.0315 | 64.7102 | 16.8896 | 401972.5702 | 33.4977 | 33.4977 | 96.5292 | 0.2 | 76.02 | 21.02 | 794556 | 66.213 | 66.213 | 66.7988 | 18.9782 | 451681.3404 | 37.6401 | 37.6401 | 103.8531 | 0.3 | 77.03 | 22.03 | 832734 | 69.3945 | 69.3945 | 68.8874 | 21.0668 | 501390.1107 | 41.7825 | 41.7825 | 111.177 | 0.4 | 78.04 | 23.04 | 870912 | 72.576 | 72.576 | 70.976 | 23.1554 | 551098.8809 | 45.9249 | 45.9249 | 118.5009 | 0.5 | 79.05 | 24.05 | 909090 | 75.7575 | 75.7575 | 73.0647 | 25.244 | 600807.6511 | 50.0673 | 50.0673 | 125.8248 | 0.6 | 80.06 | 25.06 | 947268 | 78.939 | 78.939 | 75.1533 | 27.3326 | 650516.4213 | 54.2097 | 54.2097 | 133.1487 | 0.7 | 81.07 | 26.07 | 985446 | 82.1205 | 82.1205 | 77.2419 | 29.4212 | 700225.1915 | 58.3521 | 58.3521 | 140.4726 | 0.8 | 82.08 | 27.08 | 1023624 | 85.302 | 85.302 | 79.3305 | 31.5098 | 749933.9617 | 62.4945 | 62.4945 | 147.7965 | 0.9 | 83.09 | 28.09 | 1061802 | 88.4835 | 88.4835 | 81.4191 | 33.5984 | 799642.732 | 66.6369 | 66.6369 | 155.1204 | 1 | 84.1 | 29.1 | 1099980 | 91.665 | 91.665 | 83.5077 | 35.687 | 849351.5022 | 70.7793 | 70.7793 | 162.4443 | 85 | 50 | 33.2999 | 34 | 47.6
7/11/20XX 2:00:00 PM | 0.58333 | 3 | 84.1 | 48.1 | 69.9179 | 87.7992 | 17.8813 | 40 | 84.1 |  | 84.1 | 84.4017 | 0.1 | 75.01 | 20.01 | 756378 | 63.0315 | 63.0315 | 64.7996 | 16.979 | 404100.4412 | 33.675 | 33.675 | 96.7065 | 0.2 | 76.02 | 21.02 | 794556 | 66.213 | 66.213 | 66.9777 | 19.157 | 455937.0825 | 37.9948 | 37.9948 | 104.2078 | 0.3 | 77.03 | 22.03 | 832734 | 69.3945 | 69.3945 | 69.1557 | 21.335 | 507773.7237 | 42.3145 | 42.3145 | 111.709 | 0.4 | 78.04 | 23.04 | 870912 | 72.576 | 72.576 | 71.3337 | 23.513 | 559610.365 | 46.6342 | 46.6342 | 119.2102 | 0.5 | 79.05 | 24.05 | 909090 | 75.7575 | 75.7575 | 73.5117 | 25.6911 | 611447.0062 | 50.9539 | 50.9539 | 126.7114 | 0.6 | 80.06 | 25.06 | 947268 | 78.939 | 78.939 | 75.6897 | 27.8691 | 663283.6475 | 55.2736 | 55.2736 | 134.2126 | 0.7 | 81.07 | 26.07 | 985446 | 82.1205 | 82.1205 | 77.8677 | 30.0471 | 715120.2887 | 59.5934 | 59.5934 | 141.7139 | 0.8 | 82.08 | 27.08 | 1023624 | 85.302 | 85.302 | 80.0457 | 32.2251 | 766956.93 | 63.9131 | 63.9131 | 149.2151 | 0.9 | 83.09 | 28.09 | 1061802 | 88.4835 | 88.4835 | 82.2237 | 34.4031 | 818793.5712 | 68.2328 | 68.2328 | 156.7163 | 1 | 84.1 | 29.1 | 1099980 | 91.665 | 91.665 | 84.4017 | 36.5811 | 870630.2125 | 72.5525 | 72.5525 | 164.2175 | 85 | 50 | 33.4404 | 34 | 48.1
7/11/20XX 3:00:00 PM | 0.625 | 3 | 83.6 | 49.5 | 68.7966 | 86.3826 | 17.586 | 40 | 83.6 |  | 83.6 | 85.5033 | 0.1 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 64.9098 | 17.0892 | 406722.0604 | 33.8935 | 33.8935 | 96.7675 | 0.2 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 67.198 | 19.3773 | 461180.3207 | 38.4317 | 38.4317 | 104.3297 | 0.3 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 69.4861 | 21.6655 | 515638.5811 | 42.9699 | 42.9699 | 111.8919 | 0.4 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 71.7743 | 23.9536 | 570096.8415 | 47.5081 | 47.5081 | 119.4541 | 0.5 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 74.0624 | 26.2418 | 624555.1018 | 52.0463 | 52.0463 | 127.0163 | 0.6 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 76.3506 | 28.53 | 679013.3622 | 56.5844 | 56.5844 | 134.5784 | 0.7 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 78.6388 | 30.8181 | 733471.6226 | 61.1226 | 61.1226 | 142.1406 | 0.8 | 81.68 | 26.68 | 1008504 | 84.042 | 84.042 | 80.9269 | 33.1063 | 787929.8829 | 65.6608 | 65.6608 | 149.7028 | 0.9 | 82.64 | 27.64 | 1044792 | 87.066 | 87.066 | 83.2151 | 35.3945 | 842388.1433 | 70.199 | 70.199 | 157.265 | 1 | 83.6 | 28.6 | 1081080 | 90.09 | 90.09 | 85.5033 | 37.6826 | 896846.4037 | 74.7372 | 74.7372 | 164.8272 | 85 | 50 | 33.4907 | 34 | 49.5
7/11/20XX 4:00:00 PM | 0.66667 | 3 | 81.6 | 54.8 | 80.9009 | 97.4655 | 16.5647 | 50 | 81.6 |  | 81.6 | 88.8519 | 0.1 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 65.2447 | 17.424 | 414691.8283 | 34.5577 | 34.5577 | 96.8017 | 0.2 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 67.8677 | 20.0471 | 477119.8565 | 39.76 | 39.76 | 104.398 | 0.3 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 70.4907 | 22.6701 | 539547.8848 | 44.9623 | 44.9623 | 111.9943 | 0.4 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 73.1137 | 25.2931 | 601975.913 | 50.1647 | 50.1647 | 119.5907 | 0.5 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 75.7368 | 27.9161 | 664403.9413 | 55.367 | 55.367 | 127.187 | 0.6 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 78.3598 | 30.5392 | 726831.9696 | 60.5693 | 60.5693 | 134.7833 | 0.7 | 79.32 | 24.32 | 919296 | 76.608 | 76.608 | 80.9828 | 33.1622 | 789259.9978 | 65.7717 | 65.7717 | 142.3797 | 0.8 | 80.08 | 25.08 | 948024 | 79.002 | 79.002 | 83.6058 | 35.7852 | 851688.0261 | 70.974 | 70.974 | 149.976 | 0.9 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 86.2289 | 38.4082 | 914116.0543 | 76.1763 | 76.1763 | 157.5723 | 1 | 81.6 | 26.6 | 1005480 | 83.79 | 83.79 | 88.8519 | 41.0313 | 976544.0826 | 81.3787 | 81.3787 | 165.1687 | 80 | 55 | 33.5252 | 34 | 54.8
7/11/20XX 5:00:00 PM | 0.70833 | 3 | 80.5 | 57.7 | 78.0095 | 93.973 | 15.9635 | 50 | 80.5 |  | 80.5 | 90.3014 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 65.3896 | 17.569 | 418141.6248 | 34.8451 | 34.8451 | 96.7426 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 68.1576 | 20.337 | 484019.4495 | 40.335 | 40.335 | 104.28 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 70.9256 | 23.1049 | 549897.2743 | 45.8248 | 45.8248 | 111.8173 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 73.6935 | 25.8729 | 615775.099 | 51.3146 | 51.3146 | 119.3546 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 76.4615 | 28.6409 | 681652.9238 | 56.8044 | 56.8044 | 126.8919 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 79.2295 | 31.4089 | 747530.7485 | 62.2942 | 62.2942 | 134.4292 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 81.9975 | 34.1768 | 813408.5733 | 67.784 | 67.784 | 141.9665 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 84.7654 | 36.9448 | 879286.3981 | 73.2739 | 73.2739 | 149.5039 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 87.5334 | 39.7128 | 945164.2228 | 78.7637 | 78.7637 | 157.0412 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 90.3014 | 42.4808 | 1011042.0476 | 84.2535 | 84.2535 | 164.5785 | 80 | 60 | 33.4823 | 34 | 57.7
7/11/20XX 6:00:00 PM | 0.75 | 3 | 80.3 | 56.9 | 77.4931 | 93.3492 | 15.8561 | 50 | 80.3 |  | 80.3 | 88.4338 | 0.1 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 65.2029 | 17.3822 | 413696.7947 | 34.4747 | 34.4747 | 96.3092 | 0.2 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 67.7841 | 19.9634 | 475129.7894 | 39.5941 | 39.5941 | 103.4131 | 0.3 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 70.3653 | 22.5447 | 536562.784 | 44.7136 | 44.7136 | 110.5171 | 0.4 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 72.9465 | 25.1259 | 597995.7787 | 49.833 | 49.833 | 117.621 | 0.5 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 75.5277 | 27.7071 | 659428.7734 | 54.9524 | 54.9524 | 124.7249 | 0.6 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 78.1089 | 30.2883 | 720861.7681 | 60.0718 | 60.0718 | 131.8288 | 0.7 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 80.6902 | 32.8695 | 782294.7628 | 65.1912 | 65.1912 | 138.9327 | 0.8 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 83.2714 | 35.4507 | 843727.7574 | 70.3106 | 70.3106 | 146.0366 | 0.9 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 85.8526 | 38.032 | 905160.7521 | 75.4301 | 75.4301 | 153.1406 | 1 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 88.4338 | 40.6132 | 966593.7468 | 80.5495 | 80.5495 | 160.2445 | 80 | 55 | 33.1403 | 34 | 56.9
7/11/20XX 7:00:00 PM | 0.79167 | 3 | 79 | 57.3 | 74.2046 | 89.3778 | 15.1731 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/11/20XX 8:00:00 PM | 0.83333 | 3 | 77.6 | 61.7 | 85.2591 | 99.7988 | 14.5397 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/11/20XX 9:00:00 PM | 0.875 | 3 | 76.7 | 62.7 | 82.6964 | 96.79 | 14.0936 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/11/20XX 10:00:00 PM | 0.91667 | 3 | 75.7 | 65.6 | 79.9253 | 93.5368 | 13.6115 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/11/20XX 11:00:00 PM | 0.95833 | 3 | 74.8 | 69.9 | 77.499 | 90.6884 | 13.1894 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/11/20XX 12:00:00 AM | 0 | 4 | 74.5 | 71.1 | 89.7555 | 102.8978 | 13.1423 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/12/20XX 1:00:00 AM | 0.041667 | 4 | 73.6 | 73.4 | 87.0056 | 99.7352 | 12.7296 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/12/20XX 2:00:00 AM | 0.083333 | 4 | 73.4 | 73.6 | 86.4044 | 99.0438 | 12.6394 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/12/20XX 3:00:00 AM | 0.125 | 4 | 73.1 | 74.3 | 85.5092 | 98.0145 | 12.5053 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/12/20XX 4:00:00 AM | 0.16667 | 4 | 72.6 | 74.4 | 84.035 | 96.3195 | 12.2844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/12/20XX 5:00:00 AM | 0.20833 | 4 | 71.6 | 77.9 | 81.1522 | 93.0054 | 11.8531 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/12/20XX 6:00:00 AM | 0.25 | 4 | 72.4 | 76.9 | 83.4515 | 95.6486 | 12.1971 | 70 | 72.4 |  | 72.4 | 91.8675 | 0.1 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 65.5462 | 17.7256 | 421868.9356 | 35.1557 | 35.1557 | 94.5017 | 0.2 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 68.4708 | 20.6502 | 491474.0711 | 40.9562 | 40.9562 | 99.7982 | 0.3 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 71.3954 | 23.5748 | 561079.2067 | 46.7566 | 46.7566 | 105.0946 | 0.4 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 74.32 | 26.4993 | 630684.3422 | 52.557 | 52.557 | 110.391 | 0.5 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 77.2446 | 29.4239 | 700289.4778 | 58.3575 | 58.3575 | 115.6875 | 0.6 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 80.1691 | 32.3485 | 769894.6134 | 64.1579 | 64.1579 | 120.9839 | 0.7 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 83.0937 | 35.2731 | 839499.7489 | 69.9583 | 69.9583 | 126.2803 | 0.8 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 86.0183 | 38.1977 | 909104.8845 | 75.7587 | 75.7587 | 131.5767 | 0.9 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 88.9429 | 41.1223 | 978710.02 | 81.5592 | 81.5592 | 136.8732 | 1 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 91.8675 | 44.0469 | 1048315.1556 | 87.3596 | 87.3596 | 142.1696 | 70 | 75 | 31.7367 | 32 | 76.9
7/12/20XX 7:00:00 AM | 0.29167 | 4 | 73.4 | 73.6 | 86.4044 | 99.0438 | 12.6394 | 70 | 73.4 |  | 73.4 | 90.9546 | 0.1 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 65.4549 | 17.6343 | 419696.1799 | 34.9747 | 34.9747 | 94.6357 | 0.2 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 68.2882 | 20.4676 | 487128.5597 | 40.594 | 40.594 | 100.066 | 0.3 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 71.1215 | 23.3009 | 554560.9396 | 46.2134 | 46.2134 | 105.4964 | 0.4 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 73.9548 | 26.1342 | 621993.3194 | 51.8328 | 51.8328 | 110.9268 | 0.5 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 76.7881 | 28.9675 | 689425.6993 | 57.4521 | 57.4521 | 116.3571 | 0.6 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 79.6214 | 31.8008 | 756858.0791 | 63.0715 | 63.0715 | 121.7875 | 0.7 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 82.4547 | 34.6341 | 824290.459 | 68.6909 | 68.6909 | 127.2179 | 0.8 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 85.288 | 37.4673 | 891722.8389 | 74.3102 | 74.3102 | 132.6482 | 0.9 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 88.1213 | 40.3006 | 959155.2187 | 79.9296 | 79.9296 | 138.0786 | 1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 90.9546 | 43.1339 | 1026587.5986 | 85.549 | 85.549 | 143.509 | 75 | 75 | 31.8398 | 32 | 73.6
7/12/20XX 8:00:00 AM | 0.33333 | 4 | 75.3 | 68.1 | 78.8391 | 92.2616 | 13.4225 | 60 | 75.3 |  | 75.3 | 89.7113 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 65.3306 | 17.51 | 416737.2641 | 34.7281 | 34.7281 | 94.9876 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 68.0396 | 20.2189 | 481210.7281 | 40.1009 | 40.1009 | 100.7699 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 70.7485 | 22.9279 | 545684.1922 | 45.4737 | 45.4737 | 106.5522 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 73.4575 | 25.6369 | 610157.6563 | 50.8465 | 50.8465 | 112.3345 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 76.1665 | 28.3458 | 674631.1203 | 56.2193 | 56.2193 | 118.1168 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 78.8754 | 31.0548 | 739104.5844 | 61.592 | 61.592 | 123.899 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 81.5844 | 33.7638 | 803578.0485 | 66.9648 | 66.9648 | 129.6813 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 84.2934 | 36.4728 | 868051.5125 | 72.3376 | 72.3376 | 135.4636 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 87.0024 | 39.1817 | 932524.9766 | 77.7104 | 77.7104 | 141.2459 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 89.7113 | 41.8907 | 996998.4407 | 83.0832 | 83.0832 | 147.0282 | 75 | 70 | 32.1122 | 32 | 68.1
7/12/20XX 9:00:00 AM | 0.375 | 4 | 77.6 | 61 | 85.2591 | 99.7988 | 14.5397 | 60 | 77.6 |  | 77.6 | 86.7131 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 65.0308 | 17.2101 | 409601.5052 | 34.1335 | 34.1335 | 95.1175 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 67.4399 | 19.6193 | 466939.2105 | 38.9116 | 38.9116 | 101.0296 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 69.8491 | 22.0284 | 524276.9157 | 43.6897 | 43.6897 | 106.9417 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 72.2582 | 24.4376 | 581614.6209 | 48.4679 | 48.4679 | 112.8539 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 74.6674 | 26.8467 | 638952.3262 | 53.246 | 53.246 | 118.766 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 77.0765 | 29.2559 | 696290.0314 | 58.0242 | 58.0242 | 124.6782 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 79.4857 | 31.665 | 753627.7366 | 62.8023 | 62.8023 | 130.5903 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 81.8948 | 34.0742 | 810965.4419 | 67.5805 | 67.5805 | 136.5025 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 84.304 | 36.4833 | 868303.1471 | 72.3586 | 72.3586 | 142.4146 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 86.7131 | 38.8925 | 925640.8523 | 77.1367 | 77.1367 | 148.3267 | 80 | 60 | 32.2076 | 32 | 61
7/12/20XX 10:00:00 AM | 0.41667 | 4 | 80 | 51.1 | 76.7237 | 92.42 | 15.6963 | 50 | 80 |  | 80 | 78.4503 | 0.1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 64.2045 | 16.3839 | 389936.0421 | 32.4947 | 32.4947 | 94.2347 | 0.2 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 65.7874 | 17.9667 | 427608.2843 | 35.634 | 35.634 | 99.264 | 0.3 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 67.3702 | 19.5496 | 465280.5264 | 38.7734 | 38.7734 | 104.2934 | 0.4 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 68.9531 | 21.1325 | 502952.7686 | 41.9127 | 41.9127 | 109.3227 | 0.5 | 77 | 22 | 831600 | 69.3 | 69.3 | 70.536 | 22.7153 | 540625.0107 | 45.0521 | 45.0521 | 114.3521 | 0.6 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 72.1188 | 24.2982 | 578297.2529 | 48.1914 | 48.1914 | 119.3814 | 0.7 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 73.7017 | 25.8811 | 615969.495 | 51.3308 | 51.3308 | 124.4108 | 0.8 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 75.2846 | 27.4639 | 653641.7372 | 54.4701 | 54.4701 | 129.4401 | 0.9 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 76.8674 | 29.0468 | 691313.9793 | 57.6095 | 57.6095 | 134.4695 | 1 | 80 | 25 | 945000 | 78.75 | 78.75 | 78.4503 | 30.6297 | 728986.2214 | 60.7489 | 60.7489 | 139.4989 | 80 | 50 | 31.5012 | 32 | 51.1
7/12/20XX 11:00:00 AM | 0.45833 | 4 | 82.5 | 48.2 | 66.3809 | 83.3313 | 16.9504 | 40 | 82.5 |  | 82.5 | 80.2803 | 0.1 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 64.3875 | 16.5669 | 394291.3426 | 32.8576 | 32.8576 | 95.3851 | 0.2 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 66.1534 | 18.3327 | 436318.8852 | 36.3599 | 36.3599 | 101.5649 | 0.3 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 67.9192 | 20.0986 | 478346.4278 | 39.8622 | 39.8622 | 107.7447 | 0.4 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 69.6851 | 21.8645 | 520373.9704 | 43.3645 | 43.3645 | 113.9245 | 0.5 | 78.25 | 23.25 | 878850 | 73.2375 | 73.2375 | 71.4509 | 23.6303 | 562401.5129 | 46.8668 | 46.8668 | 120.1043 | 0.6 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 73.2168 | 25.3962 | 604429.0555 | 50.3691 | 50.3691 | 126.2841 | 0.7 | 79.95 | 24.95 | 943110 | 78.5925 | 78.5925 | 74.9827 | 27.162 | 646456.5981 | 53.8714 | 53.8714 | 132.4639 | 0.8 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 76.7485 | 28.9279 | 688484.1407 | 57.3737 | 57.3737 | 138.6437 | 0.9 | 81.65 | 26.65 | 1007370 | 83.9475 | 83.9475 | 78.5144 | 30.6938 | 730511.6833 | 60.876 | 60.876 | 144.8235 | 1 | 82.5 | 27.5 | 1039500 | 86.625 | 86.625 | 80.2803 | 32.4596 | 772539.2259 | 64.3783 | 64.3783 | 151.0033 | 80 | 50 | 32.4009 | 32 | 48.2
7/12/20XX 12:00:00 PM | 0.5 | 4 | 84.2 | 45.4 | 70.1439 | 88.0847 | 17.9408 | 40 | 84.2 |  | 84.2 | 79.832 | 0.1 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 64.3427 | 16.522 | 393224.4128 | 32.7687 | 32.7687 | 95.8317 | 0.2 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 66.0637 | 18.2431 | 434185.0255 | 36.1821 | 36.1821 | 102.4581 | 0.3 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 67.7847 | 19.9641 | 475145.6383 | 39.5955 | 39.5955 | 109.0845 | 0.4 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 69.5058 | 21.6851 | 516106.251 | 43.0089 | 43.0089 | 115.7109 | 0.5 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 71.2268 | 23.4062 | 557066.8638 | 46.4222 | 46.4222 | 122.3372 | 0.6 | 80.12 | 25.12 | 949536 | 79.128 | 79.128 | 72.9478 | 25.1272 | 598027.4765 | 49.8356 | 49.8356 | 128.9636 | 0.7 | 81.14 | 26.14 | 988092 | 82.341 | 82.341 | 74.6689 | 26.8482 | 638988.0893 | 53.249 | 53.249 | 135.59 | 0.8 | 82.16 | 27.16 | 1026648 | 85.554 | 85.554 | 76.3899 | 28.5693 | 679948.702 | 56.6624 | 56.6624 | 142.2164 | 0.9 | 83.18 | 28.18 | 1065204 | 88.767 | 88.767 | 78.1109 | 30.2903 | 720909.3148 | 60.0758 | 60.0758 | 148.8428 | 1 | 84.2 | 29.2 | 1103760 | 91.98 | 91.98 | 79.832 | 32.0113 | 761869.9275 | 63.4892 | 63.4892 | 155.4692 | 85 | 45 | 32.7471 | 32 | 45.4
7/12/20XX 1:00:00 PM | 0.54167 | 4 | 84.4 | 46.1 | 70.5978 | 88.6581 | 18.0604 | 40 | 84.4 |  | 84.4 | 81.6146 | 0.1 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 64.5209 | 16.7003 | 397467.0628 | 33.1223 | 33.1223 | 96.2483 | 0.2 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 66.4202 | 18.5996 | 442670.3255 | 36.8892 | 36.8892 | 103.2912 | 0.3 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 68.3195 | 20.4989 | 487873.5883 | 40.6561 | 40.6561 | 110.3341 | 0.4 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 70.2188 | 22.3982 | 533076.8511 | 44.4231 | 44.4231 | 117.3771 | 0.5 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 72.1181 | 24.2975 | 578280.1139 | 48.19 | 48.19 | 124.42 | 0.6 | 80.24 | 25.24 | 954072 | 79.506 | 79.506 | 74.0174 | 26.1968 | 623483.3766 | 51.9569 | 51.9569 | 131.4629 | 0.7 | 81.28 | 26.28 | 993384 | 82.782 | 82.782 | 75.9167 | 28.0961 | 668686.6394 | 55.7239 | 55.7239 | 138.5059 | 0.8 | 82.32 | 27.32 | 1032696 | 86.058 | 86.058 | 77.816 | 29.9954 | 713889.9022 | 59.4908 | 59.4908 | 145.5488 | 0.9 | 83.36 | 28.36 | 1072008 | 89.334 | 89.334 | 79.7153 | 31.8947 | 759093.1649 | 63.2578 | 63.2578 | 152.5918 | 1 | 84.4 | 29.4 | 1111320 | 92.61 | 92.61 | 81.6146 | 33.794 | 804296.4277 | 67.0247 | 67.0247 | 159.6347 | 85 | 45 | 33.0762 | 34 | 46.1
7/12/20XX 2:00:00 PM | 0.58333 | 4 | 84.6 | 45.1 | 71.054 | 89.2346 | 18.1806 | 40 | 84.6 |  | 84.6 | 80.3261 | 0.1 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 64.3921 | 16.5714 | 394400.3672 | 32.8667 | 32.8667 | 96.0557 | 0.2 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 66.1625 | 18.3419 | 436536.9343 | 36.3781 | 36.3781 | 102.9061 | 0.3 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 67.933 | 20.1123 | 478673.5015 | 39.8895 | 39.8895 | 109.7565 | 0.4 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 69.7034 | 21.8828 | 520810.0687 | 43.4008 | 43.4008 | 116.6068 | 0.5 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 71.4739 | 23.6532 | 562946.6358 | 46.9122 | 46.9122 | 123.4572 | 0.6 | 80.36 | 25.36 | 958608 | 79.884 | 79.884 | 73.2443 | 25.4237 | 605083.203 | 50.4236 | 50.4236 | 130.3076 | 0.7 | 81.42 | 26.42 | 998676 | 83.223 | 83.223 | 75.0147 | 27.1941 | 647219.7702 | 53.935 | 53.935 | 137.158 | 0.8 | 82.48 | 27.48 | 1038744 | 86.562 | 86.562 | 76.7852 | 28.9646 | 689356.3373 | 57.4464 | 57.4464 | 144.0084 | 0.9 | 83.54 | 28.54 | 1078812 | 89.901 | 89.901 | 78.5556 | 30.735 | 731492.9045 | 60.9577 | 60.9577 | 150.8587 | 1 | 84.6 | 29.6 | 1118880 | 93.24 | 93.24 | 80.3261 | 32.5054 | 773629.4717 | 64.4691 | 64.4691 | 157.7091 | 85 | 45 | 32.9228 | 32 | 45.1
7/12/20XX 3:00:00 PM | 0.625 | 4 | 83.9 | 44.5 | 69.4676 | 87.2303 | 17.7627 | 40 | 83.9 |  | 83.9 | 77.4608 | 0.1 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 64.1056 | 16.2849 | 387581.051 | 32.2984 | 32.2984 | 95.2669 | 0.2 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 65.5895 | 17.7688 | 422898.302 | 35.2415 | 35.2415 | 101.3285 | 0.3 | 76.97 | 21.97 | 830466 | 69.2055 | 69.2055 | 67.0734 | 19.2528 | 458215.5531 | 38.1846 | 38.1846 | 107.3901 | 0.4 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 68.5573 | 20.7367 | 493532.8041 | 41.1277 | 41.1277 | 113.4517 | 0.5 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 70.0412 | 22.2206 | 528850.0551 | 44.0708 | 44.0708 | 119.5133 | 0.6 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 71.5251 | 23.7045 | 564167.3061 | 47.0139 | 47.0139 | 125.5749 | 0.7 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 73.0091 | 25.1884 | 599484.5571 | 49.957 | 49.957 | 131.6365 | 0.8 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 74.493 | 26.6723 | 634801.8082 | 52.9002 | 52.9002 | 137.6982 | 0.9 | 82.91 | 27.91 | 1054998 | 87.9165 | 87.9165 | 75.9769 | 28.1563 | 670119.0592 | 55.8433 | 55.8433 | 143.7598 | 1 | 83.9 | 28.9 | 1092420 | 91.035 | 91.035 | 77.4608 | 29.6402 | 705436.3102 | 58.7864 | 58.7864 | 149.8214 | 85 | 45 | 32.3012 | 32 | 44.5
7/12/20XX 4:00:00 PM | 0.66667 | 4 | 82.5 | 49.3 | 66.3809 | 83.3313 | 16.9504 | 40 | 82.5 |  | 82.5 | 82.1448 | 0.1 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 64.574 | 16.7533 | 398728.968 | 33.2274 | 33.2274 | 95.7549 | 0.2 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 66.5263 | 18.7056 | 445194.136 | 37.0995 | 37.0995 | 102.3045 | 0.3 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 68.4786 | 20.658 | 491659.3039 | 40.9716 | 40.9716 | 108.8541 | 0.4 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 70.4309 | 22.6103 | 538124.4719 | 44.8437 | 44.8437 | 115.4037 | 0.5 | 78.25 | 23.25 | 878850 | 73.2375 | 73.2375 | 72.3832 | 24.5626 | 584589.6399 | 48.7158 | 48.7158 | 121.9533 | 0.6 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 74.3355 | 26.5149 | 631054.8079 | 52.5879 | 52.5879 | 128.5029 | 0.7 | 79.95 | 24.95 | 943110 | 78.5925 | 78.5925 | 76.2879 | 28.4672 | 677519.9758 | 56.46 | 56.46 | 135.0525 | 0.8 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 78.2402 | 30.4195 | 723985.1438 | 60.3321 | 60.3321 | 141.6021 | 0.9 | 81.65 | 26.65 | 1007370 | 83.9475 | 83.9475 | 80.1925 | 32.3719 | 770450.3118 | 64.2042 | 64.2042 | 148.1517 | 1 | 82.5 | 27.5 | 1039500 | 86.625 | 86.625 | 82.1448 | 34.3242 | 816915.4798 | 68.0763 | 68.0763 | 154.7013 | 80 | 50 | 32.6935 | 32 | 49.3
7/12/20XX 5:00:00 PM | 0.70833 | 4 | 81.3 | 51.3 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 82.2356 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 64.583 | 16.7624 | 398944.9756 | 33.2454 | 33.2454 | 95.3949 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 66.5444 | 18.7238 | 445626.1511 | 37.1355 | 37.1355 | 101.5845 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 68.5058 | 20.6852 | 492307.3267 | 41.0256 | 41.0256 | 107.7741 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 70.4672 | 22.6466 | 538988.5023 | 44.9157 | 44.9157 | 113.9637 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 72.4286 | 24.608 | 585669.6779 | 48.8058 | 48.8058 | 120.1533 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 74.39 | 26.5694 | 632350.8534 | 52.6959 | 52.6959 | 126.3429 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 76.3514 | 28.5308 | 679032.029 | 56.586 | 56.586 | 132.5325 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 78.3128 | 30.4922 | 725713.2046 | 60.4761 | 60.4761 | 138.7221 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 80.2742 | 32.4535 | 772394.3801 | 64.3662 | 64.3662 | 144.9117 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 82.2356 | 34.4149 | 819075.5557 | 68.2563 | 68.2563 | 151.1013 | 80 | 50 | 32.4135 | 32 | 51.3
7/12/20XX 6:00:00 PM | 0.75 | 4 | 79.9 | 55.4 | 76.4687 | 92.1119 | 15.6433 | 50 | 79.9 |  | 79.9 | 84.916 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 64.8511 | 17.0304 | 405324.4847 | 33.777 | 33.777 | 95.4855 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 67.0805 | 19.2599 | 458385.1694 | 38.1988 | 38.1988 | 101.7658 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 69.31 | 21.4893 | 511445.8541 | 42.6205 | 42.6205 | 108.046 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 71.5394 | 23.7188 | 564506.5388 | 47.0422 | 47.0422 | 114.3262 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 73.7688 | 25.9482 | 617567.2234 | 51.4639 | 51.4639 | 120.6064 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 75.9983 | 28.1776 | 670627.9081 | 55.8857 | 55.8857 | 126.8867 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 78.2277 | 30.4071 | 723688.5928 | 60.3074 | 60.3074 | 133.1669 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 80.4572 | 32.6365 | 776749.2775 | 64.7291 | 64.7291 | 139.4471 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 82.6866 | 34.866 | 829809.9622 | 69.1508 | 69.1508 | 145.7273 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 84.916 | 37.0954 | 882870.6469 | 73.5726 | 73.5726 | 152.0076 | 80 | 55 | 32.4905 | 32 | 55.4
7/12/20XX 7:00:00 PM | 0.79167 | 4 | 79.1 | 56.8 | 74.4534 | 89.6782 | 15.2248 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/12/20XX 8:00:00 PM | 0.83333 | 4 | 77.7 | 59.9 | 71.0329 | 85.548 | 14.515 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/12/20XX 9:00:00 PM | 0.875 | 4 | 77.1 | 60.7 | 83.8273 | 98.1177 | 14.2905 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/12/20XX 10:00:00 PM | 0.91667 | 4 | 75.8 | 61.5 | 80.1988 | 93.8579 | 13.6591 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/12/20XX 11:00:00 PM | 0.95833 | 4 | 75.3 | 61.7 | 78.8391 | 92.2616 | 13.4225 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/12/20XX 12:00:00 AM | 0 | 5 | 74.7 | 62.7 | 77.2333 | 90.3765 | 13.1432 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/13/20XX 1:00:00 AM | 0.041667 | 5 | 73.9 | 66.1 | 75.1356 | 87.9141 | 12.7785 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/13/20XX 2:00:00 AM | 0.083333 | 5 | 73.4 | 68 | 73.8495 | 86.4044 | 12.5549 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/13/20XX 3:00:00 AM | 0.125 | 5 | 73 | 70.9 | 85.2126 | 97.6734 | 12.4608 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/13/20XX 4:00:00 AM | 0.16667 | 5 | 72.6 | 71.9 | 84.035 | 96.3195 | 12.2844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/13/20XX 5:00:00 AM | 0.20833 | 5 | 72.5 | 74.8 | 83.7428 | 95.9835 | 12.2407 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/13/20XX 6:00:00 AM | 0.25 | 5 | 73 | 74.2 | 85.2126 | 97.6734 | 12.4608 | 70 | 73 |  | 73 | 90.4462 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 65.4041 | 17.5835 | 418486.2049 | 34.8739 | 34.8739 | 94.4089 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 68.1865 | 20.3659 | 484708.6098 | 40.3924 | 40.3924 | 99.6124 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 70.969 | 23.1484 | 550931.0147 | 45.9109 | 45.9109 | 104.8159 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 73.7514 | 25.9308 | 617153.4196 | 51.4295 | 51.4295 | 110.0195 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 76.5339 | 28.7133 | 683375.8245 | 56.948 | 56.948 | 115.223 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 79.3164 | 31.4957 | 749598.2294 | 62.4665 | 62.4665 | 120.4265 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 82.0988 | 34.2782 | 815820.6343 | 67.9851 | 67.9851 | 125.6301 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 84.8813 | 37.0606 | 882043.0392 | 73.5036 | 73.5036 | 130.8336 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 87.6637 | 39.8431 | 948265.4441 | 79.0221 | 79.0221 | 136.0371 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 90.4462 | 42.6255 | 1014487.849 | 84.5407 | 84.5407 | 141.2407 | 75 | 75 | 31.662 | 32 | 74.2
7/13/20XX 7:00:00 AM | 0.29167 | 5 | 74.7 | 69.2 | 77.2333 | 90.3765 | 13.1432 | 60 | 74.7 |  | 74.7 | 89.325 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 65.292 | 17.4713 | 415817.9228 | 34.6515 | 34.6515 | 94.722 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 67.9623 | 20.1417 | 479372.0455 | 39.9477 | 39.9477 | 100.2387 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 70.6327 | 22.812 | 542926.1683 | 45.2438 | 45.2438 | 105.7553 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 73.303 | 25.4824 | 606480.291 | 50.54 | 50.54 | 111.272 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 75.9733 | 28.1527 | 670034.4138 | 55.8362 | 55.8362 | 116.7887 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 78.6437 | 30.823 | 733588.5365 | 61.1324 | 61.1324 | 122.3054 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 81.314 | 33.4934 | 797142.6593 | 66.4286 | 66.4286 | 127.8221 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 83.9844 | 36.1637 | 860696.782 | 71.7247 | 71.7247 | 133.3387 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 86.6547 | 38.8341 | 924250.9048 | 77.0209 | 77.0209 | 138.8554 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 89.325 | 41.5044 | 987805.0276 | 82.3171 | 82.3171 | 144.3721 | 75 | 70 | 31.9043 | 32 | 69.2
7/13/20XX 8:00:00 AM | 0.33333 | 5 | 76.5 | 65.9 | 82.1358 | 96.1318 | 13.9961 | 60 | 76.5 |  | 76.5 | 90.3935 | 0.1 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 65.3988 | 17.5782 | 418360.7304 | 34.8634 | 34.8634 | 95.5009 | 0.2 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 68.176 | 20.3554 | 484457.6608 | 40.3715 | 40.3715 | 101.7965 | 0.3 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 70.9532 | 23.1325 | 550554.5912 | 45.8795 | 45.8795 | 108.092 | 0.4 | 75 | 20 | 756000 | 63 | 63 | 73.7304 | 25.9097 | 616651.5216 | 51.3876 | 51.3876 | 114.3876 | 0.5 | 75.25 | 20.25 | 765450 | 63.7875 | 63.7875 | 76.5075 | 28.6869 | 682748.452 | 56.8957 | 56.8957 | 120.6832 | 0.6 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 79.2847 | 31.4641 | 748845.3824 | 62.4038 | 62.4038 | 126.9788 | 0.7 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 82.0619 | 34.2413 | 814942.3128 | 67.9119 | 67.9119 | 133.2744 | 0.8 | 76 | 21 | 793800 | 66.15 | 66.15 | 84.8391 | 37.0185 | 881039.2431 | 73.4199 | 73.4199 | 139.5699 | 0.9 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 87.6163 | 39.7956 | 947136.1735 | 78.928 | 78.928 | 145.8655 | 1 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 90.3935 | 42.5728 | 1013233.1039 | 84.4361 | 84.4361 | 152.1611 | 75 | 65 | 32.5138 | 32 | 65.9
7/13/20XX 9:00:00 AM | 0.375 | 5 | 78 | 63 | 86.4193 | 101.161 | 14.7417 | 60 | 78 |  | 78 | 90.8418 | 0.1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 65.4437 | 17.623 | 419427.9135 | 34.9523 | 34.9523 | 96.0623 | 0.2 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 68.2657 | 20.445 | 486592.0271 | 40.5493 | 40.5493 | 102.9193 | 0.3 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 71.0877 | 23.2671 | 553756.1406 | 46.1463 | 46.1463 | 109.7763 | 0.4 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 73.9097 | 26.0891 | 620920.2541 | 51.7434 | 51.7434 | 116.6334 | 0.5 | 76 | 21 | 793800 | 66.15 | 66.15 | 76.7317 | 28.9111 | 688084.3677 | 57.3404 | 57.3404 | 123.4904 | 0.6 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 79.5538 | 31.7331 | 755248.4812 | 62.9374 | 62.9374 | 130.3474 | 0.7 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 82.3758 | 34.5552 | 822412.5947 | 68.5344 | 68.5344 | 137.2044 | 0.8 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 85.1978 | 37.3772 | 889576.7083 | 74.1314 | 74.1314 | 144.0614 | 0.9 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 88.0198 | 40.1992 | 956740.8218 | 79.7284 | 79.7284 | 150.9184 | 1 | 78 | 23 | 869400 | 72.45 | 72.45 | 90.8418 | 43.0212 | 1023904.9353 | 85.3254 | 85.3254 | 157.7754 | 80 | 65 | 32.9527 | 32 | 63
7/13/20XX 10:00:00 AM | 0.41667 | 5 | 79.8 | 60.1 | 91.8048 | 107.4842 | 15.6795 | 60 | 79.8 |  | 79.8 | 91.9616 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 65.5556 | 17.735 | 422092.8178 | 35.1744 | 35.1744 | 96.8514 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 68.4896 | 20.669 | 491921.8357 | 40.9935 | 40.9935 | 104.4975 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 71.4236 | 23.603 | 561750.8535 | 46.8126 | 46.8126 | 112.1436 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 74.3576 | 26.537 | 631579.8714 | 52.6317 | 52.6317 | 119.7897 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 77.2916 | 29.471 | 701408.8892 | 58.4507 | 58.4507 | 127.4357 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 80.2256 | 32.405 | 771237.9071 | 64.2698 | 64.2698 | 135.0818 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 83.1596 | 35.3389 | 841066.9249 | 70.0889 | 70.0889 | 142.7279 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 86.0936 | 38.2729 | 910895.9427 | 75.908 | 75.908 | 150.374 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 89.0276 | 41.2069 | 980724.9606 | 81.7271 | 81.7271 | 158.0201 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 91.9616 | 44.1409 | 1050553.9784 | 87.5462 | 87.5462 | 165.6662 | 80 | 60 | 33.5706 | 34 | 60.1
7/13/20XX 11:00:00 AM | 0.45833 | 5 | 81.4 | 58.8 | 80.3687 | 96.8227 | 16.454 | 50 | 81.4 |  | 81.4 | 94.8482 | 0.1 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 65.8443 | 18.0237 | 428963.0655 | 35.7469 | 35.7469 | 97.9279 | 0.2 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 69.0669 | 21.2463 | 505662.3309 | 42.1385 | 42.1385 | 106.6505 | 0.3 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 72.2896 | 24.469 | 582361.5964 | 48.5301 | 48.5301 | 115.3731 | 0.4 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 75.5123 | 27.6916 | 659060.8618 | 54.9217 | 54.9217 | 124.0957 | 0.5 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 78.7349 | 30.9143 | 735760.1273 | 61.3133 | 61.3133 | 132.8183 | 0.6 | 78.44 | 23.44 | 886032 | 73.836 | 73.836 | 81.9576 | 34.1369 | 812459.3927 | 67.7049 | 67.7049 | 141.5409 | 0.7 | 79.18 | 24.18 | 914004 | 76.167 | 76.167 | 85.1802 | 37.3596 | 889158.6582 | 74.0966 | 74.0966 | 150.2636 | 0.8 | 79.92 | 24.92 | 941976 | 78.498 | 78.498 | 88.4029 | 40.5823 | 965857.9236 | 80.4882 | 80.4882 | 158.9862 | 0.9 | 80.66 | 25.66 | 969948 | 80.829 | 80.829 | 91.6256 | 43.8049 | 1042557.1891 | 86.8798 | 86.8798 | 167.7088 | 1 | 81.4 | 26.4 | 997920 | 83.16 | 83.16 | 94.8482 | 47.0276 | 1119256.4545 | 93.2714 | 93.2714 | 176.4314 | 80 | 60 | 34.4169 | 34 | 58.8
7/13/20XX 12:00:00 PM | 0.5 | 5 | 81.8 | 58.5 | 81.4359 | 98.1119 | 16.676 | 50 | 81.8 |  | 81.8 | 95.6105 | 0.1 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 65.9205 | 18.0999 | 430777.2224 | 35.8981 | 35.8981 | 98.2051 | 0.2 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 69.2194 | 21.3988 | 509290.6448 | 42.4409 | 42.4409 | 107.2049 | 0.3 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 72.5183 | 24.6976 | 587804.0672 | 48.9837 | 48.9837 | 116.2047 | 0.4 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 75.8172 | 27.9965 | 666317.4896 | 55.5265 | 55.5265 | 125.2045 | 0.5 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 79.116 | 31.2954 | 744830.912 | 62.0692 | 62.0692 | 134.2042 | 0.6 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 82.4149 | 34.5943 | 823344.3344 | 68.612 | 68.612 | 143.204 | 0.7 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 85.7138 | 37.8932 | 901857.7568 | 75.1548 | 75.1548 | 152.2038 | 0.8 | 80.24 | 25.24 | 954072 | 79.506 | 79.506 | 89.0127 | 41.1921 | 980371.1792 | 81.6976 | 81.6976 | 161.2036 | 0.9 | 81.02 | 26.02 | 983556 | 81.963 | 81.963 | 92.3116 | 44.4909 | 1058884.6016 | 88.2404 | 88.2404 | 170.2034 | 1 | 81.8 | 26.8 | 1013040 | 84.42 | 84.42 | 95.6105 | 47.7898 | 1137398.024 | 94.7832 | 94.7832 | 179.2032 | 80 | 60 | 34.6349 | 34 | 58.5
7/13/20XX 1:00:00 PM | 0.54167 | 5 | 81.6 | 58.8 | 80.9009 | 97.4655 | 16.5647 | 50 | 81.6 |  | 81.6 | 95.4778 | 0.1 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 65.9072 | 18.0866 | 430461.3956 | 35.8718 | 35.8718 | 98.1158 | 0.2 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 69.1929 | 21.3722 | 508658.9912 | 42.3882 | 42.3882 | 107.0262 | 0.3 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 72.4785 | 24.6578 | 586856.5868 | 48.9047 | 48.9047 | 115.9367 | 0.4 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 75.7641 | 27.9435 | 665054.1823 | 55.4212 | 55.4212 | 124.8472 | 0.5 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 79.0497 | 31.2291 | 743251.7779 | 61.9376 | 61.9376 | 133.7576 | 0.6 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 82.3353 | 34.5147 | 821449.3735 | 68.4541 | 68.4541 | 142.6681 | 0.7 | 79.32 | 24.32 | 919296 | 76.608 | 76.608 | 85.6209 | 37.8003 | 899646.9691 | 74.9706 | 74.9706 | 151.5786 | 0.8 | 80.08 | 25.08 | 948024 | 79.002 | 79.002 | 88.9065 | 41.0859 | 977844.5647 | 81.487 | 81.487 | 160.489 | 0.9 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 92.1922 | 44.3715 | 1056042.1603 | 88.0035 | 88.0035 | 169.3995 | 1 | 81.6 | 26.6 | 1005480 | 83.79 | 83.79 | 95.4778 | 47.6571 | 1134239.7559 | 94.52 | 94.52 | 178.31 | 80 | 60 | 34.5648 | 34 | 58.8
7/13/20XX 2:00:00 PM | 0.58333 | 5 | 82 | 59.5 | 81.9738 | 98.7617 | 16.7879 | 50 | 82 |  | 82 | 97.9223 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 66.1517 | 18.3311 | 436279.4332 | 36.3566 | 36.3566 | 98.7266 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 69.6818 | 21.8611 | 520295.0663 | 43.3579 | 43.3579 | 108.2479 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 73.2118 | 25.3912 | 604310.6995 | 50.3592 | 50.3592 | 117.7692 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 76.7419 | 28.9213 | 688326.3326 | 57.3605 | 57.3605 | 127.2905 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 80.272 | 32.4513 | 772341.9658 | 64.3618 | 64.3618 | 136.8118 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 83.802 | 35.9814 | 856357.5989 | 71.3631 | 71.3631 | 146.3331 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 87.3321 | 39.5115 | 940373.2321 | 78.3644 | 78.3644 | 155.8544 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 90.8622 | 43.0415 | 1024388.8652 | 85.3657 | 85.3657 | 165.3757 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 94.3922 | 46.5716 | 1108404.4984 | 92.367 | 92.367 | 174.897 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 97.9223 | 50.1017 | 1192420.1316 | 99.3683 | 99.3683 | 184.4183 | 80 | 60 | 35.0469 | 36 | 59.5
7/13/20XX 3:00:00 PM | 0.625 | 5 | 81.2 | 59.3 | 79.8394 | 96.1834 | 16.3439 | 50 | 81.2 |  | 81.2 | 95.0393 | 0.1 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 65.8634 | 18.0428 | 429417.7949 | 35.7848 | 35.7848 | 97.9028 | 0.2 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 69.1052 | 21.2845 | 506571.7898 | 42.2143 | 42.2143 | 106.6003 | 0.3 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 72.3469 | 24.5263 | 583725.7846 | 48.6438 | 48.6438 | 115.2978 | 0.4 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 75.5887 | 27.7681 | 660879.7795 | 55.0733 | 55.0733 | 123.9953 | 0.5 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 78.8305 | 31.0098 | 738033.7744 | 61.5028 | 61.5028 | 132.6928 | 0.6 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 82.0722 | 34.2516 | 815187.7693 | 67.9323 | 67.9323 | 141.3903 | 0.7 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 85.314 | 37.4934 | 892341.7642 | 74.3618 | 74.3618 | 150.0878 | 0.8 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 88.5557 | 40.7351 | 969495.759 | 80.7913 | 80.7913 | 158.7853 | 0.9 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 91.7975 | 43.9769 | 1046649.7539 | 87.2208 | 87.2208 | 167.4828 | 1 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 95.0393 | 47.2186 | 1123803.7488 | 93.6503 | 93.6503 | 176.1803 | 80 | 60 | 34.3976 | 34 | 59.3
7/13/20XX 4:00:00 PM | 0.66667 | 5 | 80.1 | 62.7 | 92.7289 | 108.5693 | 15.8405 | 60 | 80.1 |  | 80.1 | 97.0058 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 66.06 | 18.2394 | 434098.107 | 36.1748 | 36.1748 | 97.9463 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 69.4985 | 21.6778 | 515932.414 | 42.9944 | 42.9944 | 106.6874 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 72.9369 | 25.1162 | 597766.721 | 49.8139 | 49.8139 | 115.4284 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 76.3753 | 28.5547 | 679601.028 | 56.6334 | 56.6334 | 124.1694 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 79.8137 | 31.9931 | 761435.335 | 63.4529 | 63.4529 | 132.9104 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 83.2521 | 35.4315 | 843269.6419 | 70.2725 | 70.2725 | 141.6515 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 86.6905 | 38.8699 | 925103.9489 | 77.092 | 77.092 | 150.3925 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 90.129 | 42.3083 | 1006938.2559 | 83.9115 | 83.9115 | 159.1335 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 93.5674 | 45.7467 | 1088772.5629 | 90.731 | 90.731 | 167.8745 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 97.0058 | 49.1852 | 1170606.8699 | 97.5506 | 97.5506 | 176.6156 | 80 | 65 | 34.4354 | 34 | 62.7
7/13/20XX 5:00:00 PM | 0.70833 | 5 | 79.2 | 62.4 | 89.9794 | 105.341 | 15.3616 | 60 | 79.2 |  | 79.2 | 93.6662 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 65.7261 | 17.9055 | 426149.9223 | 35.5125 | 35.5125 | 97.0005 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 68.8306 | 21.0099 | 500036.0447 | 41.6697 | 41.6697 | 104.7957 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 71.935 | 24.1144 | 573922.167 | 47.8268 | 47.8268 | 112.5908 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 75.0395 | 27.2188 | 647808.2894 | 53.984 | 53.984 | 120.386 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 78.1439 | 30.3233 | 721694.4117 | 60.1412 | 60.1412 | 128.1812 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 81.2484 | 33.4278 | 795580.5341 | 66.2984 | 66.2984 | 135.9764 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 84.3528 | 36.5322 | 869466.6564 | 72.4556 | 72.4556 | 143.7716 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 87.4573 | 39.6367 | 943352.7788 | 78.6127 | 78.6127 | 151.5667 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 90.5618 | 42.7411 | 1017238.9011 | 84.7699 | 84.7699 | 159.3619 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 93.6662 | 45.8456 | 1091125.0235 | 90.9271 | 90.9271 | 167.1571 | 80 | 60 | 33.6903 | 34 | 62.4
7/13/20XX 6:00:00 PM | 0.75 | 5 | 78.2 | 65.2 | 87.0044 | 101.8479 | 14.8435 | 60 | 78.2 |  | 78.2 | 94.723 | 0.1 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 65.8318 | 18.0111 | 428665.111 | 35.7221 | 35.7221 | 96.8951 | 0.2 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 69.0419 | 21.2213 | 505066.4219 | 42.0889 | 42.0889 | 104.5849 | 0.3 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 72.252 | 24.4314 | 581467.7329 | 48.4556 | 48.4556 | 112.2746 | 0.4 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 75.4622 | 27.6416 | 657869.0438 | 54.8224 | 54.8224 | 119.9644 | 0.5 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 78.6723 | 30.8517 | 734270.3548 | 61.1892 | 61.1892 | 127.6542 | 0.6 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 81.8825 | 34.0618 | 810671.6657 | 67.556 | 67.556 | 135.344 | 0.7 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 85.0926 | 37.272 | 887072.9767 | 73.9227 | 73.9227 | 143.0337 | 0.8 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 88.3027 | 40.4821 | 963474.2876 | 80.2895 | 80.2895 | 150.7235 | 0.9 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 91.5129 | 43.6923 | 1039875.5986 | 86.6563 | 86.6563 | 158.4133 | 1 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 94.723 | 46.9024 | 1116276.9096 | 93.0231 | 93.0231 | 166.1031 | 80 | 65 | 33.61 | 34 | 65.2
7/13/20XX 7:00:00 PM | 0.79167 | 5 | 76.4 | 70.2 | 95.8042 | 109.8565 | 14.0523 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/13/20XX 8:00:00 PM | 0.83333 | 5 | 76.2 | 66.8 | 81.3009 | 95.1517 | 13.8508 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/13/20XX 9:00:00 PM | 0.875 | 5 | 75.6 | 68.4 | 79.6526 | 93.2166 | 13.564 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/13/20XX 10:00:00 PM | 0.91667 | 5 | 75.3 | 69.6 | 78.8391 | 92.2616 | 13.4225 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/13/20XX 11:00:00 PM | 0.95833 | 5 | 74.4 | 71 | 89.4463 | 102.5422 | 13.0959 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/13/20XX 12:00:00 AM | 0 | 6 | 73.3 | 73.1 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/14/20XX 1:00:00 AM | 0.041667 | 6 | 73 | 74.4 | 85.2126 | 97.6734 | 12.4608 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/14/20XX 2:00:00 AM | 0.083333 | 6 | 72.9 | 75.8 | 84.9169 | 97.3334 | 12.4165 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/14/20XX 3:00:00 AM | 0.125 | 6 | 72.1 | 75.8 | 82.5828 | 94.6498 | 12.0671 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/14/20XX 4:00:00 AM | 0.16667 | 6 | 71.2 | 78.2 | 80.0233 | 91.7077 | 11.6844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/14/20XX 5:00:00 AM | 0.20833 | 6 | 70.4 | 81.1 | 89.1597 | 100.5195 | 11.3598 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/14/20XX 6:00:00 AM | 0.25 | 6 | 71.4 | 78.2 | 80.586 | 92.3545 | 11.7685 | 70 | 71.4 |  | 71.4 | 90.2362 | 0.1 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 65.3831 | 17.5625 | 417986.5067 | 34.8322 | 34.8322 | 93.8632 | 0.2 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 68.1445 | 20.3239 | 483709.2133 | 40.3091 | 40.3091 | 98.5211 | 0.3 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 70.906 | 23.0854 | 549431.92 | 45.786 | 45.786 | 103.179 | 0.4 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 73.6675 | 25.8468 | 615154.6266 | 51.2629 | 51.2629 | 107.8369 | 0.5 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 76.4289 | 28.6083 | 680877.3333 | 56.7398 | 56.7398 | 112.4948 | 0.6 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 79.1904 | 31.3697 | 746600.0399 | 62.2167 | 62.2167 | 117.1527 | 0.7 | 72.18 | 17.18 | 649404 | 54.117 | 54.117 | 81.9518 | 34.1312 | 812322.7466 | 67.6936 | 67.6936 | 121.8106 | 0.8 | 71.92 | 16.92 | 639576 | 53.298 | 53.298 | 84.7133 | 36.8927 | 878045.4533 | 73.1705 | 73.1705 | 126.4685 | 0.9 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 87.4748 | 39.6541 | 943768.1599 | 78.6473 | 78.6473 | 131.1263 | 1 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 90.2362 | 42.4156 | 1009490.8666 | 84.1242 | 84.1242 | 135.7842 | 70 | 80 | 31.236 | 32 | 78.2
7/14/20XX 7:00:00 AM | 0.29167 | 6 | 72.1 | 77.7 | 82.5828 | 94.6498 | 12.0671 | 70 | 72.1 |  | 72.1 | 91.8744 | 0.1 | 73.81 | 18.81 | 711018 | 59.2515 | 59.2515 | 65.5469 | 17.7263 | 421885.409 | 35.1571 | 35.1571 | 94.4086 | 0.2 | 73.62 | 18.62 | 703836 | 58.653 | 58.653 | 68.4722 | 20.6516 | 491507.018 | 40.9589 | 40.9589 | 99.6119 | 0.3 | 73.43 | 18.43 | 696654 | 58.0545 | 58.0545 | 71.3975 | 23.5768 | 561128.6269 | 46.7607 | 46.7607 | 104.8152 | 0.4 | 73.24 | 18.24 | 689472 | 57.456 | 57.456 | 74.3227 | 26.5021 | 630750.2359 | 52.5625 | 52.5625 | 110.0185 | 0.5 | 73.05 | 18.05 | 682290 | 56.8575 | 56.8575 | 77.248 | 29.4274 | 700371.8449 | 58.3643 | 58.3643 | 115.2218 | 0.6 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 80.1733 | 32.3527 | 769993.4539 | 64.1661 | 64.1661 | 120.4251 | 0.7 | 72.67 | 17.67 | 667926 | 55.6605 | 55.6605 | 83.0986 | 35.2779 | 839615.0629 | 69.9679 | 69.9679 | 125.6284 | 0.8 | 72.48 | 17.48 | 660744 | 55.062 | 55.062 | 86.0239 | 38.2032 | 909236.6719 | 75.7697 | 75.7697 | 130.8317 | 0.9 | 72.29 | 17.29 | 653562 | 54.4635 | 54.4635 | 88.9491 | 41.1285 | 978858.2808 | 81.5715 | 81.5715 | 136.035 | 1 | 72.1 | 17.1 | 646380 | 53.865 | 53.865 | 91.8744 | 44.0538 | 1048479.8898 | 87.3733 | 87.3733 | 141.2383 | 70 | 80 | 31.664 | 32 | 77.7
7/14/20XX 8:00:00 AM | 0.33333 | 6 | 73.6 | 74.4 | 87.0056 | 99.7352 | 12.7296 | 70 | 73.6 |  | 73.6 | 92.6066 | 0.1 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 65.6201 | 17.7995 | 423628.0132 | 35.3023 | 35.3023 | 95.0263 | 0.2 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 68.6186 | 20.798 | 494992.2263 | 41.2494 | 41.2494 | 100.8474 | 0.3 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 71.6171 | 23.7965 | 566356.4395 | 47.1964 | 47.1964 | 106.6684 | 0.4 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 74.6156 | 26.795 | 637720.6526 | 53.1434 | 53.1434 | 112.4894 | 0.5 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 77.6141 | 29.7935 | 709084.8658 | 59.0904 | 59.0904 | 118.3104 | 0.6 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 80.6126 | 32.792 | 780449.079 | 65.0374 | 65.0374 | 124.1314 | 0.7 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 83.6111 | 35.7905 | 851813.2921 | 70.9844 | 70.9844 | 129.9524 | 0.8 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 86.6096 | 38.789 | 923177.5053 | 76.9315 | 76.9315 | 135.7735 | 0.9 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 89.6081 | 41.7875 | 994541.7184 | 82.8785 | 82.8785 | 141.5945 | 1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 92.6066 | 44.786 | 1065905.9316 | 88.8255 | 88.8255 | 147.4155 | 75 | 75 | 32.1473 | 32 | 74.4
7/14/20XX 9:00:00 AM | 0.375 | 6 | 74.8 | 70.4 | 90.6884 | 103.9709 | 13.2825 | 70 | 74.8 |  | 74.8 | 91.2197 | 0.1 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 65.4814 | 17.6608 | 420327.1867 | 35.0273 | 35.0273 | 95.1293 | 0.2 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 68.3412 | 20.5206 | 488390.5735 | 40.6992 | 40.6992 | 101.0532 | 0.3 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 71.2011 | 23.3804 | 556453.9602 | 46.3712 | 46.3712 | 106.9772 | 0.4 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 74.0609 | 26.2402 | 624517.3469 | 52.0431 | 52.0431 | 112.9011 | 0.5 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 76.9207 | 29.1 | 692580.7336 | 57.7151 | 57.7151 | 118.8251 | 0.6 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 79.7805 | 31.9598 | 760644.1204 | 63.387 | 63.387 | 124.749 | 0.7 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 82.6403 | 34.8196 | 828707.5071 | 69.059 | 69.059 | 130.673 | 0.8 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 85.5001 | 37.6794 | 896770.8938 | 74.7309 | 74.7309 | 136.5969 | 0.9 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 88.3599 | 40.5393 | 964834.2805 | 80.4029 | 80.4029 | 142.5209 | 1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 91.2197 | 43.3991 | 1032897.6673 | 86.0748 | 86.0748 | 148.4448 | 75 | 70 | 32.2253 | 32 | 70.4
7/14/20XX 10:00:00 AM | 0.41667 | 6 | 75.9 | 69.3 | 80.4731 | 94.1799 | 13.7068 | 60 | 75.9 |  | 75.9 | 93.2205 | 0.1 | 74.19 | 19.19 | 725382 | 60.4485 | 60.4485 | 65.6815 | 17.8609 | 425088.9871 | 35.4241 | 35.4241 | 95.8726 | 0.2 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 68.7414 | 20.9208 | 497914.1741 | 41.4928 | 41.4928 | 102.5398 | 0.3 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 71.8013 | 23.9806 | 570739.3612 | 47.5616 | 47.5616 | 109.2071 | 0.4 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 74.8612 | 27.0405 | 643564.5483 | 53.6304 | 53.6304 | 115.8744 | 0.5 | 74.95 | 19.95 | 754110 | 62.8425 | 62.8425 | 77.921 | 30.1004 | 716389.7353 | 59.6991 | 59.6991 | 122.5416 | 0.6 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 80.9809 | 33.1603 | 789214.9224 | 65.7679 | 65.7679 | 129.2089 | 0.7 | 75.33 | 20.33 | 768474 | 64.0395 | 64.0395 | 84.0408 | 36.2202 | 862040.1095 | 71.8367 | 71.8367 | 135.8762 | 0.8 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 87.1007 | 39.2801 | 934865.2965 | 77.9054 | 77.9054 | 142.5434 | 0.9 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 90.1606 | 42.3399 | 1007690.4836 | 83.9742 | 83.9742 | 149.2107 | 1 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 93.2205 | 45.3998 | 1080515.6707 | 90.043 | 90.043 | 155.878 | 75 | 70 | 32.8089 | 32 | 69.3
7/14/20XX 11:00:00 AM | 0.45833 | 6 | 78.3 | 66.4 | 87.2982 | 102.1928 | 14.8947 | 60 | 78.3 |  | 78.3 | 96.8307 | 0.1 | 74.43 | 19.43 | 734454 | 61.2045 | 61.2045 | 66.0425 | 18.2219 | 433681.4785 | 36.1401 | 36.1401 | 97.3446 | 0.2 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 69.4635 | 21.6428 | 515099.157 | 42.9249 | 42.9249 | 105.4839 | 0.3 | 75.29 | 20.29 | 766962 | 63.9135 | 63.9135 | 72.8844 | 25.0637 | 596516.8355 | 49.7097 | 49.7097 | 113.6232 | 0.4 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 76.3053 | 28.4846 | 677934.514 | 56.4945 | 56.4945 | 121.7625 | 0.5 | 76.15 | 21.15 | 799470 | 66.6225 | 66.6225 | 79.7262 | 31.9056 | 759352.1924 | 63.2793 | 63.2793 | 129.9018 | 0.6 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 83.1471 | 35.3265 | 840769.8709 | 70.0642 | 70.0642 | 138.0412 | 0.7 | 77.01 | 22.01 | 831978 | 69.3315 | 69.3315 | 86.568 | 38.7474 | 922187.5494 | 76.849 | 76.849 | 146.1805 | 0.8 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 89.9889 | 42.1683 | 1003605.2279 | 83.6338 | 83.6338 | 154.3198 | 0.9 | 77.87 | 22.87 | 864486 | 72.0405 | 72.0405 | 93.4098 | 45.5892 | 1085022.9064 | 90.4186 | 90.4186 | 162.4591 | 1 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 96.8307 | 49.0101 | 1166440.5849 | 97.2034 | 97.2034 | 170.5984 | 80 | 65 | 33.9648 | 34 | 66.4
7/14/20XX 12:00:00 PM | 0.5 | 6 | 79.7 | 63.6 | 91.4984 | 107.1246 | 15.6261 | 60 | 79.7 |  | 79.7 | 97.1238 | 0.1 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 66.0719 | 18.2512 | 434379.0317 | 36.1983 | 36.1983 | 97.8438 | 0.2 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 69.5221 | 21.7014 | 516494.2633 | 43.0412 | 43.0412 | 106.4822 | 0.3 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 72.9723 | 25.1517 | 598609.495 | 49.8841 | 49.8841 | 115.1206 | 0.4 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 76.4225 | 28.6019 | 680724.7266 | 56.7271 | 56.7271 | 123.7591 | 0.5 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 79.8727 | 32.0521 | 762839.9583 | 63.57 | 63.57 | 132.3975 | 0.6 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 83.323 | 35.5023 | 844955.1899 | 70.4129 | 70.4129 | 141.0359 | 0.7 | 77.99 | 22.99 | 869022 | 72.4185 | 72.4185 | 86.7732 | 38.9525 | 927070.4216 | 77.2559 | 77.2559 | 149.6744 | 0.8 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 90.2234 | 42.4028 | 1009185.6532 | 84.0988 | 84.0988 | 158.3128 | 0.9 | 79.13 | 24.13 | 912114 | 76.0095 | 76.0095 | 93.6736 | 45.853 | 1091300.8849 | 90.9417 | 90.9417 | 166.9512 | 1 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 97.1238 | 49.3032 | 1173416.1166 | 97.7847 | 97.7847 | 175.5897 | 80 | 65 | 34.3554 | 34 | 63.6
7/14/20XX 1:00:00 PM | 0.54167 | 6 | 80.2 | 63.1 | 93.0386 | 108.933 | 15.8944 | 60 | 80.2 |  | 80.2 | 97.9659 | 0.1 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 66.1561 | 18.3354 | 436383.1173 | 36.3653 | 36.3653 | 98.1683 | 0.2 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 69.6905 | 21.8699 | 520502.4346 | 43.3752 | 43.3752 | 107.1312 | 0.3 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 73.2249 | 25.4043 | 604621.752 | 50.3851 | 50.3851 | 116.0941 | 0.4 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 76.7593 | 28.9387 | 688741.0693 | 57.3951 | 57.3951 | 125.0571 | 0.5 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 80.2938 | 32.4731 | 772860.3866 | 64.405 | 64.405 | 134.02 | 0.6 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 83.8282 | 36.0076 | 856979.7039 | 71.415 | 71.415 | 142.983 | 0.7 | 78.34 | 23.34 | 882252 | 73.521 | 73.521 | 87.3626 | 39.542 | 941099.0212 | 78.4249 | 78.4249 | 151.9459 | 0.8 | 78.96 | 23.96 | 905688 | 75.474 | 75.474 | 90.897 | 43.0764 | 1025218.3386 | 85.4349 | 85.4349 | 160.9089 | 0.9 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 94.4315 | 46.6108 | 1109337.6559 | 92.4448 | 92.4448 | 169.8718 | 1 | 80.2 | 25.2 | 952560 | 79.38 | 79.38 | 97.9659 | 50.1453 | 1193456.9732 | 99.4547 | 99.4547 | 178.8347 | 80 | 65 | 34.6105 | 34 | 63.1
7/14/20XX 2:00:00 PM | 0.58333 | 6 | 80.4 | 62.8 | 93.6607 | 109.6634 | 16.0028 | 60 | 80.4 |  | 80.4 | 98.1414 | 0.1 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 66.1736 | 18.353 | 436800.9634 | 36.4001 | 36.4001 | 98.2661 | 0.2 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 69.7256 | 21.905 | 521338.1267 | 43.4448 | 43.4448 | 107.3268 | 0.3 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 73.2776 | 25.4569 | 605875.2901 | 50.4896 | 50.4896 | 116.3876 | 0.4 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 76.8296 | 29.0089 | 690412.4534 | 57.5344 | 57.5344 | 125.4484 | 0.5 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 80.3815 | 32.5609 | 774949.6168 | 64.5791 | 64.5791 | 134.5091 | 0.6 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 83.9335 | 36.1129 | 859486.7802 | 71.6239 | 71.6239 | 143.5699 | 0.7 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 87.4855 | 39.6649 | 944023.9435 | 78.6687 | 78.6687 | 152.6307 | 0.8 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 91.0375 | 43.2169 | 1028561.1069 | 85.7134 | 85.7134 | 161.6914 | 0.9 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 94.5895 | 46.7688 | 1113098.2702 | 92.7582 | 92.7582 | 170.7522 | 1 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 98.1414 | 50.3208 | 1197635.4336 | 99.803 | 99.803 | 179.813 | 80 | 65 | 34.6873 | 34 | 62.8
7/14/20XX 3:00:00 PM | 0.625 | 6 | 80.1 | 63.9 | 92.7289 | 108.5693 | 15.8405 | 60 | 80.1 |  | 80.1 | 98.9066 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 66.2501 | 18.4295 | 438622.1404 | 36.5518 | 36.5518 | 98.3233 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 69.8786 | 22.058 | 524980.4808 | 43.7484 | 43.7484 | 107.4414 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 73.5071 | 25.6865 | 611338.8212 | 50.9449 | 50.9449 | 116.5594 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 77.1356 | 29.315 | 697697.1616 | 58.1414 | 58.1414 | 125.6774 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 80.7641 | 32.9435 | 784055.502 | 65.338 | 65.338 | 134.7955 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 84.3926 | 36.572 | 870413.8423 | 72.5345 | 72.5345 | 143.9135 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 88.0211 | 40.2005 | 956772.1827 | 79.731 | 79.731 | 153.0315 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 91.6496 | 43.829 | 1043130.5231 | 86.9275 | 86.9275 | 162.1495 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 95.2781 | 47.4575 | 1129488.8635 | 94.1241 | 94.1241 | 171.2676 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 98.9066 | 51.086 | 1215847.2039 | 101.3206 | 101.3206 | 180.3856 | 80 | 65 | 34.7334 | 34 | 63.9
7/14/20XX 4:00:00 PM | 0.66667 | 6 | 79 | 65.2 | 89.3778 | 104.6345 | 15.2568 | 60 | 79 |  | 79 | 97.3113 | 0.1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 66.0906 | 18.27 | 434825.1596 | 36.2354 | 36.2354 | 97.6604 | 0.2 | 75 | 20 | 756000 | 63 | 63 | 69.5596 | 21.7389 | 517386.5193 | 43.1155 | 43.1155 | 106.1155 | 0.3 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 73.0285 | 25.2079 | 599947.8789 | 49.9957 | 49.9957 | 114.5707 | 0.4 | 76 | 21 | 793800 | 66.15 | 66.15 | 76.4975 | 28.6769 | 682509.2386 | 56.8758 | 56.8758 | 123.0258 | 0.5 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 79.9665 | 32.1458 | 765070.5982 | 63.7559 | 63.7559 | 131.4809 | 0.6 | 77 | 22 | 831600 | 69.3 | 69.3 | 83.4354 | 35.6148 | 847631.9578 | 70.636 | 70.636 | 139.936 | 0.7 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 86.9044 | 39.0838 | 930193.3175 | 77.5161 | 77.5161 | 148.3911 | 0.8 | 78 | 23 | 869400 | 72.45 | 72.45 | 90.3733 | 42.5527 | 1012754.6771 | 84.3962 | 84.3962 | 156.8462 | 0.9 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 93.8423 | 46.0217 | 1095316.0368 | 91.2763 | 91.2763 | 165.3013 | 1 | 79 | 24 | 907200 | 75.6 | 75.6 | 97.3113 | 49.4906 | 1177877.3964 | 98.1564 | 98.1564 | 173.7564 | 80 | 65 | 34.2125 | 34 | 65.2
7/14/20XX 5:00:00 PM | 0.70833 | 6 | 78.8 | 67.4 | 88.7794 | 103.932 | 15.1526 | 60 | 78.8 |  | 78.8 | 99.9923 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 66.3587 | 18.5381 | 441206.0531 | 36.7672 | 36.7672 | 98.1292 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 70.0958 | 22.2751 | 530148.3063 | 44.179 | 44.179 | 107.053 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 73.8328 | 26.0122 | 619090.5594 | 51.5909 | 51.5909 | 115.9769 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 77.5699 | 29.7493 | 708032.8125 | 59.0027 | 59.0027 | 124.9007 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 81.307 | 33.4863 | 796975.0656 | 66.4146 | 66.4146 | 133.8246 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 85.044 | 37.2234 | 885917.3188 | 73.8264 | 73.8264 | 142.7484 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 88.7811 | 40.9605 | 974859.5719 | 81.2383 | 81.2383 | 151.6723 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 92.5182 | 44.6976 | 1063801.825 | 88.6502 | 88.6502 | 160.5962 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 96.2553 | 48.4346 | 1152744.0781 | 96.062 | 96.062 | 169.52 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 99.9923 | 52.1717 | 1241686.3313 | 103.4739 | 103.4739 | 178.4439 | 80 | 65 | 34.5834 | 34 | 67.4
7/14/20XX 6:00:00 PM | 0.75 | 6 | 78.5 | 66.9 | 87.8882 | 102.8856 | 14.9974 | 60 | 78.5 |  | 78.5 | 98.2364 | 0.1 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 66.1831 | 18.3625 | 437026.8666 | 36.4189 | 36.4189 | 97.6864 | 0.2 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 69.7446 | 21.9239 | 521789.9332 | 43.4825 | 43.4825 | 106.1675 | 0.3 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 73.3061 | 25.4854 | 606552.9998 | 50.5461 | 50.5461 | 114.6486 | 0.4 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 76.8675 | 29.0469 | 691316.0664 | 57.6097 | 57.6097 | 123.1297 | 0.5 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 80.429 | 32.6084 | 776079.133 | 64.6733 | 64.6733 | 131.6108 | 0.6 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 83.9905 | 36.1698 | 860842.1996 | 71.7368 | 71.7368 | 140.0918 | 0.7 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 87.5519 | 39.7313 | 945605.2662 | 78.8004 | 78.8004 | 148.5729 | 0.8 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 91.1134 | 43.2928 | 1030368.3328 | 85.864 | 85.864 | 157.054 | 0.9 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 94.6749 | 46.8543 | 1115131.3994 | 92.9276 | 92.9276 | 165.5351 | 1 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 98.2364 | 50.4157 | 1199894.466 | 99.9912 | 99.9912 | 174.0162 | 80 | 65 | 34.2343 | 34 | 66.9
7/14/20XX 7:00:00 PM | 0.79167 | 6 | 77.7 | 69.4 | 85.548 | 100.1379 | 14.59 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/14/20XX 8:00:00 PM | 0.83333 | 6 | 76.5 | 72.2 | 96.1318 | 110.2335 | 14.1017 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/14/20XX 9:00:00 PM | 0.875 | 6 | 76.3 | 71.9 | 95.4774 | 109.4805 | 14.0031 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/14/20XX 10:00:00 PM | 0.91667 | 6 | 75.9 | 72.6 | 94.1799 | 107.9876 | 13.8077 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/14/20XX 11:00:00 PM | 0.95833 | 6 | 75.2 | 74.9 | 91.9451 | 105.4166 | 13.4714 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/14/20XX 12:00:00 AM | 0 | 7 | 73.7 | 79.8 | 87.3075 | 100.0824 | 12.7749 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/15/20XX 1:00:00 AM | 0.041667 | 7 | 73.5 | 80.4 | 99.389 | 112.0975 | 12.7086 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/15/20XX 2:00:00 AM | 0.083333 | 7 | 73.3 | 80 | 98.6997 | 111.3171 | 12.6175 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/15/20XX 3:00:00 AM | 0.125 | 7 | 72.6 | 82.3 | 96.3195 | 108.6226 | 12.3031 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/15/20XX 4:00:00 AM | 0.16667 | 7 | 72.3 | 82.6 | 95.3147 | 107.4852 | 12.1705 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/15/20XX 5:00:00 AM | 0.20833 | 7 | 72.1 | 83 | 94.6498 | 106.7327 | 12.0828 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/15/20XX 6:00:00 AM | 0.25 | 7 | 72.7 | 81.4 | 96.6564 | 109.004 | 12.3476 | 80 | 72.7 |  | 72.7 | 98.3851 | 0.1 | 73.87 | 18.87 | 713286 | 59.4405 | 59.4405 | 66.198 | 18.3773 | 437380.8452 | 36.4484 | 36.4484 | 95.8889 | 0.2 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 69.7743 | 21.9537 | 522497.8903 | 43.5415 | 43.5415 | 102.5725 | 0.3 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 73.3507 | 25.53 | 607614.9355 | 50.6346 | 50.6346 | 109.2561 | 0.4 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 76.927 | 29.1064 | 692731.9807 | 57.7277 | 57.7277 | 115.9397 | 0.5 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 80.5034 | 32.6827 | 777849.0259 | 64.8208 | 64.8208 | 122.6233 | 0.6 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 84.0797 | 36.2591 | 862966.071 | 71.9138 | 71.9138 | 129.3068 | 0.7 | 73.09 | 18.09 | 683802 | 56.9835 | 56.9835 | 87.6561 | 39.8354 | 948083.1162 | 79.0069 | 79.0069 | 135.9904 | 0.8 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 91.2324 | 43.4118 | 1033200.1614 | 86.1 | 86.1 | 142.674 | 0.9 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 94.8088 | 46.9881 | 1118317.2065 | 93.1931 | 93.1931 | 149.3576 | 1 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 98.3851 | 50.5645 | 1203434.2517 | 100.2862 | 100.2862 | 156.0412 | 75 | 80 | 32.8294 | 32 | 81.4
7/15/20XX 7:00:00 AM | 0.29167 | 7 | 73.8 | 78.8 | 87.6104 | 100.4307 | 12.8203 | 70 | 73.8 |  | 73.8 | 98.8922 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 66.2487 | 18.4281 | 438587.844 | 36.549 | 36.549 | 96.336 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 69.8758 | 22.0551 | 524911.8881 | 43.7427 | 43.7427 | 103.4667 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 73.5028 | 25.6822 | 611235.9321 | 50.9363 | 50.9363 | 110.5973 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 77.1299 | 29.3092 | 697559.9762 | 58.13 | 58.13 | 117.728 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 80.7569 | 32.9363 | 783884.0202 | 65.3237 | 65.3237 | 124.8587 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 84.384 | 36.5634 | 870208.0642 | 72.5173 | 72.5173 | 131.9893 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 88.0111 | 40.1904 | 956532.1083 | 79.711 | 79.711 | 139.12 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 91.6381 | 43.8175 | 1042856.1523 | 86.9047 | 86.9047 | 146.2507 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 95.2652 | 47.4445 | 1129180.1963 | 94.0983 | 94.0983 | 153.3813 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 98.8922 | 51.0716 | 1215504.2404 | 101.292 | 101.292 | 160.512 | 75 | 80 | 33.1796 | 34 | 78.8
7/15/20XX 8:00:00 AM | 0.33333 | 7 | 75.4 | 75.6 | 92.579 | 106.1458 | 13.5668 | 70 | 75.4 |  | 75.4 | 100.1764 | 0.1 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 66.3771 | 18.5565 | 441644.1442 | 36.8037 | 36.8037 | 97.0947 | 0.2 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 70.1326 | 22.312 | 531024.4883 | 44.252 | 44.252 | 104.984 | 0.3 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 73.8881 | 26.0674 | 620404.8325 | 51.7004 | 51.7004 | 112.8734 | 0.4 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 77.6435 | 29.8229 | 709785.1766 | 59.1488 | 59.1488 | 120.7628 | 0.5 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 81.399 | 33.5784 | 799165.5208 | 66.5971 | 66.5971 | 128.6521 | 0.6 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 85.1545 | 37.3339 | 888545.8649 | 74.0455 | 74.0455 | 136.5415 | 0.7 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 88.91 | 41.0893 | 977926.2091 | 81.4939 | 81.4939 | 144.4309 | 0.8 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 92.6654 | 44.8448 | 1067306.5532 | 88.9422 | 88.9422 | 152.3202 | 0.9 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 96.4209 | 48.6003 | 1156686.8974 | 96.3906 | 96.3906 | 160.2096 | 1 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 100.1764 | 52.3558 | 1246067.2416 | 103.8389 | 103.8389 | 168.0989 | 75 | 75 | 33.7746 | 34 | 75.6
7/15/20XX 9:00:00 AM | 0.375 | 7 | 77 | 72.3 | 97.7844 | 112.1352 | 14.3508 | 70 | 77 |  | 77 | 101.0851 | 0.1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 66.468 | 18.6473 | 443806.7383 | 36.9839 | 36.9839 | 97.7789 | 0.2 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 70.3143 | 22.4937 | 535349.6767 | 44.6125 | 44.6125 | 106.3525 | 0.3 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 74.1607 | 26.34 | 626892.615 | 52.2411 | 52.2411 | 114.9261 | 0.4 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 78.007 | 30.1864 | 718435.5534 | 59.8696 | 59.8696 | 123.4996 | 0.5 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 81.8533 | 34.0327 | 809978.4917 | 67.4982 | 67.4982 | 132.0732 | 0.6 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 85.6997 | 37.8791 | 901521.43 | 75.1268 | 75.1268 | 140.6468 | 0.7 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 89.546 | 41.7254 | 993064.3684 | 82.7554 | 82.7554 | 149.2204 | 0.8 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 93.3924 | 45.5717 | 1084607.3067 | 90.3839 | 90.3839 | 157.7939 | 0.9 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 97.2387 | 49.4181 | 1176150.245 | 98.0125 | 98.0125 | 166.3675 | 1 | 77 | 22 | 831600 | 69.3 | 69.3 | 101.0851 | 53.2644 | 1267693.1834 | 105.6411 | 105.6411 | 174.9411 | 75 | 70 | 34.3111 | 34 | 72.3
7/15/20XX 10:00:00 AM | 0.41667 | 7 | 78.9 | 67.6 | 89.0782 | 104.2828 | 15.2046 | 60 | 78.9 |  | 78.9 | 100.6337 | 0.1 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 66.4228 | 18.6022 | 442732.447 | 36.8944 | 36.8944 | 98.2879 | 0.2 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 70.224 | 22.4034 | 533201.094 | 44.4334 | 44.4334 | 107.3704 | 0.3 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 74.0252 | 26.2046 | 623669.741 | 51.9725 | 51.9725 | 116.453 | 0.4 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 77.8264 | 30.0058 | 714138.388 | 59.5115 | 59.5115 | 125.5355 | 0.5 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 81.6277 | 33.807 | 804607.0349 | 67.0506 | 67.0506 | 134.6181 | 0.6 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 85.4289 | 37.6082 | 895075.6819 | 74.5896 | 74.5896 | 143.7006 | 0.7 | 77.43 | 22.43 | 847854 | 70.6545 | 70.6545 | 89.2301 | 41.4094 | 985544.3289 | 82.1287 | 82.1287 | 152.7832 | 0.8 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 93.0313 | 45.2106 | 1076012.9759 | 89.6677 | 89.6677 | 161.8657 | 0.9 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 96.8325 | 49.0118 | 1166481.6229 | 97.2068 | 97.2068 | 170.9483 | 1 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 100.6337 | 52.813 | 1256950.2699 | 104.7459 | 104.7459 | 180.0309 | 80 | 70 | 34.7086 | 34 | 67.6
7/15/20XX 11:00:00 AM | 0.45833 | 7 | 81.1 | 64 | 95.865 | 112.2518 | 16.3868 | 60 | 81.1 |  | 81.1 | 102.4197 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 66.6014 | 18.7808 | 446983.234 | 37.2486 | 37.2486 | 99.3351 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 70.5812 | 22.7606 | 541702.6681 | 45.1419 | 45.1419 | 109.4649 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 74.5611 | 26.7404 | 636422.1021 | 53.0352 | 53.0352 | 119.5947 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 78.5409 | 30.7202 | 731141.5361 | 60.9285 | 60.9285 | 129.7245 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 82.5207 | 34.7 | 825860.9701 | 68.8217 | 68.8217 | 139.8542 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 86.5005 | 38.6798 | 920580.4042 | 76.715 | 76.715 | 149.984 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 90.4803 | 42.6597 | 1015299.8382 | 84.6083 | 84.6083 | 160.1138 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 94.4601 | 46.6395 | 1110019.2722 | 92.5016 | 92.5016 | 170.2436 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 98.4399 | 50.6193 | 1204738.7062 | 100.3949 | 100.3949 | 180.3734 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 102.4197 | 54.5991 | 1299458.1403 | 108.2882 | 108.2882 | 190.5032 | 80 | 65 | 35.5308 | 36 | 64
7/15/20XX 12:00:00 PM | 0.5 | 7 | 81 | 64 | 95.5475 | 111.879 | 16.3315 | 60 | 81 |  | 81 | 102.0801 | 0.1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 66.5675 | 18.7468 | 446174.9285 | 37.1812 | 37.1812 | 99.2362 | 0.2 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 70.5133 | 22.6927 | 540086.0569 | 45.0072 | 45.0072 | 109.2672 | 0.3 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 74.4592 | 26.6385 | 633997.1854 | 52.8331 | 52.8331 | 119.2981 | 0.4 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 78.405 | 30.5844 | 727908.3139 | 60.659 | 60.659 | 129.329 | 0.5 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 82.3509 | 34.5302 | 821819.4423 | 68.485 | 68.485 | 139.36 | 0.6 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 86.2967 | 38.4761 | 915730.5708 | 76.3109 | 76.3109 | 149.3909 | 0.7 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 90.2426 | 42.4219 | 1009641.6993 | 84.1368 | 84.1368 | 159.4218 | 0.8 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 94.1884 | 46.3678 | 1103552.8278 | 91.9627 | 91.9627 | 169.4527 | 0.9 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 98.1342 | 50.3136 | 1197463.9562 | 99.7887 | 99.7887 | 179.4837 | 1 | 81 | 26 | 982800 | 81.9 | 81.9 | 102.0801 | 54.2595 | 1291375.0847 | 107.6146 | 107.6146 | 189.5146 | 80 | 65 | 35.4529 | 36 | 64
7/15/20XX 1:00:00 PM | 0.54167 | 7 | 83.7 | 59.1 | 86.6644 | 104.429 | 17.7646 | 50 | 83.7 |  | 83.7 | 102.8302 | 0.1 | 74.97 | 19.97 | 754866 | 62.9055 | 62.9055 | 66.6425 | 18.8219 | 447960.1576 | 37.33 | 37.33 | 100.2355 | 0.2 | 75.94 | 20.94 | 791532 | 65.961 | 65.961 | 70.6633 | 22.8427 | 543656.5153 | 45.3047 | 45.3047 | 111.2657 | 0.3 | 76.91 | 21.91 | 828198 | 69.0165 | 69.0165 | 74.6842 | 26.8636 | 639352.8729 | 53.2794 | 53.2794 | 122.2959 | 0.4 | 77.88 | 22.88 | 864864 | 72.072 | 72.072 | 78.7051 | 30.8844 | 735049.2306 | 61.2541 | 61.2541 | 133.3261 | 0.5 | 78.85 | 23.85 | 901530 | 75.1275 | 75.1275 | 82.7259 | 34.9053 | 830745.5882 | 69.2288 | 69.2288 | 144.3563 | 0.6 | 79.82 | 24.82 | 938196 | 78.183 | 78.183 | 86.7468 | 38.9261 | 926441.9458 | 77.2035 | 77.2035 | 155.3865 | 0.7 | 80.79 | 25.79 | 974862 | 81.2385 | 81.2385 | 90.7676 | 42.947 | 1022138.3035 | 85.1782 | 85.1782 | 166.4167 | 0.8 | 81.76 | 26.76 | 1011528 | 84.294 | 84.294 | 94.7885 | 46.9678 | 1117834.6611 | 93.1529 | 93.1529 | 177.4469 | 0.9 | 82.73 | 27.73 | 1048194 | 87.3495 | 87.3495 | 98.8093 | 50.9887 | 1213531.0188 | 101.1276 | 101.1276 | 188.4771 | 1 | 83.7 | 28.7 | 1084860 | 90.405 | 90.405 | 102.8302 | 55.0096 | 1309227.3764 | 109.1023 | 109.1023 | 199.5073 | 85 | 60 | 36.2362 | 36 | 59.1
7/15/20XX 2:00:00 PM | 0.58333 | 7 | 82.7 | 60.1 | 101.064 | 118.3569 | 17.2929 | 60 | 82.7 |  | 82.7 | 101.237 | 0.1 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 66.4832 | 18.6625 | 444168.3049 | 37.014 | 37.014 | 99.6045 | 0.2 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 70.3447 | 22.5241 | 536072.8097 | 44.6727 | 44.6727 | 110.0037 | 0.3 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 74.2062 | 26.3856 | 627977.3146 | 52.3314 | 52.3314 | 120.4029 | 0.4 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 78.0678 | 30.2471 | 719881.8195 | 59.9902 | 59.9902 | 130.8022 | 0.5 | 78.35 | 23.35 | 882630 | 73.5525 | 73.5525 | 81.9293 | 34.1087 | 811786.3243 | 67.6489 | 67.6489 | 141.2014 | 0.6 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 85.7908 | 37.9702 | 903690.8292 | 75.3076 | 75.3076 | 151.6006 | 0.7 | 80.09 | 25.09 | 948402 | 79.0335 | 79.0335 | 89.6524 | 41.8317 | 995595.3341 | 82.9663 | 82.9663 | 161.9998 | 0.8 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 93.5139 | 45.6933 | 1087499.8389 | 90.625 | 90.625 | 172.399 | 0.9 | 81.83 | 26.83 | 1014174 | 84.5145 | 84.5145 | 97.3754 | 49.5548 | 1179404.3438 | 98.2837 | 98.2837 | 182.7982 | 1 | 82.7 | 27.7 | 1047060 | 87.255 | 87.255 | 101.237 | 53.4163 | 1271308.8487 | 105.9424 | 105.9424 | 193.1974 | 85 | 60 | 35.7396 | 36 | 60.1
7/15/20XX 3:00:00 PM | 0.625 | 7 | 82.8 | 58.8 | 84.1546 | 101.3965 | 17.2419 | 50 | 82.8 |  | 82.8 | 99.3275 | 0.1 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 66.2922 | 18.4716 | 439623.7123 | 36.6353 | 36.6353 | 99.2573 | 0.2 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 69.9628 | 22.1422 | 526983.6247 | 43.9153 | 43.9153 | 109.3093 | 0.3 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 73.6334 | 25.8128 | 614343.537 | 51.1953 | 51.1953 | 119.3613 | 0.4 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 77.304 | 29.4833 | 701703.4494 | 58.4753 | 58.4753 | 129.4133 | 0.5 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 80.9746 | 33.1539 | 789063.3617 | 65.7553 | 65.7553 | 139.4653 | 0.6 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 84.6451 | 36.8245 | 876423.2741 | 73.0353 | 73.0353 | 149.5173 | 0.7 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 88.3157 | 40.4951 | 963783.1864 | 80.3153 | 80.3153 | 159.5693 | 0.8 | 81.04 | 26.04 | 984312 | 82.026 | 82.026 | 91.9863 | 44.1657 | 1051143.0988 | 87.5953 | 87.5953 | 169.6213 | 0.9 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 95.6569 | 47.8363 | 1138503.0111 | 94.8753 | 94.8753 | 179.6733 | 1 | 82.8 | 27.8 | 1050840 | 87.57 | 87.57 | 99.3275 | 51.5068 | 1225862.9234 | 102.1552 | 102.1552 | 189.7252 | 85 | 60 | 35.4644 | 36 | 58.8
7/15/20XX 4:00:00 PM | 0.66667 | 7 | 83.3 | 57.5 | 85.5415 | 103.0722 | 17.5307 | 50 | 83.3 |  | 83.3 | 98.6896 | 0.1 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 66.2284 | 18.4078 | 438105.4464 | 36.5088 | 36.5088 | 99.2883 | 0.2 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 69.8352 | 22.0146 | 523947.0929 | 43.6623 | 43.6623 | 109.3713 | 0.3 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 73.442 | 25.6214 | 609788.7393 | 50.8157 | 50.8157 | 119.4542 | 0.4 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 77.0488 | 29.2282 | 695630.3858 | 57.9692 | 57.9692 | 129.5372 | 0.5 | 78.65 | 23.65 | 893970 | 74.4975 | 74.4975 | 80.6556 | 32.835 | 781472.0322 | 65.1227 | 65.1227 | 139.6202 | 0.6 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 84.2624 | 36.4418 | 867313.6787 | 72.2761 | 72.2761 | 149.7031 | 0.7 | 80.51 | 25.51 | 964278 | 80.3565 | 80.3565 | 87.8692 | 40.0485 | 953155.3251 | 79.4296 | 79.4296 | 159.7861 | 0.8 | 81.44 | 26.44 | 999432 | 83.286 | 83.286 | 91.476 | 43.6553 | 1038996.9716 | 86.5831 | 86.5831 | 169.8691 | 0.9 | 82.37 | 27.37 | 1034586 | 86.2155 | 86.2155 | 95.0828 | 47.2621 | 1124838.618 | 93.7366 | 93.7366 | 179.9521 | 1 | 83.3 | 28.3 | 1069740 | 89.145 | 89.145 | 98.6896 | 50.8689 | 1210680.2645 | 100.89 | 100.89 | 190.035 | 85 | 55 | 35.4874 | 36 | 57.5
7/15/20XX 5:00:00 PM | 0.70833 | 7 | 82.1 | 59 | 82.2439 | 99.088 | 16.8441 | 50 | 82.1 |  | 82.1 | 97.4036 | 0.1 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 66.0998 | 18.2792 | 435044.7664 | 36.2537 | 36.2537 | 98.6552 | 0.2 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 69.578 | 21.7574 | 517825.7327 | 43.1521 | 43.1521 | 108.1051 | 0.3 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 73.0562 | 25.2356 | 600606.6991 | 50.0506 | 50.0506 | 117.5551 | 0.4 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 76.5344 | 28.7138 | 683387.6654 | 56.949 | 56.949 | 127.005 | 0.5 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 80.0126 | 32.192 | 766168.6318 | 63.8474 | 63.8474 | 136.4549 | 0.6 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 83.4908 | 35.6702 | 848949.5981 | 70.7458 | 70.7458 | 145.9048 | 0.7 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 86.969 | 39.1483 | 931730.5645 | 77.6442 | 77.6442 | 155.3547 | 0.8 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 90.4472 | 42.6265 | 1014511.5309 | 84.5426 | 84.5426 | 164.8046 | 0.9 | 81.29 | 26.29 | 993762 | 82.8135 | 82.8135 | 93.9254 | 46.1047 | 1097292.4972 | 91.441 | 91.441 | 174.2545 | 1 | 82.1 | 27.1 | 1024380 | 85.365 | 85.365 | 97.4036 | 49.5829 | 1180073.4636 | 98.3395 | 98.3395 | 183.7045 | 80 | 60 | 34.9901 | 34 | 59
7/15/20XX 6:00:00 PM | 0.75 | 7 | 80.9 | 59.8 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 94.9073 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 65.8502 | 18.0296 | 429103.5973 | 35.7586 | 35.7586 | 97.7821 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 69.0788 | 21.2581 | 505943.3946 | 42.1619 | 42.1619 | 106.3589 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 72.3073 | 24.4867 | 582783.1919 | 48.5653 | 48.5653 | 114.9358 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 75.5359 | 27.7153 | 659622.9892 | 54.9686 | 54.9686 | 123.5126 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 78.7644 | 30.9438 | 736462.7865 | 61.3719 | 61.3719 | 132.0894 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 81.993 | 34.1724 | 813302.5838 | 67.7752 | 67.7752 | 140.6662 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 85.2216 | 37.4009 | 890142.381 | 74.1785 | 74.1785 | 149.243 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 88.4501 | 40.6295 | 966982.1783 | 80.5818 | 80.5818 | 157.8198 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 91.6787 | 43.8581 | 1043821.9756 | 86.9852 | 86.9852 | 166.3967 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 94.9073 | 47.0866 | 1120661.7729 | 93.3885 | 93.3885 | 174.9735 | 80 | 60 | 34.3031 | 34 | 59.8
7/15/20XX 7:00:00 PM | 0.79167 | 7 | 79.9 | 61.1 | 92.1119 | 107.8449 | 15.733 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/15/20XX 8:00:00 PM | 0.83333 | 7 | 78.5 | 63.9 | 87.8882 | 102.8856 | 14.9974 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/15/20XX 9:00:00 PM | 0.875 | 7 | 76.9 | 69.6 | 83.2602 | 97.452 | 14.1918 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/15/20XX 10:00:00 PM | 0.91667 | 7 | 76.3 | 71 | 95.4774 | 109.4805 | 14.0031 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/15/20XX 11:00:00 PM | 0.95833 | 7 | 75.9 | 70.9 | 94.1799 | 107.9876 | 13.8077 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/15/20XX 12:00:00 AM | 0 | 1 | 75.4 | 71 | 92.579 | 106.1458 | 13.5668 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/16/20XX 1:00:00 AM | 0.041667 | 1 | 75 | 71.4 | 91.3149 | 104.6916 | 13.3767 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/16/20XX 2:00:00 AM | 0.083333 | 1 | 74 | 72.6 | 88.2187 | 101.1303 | 12.9116 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/16/20XX 3:00:00 AM | 0.125 | 1 | 73.3 | 72.7 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/16/20XX 4:00:00 AM | 0.16667 | 1 | 72.9 | 74.1 | 84.9169 | 97.3334 | 12.4165 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/16/20XX 5:00:00 AM | 0.20833 | 1 | 72.6 | 74.3 | 84.035 | 96.3195 | 12.2844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/16/20XX 6:00:00 AM | 0.25 | 1 | 72.8 | 74.5 | 84.6221 | 96.9944 | 12.3723 | 70 | 72.8 |  | 72.8 | 90.1896 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.3784 | 17.5578 | 417875.6261 | 34.823 | 34.823 | 94.295 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 68.1352 | 20.3146 | 483487.4523 | 40.2906 | 40.2906 | 99.3846 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 70.892 | 23.0714 | 549099.2784 | 45.7583 | 45.7583 | 104.4743 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 73.6488 | 25.8282 | 614711.1045 | 51.2259 | 51.2259 | 109.5639 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 76.4056 | 28.585 | 680322.9306 | 56.6936 | 56.6936 | 114.6536 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 79.1624 | 31.3418 | 745934.7568 | 62.1612 | 62.1612 | 119.7432 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 81.9192 | 34.0986 | 811546.5829 | 67.6289 | 67.6289 | 124.8329 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 84.676 | 36.8554 | 877158.409 | 73.0965 | 73.0965 | 129.9225 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 87.4328 | 39.6122 | 942770.2352 | 78.5642 | 78.5642 | 135.0122 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 90.1896 | 42.369 | 1008382.0613 | 84.0318 | 84.0318 | 140.1018 | 75 | 75 | 31.5727 | 32 | 74.5
7/16/20XX 7:00:00 AM | 0.29167 | 1 | 73.9 | 71.5 | 87.9141 | 100.78 | 12.8659 | 70 | 73.9 |  | 73.9 | 89.844 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 65.3439 | 17.5232 | 417052.9797 | 34.7544 | 34.7544 | 94.5729 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 68.0661 | 20.2455 | 481842.1594 | 40.1535 | 40.1535 | 99.9405 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 70.7883 | 22.9677 | 546631.3391 | 45.5526 | 45.5526 | 105.3081 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 73.5106 | 25.6899 | 611420.5188 | 50.9517 | 50.9517 | 110.6757 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 76.2328 | 28.4122 | 676209.6984 | 56.3508 | 56.3508 | 116.0433 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 78.955 | 31.1344 | 740998.8781 | 61.7499 | 61.7499 | 121.4109 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 81.6773 | 33.8566 | 805788.0578 | 67.149 | 67.149 | 126.7785 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 84.3995 | 36.5789 | 870577.2375 | 72.5481 | 72.5481 | 132.1461 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 87.1217 | 39.3011 | 935366.4172 | 77.9472 | 77.9472 | 137.5137 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 89.844 | 42.0233 | 1000155.5969 | 83.3463 | 83.3463 | 142.8813 | 75 | 70 | 31.789 | 32 | 71.5
7/16/20XX 8:00:00 AM | 0.33333 | 1 | 75.5 | 67.9 | 79.3806 | 92.8973 | 13.5167 | 60 | 75.5 |  | 75.5 | 90.0588 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 65.3654 | 17.5447 | 417564.312 | 34.797 | 34.797 | 95.1195 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 68.1091 | 20.2884 | 482864.824 | 40.2387 | 40.2387 | 101.0337 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 70.8528 | 23.0322 | 548165.336 | 45.6804 | 45.6804 | 106.9479 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 73.5965 | 25.7759 | 613465.848 | 51.1222 | 51.1222 | 112.8622 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 76.3402 | 28.5196 | 678766.36 | 56.5639 | 56.5639 | 118.7764 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 79.0839 | 31.2633 | 744066.872 | 62.0056 | 62.0056 | 124.6906 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 81.8277 | 34.007 | 809367.384 | 67.4473 | 67.4473 | 130.6048 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 84.5714 | 36.7508 | 874667.896 | 72.889 | 72.889 | 136.519 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 87.3151 | 39.4945 | 939968.408 | 78.3307 | 78.3307 | 142.4332 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 90.0588 | 42.2382 | 1005268.92 | 83.7724 | 83.7724 | 148.3474 | 75 | 70 | 32.2157 | 32 | 67.9
7/16/20XX 9:00:00 AM | 0.375 | 1 | 77.8 | 62.8 | 85.8376 | 100.478 | 14.6404 | 60 | 77.8 |  | 77.8 | 89.9369 | 0.1 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 65.3532 | 17.5325 | 417274.1589 | 34.7728 | 34.7728 | 95.8198 | 0.2 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 68.0847 | 20.2641 | 482284.5179 | 40.1904 | 40.1904 | 102.4344 | 0.3 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 70.8162 | 22.9956 | 547294.8768 | 45.6079 | 45.6079 | 109.0489 | 0.4 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 73.5477 | 25.7271 | 612305.2358 | 51.0254 | 51.0254 | 115.6634 | 0.5 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 76.2793 | 28.4586 | 677315.5947 | 56.443 | 56.443 | 122.278 | 0.6 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 79.0108 | 31.1902 | 742325.9537 | 61.8605 | 61.8605 | 128.8925 | 0.7 | 76.66 | 21.66 | 818748 | 68.229 | 68.229 | 81.7423 | 33.9217 | 807336.3126 | 67.278 | 67.278 | 135.507 | 0.8 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 84.4739 | 36.6532 | 872346.6716 | 72.6956 | 72.6956 | 142.1216 | 0.9 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 87.2054 | 39.3847 | 937357.0305 | 78.1131 | 78.1131 | 148.7361 | 1 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 89.9369 | 42.1163 | 1002367.3895 | 83.5306 | 83.5306 | 155.3506 | 80 | 65 | 32.7618 | 32 | 62.8
7/16/20XX 10:00:00 AM | 0.41667 | 1 | 80.1 | 57.9 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 89.4215 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 65.3016 | 17.481 | 416047.4795 | 34.6706 | 34.6706 | 96.4421 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 67.9816 | 20.161 | 479831.1591 | 39.9859 | 39.9859 | 103.6789 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 70.6616 | 22.841 | 543614.8386 | 45.3012 | 45.3012 | 110.9157 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 73.3416 | 25.5209 | 607398.5182 | 50.6165 | 50.6165 | 118.1525 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 76.0216 | 28.2009 | 671182.1977 | 55.9318 | 55.9318 | 125.3893 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 78.7016 | 30.8809 | 734965.8772 | 61.2472 | 61.2472 | 132.6262 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 81.3815 | 33.5609 | 798749.5568 | 66.5625 | 66.5625 | 139.863 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 84.0615 | 36.2409 | 862533.2363 | 71.8778 | 71.8778 | 147.0998 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 86.7415 | 38.9209 | 926316.9159 | 77.1931 | 77.1931 | 154.3366 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 89.4215 | 41.6009 | 990100.5954 | 82.5084 | 82.5084 | 161.5734 | 80 | 60 | 33.2461 | 34 | 57.9
7/16/20XX 11:00:00 AM | 0.45833 | 1 | 83.3 | 52.9 | 85.5415 | 103.0722 | 17.5307 | 50 | 83.3 |  | 83.3 | 90.6254 | 0.1 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 65.422 | 17.6014 | 418912.8428 | 34.9094 | 34.9094 | 97.6889 | 0.2 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 68.2224 | 20.4018 | 485561.8856 | 40.4635 | 40.4635 | 106.1725 | 0.3 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 71.0228 | 23.2021 | 552210.9284 | 46.0176 | 46.0176 | 114.6561 | 0.4 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 73.8232 | 26.0025 | 618859.9712 | 51.5717 | 51.5717 | 123.1397 | 0.5 | 78.65 | 23.65 | 893970 | 74.4975 | 74.4975 | 76.6235 | 28.8029 | 685509.014 | 57.1258 | 57.1258 | 131.6233 | 0.6 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 79.4239 | 31.6033 | 752158.0567 | 62.6798 | 62.6798 | 140.1068 | 0.7 | 80.51 | 25.51 | 964278 | 80.3565 | 80.3565 | 82.2243 | 34.4037 | 818807.0995 | 68.2339 | 68.2339 | 148.5904 | 0.8 | 81.44 | 26.44 | 999432 | 83.286 | 83.286 | 85.0247 | 37.204 | 885456.1423 | 73.788 | 73.788 | 157.074 | 0.9 | 82.37 | 27.37 | 1034586 | 86.2155 | 86.2155 | 87.8251 | 40.0044 | 952105.1851 | 79.3421 | 79.3421 | 165.5576 | 1 | 83.3 | 28.3 | 1069740 | 89.145 | 89.145 | 90.6254 | 42.8048 | 1018754.2279 | 84.8962 | 84.8962 | 174.0412 | 85 | 55 | 34.2213 | 34 | 52.9
7/16/20XX 12:00:00 PM | 0.5 | 1 | 85.1 | 49.6 | 72.2049 | 90.6889 | 18.484 | 40 | 85.1 |  | 85.1 | 89.9495 | 0.1 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 65.3544 | 17.5338 | 417304.1887 | 34.7753 | 34.7753 | 98.1218 | 0.2 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 68.0872 | 20.2666 | 482344.5773 | 40.1954 | 40.1954 | 107.0384 | 0.3 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 70.82 | 22.9994 | 547384.966 | 45.6154 | 45.6154 | 115.9549 | 0.4 | 78.44 | 23.44 | 886032 | 73.836 | 73.836 | 73.5528 | 25.7322 | 612425.3546 | 51.0354 | 51.0354 | 124.8714 | 0.5 | 79.55 | 24.55 | 927990 | 77.3325 | 77.3325 | 76.2856 | 28.4649 | 677465.7433 | 56.4555 | 56.4555 | 133.788 | 0.6 | 80.66 | 25.66 | 969948 | 80.829 | 80.829 | 79.0184 | 31.1977 | 742506.132 | 61.8755 | 61.8755 | 142.7045 | 0.7 | 81.77 | 26.77 | 1011906 | 84.3255 | 84.3255 | 81.7512 | 33.9305 | 807546.5206 | 67.2955 | 67.2955 | 151.621 | 0.8 | 82.88 | 27.88 | 1053864 | 87.822 | 87.822 | 84.4839 | 36.6633 | 872586.9093 | 72.7156 | 72.7156 | 160.5376 | 0.9 | 83.99 | 28.99 | 1095822 | 91.3185 | 91.3185 | 87.2167 | 39.3961 | 937627.2979 | 78.1356 | 78.1356 | 169.4541 | 1 | 85.1 | 30.1 | 1137780 | 94.815 | 94.815 | 89.9495 | 42.1289 | 1002667.6866 | 83.5556 | 83.5556 | 178.3706 | 85 | 50 | 34.5574 | 34 | 49.6
7/16/20XX 1:00:00 PM | 0.54167 | 1 | 85.1 | 49.9 | 72.2049 | 90.6889 | 18.484 | 40 | 85.1 |  | 85.1 | 90.504 | 0.1 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 65.4099 | 17.5892 | 418623.9485 | 34.8853 | 34.8853 | 98.2318 | 0.2 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 68.1981 | 20.3775 | 484984.097 | 40.4153 | 40.4153 | 107.2583 | 0.3 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 70.9864 | 23.1657 | 551344.2455 | 45.9454 | 45.9454 | 116.2849 | 0.4 | 78.44 | 23.44 | 886032 | 73.836 | 73.836 | 73.7746 | 25.954 | 617704.394 | 51.4754 | 51.4754 | 125.3114 | 0.5 | 79.55 | 24.55 | 927990 | 77.3325 | 77.3325 | 76.5628 | 28.7422 | 684064.5425 | 57.0054 | 57.0054 | 134.3379 | 0.6 | 80.66 | 25.66 | 969948 | 80.829 | 80.829 | 79.3511 | 31.5304 | 750424.691 | 62.5354 | 62.5354 | 143.3644 | 0.7 | 81.77 | 26.77 | 1011906 | 84.3255 | 84.3255 | 82.1393 | 34.3187 | 816784.8395 | 68.0654 | 68.0654 | 152.3909 | 0.8 | 82.88 | 27.88 | 1053864 | 87.822 | 87.822 | 84.9276 | 37.1069 | 883144.988 | 73.5954 | 73.5954 | 161.4174 | 0.9 | 83.99 | 28.99 | 1095822 | 91.3185 | 91.3185 | 87.7158 | 39.8952 | 949505.1365 | 79.1254 | 79.1254 | 170.4439 | 1 | 85.1 | 30.1 | 1137780 | 94.815 | 94.815 | 90.504 | 42.6834 | 1015865.285 | 84.6554 | 84.6554 | 179.4704 | 85 | 50 | 34.6446 | 34 | 49.9
7/16/20XX 2:00:00 PM | 0.58333 | 1 | 85.4 | 49.6 | 72.9026 | 91.5706 | 18.6681 | 40 | 85.4 |  | 85.4 | 90.8239 | 0.1 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 65.4419 | 17.6212 | 419385.1973 | 34.9488 | 34.9488 | 98.3898 | 0.2 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 68.2621 | 20.4415 | 486506.5946 | 40.5422 | 40.5422 | 107.5742 | 0.3 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 71.0823 | 23.2617 | 553627.992 | 46.1357 | 46.1357 | 116.7587 | 0.4 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 73.9025 | 26.0819 | 620749.3893 | 51.7291 | 51.7291 | 125.9431 | 0.5 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 76.7228 | 28.9021 | 687870.7866 | 57.3226 | 57.3226 | 135.1276 | 0.6 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 79.543 | 31.7224 | 754992.1839 | 62.916 | 62.916 | 144.312 | 0.7 | 81.98 | 26.98 | 1019844 | 84.987 | 84.987 | 82.3632 | 34.5426 | 822113.5812 | 68.5095 | 68.5095 | 153.4965 | 0.8 | 83.12 | 28.12 | 1062936 | 88.578 | 88.578 | 85.1834 | 37.3628 | 889234.9786 | 74.1029 | 74.1029 | 162.6809 | 0.9 | 84.26 | 29.26 | 1106028 | 92.169 | 92.169 | 88.0037 | 40.183 | 956356.3759 | 79.6964 | 79.6964 | 171.8654 | 1 | 85.4 | 30.4 | 1149120 | 95.76 | 95.76 | 90.8239 | 43.0033 | 1023477.7732 | 85.2898 | 85.2898 | 181.0498 | 85 | 50 | 34.7685 | 34 | 49.6
7/16/20XX 3:00:00 PM | 0.625 | 1 | 85.5 | 49.4 | 73.1363 | 91.8661 | 18.7297 | 40 | 85.5 |  | 85.5 | 90.7423 | 0.1 | 75.15 | 20.15 | 761670 | 63.4725 | 63.4725 | 65.4337 | 17.6131 | 419190.9441 | 34.9326 | 34.9326 | 98.4051 | 0.2 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 68.2458 | 20.4251 | 486118.0883 | 40.5098 | 40.5098 | 107.6048 | 0.3 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 71.0578 | 23.2372 | 553045.2324 | 46.0871 | 46.0871 | 116.8046 | 0.4 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 73.8699 | 26.0493 | 619972.3766 | 51.6644 | 51.6644 | 126.0044 | 0.5 | 79.75 | 24.75 | 935550 | 77.9625 | 77.9625 | 76.682 | 28.8613 | 686899.5207 | 57.2416 | 57.2416 | 135.2041 | 0.6 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 79.494 | 31.6734 | 753826.6649 | 62.8189 | 62.8189 | 144.4039 | 0.7 | 82.05 | 27.05 | 1022490 | 85.2075 | 85.2075 | 82.3061 | 34.4855 | 820753.809 | 68.3962 | 68.3962 | 153.6037 | 0.8 | 83.2 | 28.2 | 1065960 | 88.83 | 88.83 | 85.1182 | 37.2975 | 887680.9532 | 73.9734 | 73.9734 | 162.8034 | 0.9 | 84.35 | 29.35 | 1109430 | 92.4525 | 92.4525 | 87.9302 | 40.1096 | 954608.0973 | 79.5507 | 79.5507 | 172.0032 | 1 | 85.5 | 30.5 | 1152900 | 96.075 | 96.075 | 90.7423 | 42.9216 | 1021535.2415 | 85.1279 | 85.1279 | 181.2029 | 85 | 50 | 34.7803 | 34 | 49.4
7/16/20XX 4:00:00 PM | 0.66667 | 1 | 83.8 | 52 | 86.947 | 104.7705 | 17.8235 | 50 | 83.8 |  | 83.8 | 90.5117 | 0.1 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 65.4106 | 17.59 | 418642.0619 | 34.8868 | 34.8868 | 97.8238 | 0.2 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 68.1996 | 20.379 | 485020.3239 | 40.4184 | 40.4184 | 106.4424 | 0.3 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 70.9886 | 23.168 | 551398.5858 | 45.9499 | 45.9499 | 115.0609 | 0.4 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 73.7776 | 25.957 | 617776.8478 | 51.4814 | 51.4814 | 123.6794 | 0.5 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 76.5666 | 28.746 | 684155.1097 | 57.0129 | 57.0129 | 132.2979 | 0.6 | 79.88 | 24.88 | 940464 | 78.372 | 78.372 | 79.3556 | 31.535 | 750533.3717 | 62.5444 | 62.5444 | 140.9164 | 0.7 | 80.86 | 25.86 | 977508 | 81.459 | 81.459 | 82.1447 | 34.324 | 816911.6336 | 68.076 | 68.076 | 149.535 | 0.8 | 81.84 | 26.84 | 1014552 | 84.546 | 84.546 | 84.9337 | 37.113 | 883289.8956 | 73.6075 | 73.6075 | 158.1535 | 0.9 | 82.82 | 27.82 | 1051596 | 87.633 | 87.633 | 87.7227 | 39.902 | 949668.1575 | 79.139 | 79.139 | 166.772 | 1 | 83.8 | 28.8 | 1088640 | 90.72 | 90.72 | 90.5117 | 42.691 | 1016046.4195 | 84.6705 | 84.6705 | 175.3905 | 85 | 50 | 34.3263 | 34 | 52
7/16/20XX 5:00:00 PM | 0.70833 | 1 | 83.3 | 51.9 | 85.5415 | 103.0722 | 17.5307 | 50 | 83.3 |  | 83.3 | 88.8724 | 0.1 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 65.2467 | 17.4261 | 414740.5376 | 34.5617 | 34.5617 | 97.3412 | 0.2 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 67.8718 | 20.0511 | 477217.2753 | 39.7681 | 39.7681 | 105.4771 | 0.3 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 70.4969 | 22.6762 | 539694.0129 | 44.9745 | 44.9745 | 113.613 | 0.4 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 73.1219 | 25.3013 | 602170.7506 | 50.1809 | 50.1809 | 121.7489 | 0.5 | 78.65 | 23.65 | 893970 | 74.4975 | 74.4975 | 75.747 | 27.9264 | 664647.4882 | 55.3873 | 55.3873 | 129.8848 | 0.6 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 78.3721 | 30.5514 | 727124.2259 | 60.5937 | 60.5937 | 138.0207 | 0.7 | 80.51 | 25.51 | 964278 | 80.3565 | 80.3565 | 80.9971 | 33.1765 | 789600.9635 | 65.8001 | 65.8001 | 146.1566 | 0.8 | 81.44 | 26.44 | 999432 | 83.286 | 83.286 | 83.6222 | 35.8016 | 852077.7012 | 71.0065 | 71.0065 | 154.2925 | 0.9 | 82.37 | 27.37 | 1034586 | 86.2155 | 86.2155 | 86.2473 | 38.4267 | 914554.4388 | 76.2129 | 76.2129 | 162.4284 | 1 | 83.3 | 28.3 | 1069740 | 89.145 | 89.145 | 88.8724 | 41.0517 | 977031.1765 | 81.4193 | 81.4193 | 170.5643 | 85 | 50 | 33.946 | 34 | 51.9
7/16/20XX 6:00:00 PM | 0.75 | 1 | 83.2 | 50.9 | 85.2627 | 102.7353 | 17.4726 | 50 | 83.2 |  | 83.2 | 86.8352 | 0.1 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 65.043 | 17.2224 | 409892.113 | 34.1577 | 34.1577 | 96.9057 | 0.2 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 67.4643 | 19.6437 | 467520.426 | 38.96 | 38.96 | 104.606 | 0.3 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 69.8857 | 22.0651 | 525148.739 | 43.7624 | 43.7624 | 112.3064 | 0.4 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 72.3071 | 24.4864 | 582777.052 | 48.5648 | 48.5648 | 120.0068 | 0.5 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 74.7284 | 26.9078 | 640405.365 | 53.3671 | 53.3671 | 127.7071 | 0.6 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 77.1498 | 29.3291 | 698033.678 | 58.1695 | 58.1695 | 135.4075 | 0.7 | 80.44 | 25.44 | 961632 | 80.136 | 80.136 | 79.5711 | 31.7505 | 755661.991 | 62.9718 | 62.9718 | 143.1078 | 0.8 | 81.36 | 26.36 | 996408 | 83.034 | 83.034 | 81.9925 | 34.1719 | 813290.304 | 67.7742 | 67.7742 | 150.8082 | 0.9 | 82.28 | 27.28 | 1031184 | 85.932 | 85.932 | 84.4139 | 36.5932 | 870918.617 | 72.5766 | 72.5766 | 158.5086 | 1 | 83.2 | 28.2 | 1065960 | 88.83 | 88.83 | 86.8352 | 39.0146 | 928546.93 | 77.3789 | 77.3789 | 166.2089 | 85 | 50 | 33.6016 | 34 | 50.9
7/16/20XX 7:00:00 PM | 0.79167 | 1 | 82.1 | 52.6 | 82.2439 | 99.088 | 16.8441 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/16/20XX 8:00:00 PM | 0.83333 | 1 | 80.8 | 55.7 | 78.7895 | 94.9151 | 16.1256 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/16/20XX 9:00:00 PM | 0.875 | 1 | 80.3 | 55.3 | 77.4931 | 93.3492 | 15.8561 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/16/20XX 10:00:00 PM | 0.91667 | 1 | 79.2 | 56.4 | 74.7029 | 89.9794 | 15.2766 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/16/20XX 11:00:00 PM | 0.95833 | 1 | 78.6 | 57.4 | 73.2164 | 88.1844 | 14.968 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/16/20XX 12:00:00 AM | 0 | 2 | 77.1 | 61.3 | 83.8273 | 98.1177 | 14.2905 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/17/20XX 1:00:00 AM | 0.041667 | 2 | 76.5 | 64.1 | 82.1358 | 96.1318 | 13.9961 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/17/20XX 2:00:00 AM | 0.083333 | 2 | 75 | 68 | 78.0327 | 91.3149 | 13.2822 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/17/20XX 3:00:00 AM | 0.125 | 2 | 74.5 | 70.3 | 89.7555 | 102.8978 | 13.1423 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/17/20XX 4:00:00 AM | 0.16667 | 2 | 73.9 | 71.5 | 87.9141 | 100.78 | 12.8659 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/17/20XX 5:00:00 AM | 0.20833 | 2 | 73.6 | 73.1 | 87.0056 | 99.7352 | 12.7296 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/17/20XX 6:00:00 AM | 0.25 | 2 | 73.7 | 74.8 | 87.3075 | 100.0824 | 12.7749 | 70 | 73.7 |  | 73.7 | 93.4395 | 0.1 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 65.7034 | 17.8828 | 425610.2369 | 35.4675 | 35.4675 | 95.223 | 0.2 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 68.7852 | 20.9646 | 498956.6737 | 41.5797 | 41.5797 | 101.2407 | 0.3 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 71.867 | 24.0463 | 572303.1106 | 47.6919 | 47.6919 | 107.2584 | 0.4 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 74.9488 | 27.1281 | 645649.5474 | 53.8041 | 53.8041 | 113.2761 | 0.5 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 78.0305 | 30.2099 | 718995.9843 | 59.9163 | 59.9163 | 119.2938 | 0.6 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 81.1123 | 33.2917 | 792342.4212 | 66.0285 | 66.0285 | 125.3115 | 0.7 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 84.1941 | 36.3735 | 865688.858 | 72.1407 | 72.1407 | 131.3292 | 0.8 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 87.2759 | 39.4553 | 939035.2949 | 78.2529 | 78.2529 | 137.3469 | 0.9 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 90.3577 | 42.537 | 1012381.7318 | 84.3651 | 84.3651 | 143.3646 | 1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 93.4395 | 45.6188 | 1085728.1686 | 90.4773 | 90.4773 | 149.3823 | 75 | 75 | 32.3022 | 32 | 74.8
7/17/20XX 7:00:00 AM | 0.29167 | 2 | 75.3 | 70.6 | 92.2616 | 105.7806 | 13.519 | 70 | 75.3 |  | 75.3 | 93.0727 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 65.6667 | 17.8461 | 424737.4414 | 35.3948 | 35.3948 | 95.6543 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 68.7119 | 20.8912 | 497211.0829 | 41.4343 | 41.4343 | 102.1033 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 71.757 | 23.9363 | 569684.7243 | 47.4737 | 47.4737 | 108.5522 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 74.8021 | 26.9814 | 642158.3657 | 53.5132 | 53.5132 | 115.0012 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 77.8472 | 30.0266 | 714632.0072 | 59.5527 | 59.5527 | 121.4502 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 80.8923 | 33.0717 | 787105.6486 | 65.5921 | 65.5921 | 127.8991 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 83.9374 | 36.1168 | 859579.29 | 71.6316 | 71.6316 | 134.3481 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 86.9825 | 39.1619 | 932052.9315 | 77.6711 | 77.6711 | 140.7971 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 90.0276 | 42.207 | 1004526.5729 | 83.7105 | 83.7105 | 147.246 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 93.0727 | 45.2521 | 1077000.2143 | 89.75 | 89.75 | 153.695 | 75 | 70 | 32.6383 | 32 | 70.6
7/17/20XX 8:00:00 AM | 0.33333 | 2 | 77.5 | 65.9 | 84.9711 | 99.4607 | 14.4896 | 60 | 77.5 |  | 77.5 | 93.52 | 0.1 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 65.7115 | 17.8908 | 425801.8432 | 35.4835 | 35.4835 | 96.436 | 0.2 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 68.8013 | 20.9807 | 499339.8863 | 41.6117 | 41.6117 | 103.6667 | 0.3 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 71.8911 | 24.0705 | 572877.9295 | 47.7398 | 47.7398 | 110.8973 | 0.4 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 74.981 | 27.1603 | 646415.9727 | 53.868 | 53.868 | 118.128 | 0.5 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 78.0708 | 30.2502 | 719954.0159 | 59.9962 | 59.9962 | 125.3587 | 0.6 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 81.1606 | 33.34 | 793492.059 | 66.1243 | 66.1243 | 132.5893 | 0.7 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 84.2505 | 36.4298 | 867030.1022 | 72.2525 | 72.2525 | 139.82 | 0.8 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 87.3403 | 39.5197 | 940568.1454 | 78.3807 | 78.3807 | 147.0507 | 0.9 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 90.4301 | 42.6095 | 1014106.1886 | 84.5088 | 84.5088 | 154.2813 | 1 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 93.52 | 45.6993 | 1087644.2317 | 90.637 | 90.637 | 161.512 | 75 | 65 | 33.2493 | 34 | 65.9
7/17/20XX 9:00:00 AM | 0.375 | 2 | 80 | 60.9 | 92.42 | 108.2066 | 15.7866 | 60 | 80 |  | 80 | 93.8408 | 0.1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 65.7435 | 17.9229 | 426565.3746 | 35.5471 | 35.5471 | 97.2871 | 0.2 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 68.8655 | 21.0448 | 500866.9492 | 41.7389 | 41.7389 | 105.3689 | 0.3 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 71.9874 | 24.1667 | 575168.5238 | 47.9307 | 47.9307 | 113.4507 | 0.4 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 75.1093 | 27.2887 | 649470.0983 | 54.1225 | 54.1225 | 121.5325 | 0.5 | 77 | 22 | 831600 | 69.3 | 69.3 | 78.2312 | 30.4106 | 723771.6729 | 60.3143 | 60.3143 | 129.6143 | 0.6 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 81.3531 | 33.5325 | 798073.2475 | 66.5061 | 66.5061 | 137.6961 | 0.7 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 84.475 | 36.6544 | 872374.8221 | 72.6979 | 72.6979 | 145.7779 | 0.8 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 87.597 | 39.7763 | 946676.3967 | 78.8897 | 78.8897 | 153.8597 | 0.9 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 90.7189 | 42.8982 | 1020977.9713 | 85.0815 | 85.0815 | 161.9415 | 1 | 80 | 25 | 945000 | 78.75 | 78.75 | 93.8408 | 46.0201 | 1095279.5458 | 91.2733 | 91.2733 | 170.0233 | 80 | 60 | 33.9145 | 34 | 60.9
7/17/20XX 10:00:00 AM | 0.41667 | 2 | 82.1 | 57.2 | 82.2439 | 99.088 | 16.8441 | 50 | 82.1 |  | 82.1 | 94.3716 | 0.1 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 65.7966 | 17.976 | 427828.7517 | 35.6524 | 35.6524 | 98.0539 | 0.2 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 68.9716 | 21.151 | 503393.7034 | 41.9495 | 41.9495 | 106.9025 | 0.3 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 72.1466 | 24.326 | 578958.6551 | 48.2466 | 48.2466 | 115.7511 | 0.4 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 75.3216 | 27.501 | 654523.6068 | 54.5436 | 54.5436 | 124.5996 | 0.5 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 78.4966 | 30.676 | 730088.5585 | 60.8407 | 60.8407 | 133.4482 | 0.6 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 81.6716 | 33.851 | 805653.5103 | 67.1378 | 67.1378 | 142.2968 | 0.7 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 84.8466 | 37.026 | 881218.462 | 73.4349 | 73.4349 | 151.1454 | 0.8 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 88.0216 | 40.201 | 956783.4137 | 79.732 | 79.732 | 159.994 | 0.9 | 81.29 | 26.29 | 993762 | 82.8135 | 82.8135 | 91.1966 | 43.376 | 1032348.3654 | 86.029 | 86.029 | 168.8425 | 1 | 82.1 | 27.1 | 1024380 | 85.365 | 85.365 | 94.3716 | 46.551 | 1107913.3171 | 92.3261 | 92.3261 | 177.6911 | 80 | 55 | 34.5143 | 34 | 57.2
7/17/20XX 11:00:00 AM | 0.45833 | 2 | 84.9 | 51.8 | 90.1049 | 108.5867 | 18.4818 | 50 | 84.9 |  | 84.9 | 93.4316 | 0.1 | 75.09 | 20.09 | 759402 | 63.2835 | 63.2835 | 65.7026 | 17.882 | 425591.5411 | 35.466 | 35.466 | 98.7495 | 0.2 | 76.18 | 21.18 | 800604 | 66.717 | 66.717 | 68.7836 | 20.963 | 498919.2821 | 41.5766 | 41.5766 | 108.2936 | 0.3 | 77.27 | 22.27 | 841806 | 70.1505 | 70.1505 | 71.8646 | 24.044 | 572247.0232 | 47.6873 | 47.6873 | 117.8378 | 0.4 | 78.36 | 23.36 | 883008 | 73.584 | 73.584 | 74.9456 | 27.125 | 645574.7642 | 53.7979 | 53.7979 | 127.3819 | 0.5 | 79.45 | 24.45 | 924210 | 77.0175 | 77.0175 | 78.0266 | 30.206 | 718902.5053 | 59.9085 | 59.9085 | 136.926 | 0.6 | 80.54 | 25.54 | 965412 | 80.451 | 80.451 | 81.1076 | 33.287 | 792230.2463 | 66.0192 | 66.0192 | 146.4702 | 0.7 | 81.63 | 26.63 | 1006614 | 83.8845 | 83.8845 | 84.1886 | 36.368 | 865557.9874 | 72.1298 | 72.1298 | 156.0143 | 0.8 | 82.72 | 27.72 | 1047816 | 87.318 | 87.318 | 87.2696 | 39.449 | 938885.7284 | 78.2405 | 78.2405 | 165.5585 | 0.9 | 83.81 | 28.81 | 1089018 | 90.7515 | 90.7515 | 90.3506 | 42.53 | 1012213.4695 | 84.3511 | 84.3511 | 175.1026 | 1 | 84.9 | 29.9 | 1130220 | 94.185 | 94.185 | 93.4316 | 45.611 | 1085541.2105 | 90.4618 | 90.4618 | 184.6468 | 85 | 50 | 35.0554 | 36 | 51.8
7/17/20XX 12:00:00 PM | 0.5 | 2 | 85.6 | 50.9 | 92.1623 | 111.0733 | 18.911 | 50 | 85.6 |  | 85.6 | 93.8643 | 0.1 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 65.7459 | 17.9253 | 426621.2651 | 35.5518 | 35.5518 | 99.0558 | 0.2 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 68.8702 | 21.0495 | 500978.7302 | 41.7482 | 41.7482 | 108.9062 | 0.3 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 71.9944 | 24.1738 | 575336.1953 | 47.9447 | 47.9447 | 118.7567 | 0.4 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 75.1187 | 27.2981 | 649693.6604 | 54.1411 | 54.1411 | 128.6071 | 0.5 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 78.2429 | 30.4223 | 724051.1255 | 60.3376 | 60.3376 | 138.4576 | 0.6 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 81.3672 | 33.5466 | 798408.5906 | 66.534 | 66.534 | 148.308 | 0.7 | 82.12 | 27.12 | 1025136 | 85.428 | 85.428 | 84.4915 | 36.6708 | 872766.0557 | 72.7305 | 72.7305 | 158.1585 | 0.8 | 83.28 | 28.28 | 1068984 | 89.082 | 89.082 | 87.6157 | 39.7951 | 947123.5208 | 78.927 | 78.927 | 168.009 | 0.9 | 84.44 | 29.44 | 1112832 | 92.736 | 92.736 | 90.74 | 42.9194 | 1021480.9859 | 85.1234 | 85.1234 | 177.8594 | 1 | 85.6 | 30.6 | 1156680 | 96.39 | 96.39 | 93.8643 | 46.0436 | 1095838.451 | 91.3199 | 91.3199 | 187.7099 | 85 | 50 | 35.2955 | 36 | 50.9
7/17/20XX 1:00:00 PM | 0.54167 | 2 | 86.8 | 48.2 | 76.2304 | 95.7771 | 19.5467 | 40 | 86.8 |  | 86.8 | 92.2587 | 0.1 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 65.5853 | 17.7647 | 422800.007 | 35.2333 | 35.2333 | 99.1153 | 0.2 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 68.549 | 20.7284 | 493336.2139 | 41.1114 | 41.1114 | 109.0254 | 0.3 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 71.5128 | 23.6921 | 563872.4209 | 46.9894 | 46.9894 | 118.9354 | 0.4 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 74.4765 | 26.6558 | 634408.6279 | 52.8674 | 52.8674 | 128.8454 | 0.5 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 77.4402 | 29.6195 | 704944.8349 | 58.7454 | 58.7454 | 138.7554 | 0.6 | 81.68 | 26.68 | 1008504 | 84.042 | 84.042 | 80.4039 | 32.5832 | 775481.0418 | 64.6234 | 64.6234 | 148.6654 | 0.7 | 82.96 | 27.96 | 1056888 | 88.074 | 88.074 | 83.3676 | 35.5469 | 846017.2488 | 70.5014 | 70.5014 | 158.5754 | 0.8 | 84.24 | 29.24 | 1105272 | 92.106 | 92.106 | 86.3313 | 38.5106 | 916553.4558 | 76.3795 | 76.3795 | 168.4855 | 0.9 | 85.52 | 30.52 | 1153656 | 96.138 | 96.138 | 89.295 | 41.4744 | 987089.6627 | 82.2575 | 82.2575 | 178.3955 | 1 | 86.8 | 31.8 | 1202040 | 100.17 | 100.17 | 92.2587 | 44.4381 | 1057625.8697 | 88.1355 | 88.1355 | 188.3055 | 85 | 50 | 35.3382 | 36 | 48.2
7/17/20XX 2:00:00 PM | 0.58333 | 2 | 84.5 | 53.6 | 88.946 | 107.1861 | 18.2402 | 50 | 84.5 |  | 84.5 | 95.5124 | 0.1 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 65.9107 | 18.0901 | 430543.9242 | 35.8787 | 35.8787 | 99.0362 | 0.2 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 69.1998 | 21.3792 | 508824.0484 | 42.402 | 42.402 | 108.867 | 0.3 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 72.4889 | 24.6682 | 587104.1727 | 48.9253 | 48.9253 | 118.6978 | 0.4 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 75.778 | 27.9573 | 665384.2969 | 55.4487 | 55.4487 | 128.5287 | 0.5 | 79.25 | 24.25 | 916650 | 76.3875 | 76.3875 | 79.067 | 31.2464 | 743664.4211 | 61.972 | 61.972 | 138.3595 | 0.6 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 82.3561 | 34.5355 | 821944.5453 | 68.4954 | 68.4954 | 148.1904 | 0.7 | 81.35 | 26.35 | 996030 | 83.0025 | 83.0025 | 85.6452 | 37.8246 | 900224.6696 | 75.0187 | 75.0187 | 158.0212 | 0.8 | 82.4 | 27.4 | 1035720 | 86.31 | 86.31 | 88.9343 | 41.1136 | 978504.7938 | 81.5421 | 81.5421 | 167.8521 | 0.9 | 83.45 | 28.45 | 1075410 | 89.6175 | 89.6175 | 92.2234 | 44.4027 | 1056784.918 | 88.0654 | 88.0654 | 177.6829 | 1 | 84.5 | 29.5 | 1115100 | 92.925 | 92.925 | 95.5124 | 47.6918 | 1135065.0422 | 94.5888 | 94.5888 | 187.5138 | 85 | 55 | 35.2839 | 36 | 53.6
7/17/20XX 3:00:00 PM | 0.625 | 2 | 84.8 | 53 | 89.814 | 108.2352 | 18.4212 | 50 | 84.8 |  | 84.8 | 95.3404 | 0.1 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 65.8935 | 18.0729 | 430134.3859 | 35.8445 | 35.8445 | 99.0965 | 0.2 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 69.1654 | 21.3447 | 508004.9718 | 42.3337 | 42.3337 | 108.9877 | 0.3 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 72.4373 | 24.6166 | 585875.5578 | 48.823 | 48.823 | 118.879 | 0.4 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 75.7091 | 27.8885 | 663746.1437 | 55.3122 | 55.3122 | 128.7702 | 0.5 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 78.981 | 31.1604 | 741616.7296 | 61.8014 | 61.8014 | 138.6614 | 0.6 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 82.2529 | 34.4322 | 819487.3155 | 68.2906 | 68.2906 | 148.5526 | 0.7 | 81.56 | 26.56 | 1003968 | 83.664 | 83.664 | 85.5247 | 37.7041 | 897357.9014 | 74.7798 | 74.7798 | 158.4438 | 0.8 | 82.64 | 27.64 | 1044792 | 87.066 | 87.066 | 88.7966 | 40.976 | 975228.4873 | 81.269 | 81.269 | 168.335 | 0.9 | 83.72 | 28.72 | 1085616 | 90.468 | 90.468 | 92.0685 | 44.2479 | 1053099.0733 | 87.7583 | 87.7583 | 178.2263 | 1 | 84.8 | 29.8 | 1126440 | 93.87 | 93.87 | 95.3404 | 47.5197 | 1130969.6592 | 94.2475 | 94.2475 | 188.1175 | 85 | 55 | 35.3307 | 36 | 53
7/17/20XX 4:00:00 PM | 0.66667 | 2 | 83.4 | 55.7 | 85.8211 | 103.4101 | 17.5889 | 50 | 83.4 |  | 83.4 | 95.8468 | 0.1 | 74.94 | 19.94 | 753732 | 62.811 | 62.811 | 65.9442 | 18.1235 | 431339.7515 | 35.945 | 35.945 | 98.756 | 0.2 | 75.88 | 20.88 | 789264 | 65.772 | 65.772 | 69.2667 | 21.446 | 510415.703 | 42.5346 | 42.5346 | 108.3066 | 0.3 | 76.82 | 21.82 | 824796 | 68.733 | 68.733 | 72.5892 | 24.7686 | 589491.6544 | 49.1243 | 49.1243 | 117.8573 | 0.4 | 77.76 | 22.76 | 860328 | 71.694 | 71.694 | 75.9117 | 28.0911 | 668567.6059 | 55.714 | 55.714 | 127.408 | 0.5 | 78.7 | 23.7 | 895860 | 74.655 | 74.655 | 79.2342 | 31.4136 | 747643.5574 | 62.3036 | 62.3036 | 136.9586 | 0.6 | 79.64 | 24.64 | 931392 | 77.616 | 77.616 | 82.5567 | 34.7361 | 826719.5089 | 68.8933 | 68.8933 | 146.5093 | 0.7 | 80.58 | 25.58 | 966924 | 80.577 | 80.577 | 85.8793 | 38.0586 | 905795.4603 | 75.483 | 75.483 | 156.06 | 0.8 | 81.52 | 26.52 | 1002456 | 83.538 | 83.538 | 89.2018 | 41.3812 | 984871.4118 | 82.0726 | 82.0726 | 165.6106 | 0.9 | 82.46 | 27.46 | 1037988 | 86.499 | 86.499 | 92.5243 | 44.7037 | 1063947.3633 | 88.6623 | 88.6623 | 175.1613 | 1 | 83.4 | 28.4 | 1073520 | 89.46 | 89.46 | 95.8468 | 48.0262 | 1143023.3148 | 95.2519 | 95.2519 | 184.7119 | 85 | 55 | 35.0657 | 36 | 55.7
7/17/20XX 5:00:00 PM | 0.70833 | 2 | 82.5 | 56 | 83.3313 | 100.4018 | 17.0705 | 50 | 82.5 |  | 82.5 | 93.5736 | 0.1 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 65.7168 | 17.8962 | 425929.5195 | 35.4941 | 35.4941 | 98.0216 | 0.2 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 68.812 | 20.9914 | 499595.2389 | 41.6329 | 41.6329 | 106.8379 | 0.3 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 71.9072 | 24.0866 | 573260.9584 | 47.7717 | 47.7717 | 115.6542 | 0.4 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 75.0024 | 27.1818 | 646926.6778 | 53.9106 | 53.9106 | 124.4706 | 0.5 | 78.25 | 23.25 | 878850 | 73.2375 | 73.2375 | 78.0976 | 30.277 | 720592.3973 | 60.0494 | 60.0494 | 133.2869 | 0.6 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 81.1928 | 33.3722 | 794258.1167 | 66.1882 | 66.1882 | 142.1032 | 0.7 | 79.95 | 24.95 | 943110 | 78.5925 | 78.5925 | 84.288 | 36.4674 | 867923.8362 | 72.327 | 72.327 | 150.9195 | 0.8 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 87.3832 | 39.5626 | 941589.5556 | 78.4658 | 78.4658 | 159.7358 | 0.9 | 81.65 | 26.65 | 1007370 | 83.9475 | 83.9475 | 90.4784 | 42.6578 | 1015255.2751 | 84.6046 | 84.6046 | 168.5521 | 1 | 82.5 | 27.5 | 1039500 | 86.625 | 86.625 | 93.5736 | 45.753 | 1088920.9945 | 90.7434 | 90.7434 | 177.3684 | 80 | 55 | 34.4874 | 34 | 56
7/17/20XX 6:00:00 PM | 0.75 | 2 | 82 | 57.6 | 81.9738 | 98.7617 | 16.7879 | 50 | 82 |  | 82 | 94.7326 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 65.8327 | 18.0121 | 428687.9412 | 35.724 | 35.724 | 98.094 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 69.0438 | 21.2232 | 505112.0823 | 42.0927 | 42.0927 | 106.9827 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 72.2549 | 24.4343 | 581536.2235 | 48.4614 | 48.4614 | 115.8714 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 75.466 | 27.6454 | 657960.3646 | 54.83 | 54.83 | 124.76 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 78.6771 | 30.8565 | 734384.5058 | 61.1987 | 61.1987 | 133.6487 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 81.8882 | 34.0676 | 810808.647 | 67.5674 | 67.5674 | 142.5374 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 85.0993 | 37.2787 | 887232.7881 | 73.9361 | 73.9361 | 151.4261 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 88.3104 | 40.4898 | 963656.9293 | 80.3047 | 80.3047 | 160.3147 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 91.5215 | 43.7009 | 1040081.0704 | 86.6734 | 86.6734 | 169.2034 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 94.7326 | 46.912 | 1116505.2116 | 93.0421 | 93.0421 | 178.0921 | 80 | 60 | 34.5463 | 34 | 57.6
7/17/20XX 7:00:00 PM | 0.79167 | 2 | 81.1 | 58.8 | 79.5759 | 95.865 | 16.2891 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/17/20XX 8:00:00 PM | 0.83333 | 2 | 80.1 | 60.1 | 92.7289 | 108.5693 | 15.8405 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/17/20XX 9:00:00 PM | 0.875 | 2 | 79.1 | 64 | 89.6782 | 104.9873 | 15.3091 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/17/20XX 10:00:00 PM | 0.91667 | 2 | 78.6 | 66 | 88.1844 | 103.2334 | 15.049 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/17/20XX 11:00:00 PM | 0.95833 | 2 | 77.8 | 67.9 | 85.8376 | 100.478 | 14.6404 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/17/20XX 12:00:00 AM | 0 | 3 | 77.5 | 68.3 | 84.9711 | 99.4607 | 14.4896 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/18/20XX 1:00:00 AM | 0.041667 | 3 | 76.9 | 70.4 | 97.452 | 111.7526 | 14.3007 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/18/20XX 2:00:00 AM | 0.083333 | 3 | 76.4 | 71.4 | 95.8042 | 109.8565 | 14.0523 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/18/20XX 3:00:00 AM | 0.125 | 3 | 75.1 | 72.4 | 91.6296 | 105.0536 | 13.424 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/18/20XX 4:00:00 AM | 0.16667 | 3 | 74.8 | 72.4 | 90.6884 | 103.9709 | 13.2825 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/18/20XX 5:00:00 AM | 0.20833 | 3 | 74.7 | 73.3 | 90.3765 | 103.6122 | 13.2356 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/18/20XX 6:00:00 AM | 0.25 | 3 | 74.7 | 74.2 | 90.3765 | 103.6122 | 13.2356 | 70 | 74.7 |  | 74.7 | 95.9355 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 65.953 | 18.1324 | 431550.7459 | 35.9626 | 35.9626 | 96.0331 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 69.2844 | 21.4638 | 510837.6919 | 42.5698 | 42.5698 | 102.8608 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 72.6158 | 24.7952 | 590124.6378 | 49.1771 | 49.1771 | 109.6886 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 75.9472 | 28.1265 | 669411.5838 | 55.7843 | 55.7843 | 116.5163 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 79.2786 | 31.4579 | 748698.5297 | 62.3915 | 62.3915 | 123.344 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 82.6099 | 34.7893 | 827985.4757 | 68.9988 | 68.9988 | 130.1718 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 85.9413 | 38.1207 | 907272.4216 | 75.606 | 75.606 | 136.9995 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 89.2727 | 41.4521 | 986559.3676 | 82.2133 | 82.2133 | 143.8273 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 92.6041 | 44.7835 | 1065846.3135 | 88.8205 | 88.8205 | 150.655 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 95.9355 | 48.1148 | 1145133.2595 | 95.4278 | 95.4278 | 157.4828 | 75 | 75 | 32.9386 | 32 | 74.2
7/18/20XX 7:00:00 AM | 0.29167 | 3 | 76.1 | 71.2 | 94.8268 | 108.7319 | 13.9051 | 70 | 76.1 |  | 76.1 | 96.4954 | 0.1 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 66.009 | 18.1884 | 432883.4272 | 36.0736 | 36.0736 | 96.5851 | 0.2 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 69.3964 | 21.5758 | 513503.0543 | 42.7919 | 42.7919 | 103.9649 | 0.3 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 72.7838 | 24.9631 | 594122.6815 | 49.5102 | 49.5102 | 111.3447 | 0.4 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 76.1711 | 28.3505 | 674742.3087 | 56.2285 | 56.2285 | 118.7245 | 0.5 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 79.5585 | 31.7379 | 755361.9358 | 62.9468 | 62.9468 | 126.1043 | 0.6 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 82.9459 | 35.1253 | 835981.563 | 69.6651 | 69.6651 | 133.4841 | 0.7 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 86.3333 | 38.5127 | 916601.1902 | 76.3834 | 76.3834 | 140.8639 | 0.8 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 89.7207 | 41.9 | 997220.8173 | 83.1017 | 83.1017 | 148.2437 | 0.9 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 93.108 | 45.2874 | 1077840.4445 | 89.82 | 89.82 | 155.6235 | 1 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 96.4954 | 48.6748 | 1158460.0716 | 96.5383 | 96.5383 | 163.0033 | 75 | 70 | 33.3708 | 34 | 71.2
7/18/20XX 8:00:00 AM | 0.33333 | 3 | 77.3 | 69.4 | 84.3976 | 98.7873 | 14.3897 | 60 | 77.3 |  | 77.3 | 97.9239 | 0.1 | 74.33 | 19.33 | 730674 | 60.8895 | 60.8895 | 66.1519 | 18.3312 | 436283.2153 | 36.3569 | 36.3569 | 97.2464 | 0.2 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 69.6821 | 21.8615 | 520302.6307 | 43.3586 | 43.3586 | 105.2876 | 0.3 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 73.2123 | 25.3917 | 604322.046 | 50.3602 | 50.3602 | 113.3287 | 0.4 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 76.7425 | 28.9219 | 688341.4614 | 57.3618 | 57.3618 | 121.3698 | 0.5 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 80.2728 | 32.4521 | 772360.8767 | 64.3634 | 64.3634 | 129.4109 | 0.6 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 83.803 | 35.9824 | 856380.2921 | 71.365 | 71.365 | 137.452 | 0.7 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 87.3332 | 39.5126 | 940399.7074 | 78.3666 | 78.3666 | 145.4931 | 0.8 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 90.8635 | 43.0428 | 1024419.1228 | 85.3683 | 85.3683 | 153.5343 | 0.9 | 76.97 | 21.97 | 830466 | 69.2055 | 69.2055 | 94.3937 | 46.573 | 1108438.5381 | 92.3699 | 92.3699 | 161.5754 | 1 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 97.9239 | 50.1033 | 1192457.9535 | 99.3715 | 99.3715 | 169.6165 | 75 | 70 | 33.8899 | 34 | 69.4
7/18/20XX 9:00:00 AM | 0.375 | 3 | 79.5 | 64.2 | 90.8883 | 106.4082 | 15.5199 | 60 | 79.5 |  | 79.5 | 97.4066 | 0.1 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 66.1001 | 18.2795 | 435052.1139 | 36.2543 | 36.2543 | 97.8368 | 0.2 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 69.5786 | 21.758 | 517840.4277 | 43.1534 | 43.1534 | 106.4684 | 0.3 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 73.0571 | 25.2365 | 600628.7416 | 50.0524 | 50.0524 | 115.0999 | 0.4 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 76.5356 | 28.715 | 683417.0555 | 56.9514 | 56.9514 | 123.7314 | 0.5 | 76.75 | 21.75 | 822150 | 68.5125 | 68.5125 | 80.0141 | 32.1935 | 766205.3694 | 63.8504 | 63.8504 | 132.3629 | 0.6 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 83.4926 | 35.672 | 848993.6832 | 70.7495 | 70.7495 | 140.9945 | 0.7 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 86.9711 | 39.1505 | 931781.9971 | 77.6485 | 77.6485 | 149.626 | 0.8 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 90.4496 | 42.629 | 1014570.311 | 84.5475 | 84.5475 | 158.2575 | 0.9 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 93.9281 | 46.1075 | 1097358.6248 | 91.4466 | 91.4466 | 166.8891 | 1 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 97.4066 | 49.586 | 1180146.9387 | 98.3456 | 98.3456 | 175.5206 | 80 | 65 | 34.3505 | 34 | 64.2
7/18/20XX 10:00:00 AM | 0.41667 | 3 | 82.5 | 58 | 83.3313 | 100.4018 | 17.0705 | 50 | 82.5 |  | 82.5 | 96.9877 | 0.1 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 66.0582 | 18.2376 | 434055.0555 | 36.1713 | 36.1713 | 98.6988 | 0.2 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 69.4948 | 21.6742 | 515846.3109 | 42.9872 | 42.9872 | 108.1922 | 0.3 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 72.9315 | 25.1108 | 597637.5664 | 49.8031 | 49.8031 | 117.6856 | 0.4 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 76.3681 | 28.5474 | 679428.8219 | 56.6191 | 56.6191 | 127.1791 | 0.5 | 78.25 | 23.25 | 878850 | 73.2375 | 73.2375 | 79.8047 | 31.984 | 761220.0773 | 63.435 | 63.435 | 136.6725 | 0.6 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 83.2413 | 35.4206 | 843011.3328 | 70.2509 | 70.2509 | 146.1659 | 0.7 | 79.95 | 24.95 | 943110 | 78.5925 | 78.5925 | 86.6779 | 38.8573 | 924802.5883 | 77.0669 | 77.0669 | 155.6594 | 0.8 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 90.1145 | 42.2939 | 1006593.8437 | 83.8828 | 83.8828 | 165.1528 | 0.9 | 81.65 | 26.65 | 1007370 | 83.9475 | 83.9475 | 93.5511 | 45.7305 | 1088385.0992 | 90.6988 | 90.6988 | 174.6463 | 1 | 82.5 | 27.5 | 1039500 | 86.625 | 86.625 | 96.9877 | 49.1671 | 1170176.3547 | 97.5147 | 97.5147 | 184.1397 | 80 | 60 | 35.0233 | 36 | 58
7/18/20XX 11:00:00 AM | 0.45833 | 3 | 85.9 | 52 | 93.0555 | 112.1529 | 19.0974 | 50 | 85.9 |  | 85.9 | 96.875 | 0.1 | 75.19 | 20.19 | 763182 | 63.5985 | 63.5985 | 66.047 | 18.2263 | 433786.8198 | 36.1489 | 36.1489 | 99.7474 | 0.2 | 76.38 | 21.38 | 808164 | 67.347 | 67.347 | 69.4723 | 21.6517 | 515309.8396 | 42.9425 | 42.9425 | 110.2895 | 0.3 | 77.57 | 22.57 | 853146 | 71.0955 | 71.0955 | 72.8976 | 25.077 | 596832.8594 | 49.7361 | 49.7361 | 120.8316 | 0.4 | 78.76 | 23.76 | 898128 | 74.844 | 74.844 | 76.323 | 28.5023 | 678355.8792 | 56.5297 | 56.5297 | 131.3737 | 0.5 | 79.95 | 24.95 | 943110 | 78.5925 | 78.5925 | 79.7483 | 31.9277 | 759878.899 | 63.3232 | 63.3232 | 141.9157 | 0.6 | 81.14 | 26.14 | 988092 | 82.341 | 82.341 | 83.1737 | 35.353 | 841401.9188 | 70.1168 | 70.1168 | 152.4578 | 0.7 | 82.33 | 27.33 | 1033074 | 86.0895 | 86.0895 | 86.599 | 38.7784 | 922924.9387 | 76.9104 | 76.9104 | 162.9999 | 0.8 | 83.52 | 28.52 | 1078056 | 89.838 | 89.838 | 90.0243 | 42.2037 | 1004447.9585 | 83.704 | 83.704 | 173.542 | 0.9 | 84.71 | 29.71 | 1123038 | 93.5865 | 93.5865 | 93.4497 | 45.629 | 1085970.9783 | 90.4976 | 90.4976 | 184.0841 | 1 | 85.9 | 30.9 | 1168020 | 97.335 | 97.335 | 96.875 | 49.0544 | 1167493.9981 | 97.2912 | 97.2912 | 194.6262 | 85 | 50 | 35.8425 | 36 | 52
7/18/20XX 12:00:00 PM | 0.5 | 3 | 87.4 | 46.9 | 77.6933 | 97.6266 | 19.9333 | 40 | 87.4 |  | 87.4 | 91.4473 | 0.1 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 65.5042 | 17.6836 | 420868.9453 | 35.0724 | 35.0724 | 99.1434 | 0.2 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 68.3868 | 20.5661 | 489474.0907 | 40.7895 | 40.7895 | 109.0815 | 0.3 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 71.2693 | 23.4487 | 558079.236 | 46.5066 | 46.5066 | 119.0196 | 0.4 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 74.1519 | 26.3313 | 626684.3813 | 52.2237 | 52.2237 | 128.9577 | 0.5 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 77.0345 | 29.2138 | 695289.5267 | 57.9408 | 57.9408 | 138.8958 | 0.6 | 82.04 | 27.04 | 1022112 | 85.176 | 85.176 | 79.917 | 32.0964 | 763894.672 | 63.6579 | 63.6579 | 148.8339 | 0.7 | 83.38 | 28.38 | 1072764 | 89.397 | 89.397 | 82.7996 | 34.979 | 832499.8173 | 69.375 | 69.375 | 158.772 | 0.8 | 84.72 | 29.72 | 1123416 | 93.618 | 93.618 | 85.6822 | 37.8616 | 901104.9626 | 75.0921 | 75.0921 | 168.7101 | 0.9 | 86.06 | 31.06 | 1174068 | 97.839 | 97.839 | 88.5648 | 40.7441 | 969710.108 | 80.8092 | 80.8092 | 178.6482 | 1 | 87.4 | 32.4 | 1224720 | 102.06 | 102.06 | 91.4473 | 43.6267 | 1038315.2533 | 86.5263 | 86.5263 | 188.5863 | 85 | 45 | 35.3581 | 36 | 46.9
7/18/20XX 1:00:00 PM | 0.54167 | 3 | 88.1 | 44.1 | 79.4283 | 99.8204 | 20.3922 | 40 | 88.1 |  | 88.1 | 87.789 | 0.1 | 75.41 | 20.41 | 771498 | 64.2915 | 64.2915 | 65.1384 | 17.3177 | 412162.2429 | 34.3469 | 34.3469 | 98.6384 | 0.2 | 76.82 | 21.82 | 824796 | 68.733 | 68.733 | 67.6551 | 19.8345 | 472060.6858 | 39.3384 | 39.3384 | 108.0714 | 0.3 | 78.23 | 23.23 | 878094 | 73.1745 | 73.1745 | 70.1719 | 22.3512 | 531959.1286 | 44.3299 | 44.3299 | 117.5044 | 0.4 | 79.64 | 24.64 | 931392 | 77.616 | 77.616 | 72.6886 | 24.868 | 591857.5715 | 49.3215 | 49.3215 | 126.9375 | 0.5 | 81.05 | 26.05 | 984690 | 82.0575 | 82.0575 | 75.2053 | 27.3847 | 651756.0144 | 54.313 | 54.313 | 136.3705 | 0.6 | 82.46 | 27.46 | 1037988 | 86.499 | 86.499 | 77.7221 | 29.9014 | 711654.4573 | 59.3045 | 59.3045 | 145.8035 | 0.7 | 83.87 | 28.87 | 1091286 | 90.9405 | 90.9405 | 80.2388 | 32.4182 | 771552.9002 | 64.2961 | 64.2961 | 155.2366 | 0.8 | 85.28 | 30.28 | 1144584 | 95.382 | 95.382 | 82.7556 | 34.9349 | 831451.343 | 69.2876 | 69.2876 | 164.6696 | 0.9 | 86.69 | 31.69 | 1197882 | 99.8235 | 99.8235 | 85.2723 | 37.4517 | 891349.7859 | 74.2791 | 74.2791 | 174.1026 | 1 | 88.1 | 33.1 | 1251180 | 104.265 | 104.265 | 87.789 | 39.9684 | 951248.2288 | 79.2707 | 79.2707 | 183.5357 | 90 | 45 | 34.9547 | 34 | 44.1
7/18/20XX 2:00:00 PM | 0.58333 | 3 | 87.8 | 46.8 | 78.681 | 98.8755 | 20.1945 | 40 | 87.8 |  | 87.8 | 92.4132 | 0.1 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 65.6008 | 17.7802 | 423167.8147 | 35.264 | 35.264 | 99.461 | 0.2 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 68.58 | 20.7593 | 494071.8294 | 41.1727 | 41.1727 | 109.7167 | 0.3 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 71.5591 | 23.7385 | 564975.844 | 47.0813 | 47.0813 | 119.9723 | 0.4 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 74.5383 | 26.7176 | 635879.8587 | 52.99 | 52.99 | 130.228 | 0.5 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 77.5174 | 29.6968 | 706783.8734 | 58.8987 | 58.8987 | 140.4837 | 0.6 | 82.28 | 27.28 | 1031184 | 85.932 | 85.932 | 80.4966 | 32.676 | 777687.8881 | 64.8073 | 64.8073 | 150.7393 | 0.7 | 83.66 | 28.66 | 1083348 | 90.279 | 90.279 | 83.4758 | 35.6551 | 848591.9028 | 70.716 | 70.716 | 160.995 | 0.8 | 85.04 | 30.04 | 1135512 | 94.626 | 94.626 | 86.4549 | 38.6343 | 919495.9174 | 76.6247 | 76.6247 | 171.2507 | 0.9 | 86.42 | 31.42 | 1187676 | 98.973 | 98.973 | 89.4341 | 41.6134 | 990399.9321 | 82.5333 | 82.5333 | 181.5063 | 1 | 87.8 | 32.8 | 1239840 | 103.32 | 103.32 | 92.4132 | 44.5926 | 1061303.9468 | 88.442 | 88.442 | 191.762 | 90 | 45 | 35.6084 | 36 | 46.8
7/18/20XX 3:00:00 PM | 0.625 | 3 | 85.6 | 51.1 | 92.1623 | 111.0733 | 18.911 | 50 | 85.6 |  | 85.6 | 94.2425 | 0.1 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 65.7837 | 17.9631 | 427521.4285 | 35.6268 | 35.6268 | 99.1308 | 0.2 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 68.9458 | 21.1252 | 502779.0569 | 41.8983 | 41.8983 | 109.0563 | 0.3 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 72.1079 | 24.2873 | 578036.6854 | 48.1697 | 48.1697 | 118.9817 | 0.4 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 75.27 | 27.4493 | 653294.3139 | 54.4412 | 54.4412 | 128.9072 | 0.5 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 78.4321 | 30.6114 | 728551.9424 | 60.7127 | 60.7127 | 138.8327 | 0.6 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 81.5941 | 33.7735 | 803809.5708 | 66.9841 | 66.9841 | 148.7581 | 0.7 | 82.12 | 27.12 | 1025136 | 85.428 | 85.428 | 84.7562 | 36.9356 | 879067.1993 | 73.2556 | 73.2556 | 158.6836 | 0.8 | 83.28 | 28.28 | 1068984 | 89.082 | 89.082 | 87.9183 | 40.0977 | 954324.8278 | 79.5271 | 79.5271 | 168.6091 | 0.9 | 84.44 | 29.44 | 1112832 | 92.736 | 92.736 | 91.0804 | 43.2598 | 1029582.4562 | 85.7985 | 85.7985 | 178.5345 | 1 | 85.6 | 30.6 | 1156680 | 96.39 | 96.39 | 94.2425 | 46.4219 | 1104840.0847 | 92.07 | 92.07 | 188.46 | 85 | 50 | 35.355 | 36 | 51.1
7/18/20XX 4:00:00 PM | 0.66667 | 3 | 83.9 | 55 | 87.2303 | 105.1128 | 17.8825 | 50 | 83.9 |  | 83.9 | 96.1716 | 0.1 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 65.9766 | 18.156 | 432112.6078 | 36.0094 | 36.0094 | 98.9779 | 0.2 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 69.3316 | 21.511 | 511961.4156 | 42.6635 | 42.6635 | 108.7505 | 0.3 | 76.97 | 21.97 | 830466 | 69.2055 | 69.2055 | 72.6866 | 24.866 | 591810.2234 | 49.3175 | 49.3175 | 118.523 | 0.4 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 76.0416 | 28.221 | 671659.0312 | 55.9716 | 55.9716 | 128.2956 | 0.5 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 79.3966 | 31.576 | 751507.8389 | 62.6257 | 62.6257 | 138.0682 | 0.6 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 82.7516 | 34.931 | 831356.6467 | 69.2797 | 69.2797 | 147.8407 | 0.7 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 86.1066 | 38.2859 | 911205.4545 | 75.9338 | 75.9338 | 157.6133 | 0.8 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 89.4616 | 41.6409 | 991054.2623 | 82.5879 | 82.5879 | 167.3859 | 0.9 | 82.91 | 27.91 | 1054998 | 87.9165 | 87.9165 | 92.8166 | 44.9959 | 1070903.0701 | 89.2419 | 89.2419 | 177.1584 | 1 | 83.9 | 28.9 | 1092420 | 91.035 | 91.035 | 96.1716 | 48.3509 | 1150751.8779 | 95.896 | 95.896 | 186.931 | 85 | 55 | 35.2397 | 36 | 55
7/18/20XX 5:00:00 PM | 0.70833 | 3 | 82.7 | 56.1 | 83.8795 | 101.064 | 17.1846 | 50 | 82.7 |  | 82.7 | 94.3621 | 0.1 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 65.7957 | 17.975 | 427806.0186 | 35.6505 | 35.6505 | 98.241 | 0.2 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 68.9697 | 21.1491 | 503348.2372 | 41.9457 | 41.9457 | 107.2767 | 0.3 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 72.1438 | 24.3231 | 578890.4559 | 48.2409 | 48.2409 | 116.3124 | 0.4 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 75.3178 | 27.4972 | 654432.6745 | 54.5361 | 54.5361 | 125.3481 | 0.5 | 78.35 | 23.35 | 882630 | 73.5525 | 73.5525 | 78.4918 | 30.6712 | 729974.8931 | 60.8312 | 60.8312 | 134.3837 | 0.6 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 81.6659 | 33.8453 | 805517.1117 | 67.1264 | 67.1264 | 143.4194 | 0.7 | 80.09 | 25.09 | 948402 | 79.0335 | 79.0335 | 84.8399 | 37.0193 | 881059.3303 | 73.4216 | 73.4216 | 152.4551 | 0.8 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 88.014 | 40.1933 | 956601.5489 | 79.7168 | 79.7168 | 161.4908 | 0.9 | 81.83 | 26.83 | 1014174 | 84.5145 | 84.5145 | 91.188 | 43.3674 | 1032143.7676 | 86.012 | 86.012 | 170.5265 | 1 | 82.7 | 27.7 | 1047060 | 87.255 | 87.255 | 94.3621 | 46.5414 | 1107685.9862 | 92.3072 | 92.3072 | 179.5622 | 85 | 55 | 34.6604 | 34 | 56.1
7/18/20XX 6:00:00 PM | 0.75 | 3 | 82.2 | 56.8 | 82.5146 | 99.4151 | 16.9005 | 50 | 82.2 |  | 82.2 | 94.0069 | 0.1 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 65.7602 | 17.9395 | 426960.8454 | 35.5801 | 35.5801 | 98.0131 | 0.2 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 68.8987 | 21.0781 | 501657.8908 | 41.8048 | 41.8048 | 106.8208 | 0.3 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 72.0372 | 24.2166 | 576354.9362 | 48.0296 | 48.0296 | 115.6286 | 0.4 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 75.1758 | 27.3551 | 651051.9816 | 54.2543 | 54.2543 | 124.4363 | 0.5 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 78.3143 | 30.4937 | 725749.0271 | 60.4791 | 60.4791 | 133.2441 | 0.6 | 78.92 | 23.92 | 904176 | 75.348 | 75.348 | 81.4528 | 33.6322 | 800446.0725 | 66.7038 | 66.7038 | 142.0518 | 0.7 | 79.74 | 24.74 | 935172 | 77.931 | 77.931 | 84.5914 | 36.7707 | 875143.1179 | 72.9286 | 72.9286 | 150.8596 | 0.8 | 80.56 | 25.56 | 966168 | 80.514 | 80.514 | 87.7299 | 39.9093 | 949840.1633 | 79.1533 | 79.1533 | 159.6673 | 0.9 | 81.38 | 26.38 | 997164 | 83.097 | 83.097 | 90.8684 | 43.0478 | 1024537.2087 | 85.3781 | 85.3781 | 168.4751 | 1 | 82.2 | 27.2 | 1028160 | 85.68 | 85.68 | 94.0069 | 46.1863 | 1099234.2541 | 91.6029 | 91.6029 | 177.2829 | 80 | 55 | 34.4816 | 34 | 56.8
7/18/20XX 7:00:00 PM | 0.79167 | 3 | 81.1 | 58.1 | 79.5759 | 95.865 | 16.2891 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/18/20XX 8:00:00 PM | 0.83333 | 3 | 79.8 | 60.2 | 91.8048 | 107.4842 | 15.6795 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/18/20XX 9:00:00 PM | 0.875 | 3 | 79.1 | 64 | 89.6782 | 104.9873 | 15.3091 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/18/20XX 10:00:00 PM | 0.91667 | 3 | 77.8 | 67 | 85.8376 | 100.478 | 14.6404 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/18/20XX 11:00:00 PM | 0.95833 | 3 | 77.1 | 68 | 83.8273 | 98.1177 | 14.2905 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/18/20XX 12:00:00 AM | 0 | 4 | 76.2 | 69.1 | 81.3009 | 95.1517 | 13.8508 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/19/20XX 1:00:00 AM | 0.041667 | 4 | 76.1 | 68.2 | 81.0242 | 94.8268 | 13.8027 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/19/20XX 2:00:00 AM | 0.083333 | 4 | 75.3 | 69.9 | 78.8391 | 92.2616 | 13.4225 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/19/20XX 3:00:00 AM | 0.125 | 4 | 74.7 | 71.8 | 90.3765 | 103.6122 | 13.2356 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/19/20XX 4:00:00 AM | 0.16667 | 4 | 74.4 | 68 | 76.4409 | 89.4463 | 13.0054 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/19/20XX 5:00:00 AM | 0.20833 | 4 | 74 | 67.9 | 75.3952 | 88.2187 | 12.8236 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/19/20XX 6:00:00 AM | 0.25 | 4 | 74.1 | 67.5 | 75.6554 | 88.5243 | 12.8688 | 60 | 74.1 |  | 74.1 | 85.3071 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 64.8902 | 17.0695 | 406255.1116 | 33.8546 | 33.8546 | 93.7361 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 67.1587 | 19.3381 | 460246.4232 | 38.3539 | 38.3539 | 98.2669 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 69.4273 | 21.6066 | 514237.7348 | 42.8531 | 42.8531 | 102.7976 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 71.6958 | 23.8752 | 568229.0464 | 47.3524 | 47.3524 | 107.3284 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 73.9643 | 26.1437 | 622220.358 | 51.8517 | 51.8517 | 111.8592 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 76.2329 | 28.4123 | 676211.6697 | 56.351 | 56.351 | 116.39 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 78.5014 | 30.6808 | 730202.9813 | 60.8502 | 60.8502 | 120.9207 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 80.77 | 32.9493 | 784194.2929 | 65.3495 | 65.3495 | 125.4515 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 83.0385 | 35.2179 | 838185.6045 | 69.8488 | 69.8488 | 129.9823 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 85.3071 | 37.4864 | 892176.9161 | 74.3481 | 74.3481 | 134.5131 | 75 | 65 | 31.1284 | 32 | 67.5
7/19/20XX 7:00:00 AM | 0.29167 | 4 | 75.5 | 64.5 | 79.3806 | 92.8973 | 13.5167 | 60 | 75.5 |  | 75.5 | 85.4631 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 64.9058 | 17.0852 | 406626.5888 | 33.8855 | 33.8855 | 94.208 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 67.1899 | 19.3693 | 460989.3776 | 38.4158 | 38.4158 | 99.2108 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 69.4741 | 21.6535 | 515352.1663 | 42.946 | 42.946 | 104.2135 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 71.7582 | 23.9376 | 569714.9551 | 47.4762 | 47.4762 | 109.2162 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 74.0424 | 26.2218 | 624077.7439 | 52.0065 | 52.0065 | 114.219 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 76.3265 | 28.5059 | 678440.5327 | 56.5367 | 56.5367 | 119.2217 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 78.6107 | 30.7901 | 732803.3214 | 61.0669 | 61.0669 | 124.2244 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 80.8948 | 33.0742 | 787166.1102 | 65.5972 | 65.5972 | 129.2272 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 83.179 | 35.3584 | 841528.899 | 70.1274 | 70.1274 | 134.2299 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 85.4631 | 37.6425 | 895891.6878 | 74.6576 | 74.6576 | 139.2326 | 75 | 65 | 31.4964 | 32 | 64.5
7/19/20XX 8:00:00 AM | 0.33333 | 4 | 75.9 | 66.2 | 80.4731 | 94.1799 | 13.7068 | 60 | 75.9 |  | 75.9 | 88.9713 | 0.1 | 74.19 | 19.19 | 725382 | 60.4485 | 60.4485 | 65.2566 | 17.436 | 414976.1244 | 34.5813 | 34.5813 | 95.0298 | 0.2 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 67.8916 | 20.0709 | 477688.4488 | 39.8074 | 39.8074 | 100.8544 | 0.3 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 70.5265 | 22.7059 | 540400.7732 | 45.0334 | 45.0334 | 106.6789 | 0.4 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 73.1615 | 25.3409 | 603113.0976 | 50.2594 | 50.2594 | 112.5034 | 0.5 | 74.95 | 19.95 | 754110 | 62.8425 | 62.8425 | 75.7965 | 27.9759 | 665825.422 | 55.4855 | 55.4855 | 118.328 | 0.6 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 78.4315 | 30.6108 | 728537.7465 | 60.7115 | 60.7115 | 124.1525 | 0.7 | 75.33 | 20.33 | 768474 | 64.0395 | 64.0395 | 81.0664 | 33.2458 | 791250.0709 | 65.9375 | 65.9375 | 129.977 | 0.8 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 83.7014 | 35.8808 | 853962.3953 | 71.1635 | 71.1635 | 135.8015 | 0.9 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 86.3364 | 38.5157 | 916674.7197 | 76.3896 | 76.3896 | 141.6261 | 1 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 88.9713 | 41.1507 | 979387.0441 | 81.6156 | 81.6156 | 147.4506 | 75 | 65 | 32.1438 | 32 | 66.2
7/19/20XX 9:00:00 AM | 0.375 | 4 | 77.7 | 63.1 | 85.548 | 100.1379 | 14.59 | 60 | 77.7 |  | 77.7 | 90.0708 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 65.3666 | 17.5459 | 417592.934 | 34.7994 | 34.7994 | 95.8149 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 68.1115 | 20.2908 | 482922.0679 | 40.2435 | 40.2435 | 102.4245 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 70.8564 | 23.0358 | 548251.2019 | 45.6876 | 45.6876 | 109.0341 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 73.6013 | 25.7807 | 613580.3358 | 51.1317 | 51.1317 | 115.6437 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 76.3462 | 28.5256 | 678909.4698 | 56.5758 | 56.5758 | 122.2533 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 79.0912 | 31.2705 | 744238.6037 | 62.0199 | 62.0199 | 128.8629 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 81.8361 | 34.0155 | 809567.7377 | 67.464 | 67.464 | 135.4725 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 84.581 | 36.7604 | 874896.8716 | 72.9081 | 72.9081 | 142.0821 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 87.3259 | 39.5053 | 940226.0056 | 78.3522 | 78.3522 | 148.6917 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 90.0708 | 42.2502 | 1005555.1395 | 83.7963 | 83.7963 | 155.3013 | 80 | 65 | 32.7582 | 32 | 63.1
7/19/20XX 10:00:00 AM | 0.41667 | 4 | 79.7 | 57.2 | 75.9607 | 91.4984 | 15.5378 | 50 | 79.7 |  | 79.7 | 87.1479 | 0.1 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 65.0743 | 17.2536 | 410636.2074 | 34.2197 | 34.2197 | 95.8652 | 0.2 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 67.5269 | 19.7062 | 469008.6147 | 39.0841 | 39.0841 | 102.5251 | 0.3 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 69.9795 | 22.1589 | 527381.0221 | 43.9484 | 43.9484 | 109.1849 | 0.4 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 72.4321 | 24.6115 | 585753.4294 | 48.8128 | 48.8128 | 115.8448 | 0.5 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 74.8847 | 27.0641 | 644125.8368 | 53.6772 | 53.6772 | 122.5047 | 0.6 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 77.3374 | 29.5167 | 702498.2442 | 58.5415 | 58.5415 | 129.1645 | 0.7 | 77.99 | 22.99 | 869022 | 72.4185 | 72.4185 | 79.79 | 31.9694 | 760870.6515 | 63.4059 | 63.4059 | 135.8244 | 0.8 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 82.2426 | 34.422 | 819243.0589 | 68.2703 | 68.2703 | 142.4843 | 0.9 | 79.13 | 24.13 | 912114 | 76.0095 | 76.0095 | 84.6952 | 36.8746 | 877615.4663 | 73.1346 | 73.1346 | 149.1441 | 1 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 87.1479 | 39.3272 | 935987.8736 | 77.999 | 77.999 | 155.804 | 80 | 55 | 32.7913 | 32 | 57.2
7/19/20XX 11:00:00 AM | 0.45833 | 4 | 82.4 | 51.1 | 83.0584 | 100.072 | 17.0136 | 50 | 82.4 |  | 82.4 | 84.9299 | 0.1 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 64.8525 | 17.0318 | 405357.4193 | 33.7798 | 33.7798 | 96.2758 | 0.2 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 67.0833 | 19.2626 | 458451.0386 | 38.2043 | 38.2043 | 103.3463 | 0.3 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 69.3141 | 21.4935 | 511544.658 | 42.6287 | 42.6287 | 110.4167 | 0.4 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 71.5449 | 23.7243 | 564638.2773 | 47.0532 | 47.0532 | 117.4872 | 0.5 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 73.7758 | 25.9551 | 617731.8966 | 51.4777 | 51.4777 | 124.5577 | 0.6 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 76.0066 | 28.1859 | 670825.5159 | 55.9021 | 55.9021 | 131.6281 | 0.7 | 79.88 | 24.88 | 940464 | 78.372 | 78.372 | 78.2374 | 30.4168 | 723919.1353 | 60.3266 | 60.3266 | 138.6986 | 0.8 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 80.4682 | 32.6476 | 777012.7546 | 64.7511 | 64.7511 | 145.7691 | 0.9 | 81.56 | 26.56 | 1003968 | 83.664 | 83.664 | 82.6991 | 34.8784 | 830106.3739 | 69.1755 | 69.1755 | 152.8395 | 1 | 82.4 | 27.4 | 1035720 | 86.31 | 86.31 | 84.9299 | 37.1092 | 883199.9932 | 73.6 | 73.6 | 159.91 | 80 | 50 | 33.1061 | 34 | 51.1
7/19/20XX 12:00:00 PM | 0.5 | 4 | 84.1 | 47.6 | 69.9179 | 87.7992 | 17.8813 | 40 | 84.1 |  | 84.1 | 83.5077 | 0.1 | 75.01 | 20.01 | 756378 | 63.0315 | 63.0315 | 64.7102 | 16.8896 | 401972.5702 | 33.4977 | 33.4977 | 96.5292 | 0.2 | 76.02 | 21.02 | 794556 | 66.213 | 66.213 | 66.7988 | 18.9782 | 451681.3404 | 37.6401 | 37.6401 | 103.8531 | 0.3 | 77.03 | 22.03 | 832734 | 69.3945 | 69.3945 | 68.8874 | 21.0668 | 501390.1107 | 41.7825 | 41.7825 | 111.177 | 0.4 | 78.04 | 23.04 | 870912 | 72.576 | 72.576 | 70.976 | 23.1554 | 551098.8809 | 45.9249 | 45.9249 | 118.5009 | 0.5 | 79.05 | 24.05 | 909090 | 75.7575 | 75.7575 | 73.0647 | 25.244 | 600807.6511 | 50.0673 | 50.0673 | 125.8248 | 0.6 | 80.06 | 25.06 | 947268 | 78.939 | 78.939 | 75.1533 | 27.3326 | 650516.4213 | 54.2097 | 54.2097 | 133.1487 | 0.7 | 81.07 | 26.07 | 985446 | 82.1205 | 82.1205 | 77.2419 | 29.4212 | 700225.1915 | 58.3521 | 58.3521 | 140.4726 | 0.8 | 82.08 | 27.08 | 1023624 | 85.302 | 85.302 | 79.3305 | 31.5098 | 749933.9617 | 62.4945 | 62.4945 | 147.7965 | 0.9 | 83.09 | 28.09 | 1061802 | 88.4835 | 88.4835 | 81.4191 | 33.5984 | 799642.732 | 66.6369 | 66.6369 | 155.1204 | 1 | 84.1 | 29.1 | 1099980 | 91.665 | 91.665 | 83.5077 | 35.687 | 849351.5022 | 70.7793 | 70.7793 | 162.4443 | 85 | 50 | 33.2999 | 34 | 47.6
7/19/20XX 1:00:00 PM | 0.54167 | 4 | 84.9 | 48.1 | 71.7427 | 90.1049 | 18.3622 | 40 | 84.9 |  | 84.9 | 86.6161 | 0.1 | 75.09 | 20.09 | 759402 | 63.2835 | 63.2835 | 65.0211 | 17.2004 | 409370.5583 | 34.1142 | 34.1142 | 97.3977 | 0.2 | 76.18 | 21.18 | 800604 | 66.717 | 66.717 | 67.4205 | 19.5999 | 466477.3165 | 38.8731 | 38.8731 | 105.5901 | 0.3 | 77.27 | 22.27 | 841806 | 70.1505 | 70.1505 | 69.82 | 21.9993 | 523584.0748 | 43.632 | 43.632 | 113.7825 | 0.4 | 78.36 | 23.36 | 883008 | 73.584 | 73.584 | 72.2194 | 24.3988 | 580690.8331 | 48.3909 | 48.3909 | 121.9749 | 0.5 | 79.45 | 24.45 | 924210 | 77.0175 | 77.0175 | 74.6189 | 26.7982 | 637797.5913 | 53.1498 | 53.1498 | 130.1673 | 0.6 | 80.54 | 25.54 | 965412 | 80.451 | 80.451 | 77.0183 | 29.1977 | 694904.3496 | 57.9087 | 57.9087 | 138.3597 | 0.7 | 81.63 | 26.63 | 1006614 | 83.8845 | 83.8845 | 79.4177 | 31.5971 | 752011.1079 | 62.6676 | 62.6676 | 146.5521 | 0.8 | 82.72 | 27.72 | 1047816 | 87.318 | 87.318 | 81.8172 | 33.9965 | 809117.8661 | 67.4265 | 67.4265 | 154.7445 | 0.9 | 83.81 | 28.81 | 1089018 | 90.7515 | 90.7515 | 84.2166 | 36.396 | 866224.6244 | 72.1854 | 72.1854 | 162.9369 | 1 | 84.9 | 29.9 | 1130220 | 94.185 | 94.185 | 86.6161 | 38.7954 | 923331.3827 | 76.9443 | 76.9443 | 171.1293 | 85 | 50 | 33.9846 | 34 | 48.1
7/19/20XX 2:00:00 PM | 0.58333 | 4 | 84.5 | 47.9 | 70.8256 | 88.946 | 18.1204 | 40 | 84.5 |  | 84.5 | 85.1407 | 0.1 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 64.8735 | 17.0529 | 405859.1695 | 33.8216 | 33.8216 | 96.9791 | 0.2 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 67.1254 | 19.3048 | 459454.5391 | 38.2879 | 38.2879 | 104.7529 | 0.3 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 69.3774 | 21.5567 | 513049.9086 | 42.7542 | 42.7542 | 112.5267 | 0.4 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 71.6293 | 23.8086 | 566645.2782 | 47.2204 | 47.2204 | 120.3004 | 0.5 | 79.25 | 24.25 | 916650 | 76.3875 | 76.3875 | 73.8812 | 26.0605 | 620240.6477 | 51.6867 | 51.6867 | 128.0742 | 0.6 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 76.1331 | 28.3124 | 673836.0173 | 56.153 | 56.153 | 135.848 | 0.7 | 81.35 | 26.35 | 996030 | 83.0025 | 83.0025 | 78.385 | 30.5643 | 727431.3868 | 60.6193 | 60.6193 | 143.6218 | 0.8 | 82.4 | 27.4 | 1035720 | 86.31 | 86.31 | 80.6369 | 32.8163 | 781026.7564 | 65.0856 | 65.0856 | 151.3956 | 0.9 | 83.45 | 28.45 | 1075410 | 89.6175 | 89.6175 | 82.8888 | 35.0682 | 834622.1259 | 69.5518 | 69.5518 | 159.1693 | 1 | 84.5 | 29.5 | 1115100 | 92.925 | 92.925 | 85.1407 | 37.3201 | 888217.4955 | 74.0181 | 74.0181 | 166.9431 | 85 | 50 | 33.6546 | 34 | 47.9
7/19/20XX 3:00:00 PM | 0.625 | 4 | 84.2 | 48.6 | 70.1439 | 88.0847 | 17.9408 | 40 | 84.2 |  | 84.2 | 85.573 | 0.1 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 64.9168 | 17.0961 | 406888.1351 | 33.9073 | 33.9073 | 96.9703 | 0.2 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 67.2119 | 19.3913 | 461512.4702 | 38.4594 | 38.4594 | 104.7354 | 0.3 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 69.5071 | 21.6864 | 516136.8053 | 43.0114 | 43.0114 | 112.5004 | 0.4 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 71.8022 | 23.9816 | 570761.1404 | 47.5634 | 47.5634 | 120.2654 | 0.5 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 74.0973 | 26.2767 | 625385.4755 | 52.1155 | 52.1155 | 128.0305 | 0.6 | 80.12 | 25.12 | 949536 | 79.128 | 79.128 | 76.3925 | 28.5718 | 680009.8106 | 56.6675 | 56.6675 | 135.7955 | 0.7 | 81.14 | 26.14 | 988092 | 82.341 | 82.341 | 78.6876 | 30.867 | 734634.1456 | 61.2195 | 61.2195 | 143.5605 | 0.8 | 82.16 | 27.16 | 1026648 | 85.554 | 85.554 | 80.9828 | 33.1621 | 789258.4807 | 65.7715 | 65.7715 | 151.3255 | 0.9 | 83.18 | 28.18 | 1065204 | 88.767 | 88.767 | 83.2779 | 35.4573 | 843882.8158 | 70.3236 | 70.3236 | 159.0906 | 1 | 84.2 | 29.2 | 1103760 | 91.98 | 91.98 | 85.573 | 37.7524 | 898507.1509 | 74.8756 | 74.8756 | 166.8556 | 85 | 50 | 33.6489 | 34 | 48.6
7/19/20XX 4:00:00 PM | 0.66667 | 4 | 84.8 | 48.4 | 71.5125 | 89.814 | 18.3015 | 40 | 84.8 |  | 84.8 | 86.8858 | 0.1 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 65.048 | 17.2274 | 410012.4735 | 34.1677 | 34.1677 | 97.4197 | 0.2 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 67.4745 | 19.6538 | 467761.1469 | 38.9801 | 38.9801 | 105.6341 | 0.3 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 69.9009 | 22.0802 | 525509.8204 | 43.7925 | 43.7925 | 113.8485 | 0.4 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 72.3273 | 24.5067 | 583258.4939 | 48.6049 | 48.6049 | 122.0629 | 0.5 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 74.7537 | 26.9331 | 641007.1673 | 53.4173 | 53.4173 | 130.2773 | 0.6 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 77.1801 | 29.3595 | 698755.8408 | 58.2297 | 58.2297 | 138.4917 | 0.7 | 81.56 | 26.56 | 1003968 | 83.664 | 83.664 | 79.6065 | 31.7859 | 756504.5143 | 63.042 | 63.042 | 146.706 | 0.8 | 82.64 | 27.64 | 1044792 | 87.066 | 87.066 | 82.033 | 34.2123 | 814253.1877 | 67.8544 | 67.8544 | 154.9204 | 0.9 | 83.72 | 28.72 | 1085616 | 90.468 | 90.468 | 84.4594 | 36.6387 | 872001.8612 | 72.6668 | 72.6668 | 163.1348 | 1 | 84.8 | 29.8 | 1126440 | 93.87 | 93.87 | 86.8858 | 39.0651 | 929750.5347 | 77.4792 | 77.4792 | 171.3492 | 85 | 50 | 34.0024 | 34 | 48.4
7/19/20XX 5:00:00 PM | 0.70833 | 4 | 84 | 47.8 | 69.6925 | 87.5144 | 17.8219 | 40 | 84 |  | 84 | 83.5935 | 0.1 | 75 | 20 | 756000 | 63 | 63 | 64.7188 | 16.8982 | 402176.9352 | 33.5147 | 33.5147 | 96.5147 | 0.2 | 76 | 21 | 793800 | 66.15 | 66.15 | 66.816 | 18.9954 | 452090.0704 | 37.6742 | 37.6742 | 103.8242 | 0.3 | 77 | 22 | 831600 | 69.3 | 69.3 | 68.9132 | 21.0926 | 502003.2056 | 41.8336 | 41.8336 | 111.1336 | 0.4 | 78 | 23 | 869400 | 72.45 | 72.45 | 71.0104 | 23.1898 | 551916.3409 | 45.993 | 45.993 | 118.443 | 0.5 | 79 | 24 | 907200 | 75.6 | 75.6 | 73.1076 | 25.287 | 601829.4761 | 50.1525 | 50.1525 | 125.7525 | 0.6 | 80 | 25 | 945000 | 78.75 | 78.75 | 75.2048 | 27.3841 | 651742.6113 | 54.3119 | 54.3119 | 133.0619 | 0.7 | 81 | 26 | 982800 | 81.9 | 81.9 | 77.302 | 29.4813 | 701655.7465 | 58.4713 | 58.4713 | 140.3713 | 0.8 | 82 | 27 | 1020600 | 85.05 | 85.05 | 79.3992 | 31.5785 | 751568.8817 | 62.6307 | 62.6307 | 147.6807 | 0.9 | 83 | 28 | 1058400 | 88.2 | 88.2 | 81.4963 | 33.6757 | 801482.0169 | 66.7902 | 66.7902 | 154.9902 | 1 | 84 | 29 | 1096200 | 91.35 | 91.35 | 83.5935 | 35.7729 | 851395.1521 | 70.9496 | 70.9496 | 162.2996 | 85 | 50 | 33.2889 | 34 | 47.8
7/19/20XX 6:00:00 PM | 0.75 | 4 | 82.6 | 52 | 83.605 | 100.7325 | 17.1274 | 50 | 82.6 |  | 82.6 | 87.0305 | 0.1 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 65.0625 | 17.2419 | 410356.9724 | 34.1964 | 34.1964 | 96.7554 | 0.2 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 67.5034 | 19.6828 | 468450.1449 | 39.0375 | 39.0375 | 104.3055 | 0.3 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 69.9443 | 22.1237 | 526543.3173 | 43.8786 | 43.8786 | 111.8556 | 0.4 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 72.3852 | 24.5646 | 584636.4898 | 48.7197 | 48.7197 | 119.4057 | 0.5 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 74.8261 | 27.0054 | 642729.6622 | 53.5608 | 53.5608 | 126.9558 | 0.6 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 77.267 | 29.4463 | 700822.8346 | 58.4019 | 58.4019 | 134.5059 | 0.7 | 80.02 | 25.02 | 945756 | 78.813 | 78.813 | 79.7079 | 31.8872 | 758916.0071 | 63.243 | 63.243 | 142.056 | 0.8 | 80.88 | 25.88 | 978264 | 81.522 | 81.522 | 82.1487 | 34.3281 | 817009.1795 | 68.0841 | 68.0841 | 149.6061 | 0.9 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 84.5896 | 36.769 | 875102.352 | 72.9252 | 72.9252 | 157.1562 | 1 | 82.6 | 27.6 | 1043280 | 86.94 | 86.94 | 87.0305 | 39.2099 | 933195.5244 | 77.7663 | 77.7663 | 164.7063 | 85 | 50 | 33.485 | 34 | 52
7/19/20XX 7:00:00 PM | 0.79167 | 4 | 80.8 | 54.6 | 78.7895 | 94.9151 | 16.1256 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/19/20XX 8:00:00 PM | 0.83333 | 4 | 79.6 | 56.3 | 75.7077 | 91.1929 | 15.4852 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/19/20XX 9:00:00 PM | 0.875 | 4 | 79 | 58.8 | 74.2046 | 89.3778 | 15.1731 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/19/20XX 10:00:00 PM | 0.91667 | 4 | 78.2 | 60.5 | 87.0044 | 101.8479 | 14.8435 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/19/20XX 11:00:00 PM | 0.95833 | 4 | 77.9 | 62.7 | 86.1281 | 100.819 | 14.691 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/19/20XX 12:00:00 AM | 0 | 5 | 77 | 65.3 | 83.5433 | 97.7844 | 14.241 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/20/20XX 1:00:00 AM | 0.041667 | 5 | 76.5 | 68.1 | 82.1358 | 96.1318 | 13.9961 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/20/20XX 2:00:00 AM | 0.083333 | 5 | 75.7 | 70.5 | 93.5368 | 107.2477 | 13.7109 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/20/20XX 3:00:00 AM | 0.125 | 5 | 75.6 | 71 | 93.2166 | 106.8793 | 13.6627 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/20/20XX 4:00:00 AM | 0.16667 | 5 | 73.8 | 75.7 | 87.6104 | 100.4307 | 12.8203 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/20/20XX 5:00:00 AM | 0.20833 | 5 | 73.5 | 76.6 | 86.7045 | 99.389 | 12.6844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/20/20XX 6:00:00 AM | 0.25 | 5 | 73.4 | 75.8 | 86.4044 | 99.0438 | 12.6394 | 70 | 73.4 |  | 73.4 | 93.7352 | 0.1 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 65.733 | 17.9124 | 426314.1914 | 35.5262 | 35.5262 | 95.1872 | 0.2 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 68.8444 | 21.0237 | 500364.5827 | 41.697 | 41.697 | 101.169 | 0.3 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 71.9557 | 24.1351 | 574414.9741 | 47.8679 | 47.8679 | 107.1509 | 0.4 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 75.0671 | 27.2464 | 648465.3655 | 54.0388 | 54.0388 | 113.1328 | 0.5 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 78.1784 | 30.3578 | 722515.7569 | 60.2096 | 60.2096 | 119.1146 | 0.6 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 81.2898 | 33.4692 | 796566.1482 | 66.3805 | 66.3805 | 125.0965 | 0.7 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 84.4012 | 36.5805 | 870616.5396 | 72.5514 | 72.5514 | 131.0784 | 0.8 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 87.5125 | 39.6919 | 944666.931 | 78.7222 | 78.7222 | 137.0602 | 0.9 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 90.6239 | 42.8032 | 1018717.3224 | 84.8931 | 84.8931 | 143.0421 | 1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 93.7352 | 45.9146 | 1092767.7137 | 91.064 | 91.064 | 149.024 | 75 | 75 | 32.2746 | 32 | 75.8
7/20/20XX 7:00:00 AM | 0.29167 | 5 | 75.1 | 71.6 | 91.6296 | 105.0536 | 13.424 | 70 | 75.1 |  | 75.1 | 93.7774 | 0.1 | 74.11 | 19.11 | 722358 | 60.1965 | 60.1965 | 65.7372 | 17.9166 | 426414.5242 | 35.5345 | 35.5345 | 95.731 | 0.2 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 68.8528 | 21.0322 | 500565.2484 | 41.7138 | 41.7138 | 102.2568 | 0.3 | 74.33 | 19.33 | 730674 | 60.8895 | 60.8895 | 71.9684 | 24.1477 | 574715.9726 | 47.893 | 47.893 | 108.7825 | 0.4 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 75.0839 | 27.2633 | 648866.6968 | 54.0722 | 54.0722 | 115.3082 | 0.5 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 78.1995 | 30.3789 | 723017.421 | 60.2515 | 60.2515 | 121.834 | 0.6 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 81.3151 | 33.4945 | 797168.1453 | 66.4307 | 66.4307 | 128.3597 | 0.7 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 84.4307 | 36.61 | 871318.8695 | 72.6099 | 72.6099 | 134.8854 | 0.8 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 87.5462 | 39.7256 | 945469.5937 | 78.7891 | 78.7891 | 141.4111 | 0.9 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 90.6618 | 42.8412 | 1019620.3179 | 84.9684 | 84.9684 | 147.9369 | 1 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 93.7774 | 45.9568 | 1093771.0421 | 91.1476 | 91.1476 | 154.4626 | 75 | 70 | 32.6993 | 32 | 71.6
7/20/20XX 8:00:00 AM | 0.33333 | 5 | 76.8 | 66.4 | 82.9779 | 97.1205 | 14.1426 | 60 | 76.8 |  | 76.8 | 92.0292 | 0.1 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 65.5624 | 17.7418 | 422253.7368 | 35.1878 | 35.1878 | 95.9198 | 0.2 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 68.5031 | 20.6825 | 492243.6736 | 41.0203 | 41.0203 | 102.6343 | 0.3 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 71.4439 | 23.6233 | 562233.6104 | 46.8528 | 46.8528 | 109.3488 | 0.4 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 74.3846 | 26.564 | 632223.5471 | 52.6853 | 52.6853 | 116.0633 | 0.5 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 77.3254 | 29.5048 | 702213.4839 | 58.5178 | 58.5178 | 122.7778 | 0.6 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 80.2662 | 32.4455 | 772203.4207 | 64.3503 | 64.3503 | 129.4923 | 0.7 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 83.2069 | 35.3863 | 842193.3575 | 70.1828 | 70.1828 | 136.2068 | 0.8 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 86.1477 | 38.327 | 912183.2943 | 76.0153 | 76.0153 | 142.9213 | 0.9 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 89.0884 | 41.2678 | 982173.2311 | 81.8478 | 81.8478 | 149.6358 | 1 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 92.0292 | 44.2085 | 1052163.1679 | 87.6803 | 87.6803 | 156.3503 | 75 | 65 | 32.8437 | 32 | 66.4
7/20/20XX 9:00:00 AM | 0.375 | 5 | 78.4 | 63.8 | 87.5927 | 102.5387 | 14.946 | 60 | 78.4 |  | 78.4 | 93.2722 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 65.6867 | 17.8661 | 425212.1684 | 35.4343 | 35.4343 | 96.6703 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 68.7517 | 20.9311 | 498160.5368 | 41.5134 | 41.5134 | 104.1354 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 71.8168 | 23.9962 | 571108.9052 | 47.5924 | 47.5924 | 111.6004 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 74.8819 | 27.0612 | 644057.2736 | 53.6714 | 53.6714 | 119.0654 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 77.9469 | 30.1263 | 717005.642 | 59.7505 | 59.7505 | 126.5305 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 81.012 | 33.1913 | 789954.0104 | 65.8295 | 65.8295 | 133.9955 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 84.077 | 36.2564 | 862902.3788 | 71.9085 | 71.9085 | 141.4605 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 87.1421 | 39.3215 | 935850.7472 | 77.9876 | 77.9876 | 148.9256 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 90.2071 | 42.3865 | 1008799.1156 | 84.0666 | 84.0666 | 156.3906 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 93.2722 | 45.4516 | 1081747.484 | 90.1456 | 90.1456 | 163.8556 | 80 | 65 | 33.4318 | 34 | 63.8
7/20/20XX 10:00:00 AM | 0.41667 | 5 | 79.4 | 60 | 90.5845 | 106.0515 | 15.4669 | 60 | 79.4 |  | 79.4 | 90.5845 | 0.1 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 65.4179 | 17.5973 | 418815.4329 | 34.9013 | 34.9013 | 96.4523 | 0.2 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 68.2142 | 20.3936 | 485367.0658 | 40.4473 | 40.4473 | 103.6993 | 0.3 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 71.0105 | 23.1899 | 551918.6987 | 45.9932 | 45.9932 | 110.9462 | 0.4 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 73.8068 | 25.9861 | 618470.3316 | 51.5392 | 51.5392 | 118.1932 | 0.5 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 76.6031 | 28.7824 | 685021.9645 | 57.0852 | 57.0852 | 125.4402 | 0.6 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 79.3994 | 31.5787 | 751573.5974 | 62.6311 | 62.6311 | 132.6871 | 0.7 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 82.1956 | 34.375 | 818125.2303 | 68.1771 | 68.1771 | 139.9341 | 0.8 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 84.9919 | 37.1713 | 884676.8632 | 73.7231 | 73.7231 | 147.1811 | 0.9 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 87.7882 | 39.9676 | 951228.4962 | 79.269 | 79.269 | 154.428 | 1 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 90.5845 | 42.7639 | 1017780.1291 | 84.815 | 84.815 | 161.675 | 80 | 60 | 33.2564 | 34 | 60
7/20/20XX 11:00:00 AM | 0.45833 | 5 | 81.9 | 54.9 | 81.7045 | 98.4363 | 16.7319 | 50 | 81.9 |  | 81.9 | 89.9031 | 0.1 | 74.79 | 19.79 | 748062 | 62.3385 | 62.3385 | 65.3498 | 17.5291 | 417193.684 | 34.7661 | 34.7661 | 97.1046 | 0.2 | 75.58 | 20.58 | 777924 | 64.827 | 64.827 | 68.0779 | 20.2573 | 482123.5679 | 40.177 | 40.177 | 105.004 | 0.3 | 76.37 | 21.37 | 807786 | 67.3155 | 67.3155 | 70.8061 | 22.9854 | 547053.4519 | 45.5878 | 45.5878 | 112.9033 | 0.4 | 77.16 | 22.16 | 837648 | 69.804 | 69.804 | 73.5342 | 25.7136 | 611983.3358 | 50.9986 | 50.9986 | 120.8026 | 0.5 | 77.95 | 22.95 | 867510 | 72.2925 | 72.2925 | 76.2624 | 28.4417 | 676913.2198 | 56.4094 | 56.4094 | 128.7019 | 0.6 | 78.74 | 23.74 | 897372 | 74.781 | 74.781 | 78.9905 | 31.1699 | 741843.1037 | 61.8203 | 61.8203 | 136.6013 | 0.7 | 79.53 | 24.53 | 927234 | 77.2695 | 77.2695 | 81.7187 | 33.898 | 806772.9877 | 67.2311 | 67.2311 | 144.5006 | 0.8 | 80.32 | 25.32 | 957096 | 79.758 | 79.758 | 84.4468 | 36.6262 | 871702.8716 | 72.6419 | 72.6419 | 152.3999 | 0.9 | 81.11 | 26.11 | 986958 | 82.2465 | 82.2465 | 87.1749 | 39.3543 | 936632.7556 | 78.0527 | 78.0527 | 160.2992 | 1 | 81.9 | 26.9 | 1016820 | 84.735 | 84.735 | 89.9031 | 42.0825 | 1001562.6395 | 83.4636 | 83.4636 | 168.1986 | 80 | 55 | 33.7639 | 34 | 54.9
7/20/20XX 12:00:00 PM | 0.5 | 5 | 83.2 | 52 | 85.2627 | 102.7353 | 17.4726 | 50 | 83.2 |  | 83.2 | 88.7572 | 0.1 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 65.2352 | 17.4146 | 414466.4424 | 34.5389 | 34.5389 | 97.2869 | 0.2 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 67.8487 | 20.0281 | 476669.0849 | 39.7224 | 39.7224 | 105.3684 | 0.3 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 70.4623 | 22.6417 | 538871.7273 | 44.906 | 44.906 | 113.45 | 0.4 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 73.0759 | 25.2552 | 601074.3697 | 50.0895 | 50.0895 | 121.5315 | 0.5 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 75.6894 | 27.8688 | 663277.0122 | 55.2731 | 55.2731 | 129.6131 | 0.6 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 78.303 | 30.4823 | 725479.6546 | 60.4566 | 60.4566 | 137.6946 | 0.7 | 80.44 | 25.44 | 961632 | 80.136 | 80.136 | 80.9165 | 33.0959 | 787682.297 | 65.6402 | 65.6402 | 145.7762 | 0.8 | 81.36 | 26.36 | 996408 | 83.034 | 83.034 | 83.5301 | 35.7095 | 849884.9394 | 70.8237 | 70.8237 | 153.8577 | 0.9 | 82.28 | 27.28 | 1031184 | 85.932 | 85.932 | 86.1436 | 38.323 | 912087.5819 | 76.0073 | 76.0073 | 161.9393 | 1 | 83.2 | 28.2 | 1065960 | 88.83 | 88.83 | 88.7572 | 40.9366 | 974290.2243 | 81.1909 | 81.1909 | 170.0209 | 85 | 50 | 33.9034 | 34 | 52
7/20/20XX 1:00:00 PM | 0.54167 | 5 | 83.2 | 53.1 | 85.2627 | 102.7353 | 17.4726 | 50 | 83.2 |  | 83.2 | 90.6792 | 0.1 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 65.4274 | 17.6068 | 419040.7719 | 34.9201 | 34.9201 | 97.6681 | 0.2 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 68.2331 | 20.4125 | 485817.7437 | 40.4848 | 40.4848 | 106.1308 | 0.3 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 71.0389 | 23.2183 | 552594.7156 | 46.0496 | 46.0496 | 114.5936 | 0.4 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 73.8447 | 26.024 | 619371.6875 | 51.6143 | 51.6143 | 123.0563 | 0.5 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 76.6504 | 28.8298 | 686148.6593 | 57.1791 | 57.1791 | 131.5191 | 0.6 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 79.4562 | 31.6355 | 752925.6312 | 62.7438 | 62.7438 | 139.9818 | 0.7 | 80.44 | 25.44 | 961632 | 80.136 | 80.136 | 82.2619 | 34.4413 | 819702.603 | 68.3086 | 68.3086 | 148.4446 | 0.8 | 81.36 | 26.36 | 996408 | 83.034 | 83.034 | 85.0677 | 37.247 | 886479.5749 | 73.8733 | 73.8733 | 156.9073 | 0.9 | 82.28 | 27.28 | 1031184 | 85.932 | 85.932 | 87.8734 | 40.0528 | 953256.5468 | 79.438 | 79.438 | 165.37 | 1 | 83.2 | 28.2 | 1065960 | 88.83 | 88.83 | 90.6792 | 42.8586 | 1020033.5186 | 85.0028 | 85.0028 | 173.8328 | 85 | 55 | 34.2051 | 34 | 53.1
7/20/20XX 2:00:00 PM | 0.58333 | 5 | 82.9 | 53.9 | 84.4305 | 101.7299 | 17.2993 | 50 | 82.9 |  | 82.9 | 91.1773 | 0.1 | 74.89 | 19.89 | 751842 | 62.6535 | 62.6535 | 65.4772 | 17.6566 | 420226.2269 | 35.0189 | 35.0189 | 97.6724 | 0.2 | 75.78 | 20.78 | 785484 | 65.457 | 65.457 | 68.3328 | 20.5121 | 488188.6538 | 40.6824 | 40.6824 | 106.1394 | 0.3 | 76.67 | 21.67 | 819126 | 68.2605 | 68.2605 | 71.1883 | 23.3677 | 556151.0807 | 46.3459 | 46.3459 | 114.6064 | 0.4 | 77.56 | 22.56 | 852768 | 71.064 | 71.064 | 74.0439 | 26.2233 | 624113.5076 | 52.0095 | 52.0095 | 123.0735 | 0.5 | 78.45 | 23.45 | 886410 | 73.8675 | 73.8675 | 76.8995 | 29.0788 | 692075.9345 | 57.673 | 57.673 | 131.5405 | 0.6 | 79.34 | 24.34 | 920052 | 76.671 | 76.671 | 79.755 | 31.9344 | 760038.3614 | 63.3365 | 63.3365 | 140.0075 | 0.7 | 80.23 | 25.23 | 953694 | 79.4745 | 79.4745 | 82.6106 | 34.7899 | 828000.7883 | 69.0001 | 69.0001 | 148.4746 | 0.8 | 81.12 | 26.12 | 987336 | 82.278 | 82.278 | 85.4661 | 37.6455 | 895963.2152 | 74.6636 | 74.6636 | 156.9416 | 0.9 | 82.01 | 27.01 | 1020978 | 85.0815 | 85.0815 | 88.3217 | 40.5011 | 963925.6421 | 80.3271 | 80.3271 | 165.4086 | 1 | 82.9 | 27.9 | 1054620 | 87.885 | 87.885 | 91.1773 | 43.3566 | 1031888.069 | 85.9907 | 85.9907 | 173.8757 | 85 | 55 | 34.2096 | 34 | 53.9
7/20/20XX 3:00:00 PM | 0.625 | 5 | 82.6 | 52.7 | 83.605 | 100.7325 | 17.1274 | 50 | 82.6 |  | 82.6 | 88.2294 | 0.1 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 65.1824 | 17.3618 | 413210.4027 | 34.4342 | 34.4342 | 96.9932 | 0.2 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 67.7432 | 19.9226 | 474157.0053 | 39.5131 | 39.5131 | 104.7811 | 0.3 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 70.304 | 22.4833 | 535103.608 | 44.592 | 44.592 | 112.569 | 0.4 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 72.8648 | 25.0441 | 596050.2107 | 49.6709 | 49.6709 | 120.3569 | 0.5 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 75.4255 | 27.6049 | 656996.8133 | 54.7497 | 54.7497 | 128.1447 | 0.6 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 77.9863 | 30.1657 | 717943.416 | 59.8286 | 59.8286 | 135.9326 | 0.7 | 80.02 | 25.02 | 945756 | 78.813 | 78.813 | 80.5471 | 32.7265 | 778890.0186 | 64.9075 | 64.9075 | 143.7205 | 0.8 | 80.88 | 25.88 | 978264 | 81.522 | 81.522 | 83.1079 | 35.2873 | 839836.6213 | 69.9864 | 69.9864 | 151.5084 | 0.9 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 85.6687 | 37.848 | 900783.224 | 75.0653 | 75.0653 | 159.2963 | 1 | 82.6 | 27.6 | 1043280 | 86.94 | 86.94 | 88.2294 | 40.4088 | 961729.8266 | 80.1442 | 80.1442 | 167.0842 | 85 | 55 | 33.6732 | 34 | 52.7
7/20/20XX 4:00:00 PM | 0.66667 | 5 | 82 | 53.9 | 81.9738 | 98.7617 | 16.7879 | 50 | 82 |  | 82 | 88.5211 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 65.2116 | 17.3909 | 413904.5094 | 34.492 | 34.492 | 96.862 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 67.8015 | 19.9809 | 475545.2187 | 39.6288 | 39.6288 | 104.5188 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 70.3915 | 22.5708 | 537185.9281 | 44.7655 | 44.7655 | 112.1755 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 72.9814 | 25.1608 | 598826.6375 | 49.9022 | 49.9022 | 119.8322 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 75.5714 | 27.7507 | 660467.3469 | 55.0389 | 55.0389 | 127.4889 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 78.1613 | 30.3407 | 722108.0562 | 60.1757 | 60.1757 | 135.1457 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 80.7513 | 32.9306 | 783748.7656 | 65.3124 | 65.3124 | 142.8024 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 83.3412 | 35.5206 | 845389.475 | 70.4491 | 70.4491 | 150.4591 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 85.9311 | 38.1105 | 907030.1844 | 75.5858 | 75.5858 | 158.1158 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 88.5211 | 40.7005 | 968670.8937 | 80.7226 | 80.7226 | 165.7726 | 80 | 55 | 33.5716 | 34 | 53.9
7/20/20XX 5:00:00 PM | 0.70833 | 5 | 81.4 | 53.6 | 80.3687 | 96.8227 | 16.454 | 50 | 81.4 |  | 81.4 | 86.2921 | 0.1 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 64.9887 | 17.1681 | 408599.6186 | 34.05 | 34.05 | 96.231 | 0.2 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 67.3557 | 19.5351 | 464935.4372 | 38.7446 | 38.7446 | 103.2566 | 0.3 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 69.7228 | 21.9022 | 521271.2558 | 43.4393 | 43.4393 | 110.2823 | 0.4 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 72.0898 | 24.2692 | 577607.0744 | 48.1339 | 48.1339 | 117.3079 | 0.5 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 74.4569 | 26.6363 | 633942.893 | 52.8286 | 52.8286 | 124.3336 | 0.6 | 78.44 | 23.44 | 886032 | 73.836 | 73.836 | 76.8239 | 29.0033 | 690278.7115 | 57.5232 | 57.5232 | 131.3592 | 0.7 | 79.18 | 24.18 | 914004 | 76.167 | 76.167 | 79.191 | 31.3704 | 746614.5301 | 62.2179 | 62.2179 | 138.3849 | 0.8 | 79.92 | 24.92 | 941976 | 78.498 | 78.498 | 81.558 | 33.7374 | 802950.3487 | 66.9125 | 66.9125 | 145.4105 | 0.9 | 80.66 | 25.66 | 969948 | 80.829 | 80.829 | 83.9251 | 36.1045 | 859286.1673 | 71.6072 | 71.6072 | 152.4362 | 1 | 81.4 | 26.4 | 997920 | 83.16 | 83.16 | 86.2921 | 38.4715 | 915621.9859 | 76.3018 | 76.3018 | 159.4618 | 80 | 55 | 33.0745 | 34 | 53.6
7/20/20XX 6:00:00 PM | 0.75 | 5 | 79.6 | 56.9 | 75.7077 | 91.1929 | 15.4852 | 50 | 79.6 |  | 79.6 | 86.3925 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 64.9987 | 17.1781 | 408838.5147 | 34.0699 | 34.0699 | 95.6839 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 67.3758 | 19.5552 | 465413.2294 | 38.7844 | 38.7844 | 102.1624 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 69.7529 | 21.9323 | 521987.9441 | 43.499 | 43.499 | 108.641 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 72.13 | 24.3094 | 578562.6588 | 48.2136 | 48.2136 | 115.1196 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 74.5071 | 26.6864 | 635137.3735 | 52.9281 | 52.9281 | 121.5981 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 76.8842 | 29.0635 | 691712.0882 | 57.6427 | 57.6427 | 128.0767 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 79.2613 | 31.4406 | 748286.8029 | 62.3572 | 62.3572 | 134.5552 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 81.6383 | 33.8177 | 804861.5176 | 67.0718 | 67.0718 | 141.0338 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 84.0154 | 36.1948 | 861436.2323 | 71.7864 | 71.7864 | 147.5124 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 86.3925 | 38.5719 | 918010.947 | 76.5009 | 76.5009 | 153.9909 | 80 | 55 | 32.6484 | 32 | 56.9
7/20/20XX 7:00:00 PM | 0.79167 | 5 | 78.8 | 58.2 | 73.7091 | 88.7794 | 15.0703 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/20/20XX 8:00:00 PM | 0.83333 | 5 | 76.5 | 64.3 | 82.1358 | 96.1318 | 13.9961 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/20/20XX 9:00:00 PM | 0.875 | 5 | 75.8 | 66.2 | 80.1988 | 93.8579 | 13.6591 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/20/20XX 10:00:00 PM | 0.91667 | 5 | 75.5 | 66.7 | 79.3806 | 92.8973 | 13.5167 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/20/20XX 11:00:00 PM | 0.95833 | 5 | 74.9 | 69.4 | 77.7654 | 91.0012 | 13.2358 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/20/20XX 12:00:00 AM | 0 | 6 | 74.6 | 70.8 | 90.0655 | 103.2545 | 13.1889 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/21/20XX 1:00:00 AM | 0.041667 | 6 | 74 | 73.7 | 88.2187 | 101.1303 | 12.9116 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/21/20XX 2:00:00 AM | 0.083333 | 6 | 73.9 | 73.4 | 87.9141 | 100.78 | 12.8659 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/21/20XX 3:00:00 AM | 0.125 | 6 | 73.5 | 74.3 | 86.7045 | 99.389 | 12.6844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/21/20XX 4:00:00 AM | 0.16667 | 6 | 72.9 | 75.7 | 84.9169 | 97.3334 | 12.4165 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/21/20XX 5:00:00 AM | 0.20833 | 6 | 73.1 | 76.1 | 85.5092 | 98.0145 | 12.5053 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/21/20XX 6:00:00 AM | 0.25 | 6 | 73.3 | 74.9 | 86.1051 | 98.6997 | 12.5946 | 70 | 73.3 |  | 73.3 | 92.2764 | 0.1 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 65.5871 | 17.7665 | 422842.2457 | 35.2369 | 35.2369 | 94.8664 | 0.2 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 68.5526 | 20.732 | 493420.6914 | 41.1184 | 41.1184 | 100.5274 | 0.3 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 71.5181 | 23.6974 | 563999.1372 | 46.9999 | 46.9999 | 106.1884 | 0.4 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 74.4836 | 26.6629 | 634577.5829 | 52.8815 | 52.8815 | 111.8495 | 0.5 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 77.449 | 29.6284 | 705156.0286 | 58.763 | 58.763 | 117.5105 | 0.6 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 80.4145 | 32.5939 | 775734.4743 | 64.6445 | 64.6445 | 123.1715 | 0.7 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 83.38 | 35.5594 | 846312.9201 | 70.5261 | 70.5261 | 128.8326 | 0.8 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 86.3455 | 38.5248 | 916891.3658 | 76.4076 | 76.4076 | 134.4936 | 0.9 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 89.311 | 41.4903 | 987469.8115 | 82.2892 | 82.2892 | 140.1547 | 1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 92.2764 | 44.4558 | 1058048.2572 | 88.1707 | 88.1707 | 145.8157 | 75 | 75 | 32.0219 | 32 | 74.9
7/21/20XX 7:00:00 AM | 0.29167 | 6 | 74 | 72.9 | 88.2187 | 101.1303 | 12.9116 | 70 | 74 |  | 74 | 91.9631 | 0.1 | 74 | 19 | 718200 | 59.85 | 59.85 | 65.5558 | 17.7351 | 422096.4849 | 35.1747 | 35.1747 | 95.0247 | 0.2 | 74 | 19 | 718200 | 59.85 | 59.85 | 68.4899 | 20.6693 | 491929.1698 | 40.9941 | 40.9941 | 100.8441 | 0.3 | 74 | 19 | 718200 | 59.85 | 59.85 | 71.4241 | 23.6034 | 561761.8547 | 46.8135 | 46.8135 | 106.6635 | 0.4 | 74 | 19 | 718200 | 59.85 | 59.85 | 74.3582 | 26.5376 | 631594.5397 | 52.6329 | 52.6329 | 112.4829 | 0.5 | 74 | 19 | 718200 | 59.85 | 59.85 | 77.2924 | 29.4717 | 701427.2246 | 58.4523 | 58.4523 | 118.3023 | 0.6 | 74 | 19 | 718200 | 59.85 | 59.85 | 80.2265 | 32.4059 | 771259.9095 | 64.2717 | 64.2717 | 124.1217 | 0.7 | 74 | 19 | 718200 | 59.85 | 59.85 | 83.1607 | 35.34 | 841092.5944 | 70.091 | 70.091 | 129.941 | 0.8 | 74 | 19 | 718200 | 59.85 | 59.85 | 86.0948 | 38.2742 | 910925.2793 | 75.9104 | 75.9104 | 135.7604 | 0.9 | 74 | 19 | 718200 | 59.85 | 59.85 | 89.029 | 41.2083 | 980757.9642 | 81.7298 | 81.7298 | 141.5798 | 1 | 74 | 19 | 718200 | 59.85 | 59.85 | 91.9631 | 44.1425 | 1050590.6492 | 87.5492 | 87.5492 | 147.3992 | 75 | 75 | 32.145 | 32 | 72.9
7/21/20XX 8:00:00 AM | 0.33333 | 6 | 75.1 | 69.3 | 78.3007 | 91.6296 | 13.3289 | 60 | 75.1 |  | 75.1 | 90.6965 | 0.1 | 74.11 | 19.11 | 722358 | 60.1965 | 60.1965 | 65.4291 | 17.6085 | 419082.0803 | 34.9235 | 34.9235 | 95.12 | 0.2 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 68.2366 | 20.416 | 485900.3606 | 40.4917 | 40.4917 | 101.0347 | 0.3 | 74.33 | 19.33 | 730674 | 60.8895 | 60.8895 | 71.0441 | 23.2235 | 552718.6409 | 46.0599 | 46.0599 | 106.9494 | 0.4 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 73.8516 | 26.031 | 619536.9212 | 51.6281 | 51.6281 | 112.8641 | 0.5 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 76.6591 | 28.8385 | 686355.2014 | 57.1963 | 57.1963 | 118.7788 | 0.6 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 79.4666 | 31.6459 | 753173.4817 | 62.7645 | 62.7645 | 124.6935 | 0.7 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 82.2741 | 34.4534 | 819991.762 | 68.3326 | 68.3326 | 130.6081 | 0.8 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 85.0816 | 37.2609 | 886810.0423 | 73.9008 | 73.9008 | 136.5228 | 0.9 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 87.889 | 40.0684 | 953628.3226 | 79.469 | 79.469 | 142.4375 | 1 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 90.6965 | 42.8759 | 1020446.6029 | 85.0372 | 85.0372 | 148.3522 | 75 | 70 | 32.2172 | 32 | 69.3
7/21/20XX 9:00:00 AM | 0.375 | 6 | 76.9 | 64.5 | 83.2602 | 97.452 | 14.1918 | 60 | 76.9 |  | 76.9 | 89.6465 | 0.1 | 74.29 | 19.29 | 729162 | 60.7635 | 60.7635 | 65.3241 | 17.5035 | 416582.9798 | 34.7152 | 34.7152 | 95.4787 | 0.2 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 68.0266 | 20.206 | 480902.1595 | 40.0752 | 40.0752 | 101.7522 | 0.3 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 70.7291 | 22.9085 | 545221.3393 | 45.4351 | 45.4351 | 108.0256 | 0.4 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 73.4316 | 25.6109 | 609540.519 | 50.795 | 50.795 | 114.299 | 0.5 | 75.45 | 20.45 | 773010 | 64.4175 | 64.4175 | 76.1341 | 28.3134 | 673859.6988 | 56.155 | 56.155 | 120.5725 | 0.6 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 78.8366 | 31.0159 | 738178.8786 | 61.5149 | 61.5149 | 126.8459 | 0.7 | 76.03 | 21.03 | 794934 | 66.2445 | 66.2445 | 81.539 | 33.7184 | 802498.0583 | 66.8748 | 66.8748 | 133.1193 | 0.8 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 84.2415 | 36.4209 | 866817.2381 | 72.2348 | 72.2348 | 139.3928 | 0.9 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 86.944 | 39.1234 | 931136.4178 | 77.5947 | 77.5947 | 145.6662 | 1 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 89.6465 | 41.8259 | 995455.5976 | 82.9546 | 82.9546 | 151.9396 | 75 | 65 | 32.4951 | 32 | 64.5
7/21/20XX 10:00:00 AM | 0.41667 | 6 | 79 | 59.7 | 74.2046 | 89.3778 | 15.1731 | 50 | 79 |  | 79 | 88.9226 | 0.1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 65.2517 | 17.4311 | 414860.0018 | 34.5717 | 34.5717 | 95.9967 | 0.2 | 75 | 20 | 756000 | 63 | 63 | 67.8818 | 20.0612 | 477456.2035 | 39.788 | 39.788 | 102.788 | 0.3 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 70.5119 | 22.6913 | 540052.4053 | 45.0044 | 45.0044 | 109.5794 | 0.4 | 76 | 21 | 793800 | 66.15 | 66.15 | 73.142 | 25.3214 | 602648.607 | 50.2207 | 50.2207 | 116.3707 | 0.5 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 75.7721 | 27.9515 | 665244.8088 | 55.4371 | 55.4371 | 123.1621 | 0.6 | 77 | 22 | 831600 | 69.3 | 69.3 | 78.4022 | 30.5816 | 727841.0106 | 60.6534 | 60.6534 | 129.9534 | 0.7 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 81.0323 | 33.2116 | 790437.2123 | 65.8698 | 65.8698 | 136.7448 | 0.8 | 78 | 23 | 869400 | 72.45 | 72.45 | 83.6624 | 35.8417 | 853033.4141 | 71.0861 | 71.0861 | 143.5361 | 0.9 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 86.2925 | 38.4718 | 915629.6159 | 76.3025 | 76.3025 | 150.3275 | 1 | 79 | 24 | 907200 | 75.6 | 75.6 | 88.9226 | 41.1019 | 978225.8176 | 81.5188 | 81.5188 | 157.1188 | 80 | 60 | 32.8976 | 32 | 59.7
7/21/20XX 11:00:00 AM | 0.45833 | 6 | 81.4 | 55.5 | 80.3687 | 96.8227 | 16.454 | 50 | 81.4 |  | 81.4 | 89.4184 | 0.1 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 65.3013 | 17.4807 | 416040.1088 | 34.67 | 34.67 | 96.851 | 0.2 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 67.981 | 20.1604 | 479816.4176 | 39.9847 | 39.9847 | 104.4967 | 0.3 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 70.6607 | 22.84 | 543592.7264 | 45.2994 | 45.2994 | 112.1424 | 0.4 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 73.3403 | 25.5197 | 607369.0352 | 50.6141 | 50.6141 | 119.7881 | 0.5 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 76.02 | 28.1994 | 671145.344 | 55.9288 | 55.9288 | 127.4338 | 0.6 | 78.44 | 23.44 | 886032 | 73.836 | 73.836 | 78.6997 | 30.8791 | 734921.6527 | 61.2435 | 61.2435 | 135.0795 | 0.7 | 79.18 | 24.18 | 914004 | 76.167 | 76.167 | 81.3794 | 33.5587 | 798697.9615 | 66.5582 | 66.5582 | 142.7252 | 0.8 | 79.92 | 24.92 | 941976 | 78.498 | 78.498 | 84.059 | 36.2384 | 862474.2703 | 71.8729 | 71.8729 | 150.3709 | 0.9 | 80.66 | 25.66 | 969948 | 80.829 | 80.829 | 86.7387 | 38.9181 | 926250.5791 | 77.1875 | 77.1875 | 158.0165 | 1 | 81.4 | 26.4 | 997920 | 83.16 | 83.16 | 89.4184 | 41.5978 | 990026.8879 | 82.5022 | 82.5022 | 165.6622 | 80 | 55 | 33.565 | 34 | 55.5
7/21/20XX 12:00:00 PM | 0.5 | 6 | 82.6 | 51.6 | 83.605 | 100.7325 | 17.1274 | 50 | 82.6 |  | 82.6 | 86.3454 | 0.1 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 64.994 | 17.1734 | 408726.4409 | 34.0605 | 34.0605 | 96.6195 | 0.2 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 67.3664 | 19.5458 | 465189.0818 | 38.7658 | 38.7658 | 104.0338 | 0.3 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 69.7388 | 21.9181 | 521651.7227 | 43.471 | 43.471 | 111.448 | 0.4 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 72.1112 | 24.2905 | 578114.3635 | 48.1762 | 48.1762 | 118.8622 | 0.5 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 74.4835 | 26.6629 | 634577.0044 | 52.8814 | 52.8814 | 126.2764 | 0.6 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 76.8559 | 29.0353 | 691039.6453 | 57.5866 | 57.5866 | 133.6906 | 0.7 | 80.02 | 25.02 | 945756 | 78.813 | 78.813 | 79.2283 | 31.4077 | 747502.2862 | 62.2919 | 62.2919 | 141.1049 | 0.8 | 80.88 | 25.88 | 978264 | 81.522 | 81.522 | 81.6007 | 33.78 | 803964.9271 | 66.9971 | 66.9971 | 148.5191 | 0.9 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 83.9731 | 36.1524 | 860427.568 | 71.7023 | 71.7023 | 155.9333 | 1 | 82.6 | 27.6 | 1043280 | 86.94 | 86.94 | 86.3454 | 38.5248 | 916890.2089 | 76.4075 | 76.4075 | 163.3475 | 85 | 50 | 33.3774 | 34 | 51.6
7/21/20XX 1:00:00 PM | 0.54167 | 6 | 83.9 | 50.7 | 87.2303 | 105.1128 | 17.8825 | 50 | 83.9 |  | 83.9 | 88.4821 | 0.1 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 65.2077 | 17.387 | 413811.6164 | 34.4843 | 34.4843 | 97.4528 | 0.2 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 67.7937 | 19.9731 | 475359.4329 | 39.6133 | 39.6133 | 105.7003 | 0.3 | 76.97 | 21.97 | 830466 | 69.2055 | 69.2055 | 70.3798 | 22.5591 | 536907.2493 | 44.7423 | 44.7423 | 113.9478 | 0.4 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 72.9658 | 25.1452 | 598455.0658 | 49.8713 | 49.8713 | 122.1953 | 0.5 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 75.5518 | 27.7312 | 660002.8822 | 55.0002 | 55.0002 | 130.4427 | 0.6 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 78.1379 | 30.3173 | 721550.6987 | 60.1292 | 60.1292 | 138.6902 | 0.7 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 80.7239 | 32.9033 | 783098.5151 | 65.2582 | 65.2582 | 146.9377 | 0.8 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 83.31 | 35.4893 | 844646.3316 | 70.3872 | 70.3872 | 155.1852 | 0.9 | 82.91 | 27.91 | 1054998 | 87.9165 | 87.9165 | 85.896 | 38.0754 | 906194.148 | 75.5162 | 75.5162 | 163.4327 | 1 | 83.9 | 28.9 | 1092420 | 91.035 | 91.035 | 88.4821 | 40.6614 | 967741.9645 | 80.6452 | 80.6452 | 171.6802 | 85 | 50 | 34.0321 | 34 | 50.7
7/21/20XX 2:00:00 PM | 0.58333 | 6 | 83.6 | 51.8 | 86.3826 | 104.0885 | 17.7059 | 50 | 83.6 |  | 83.6 | 89.5696 | 0.1 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 65.3164 | 17.4958 | 416399.9989 | 34.7 | 34.7 | 97.574 | 0.2 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 68.0112 | 20.1906 | 480536.1978 | 40.0447 | 40.0447 | 105.9427 | 0.3 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 70.706 | 22.8854 | 544672.3967 | 45.3894 | 45.3894 | 114.3114 | 0.4 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 73.4008 | 25.5802 | 608808.5956 | 50.734 | 50.734 | 122.68 | 0.5 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 76.0956 | 28.275 | 672944.7945 | 56.0787 | 56.0787 | 131.0487 | 0.6 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 78.7904 | 30.9698 | 737080.9934 | 61.4234 | 61.4234 | 139.4174 | 0.7 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 81.4852 | 33.6646 | 801217.1922 | 66.7681 | 66.7681 | 147.7861 | 0.8 | 81.68 | 26.68 | 1008504 | 84.042 | 84.042 | 84.18 | 36.3594 | 865353.3911 | 72.1128 | 72.1128 | 156.1548 | 0.9 | 82.64 | 27.64 | 1044792 | 87.066 | 87.066 | 86.8748 | 39.0542 | 929489.59 | 77.4575 | 77.4575 | 164.5235 | 1 | 83.6 | 28.6 | 1081080 | 90.09 | 90.09 | 89.5696 | 41.749 | 993625.7889 | 82.8021 | 82.8021 | 172.8921 | 85 | 50 | 34.1292 | 34 | 51.8
7/21/20XX 3:00:00 PM | 0.625 | 6 | 83.1 | 54.8 | 84.9846 | 102.3992 | 17.4147 | 50 | 83.1 |  | 83.1 | 93.3436 | 0.1 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 65.6938 | 17.8732 | 425382.1008 | 35.4485 | 35.4485 | 98.165 | 0.2 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 68.766 | 20.9454 | 498500.4016 | 41.5417 | 41.5417 | 107.1247 | 0.3 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 71.8382 | 24.0176 | 571618.7024 | 47.6349 | 47.6349 | 116.0844 | 0.4 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 74.9104 | 27.0898 | 644737.0032 | 53.7281 | 53.7281 | 125.0441 | 0.5 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 77.9826 | 30.162 | 717855.3039 | 59.8213 | 59.8213 | 134.0038 | 0.6 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 81.0548 | 33.2342 | 790973.6047 | 65.9145 | 65.9145 | 142.9635 | 0.7 | 80.37 | 25.37 | 958986 | 79.9155 | 79.9155 | 84.127 | 36.3064 | 864091.9055 | 72.0077 | 72.0077 | 151.9232 | 0.8 | 81.28 | 26.28 | 993384 | 82.782 | 82.782 | 87.1992 | 39.3786 | 937210.2063 | 78.1009 | 78.1009 | 160.8829 | 0.9 | 82.19 | 27.19 | 1027782 | 85.6485 | 85.6485 | 90.2714 | 42.4508 | 1010328.5071 | 84.194 | 84.194 | 169.8425 | 1 | 83.1 | 28.1 | 1062180 | 88.515 | 88.515 | 93.3436 | 45.523 | 1083446.8079 | 90.2872 | 90.2872 | 178.8022 | 85 | 55 | 34.5989 | 34 | 54.8
7/21/20XX 4:00:00 PM | 0.66667 | 6 | 83 | 55 | 84.7072 | 102.0641 | 17.3569 | 50 | 83 |  | 83 | 93.3856 | 0.1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 65.698 | 17.8774 | 425482.1409 | 35.4568 | 35.4568 | 98.1418 | 0.2 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 68.7744 | 20.9538 | 498700.4819 | 41.5584 | 41.5584 | 107.0784 | 0.3 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 71.8508 | 24.0302 | 571918.8228 | 47.6599 | 47.6599 | 116.0149 | 0.4 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 74.9272 | 27.1066 | 645137.1638 | 53.7614 | 53.7614 | 124.9514 | 0.5 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 78.0036 | 30.183 | 718355.5047 | 59.863 | 59.863 | 133.888 | 0.6 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 81.08 | 33.2594 | 791573.8457 | 65.9645 | 65.9645 | 142.8245 | 0.7 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 84.1564 | 36.3358 | 864792.1866 | 72.066 | 72.066 | 151.761 | 0.8 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 87.2328 | 39.4122 | 938010.5276 | 78.1675 | 78.1675 | 160.6975 | 0.9 | 82.1 | 27.1 | 1024380 | 85.365 | 85.365 | 90.3092 | 42.4886 | 1011228.8685 | 84.2691 | 84.2691 | 169.6341 | 1 | 83 | 28 | 1058400 | 88.2 | 88.2 | 93.3856 | 45.565 | 1084447.2094 | 90.3706 | 90.3706 | 178.5706 | 85 | 55 | 34.5809 | 34 | 55
7/21/20XX 5:00:00 PM | 0.70833 | 6 | 81.7 | 56.8 | 81.168 | 97.7883 | 16.6202 | 50 | 81.7 |  | 81.7 | 92.4698 | 0.1 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 65.6064 | 17.7858 | 423302.3814 | 35.2752 | 35.2752 | 97.5507 | 0.2 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 68.5913 | 20.7706 | 494340.9627 | 41.1951 | 41.1951 | 105.8961 | 0.3 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 71.5761 | 23.7554 | 565379.5441 | 47.115 | 47.115 | 114.2415 | 0.4 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 74.5609 | 26.7403 | 636418.1255 | 53.0348 | 53.0348 | 122.5868 | 0.5 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 77.5457 | 29.7251 | 707456.7068 | 58.9547 | 58.9547 | 130.9322 | 0.6 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 80.5305 | 32.7099 | 778495.2882 | 64.8746 | 64.8746 | 139.2776 | 0.7 | 79.39 | 24.39 | 921942 | 76.8285 | 76.8285 | 83.5153 | 35.6947 | 849533.8696 | 70.7945 | 70.7945 | 147.623 | 0.8 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 86.5001 | 38.6795 | 920572.4509 | 76.7144 | 76.7144 | 155.9684 | 0.9 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 89.485 | 41.6643 | 991611.0323 | 82.6343 | 82.6343 | 164.3138 | 1 | 81.7 | 26.7 | 1009260 | 84.105 | 84.105 | 92.4698 | 44.6491 | 1062649.6136 | 88.5541 | 88.5541 | 172.6591 | 80 | 55 | 34.1175 | 34 | 56.8
7/21/20XX 6:00:00 PM | 0.75 | 6 | 80.7 | 60.5 | 94.6002 | 110.7667 | 16.1665 | 60 | 80.7 |  | 80.7 | 95.4085 | 0.1 | 74.67 | 19.67 | 743526 | 61.9605 | 61.9605 | 65.9003 | 18.0797 | 430296.5941 | 35.858 | 35.858 | 97.8185 | 0.2 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 69.179 | 21.3584 | 508329.3882 | 42.3608 | 42.3608 | 106.4318 | 0.3 | 76.01 | 21.01 | 794178 | 66.1815 | 66.1815 | 72.4577 | 24.6371 | 586362.1822 | 48.8635 | 48.8635 | 115.045 | 0.4 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 75.7364 | 27.9158 | 664394.9763 | 55.3662 | 55.3662 | 123.6582 | 0.5 | 77.35 | 22.35 | 844830 | 70.4025 | 70.4025 | 79.0151 | 31.1944 | 742427.7704 | 61.869 | 61.869 | 132.2715 | 0.6 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 82.2938 | 34.4731 | 820460.5645 | 68.3717 | 68.3717 | 140.8847 | 0.7 | 78.69 | 23.69 | 895482 | 74.6235 | 74.6235 | 85.5725 | 37.7518 | 898493.3585 | 74.8744 | 74.8744 | 149.4979 | 0.8 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 88.8511 | 41.0305 | 976526.1526 | 81.3772 | 81.3772 | 158.1112 | 0.9 | 80.03 | 25.03 | 946134 | 78.8445 | 78.8445 | 92.1298 | 44.3092 | 1054558.9467 | 87.8799 | 87.8799 | 166.7244 | 1 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 95.4085 | 47.5879 | 1132591.7408 | 94.3826 | 94.3826 | 175.3376 | 80 | 60 | 34.3325 | 34 | 60.5
7/21/20XX 7:00:00 PM | 0.79167 | 6 | 78.8 | 64.2 | 88.7794 | 103.932 | 15.1526 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/21/20XX 8:00:00 PM | 0.83333 | 6 | 76.8 | 70 | 97.1205 | 111.3712 | 14.2507 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/21/20XX 9:00:00 PM | 0.875 | 6 | 76.1 | 70.9 | 94.8268 | 108.7319 | 13.9051 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/21/20XX 10:00:00 PM | 0.91667 | 6 | 76 | 71.2 | 94.5029 | 108.3592 | 13.8563 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/21/20XX 11:00:00 PM | 0.95833 | 6 | 75.4 | 73.2 | 92.579 | 106.1458 | 13.5668 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/21/20XX 12:00:00 AM | 0 | 7 | 75.5 | 71.6 | 92.8973 | 106.512 | 13.6147 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/22/20XX 1:00:00 AM | 0.041667 | 7 | 75.3 | 72.7 | 92.2616 | 105.7806 | 13.519 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/22/20XX 2:00:00 AM | 0.083333 | 7 | 74.5 | 74.5 | 89.7555 | 102.8978 | 13.1423 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/22/20XX 3:00:00 AM | 0.125 | 7 | 74.1 | 75 | 88.5243 | 101.4817 | 12.9575 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/22/20XX 4:00:00 AM | 0.16667 | 7 | 73.5 | 75.9 | 86.7045 | 99.389 | 12.6844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/22/20XX 5:00:00 AM | 0.20833 | 7 | 73.1 | 76.7 | 85.5092 | 98.0145 | 12.5053 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/22/20XX 6:00:00 AM | 0.25 | 7 | 73.1 | 76.6 | 85.5092 | 98.0145 | 12.5053 | 70 | 73.1 |  | 73.1 | 93.7627 | 0.1 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 65.7357 | 17.9151 | 426379.5562 | 35.5316 | 35.5316 | 95.0981 | 0.2 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 68.8498 | 21.0292 | 500495.3123 | 41.7079 | 41.7079 | 100.9909 | 0.3 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 71.964 | 24.1433 | 574611.0685 | 47.8843 | 47.8843 | 106.8838 | 0.4 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 75.0781 | 27.2574 | 648726.8246 | 54.0606 | 54.0606 | 112.7766 | 0.5 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 78.1922 | 30.3715 | 722842.5808 | 60.2369 | 60.2369 | 118.6694 | 0.6 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 81.3063 | 33.4856 | 796958.337 | 66.4132 | 66.4132 | 124.5622 | 0.7 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 84.4204 | 36.5998 | 871074.0931 | 72.5895 | 72.5895 | 130.455 | 0.8 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 87.5345 | 39.7139 | 945189.8493 | 78.7658 | 78.7658 | 136.3478 | 0.9 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 90.6486 | 42.828 | 1019305.6055 | 84.9421 | 84.9421 | 142.2406 | 1 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 93.7627 | 45.9421 | 1093421.3616 | 91.1184 | 91.1184 | 148.1334 | 75 | 75 | 32.2051 | 32 | 76.6
7/22/20XX 7:00:00 AM | 0.29167 | 7 | 74.7 | 72 | 90.3765 | 103.6122 | 13.2356 | 70 | 74.7 |  | 74.7 | 93.0236 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 65.6618 | 17.8412 | 424620.5597 | 35.385 | 35.385 | 95.4555 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 68.702 | 20.8814 | 496977.3193 | 41.4148 | 41.4148 | 101.7058 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 71.7422 | 23.9216 | 569334.079 | 47.4445 | 47.4445 | 107.956 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 74.7824 | 26.9618 | 641690.8387 | 53.4742 | 53.4742 | 114.2062 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 77.8226 | 30.002 | 714047.5983 | 59.504 | 59.504 | 120.4565 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 80.8628 | 33.0422 | 786404.358 | 65.5337 | 65.5337 | 126.7067 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 83.903 | 36.0824 | 858761.1177 | 71.5634 | 71.5634 | 132.9569 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 86.9432 | 39.1226 | 931117.8774 | 77.5932 | 77.5932 | 139.2072 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 89.9834 | 42.1628 | 1003474.637 | 83.6229 | 83.6229 | 145.4574 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 93.0236 | 45.203 | 1075831.3967 | 89.6526 | 89.6526 | 151.7076 | 75 | 70 | 32.483 | 32 | 72
7/22/20XX 8:00:00 AM | 0.33333 | 7 | 76.3 | 67.1 | 81.5784 | 95.4774 | 13.8991 | 60 | 76.3 |  | 76.3 | 91.4467 | 0.1 | 74.23 | 19.23 | 726894 | 60.5745 | 60.5745 | 65.5041 | 17.6835 | 420867.496 | 35.0723 | 35.0723 | 95.6468 | 0.2 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 68.3866 | 20.566 | 489471.192 | 40.7893 | 40.7893 | 102.0883 | 0.3 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 71.2692 | 23.4485 | 558074.888 | 46.5062 | 46.5062 | 108.5297 | 0.4 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 74.1517 | 26.331 | 626678.5841 | 52.2232 | 52.2232 | 114.9712 | 0.5 | 75.15 | 20.15 | 761670 | 63.4725 | 63.4725 | 77.0342 | 29.2135 | 695282.2801 | 57.9402 | 57.9402 | 121.4127 | 0.6 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 79.9167 | 32.096 | 763885.9761 | 63.6572 | 63.6572 | 127.8542 | 0.7 | 75.61 | 20.61 | 779058 | 64.9215 | 64.9215 | 82.7992 | 34.9786 | 832489.6721 | 69.3741 | 69.3741 | 134.2956 | 0.8 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 85.6817 | 37.8611 | 901093.3681 | 75.0911 | 75.0911 | 140.7371 | 0.9 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 88.5642 | 40.7436 | 969697.0641 | 80.8081 | 80.8081 | 147.1786 | 1 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 91.4467 | 43.6261 | 1038300.7601 | 86.5251 | 86.5251 | 153.6201 | 75 | 65 | 32.6296 | 32 | 67.1
7/22/20XX 9:00:00 AM | 0.375 | 7 | 78.3 | 64 | 87.2982 | 102.1928 | 14.8947 | 60 | 78.3 |  | 78.3 | 93.256 | 0.1 | 74.43 | 19.43 | 734454 | 61.2045 | 61.2045 | 65.6851 | 17.8644 | 425173.6436 | 35.4311 | 35.4311 | 96.6356 | 0.2 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 68.7485 | 20.9279 | 498083.4873 | 41.507 | 41.507 | 104.066 | 0.3 | 75.29 | 20.29 | 766962 | 63.9135 | 63.9135 | 71.8119 | 23.9913 | 570993.3309 | 47.5828 | 47.5828 | 111.4963 | 0.4 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 74.8754 | 27.0548 | 643903.1746 | 53.6586 | 53.6586 | 118.9266 | 0.5 | 76.15 | 21.15 | 799470 | 66.6225 | 66.6225 | 77.9388 | 30.1182 | 716813.0182 | 59.7344 | 59.7344 | 126.3569 | 0.6 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 81.0023 | 33.1816 | 789722.8619 | 65.8102 | 65.8102 | 133.7872 | 0.7 | 77.01 | 22.01 | 831978 | 69.3315 | 69.3315 | 84.0657 | 36.2451 | 862632.7055 | 71.8861 | 71.8861 | 141.2176 | 0.8 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 87.1291 | 39.3085 | 935542.5492 | 77.9619 | 77.9619 | 148.6479 | 0.9 | 77.87 | 22.87 | 864486 | 72.0405 | 72.0405 | 90.1926 | 42.3719 | 1008452.3928 | 84.0377 | 84.0377 | 156.0782 | 1 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 93.256 | 45.4354 | 1081362.2365 | 90.1135 | 90.1135 | 163.5085 | 80 | 65 | 33.4047 | 34 | 64
7/22/20XX 10:00:00 AM | 0.41667 | 7 | 81.1 | 58.4 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 93.2587 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 65.6853 | 17.8647 | 425180.0923 | 35.4317 | 35.4317 | 97.5182 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 68.7491 | 20.9284 | 498096.3846 | 41.508 | 41.508 | 105.831 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 71.8128 | 23.9921 | 571012.6769 | 47.5844 | 47.5844 | 114.1439 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 74.8765 | 27.0558 | 643928.9692 | 53.6607 | 53.6607 | 122.4567 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 77.9402 | 30.1195 | 716845.2615 | 59.7371 | 59.7371 | 130.7696 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 81.0039 | 33.1833 | 789761.5537 | 65.8135 | 65.8135 | 139.0825 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 84.0676 | 36.247 | 862677.846 | 71.8898 | 71.8898 | 147.3953 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 87.1313 | 39.3107 | 935594.1383 | 77.9662 | 77.9662 | 155.7082 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 90.195 | 42.3744 | 1008510.4306 | 84.0425 | 84.0425 | 164.021 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 93.2587 | 45.4381 | 1081426.7229 | 90.1189 | 90.1189 | 172.3339 | 80 | 60 | 34.0937 | 34 | 58.4
7/22/20XX 11:00:00 AM | 0.45833 | 7 | 84.1 | 53.1 | 87.7992 | 105.8003 | 18.0011 | 50 | 84.1 |  | 84.1 | 93.3795 | 0.1 | 75.01 | 20.01 | 756378 | 63.0315 | 63.0315 | 65.6974 | 17.8768 | 425467.5648 | 35.4556 | 35.4556 | 98.4871 | 0.2 | 76.02 | 21.02 | 794556 | 66.213 | 66.213 | 68.7732 | 20.9526 | 498671.3296 | 41.5559 | 41.5559 | 107.7689 | 0.3 | 77.03 | 22.03 | 832734 | 69.3945 | 69.3945 | 71.849 | 24.0284 | 571875.0944 | 47.6563 | 47.6563 | 117.0508 | 0.4 | 78.04 | 23.04 | 870912 | 72.576 | 72.576 | 74.9248 | 27.1042 | 645078.8592 | 53.7566 | 53.7566 | 126.3326 | 0.5 | 79.05 | 24.05 | 909090 | 75.7575 | 75.7575 | 78.0006 | 30.1799 | 718282.624 | 59.8569 | 59.8569 | 135.6144 | 0.6 | 80.06 | 25.06 | 947268 | 78.939 | 78.939 | 81.0764 | 33.2557 | 791486.3888 | 65.9572 | 65.9572 | 144.8962 | 0.7 | 81.07 | 26.07 | 985446 | 82.1205 | 82.1205 | 84.1522 | 36.3315 | 864690.1536 | 72.0575 | 72.0575 | 154.178 | 0.8 | 82.08 | 27.08 | 1023624 | 85.302 | 85.302 | 87.2279 | 39.4073 | 937893.9184 | 78.1578 | 78.1578 | 163.4598 | 0.9 | 83.09 | 28.09 | 1061802 | 88.4835 | 88.4835 | 90.3037 | 42.4831 | 1011097.6832 | 84.2581 | 84.2581 | 172.7416 | 1 | 84.1 | 29.1 | 1099980 | 91.665 | 91.665 | 93.3795 | 45.5589 | 1084301.4481 | 90.3585 | 90.3585 | 182.0235 | 85 | 55 | 34.8504 | 34 | 53.1
7/22/20XX 12:00:00 PM | 0.5 | 7 | 85.7 | 50.8 | 92.4593 | 111.4322 | 18.973 | 50 | 85.7 |  | 85.7 | 93.9771 | 0.1 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 65.7572 | 17.9365 | 426889.7919 | 35.5741 | 35.5741 | 99.1096 | 0.2 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 68.8927 | 21.0721 | 501515.7837 | 41.793 | 41.793 | 109.014 | 0.3 | 77.51 | 22.51 | 850878 | 70.9065 | 70.9065 | 72.0283 | 24.2076 | 576141.7756 | 48.0118 | 48.0118 | 118.9183 | 0.4 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 75.1638 | 27.3432 | 650767.7674 | 54.2306 | 54.2306 | 128.8226 | 0.5 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 78.2994 | 30.4787 | 725393.7593 | 60.4495 | 60.4495 | 138.727 | 0.6 | 81.02 | 26.02 | 983556 | 81.963 | 81.963 | 81.4349 | 33.6143 | 800019.7511 | 66.6683 | 66.6683 | 148.6313 | 0.7 | 82.19 | 27.19 | 1027782 | 85.6485 | 85.6485 | 84.5705 | 36.7498 | 874645.743 | 72.8871 | 72.8871 | 158.5356 | 0.8 | 83.36 | 28.36 | 1072008 | 89.334 | 89.334 | 87.706 | 39.8854 | 949271.7348 | 79.106 | 79.106 | 168.44 | 0.9 | 84.53 | 29.53 | 1116234 | 93.0195 | 93.0195 | 90.8415 | 43.0209 | 1023897.7267 | 85.3248 | 85.3248 | 178.3443 | 1 | 85.7 | 30.7 | 1160460 | 96.705 | 96.705 | 93.9771 | 46.1565 | 1098523.7185 | 91.5436 | 91.5436 | 188.2486 | 85 | 50 | 35.3378 | 36 | 50.8
7/22/20XX 1:00:00 PM | 0.54167 | 7 | 85.6 | 51.1 | 92.1623 | 111.0733 | 18.911 | 50 | 85.6 |  | 85.6 | 94.2425 | 0.1 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 65.7837 | 17.9631 | 427521.4285 | 35.6268 | 35.6268 | 99.1308 | 0.2 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 68.9458 | 21.1252 | 502779.0569 | 41.8983 | 41.8983 | 109.0563 | 0.3 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 72.1079 | 24.2873 | 578036.6854 | 48.1697 | 48.1697 | 118.9817 | 0.4 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 75.27 | 27.4493 | 653294.3139 | 54.4412 | 54.4412 | 128.9072 | 0.5 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 78.4321 | 30.6114 | 728551.9424 | 60.7127 | 60.7127 | 138.8327 | 0.6 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 81.5941 | 33.7735 | 803809.5708 | 66.9841 | 66.9841 | 148.7581 | 0.7 | 82.12 | 27.12 | 1025136 | 85.428 | 85.428 | 84.7562 | 36.9356 | 879067.1993 | 73.2556 | 73.2556 | 158.6836 | 0.8 | 83.28 | 28.28 | 1068984 | 89.082 | 89.082 | 87.9183 | 40.0977 | 954324.8278 | 79.5271 | 79.5271 | 168.6091 | 0.9 | 84.44 | 29.44 | 1112832 | 92.736 | 92.736 | 91.0804 | 43.2598 | 1029582.4562 | 85.7985 | 85.7985 | 178.5345 | 1 | 85.6 | 30.6 | 1156680 | 96.39 | 96.39 | 94.2425 | 46.4219 | 1104840.0847 | 92.07 | 92.07 | 188.46 | 85 | 50 | 35.355 | 36 | 51.1
7/22/20XX 2:00:00 PM | 0.58333 | 7 | 86.9 | 49.1 | 76.4727 | 96.0834 | 19.6107 | 40 | 86.9 |  | 86.9 | 94.3184 | 0.1 | 75.29 | 20.29 | 766962 | 63.9135 | 63.9135 | 65.7913 | 17.9707 | 427702.1717 | 35.6418 | 35.6418 | 99.5553 | 0.2 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 68.961 | 21.1404 | 503140.5435 | 41.9284 | 41.9284 | 109.9054 | 0.3 | 77.87 | 22.87 | 864486 | 72.0405 | 72.0405 | 72.1307 | 24.31 | 578578.9152 | 48.2149 | 48.2149 | 120.2554 | 0.4 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 75.3004 | 27.4797 | 654017.2869 | 54.5014 | 54.5014 | 130.6054 | 0.5 | 80.45 | 25.45 | 962010 | 80.1675 | 80.1675 | 78.47 | 30.6494 | 729455.6587 | 60.788 | 60.788 | 140.9555 | 0.6 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 81.6397 | 33.8191 | 804894.0304 | 67.0745 | 67.0745 | 151.3055 | 0.7 | 83.03 | 28.03 | 1059534 | 88.2945 | 88.2945 | 84.8094 | 36.9888 | 880332.4022 | 73.361 | 73.361 | 161.6555 | 0.8 | 84.32 | 29.32 | 1108296 | 92.358 | 92.358 | 87.9791 | 40.1584 | 955770.7739 | 79.6476 | 79.6476 | 172.0056 | 0.9 | 85.61 | 30.61 | 1157058 | 96.4215 | 96.4215 | 91.1487 | 43.3281 | 1031209.1456 | 85.9341 | 85.9341 | 182.3556 | 1 | 86.9 | 31.9 | 1205820 | 100.485 | 100.485 | 94.3184 | 46.4978 | 1106647.5174 | 92.2206 | 92.2206 | 192.7056 | 85 | 50 | 35.6867 | 36 | 49.1
7/22/20XX 3:00:00 PM | 0.625 | 7 | 85.6 | 52.5 | 92.1623 | 111.0733 | 18.911 | 50 | 85.6 |  | 85.6 | 96.89 | 0.1 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 66.0485 | 18.2278 | 433822.5721 | 36.1519 | 36.1519 | 99.6559 | 0.2 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 69.4753 | 21.6547 | 515381.3442 | 42.9484 | 42.9484 | 110.1064 | 0.3 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 72.9021 | 25.0815 | 596940.1162 | 49.745 | 49.745 | 120.557 | 0.4 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 76.329 | 28.5084 | 678498.8883 | 56.5416 | 56.5416 | 131.0076 | 0.5 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 79.7558 | 31.9352 | 760057.6604 | 63.3381 | 63.3381 | 141.4581 | 0.6 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 83.1827 | 35.362 | 841616.4325 | 70.1347 | 70.1347 | 151.9087 | 0.7 | 82.12 | 27.12 | 1025136 | 85.428 | 85.428 | 86.6095 | 38.7889 | 923175.2046 | 76.9313 | 76.9313 | 162.3593 | 0.8 | 83.28 | 28.28 | 1068984 | 89.082 | 89.082 | 90.0363 | 42.2157 | 1004733.9767 | 83.7278 | 83.7278 | 172.8098 | 0.9 | 84.44 | 29.44 | 1112832 | 92.736 | 92.736 | 93.4632 | 45.6426 | 1086292.7487 | 90.5244 | 90.5244 | 183.2604 | 1 | 85.6 | 30.6 | 1156680 | 96.39 | 96.39 | 96.89 | 49.0694 | 1167851.5208 | 97.321 | 97.321 | 193.711 | 85 | 50 | 35.771 | 36 | 52.5
7/22/20XX 4:00:00 PM | 0.66667 | 7 | 85.2 | 53.2 | 90.982 | 109.6468 | 18.6648 | 50 | 85.2 |  | 85.2 | 96.9548 | 0.1 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 66.0549 | 18.2343 | 433976.6441 | 36.1647 | 36.1647 | 99.5427 | 0.2 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 69.4883 | 21.6676 | 515689.4882 | 42.9741 | 42.9741 | 109.8801 | 0.3 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 72.9216 | 25.1009 | 597402.3322 | 49.7835 | 49.7835 | 120.2175 | 0.4 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 76.3549 | 28.5343 | 679115.1763 | 56.5929 | 56.5929 | 130.5549 | 0.5 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 79.7882 | 31.9676 | 760828.0204 | 63.4023 | 63.4023 | 140.8923 | 0.6 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 83.2215 | 35.4009 | 842540.8645 | 70.2117 | 70.2117 | 151.2297 | 0.7 | 81.84 | 26.84 | 1014552 | 84.546 | 84.546 | 86.6548 | 38.8342 | 924253.7085 | 77.0211 | 77.0211 | 161.5671 | 0.8 | 82.96 | 27.96 | 1056888 | 88.074 | 88.074 | 90.0881 | 42.2675 | 1005966.5526 | 83.8305 | 83.8305 | 171.9045 | 0.9 | 84.08 | 29.08 | 1099224 | 91.602 | 91.602 | 93.5214 | 45.7008 | 1087679.3967 | 90.6399 | 90.6399 | 182.2419 | 1 | 85.2 | 30.2 | 1141560 | 95.13 | 95.13 | 96.9548 | 49.1341 | 1169392.2408 | 97.4494 | 97.4494 | 192.5794 | 85 | 55 | 35.6827 | 36 | 53.2
7/22/20XX 5:00:00 PM | 0.70833 | 7 | 83.9 | 55.5 | 87.2303 | 105.1128 | 17.8825 | 50 | 83.9 |  | 83.9 | 97.0657 | 0.1 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 66.066 | 18.2454 | 434240.63 | 36.1867 | 36.1867 | 99.1552 | 0.2 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 69.5104 | 21.6898 | 516217.4601 | 43.0181 | 43.0181 | 109.1051 | 0.3 | 76.97 | 21.97 | 830466 | 69.2055 | 69.2055 | 72.9548 | 25.1342 | 598194.2901 | 49.8495 | 49.8495 | 119.055 | 0.4 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 76.3993 | 28.5786 | 680171.1202 | 56.6809 | 56.6809 | 129.0049 | 0.5 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 79.8437 | 32.023 | 762147.9502 | 63.5123 | 63.5123 | 138.9548 | 0.6 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 83.2881 | 35.4674 | 844124.7802 | 70.3437 | 70.3437 | 148.9047 | 0.7 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 86.7325 | 38.9118 | 926101.6103 | 77.1751 | 77.1751 | 158.8546 | 0.8 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 90.1769 | 42.3562 | 1008078.4403 | 84.0065 | 84.0065 | 168.8045 | 0.9 | 82.91 | 27.91 | 1054998 | 87.9165 | 87.9165 | 93.6213 | 45.8006 | 1090055.2703 | 90.8379 | 90.8379 | 178.7544 | 1 | 83.9 | 28.9 | 1092420 | 91.035 | 91.035 | 97.0657 | 49.245 | 1172032.1004 | 97.6693 | 97.6693 | 188.7043 | 85 | 55 | 35.3802 | 36 | 55.5
7/22/20XX 6:00:00 PM | 0.75 | 7 | 81.9 | 58.5 | 81.7045 | 98.4363 | 16.7319 | 50 | 81.9 |  | 81.9 | 95.9266 | 0.1 | 74.79 | 19.79 | 748062 | 62.3385 | 62.3385 | 65.9521 | 18.1315 | 431529.547 | 35.9608 | 35.9608 | 98.2993 | 0.2 | 75.58 | 20.58 | 777924 | 64.827 | 64.827 | 69.2826 | 21.462 | 510795.294 | 42.5663 | 42.5663 | 107.3933 | 0.3 | 76.37 | 21.37 | 807786 | 67.3155 | 67.3155 | 72.6131 | 24.7925 | 590061.0411 | 49.1718 | 49.1718 | 116.4873 | 0.4 | 77.16 | 22.16 | 837648 | 69.804 | 69.804 | 75.9436 | 28.123 | 669326.7881 | 55.7772 | 55.7772 | 125.5812 | 0.5 | 77.95 | 22.95 | 867510 | 72.2925 | 72.2925 | 79.2741 | 31.4535 | 748592.5351 | 62.3827 | 62.3827 | 134.6752 | 0.6 | 78.74 | 23.74 | 897372 | 74.781 | 74.781 | 82.6046 | 34.784 | 827858.2821 | 68.9882 | 68.9882 | 143.7692 | 0.7 | 79.53 | 24.53 | 927234 | 77.2695 | 77.2695 | 85.9351 | 38.1145 | 907124.0291 | 75.5937 | 75.5937 | 152.8632 | 0.8 | 80.32 | 25.32 | 957096 | 79.758 | 79.758 | 89.2656 | 41.4449 | 986389.7762 | 82.1991 | 82.1991 | 161.9571 | 0.9 | 81.11 | 26.11 | 986958 | 82.2465 | 82.2465 | 92.5961 | 44.7754 | 1065655.5232 | 88.8046 | 88.8046 | 171.0511 | 1 | 81.9 | 26.9 | 1016820 | 84.735 | 84.735 | 95.9266 | 48.1059 | 1144921.2702 | 95.4101 | 95.4101 | 180.1451 | 80 | 60 | 34.7091 | 34 | 58.5
7/22/20XX 7:00:00 PM | 0.79167 | 7 | 80.8 | 61.5 | 94.9151 | 111.1364 | 16.2213 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/22/20XX 8:00:00 PM | 0.83333 | 7 | 79.8 | 62.2 | 91.8048 | 107.4842 | 15.6795 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/22/20XX 9:00:00 PM | 0.875 | 7 | 78.5 | 68.1 | 87.8882 | 102.8856 | 14.9974 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/22/20XX 10:00:00 PM | 0.91667 | 7 | 78.4 | 67.8 | 87.5927 | 102.5387 | 14.946 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/22/20XX 11:00:00 PM | 0.95833 | 7 | 77.3 | 70.4 | 98.7873 | 113.2894 | 14.5021 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/22/20XX 12:00:00 AM | 0 | 1 | 76.9 | 70.9 | 97.452 | 111.7526 | 14.3007 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/23/20XX 1:00:00 AM | 0.041667 | 1 | 76.4 | 71.4 | 95.8042 | 109.8565 | 14.0523 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/23/20XX 2:00:00 AM | 0.083333 | 1 | 75.5 | 73.6 | 92.8973 | 106.512 | 13.6147 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/23/20XX 3:00:00 AM | 0.125 | 1 | 75.1 | 74.5 | 91.6296 | 105.0536 | 13.424 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/23/20XX 4:00:00 AM | 0.16667 | 1 | 75.2 | 75.7 | 91.9451 | 105.4166 | 13.4714 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/23/20XX 5:00:00 AM | 0.20833 | 1 | 74.6 | 76.6 | 90.0655 | 103.2545 | 13.1889 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/23/20XX 6:00:00 AM | 0.25 | 1 | 74.4 | 76.4 | 89.4463 | 102.5422 | 13.0959 | 70 | 74.4 |  | 74.4 | 97.8277 | 0.1 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 66.1422 | 18.3216 | 436054.2046 | 36.3379 | 36.3379 | 96.3139 | 0.2 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 69.6628 | 21.8422 | 519844.6091 | 43.3204 | 43.3204 | 103.4224 | 0.3 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 73.1834 | 25.3628 | 603635.0137 | 50.3029 | 50.3029 | 110.5309 | 0.4 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 76.7041 | 28.8834 | 687425.4182 | 57.2855 | 57.2855 | 117.6395 | 0.5 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 80.2247 | 32.404 | 771215.8228 | 64.268 | 64.268 | 124.748 | 0.6 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 83.7453 | 35.9246 | 855006.2273 | 71.2505 | 71.2505 | 131.8565 | 0.7 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 87.2659 | 39.4452 | 938796.6319 | 78.2331 | 78.2331 | 138.9651 | 0.8 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 90.7865 | 42.9658 | 1022587.0364 | 85.2156 | 85.2156 | 146.0736 | 0.9 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 94.3071 | 46.4864 | 1106377.441 | 92.1981 | 92.1981 | 153.1821 | 1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 97.8277 | 50.0071 | 1190167.8455 | 99.1807 | 99.1807 | 160.2907 | 75 | 75 | 33.1608 | 34 | 76.4
7/23/20XX 7:00:00 AM | 0.29167 | 1 | 75.5 | 75.3 | 92.8973 | 106.512 | 13.6147 | 70 | 75.5 |  | 75.5 | 100.1131 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 66.3708 | 18.5501 | 441493.504 | 36.7911 | 36.7911 | 97.1136 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 70.1199 | 22.2993 | 530723.208 | 44.2269 | 44.2269 | 105.0219 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 73.8691 | 26.0484 | 619952.912 | 51.6627 | 51.6627 | 112.9302 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 77.6182 | 29.7976 | 709182.616 | 59.0986 | 59.0986 | 120.8386 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 81.3674 | 33.5467 | 798412.32 | 66.5344 | 66.5344 | 128.7469 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 85.1165 | 37.2959 | 887642.024 | 73.9702 | 73.9702 | 136.6552 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 88.8657 | 41.045 | 976871.728 | 81.406 | 81.406 | 144.5635 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 92.6148 | 44.7942 | 1066101.432 | 88.8418 | 88.8418 | 152.4718 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 96.364 | 48.5433 | 1155331.136 | 96.2776 | 96.2776 | 160.3801 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 100.1131 | 52.2925 | 1244560.84 | 103.7134 | 103.7134 | 168.2884 | 75 | 75 | 33.7894 | 34 | 75.3
7/23/20XX 8:00:00 AM | 0.33333 | 1 | 76.6 | 72.2 | 96.4605 | 110.6117 | 14.1512 | 70 | 76.6 |  | 76.6 | 99.5737 | 0.1 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 66.3168 | 18.4962 | 440209.7701 | 36.6841 | 36.6841 | 97.3531 | 0.2 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 70.0121 | 22.1914 | 528155.7402 | 44.013 | 44.013 | 105.501 | 0.3 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 73.7073 | 25.8866 | 616101.7103 | 51.3418 | 51.3418 | 113.6488 | 0.4 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 77.4025 | 29.5818 | 704047.6805 | 58.6706 | 58.6706 | 121.7966 | 0.5 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 81.0977 | 33.277 | 791993.6506 | 65.9995 | 65.9995 | 129.9445 | 0.6 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 84.7929 | 36.9723 | 879939.6207 | 73.3283 | 73.3283 | 138.0923 | 0.7 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 88.4881 | 40.6675 | 967885.5908 | 80.6571 | 80.6571 | 146.2401 | 0.8 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 92.1833 | 44.3627 | 1055831.5609 | 87.986 | 87.986 | 154.388 | 0.9 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 95.8785 | 48.0579 | 1143777.531 | 95.3148 | 95.3148 | 162.5358 | 1 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 99.5737 | 51.7531 | 1231723.5011 | 102.6436 | 102.6436 | 170.6836 | 75 | 70 | 33.9759 | 34 | 72.2
7/23/20XX 9:00:00 AM | 0.375 | 1 | 78.5 | 67.7 | 87.8882 | 102.8856 | 14.9974 | 60 | 78.5 |  | 78.5 | 99.4362 | 0.1 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 66.3031 | 18.4825 | 439882.3713 | 36.6569 | 36.6569 | 97.9244 | 0.2 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 69.9845 | 22.1639 | 527500.9426 | 43.9584 | 43.9584 | 106.6434 | 0.3 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 73.666 | 25.8454 | 615119.5139 | 51.26 | 51.26 | 115.3625 | 0.4 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 77.3474 | 29.5268 | 702738.0852 | 58.5615 | 58.5615 | 124.0815 | 0.5 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 81.0289 | 33.2083 | 790356.6565 | 65.8631 | 65.8631 | 132.8006 | 0.6 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 84.7103 | 36.8897 | 877975.2278 | 73.1646 | 73.1646 | 141.5196 | 0.7 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 88.3918 | 40.5712 | 965593.7991 | 80.4661 | 80.4661 | 150.2386 | 0.8 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 92.0733 | 44.2526 | 1053212.3704 | 87.7677 | 87.7677 | 158.9577 | 0.9 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 95.7547 | 47.9341 | 1140830.9417 | 95.0692 | 95.0692 | 167.6767 | 1 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 99.4362 | 51.6155 | 1228449.513 | 102.3708 | 102.3708 | 176.3958 | 80 | 70 | 34.4224 | 34 | 67.7
7/23/20XX 10:00:00 AM | 0.41667 | 1 | 80.7 | 64.1 | 94.6002 | 110.7667 | 16.1665 | 60 | 80.7 |  | 80.7 | 101.2284 | 0.1 | 74.67 | 19.67 | 743526 | 61.9605 | 61.9605 | 66.4823 | 18.6617 | 444148.0128 | 37.0123 | 37.0123 | 98.9728 | 0.2 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 70.343 | 22.5224 | 536032.2257 | 44.6694 | 44.6694 | 108.7404 | 0.3 | 76.01 | 21.01 | 794178 | 66.1815 | 66.1815 | 74.2037 | 26.383 | 627916.4385 | 52.3264 | 52.3264 | 118.5079 | 0.4 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 78.0644 | 30.2437 | 719800.6514 | 59.9834 | 59.9834 | 128.2754 | 0.5 | 77.35 | 22.35 | 844830 | 70.4025 | 70.4025 | 81.925 | 34.1044 | 811684.8642 | 67.6404 | 67.6404 | 138.0429 | 0.6 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 85.7857 | 37.9651 | 903569.0771 | 75.2974 | 75.2974 | 147.8104 | 0.7 | 78.69 | 23.69 | 895482 | 74.6235 | 74.6235 | 89.6464 | 41.8258 | 995453.2899 | 82.9544 | 82.9544 | 157.5779 | 0.8 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 93.5071 | 45.6864 | 1087337.5028 | 90.6115 | 90.6115 | 167.3455 | 0.9 | 80.03 | 25.03 | 946134 | 78.8445 | 78.8445 | 97.3678 | 49.5471 | 1179221.7156 | 98.2685 | 98.2685 | 177.113 | 1 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 101.2284 | 53.4078 | 1271105.9285 | 105.9255 | 105.9255 | 186.8805 | 80 | 65 | 35.2454 | 36 | 64.1
7/23/20XX 11:00:00 AM | 0.45833 | 1 | 82 | 62.6 | 98.7617 | 115.6533 | 16.8916 | 60 | 82 |  | 82 | 103.1535 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 66.6748 | 18.8542 | 448729.7157 | 37.3941 | 37.3941 | 99.7641 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 70.728 | 22.9074 | 545195.6315 | 45.433 | 45.433 | 110.323 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 74.7812 | 26.9606 | 641661.5472 | 53.4718 | 53.4718 | 120.8818 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 78.8344 | 31.0138 | 738127.4629 | 61.5106 | 61.5106 | 131.4406 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 82.8876 | 35.0669 | 834593.3787 | 69.5494 | 69.5494 | 141.9994 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 86.9408 | 39.1201 | 931059.2944 | 77.5883 | 77.5883 | 152.5583 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 90.994 | 43.1733 | 1027525.2101 | 85.6271 | 85.6271 | 163.1171 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 95.0472 | 47.2265 | 1123991.1258 | 93.6659 | 93.6659 | 173.6759 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 99.1003 | 51.2797 | 1220457.0416 | 101.7048 | 101.7048 | 184.2348 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 103.1535 | 55.3329 | 1316922.9573 | 109.7436 | 109.7436 | 194.7936 | 80 | 65 | 35.8678 | 36 | 62.6
7/23/20XX 12:00:00 PM | 0.5 | 1 | 82.6 | 63.8 | 100.7325 | 117.9676 | 17.2351 | 60 | 82.6 |  | 82.6 | 107.2818 | 0.1 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 67.0876 | 19.267 | 458555.01 | 38.2129 | 38.2129 | 100.7719 | 0.2 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 71.5537 | 23.733 | 564846.22 | 47.0705 | 47.0705 | 112.3385 | 0.3 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 76.0197 | 28.1991 | 671137.4299 | 55.9281 | 55.9281 | 123.9051 | 0.4 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 80.4857 | 32.6651 | 777428.6399 | 64.7857 | 64.7857 | 135.4717 | 0.5 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 84.9517 | 37.1311 | 883719.8499 | 73.6433 | 73.6433 | 147.0383 | 0.6 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 89.4177 | 41.5971 | 990011.0599 | 82.5009 | 82.5009 | 158.6049 | 0.7 | 80.02 | 25.02 | 945756 | 78.813 | 78.813 | 93.8838 | 46.0631 | 1096302.2698 | 91.3585 | 91.3585 | 170.1715 | 0.8 | 80.88 | 25.88 | 978264 | 81.522 | 81.522 | 98.3498 | 50.5291 | 1202593.4798 | 100.2161 | 100.2161 | 181.7381 | 0.9 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 102.8158 | 54.9952 | 1308884.6898 | 109.0737 | 109.0737 | 193.3047 | 1 | 82.6 | 27.6 | 1043280 | 86.94 | 86.94 | 107.2818 | 59.4612 | 1415175.8998 | 117.9313 | 117.9313 | 204.8713 | 85 | 65 | 36.6638 | 36 | 63.8
7/23/20XX 1:00:00 PM | 0.54167 | 1 | 83.2 | 63.6 | 102.7353 | 120.3195 | 17.5842 | 60 | 83.2 |  | 83.2 | 109.0656 | 0.1 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 67.266 | 19.4454 | 462800.4302 | 38.5667 | 38.5667 | 101.3147 | 0.2 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 71.9104 | 24.0898 | 573337.0603 | 47.7781 | 47.7781 | 113.4241 | 0.3 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 76.5548 | 28.7342 | 683873.6905 | 56.9895 | 56.9895 | 125.5335 | 0.4 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 81.1992 | 33.3786 | 794410.3207 | 66.2009 | 66.2009 | 137.6429 | 0.5 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 85.8436 | 38.023 | 904946.9508 | 75.4122 | 75.4122 | 149.7522 | 0.6 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 90.488 | 42.6674 | 1015483.581 | 84.6236 | 84.6236 | 161.8616 | 0.7 | 80.44 | 25.44 | 961632 | 80.136 | 80.136 | 95.1324 | 47.3118 | 1126020.2112 | 93.835 | 93.835 | 173.971 | 0.8 | 81.36 | 26.36 | 996408 | 83.034 | 83.034 | 99.7768 | 51.9562 | 1236556.8413 | 103.0464 | 103.0464 | 186.0804 | 0.9 | 82.28 | 27.28 | 1031184 | 85.932 | 85.932 | 104.4212 | 56.6006 | 1347093.4715 | 112.2578 | 112.2578 | 198.1898 | 1 | 83.2 | 28.2 | 1065960 | 88.83 | 88.83 | 109.0656 | 61.245 | 1457630.1016 | 121.4692 | 121.4692 | 210.2992 | 85 | 65 | 37.0919 | 36 | 63.6
7/23/20XX 2:00:00 PM | 0.58333 | 1 | 83.2 | 63.1 | 102.7353 | 120.3195 | 17.5842 | 60 | 83.2 |  | 83.2 | 108.1864 | 0.1 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 67.1781 | 19.3575 | 460707.9111 | 38.3923 | 38.3923 | 101.1403 | 0.2 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 71.7346 | 23.914 | 569152.0222 | 47.4293 | 47.4293 | 113.0753 | 0.3 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 76.2911 | 28.4704 | 677596.1333 | 56.4663 | 56.4663 | 125.0103 | 0.4 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 80.8475 | 33.0269 | 786040.2444 | 65.5034 | 65.5034 | 136.9454 | 0.5 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 85.404 | 37.5834 | 894484.3555 | 74.5404 | 74.5404 | 148.8804 | 0.6 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 89.9605 | 42.1399 | 1002928.4666 | 83.5774 | 83.5774 | 160.8154 | 0.7 | 80.44 | 25.44 | 961632 | 80.136 | 80.136 | 94.517 | 46.6963 | 1111372.5777 | 92.6144 | 92.6144 | 172.7504 | 0.8 | 81.36 | 26.36 | 996408 | 83.034 | 83.034 | 99.0734 | 51.2528 | 1219816.6887 | 101.6514 | 101.6514 | 184.6854 | 0.9 | 82.28 | 27.28 | 1031184 | 85.932 | 85.932 | 103.6299 | 55.8093 | 1328260.7998 | 110.6884 | 110.6884 | 196.6204 | 1 | 83.2 | 28.2 | 1065960 | 88.83 | 88.83 | 108.1864 | 60.3658 | 1436704.9109 | 119.7254 | 119.7254 | 208.5554 | 85 | 65 | 36.9539 | 36 | 63.1
7/23/20XX 3:00:00 PM | 0.625 | 1 | 83 | 63.3 | 102.0641 | 119.5313 | 17.4672 | 60 | 83 |  | 83 | 107.8283 | 0.1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 67.1423 | 19.3217 | 459855.6087 | 38.3213 | 38.3213 | 101.0063 | 0.2 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 71.663 | 23.8423 | 567447.4175 | 47.2873 | 47.2873 | 112.8073 | 0.3 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 76.1836 | 28.363 | 675039.2262 | 56.2533 | 56.2533 | 124.6083 | 0.4 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 80.7043 | 32.8837 | 782631.0349 | 65.2193 | 65.2193 | 136.4093 | 0.5 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 85.225 | 37.4043 | 890222.8436 | 74.1852 | 74.1852 | 148.2102 | 0.6 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 89.7456 | 41.925 | 997814.6524 | 83.1512 | 83.1512 | 160.0112 | 0.7 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 94.2663 | 46.4456 | 1105406.4611 | 92.1172 | 92.1172 | 171.8122 | 0.8 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 98.7869 | 50.9663 | 1212998.2698 | 101.0832 | 101.0832 | 183.6132 | 0.9 | 82.1 | 27.1 | 1024380 | 85.365 | 85.365 | 103.3076 | 55.487 | 1320590.0785 | 110.0492 | 110.0492 | 195.4142 | 1 | 83 | 28 | 1058400 | 88.2 | 88.2 | 107.8283 | 60.0076 | 1428181.8873 | 119.0152 | 119.0152 | 207.2152 | 85 | 65 | 36.8483 | 36 | 63.3
7/23/20XX 4:00:00 PM | 0.66667 | 1 | 82.2 | 65.8 | 99.4151 | 116.4206 | 17.0055 | 60 | 82.2 |  | 82.2 | 109.2783 | 0.1 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 67.2873 | 19.4667 | 463306.5854 | 38.6089 | 38.6089 | 101.0419 | 0.2 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 71.953 | 24.1323 | 574349.3708 | 47.8624 | 47.8624 | 112.8784 | 0.3 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 76.6186 | 28.798 | 685392.1562 | 57.116 | 57.116 | 124.715 | 0.4 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 81.2843 | 33.4637 | 796434.9416 | 66.3696 | 66.3696 | 136.5516 | 0.5 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 85.9499 | 38.1293 | 907477.727 | 75.6231 | 75.6231 | 148.3881 | 0.6 | 78.92 | 23.92 | 904176 | 75.348 | 75.348 | 90.6156 | 42.795 | 1018520.5124 | 84.8767 | 84.8767 | 160.2247 | 0.7 | 79.74 | 24.74 | 935172 | 77.931 | 77.931 | 95.2813 | 47.4606 | 1129563.2978 | 94.1303 | 94.1303 | 172.0613 | 0.8 | 80.56 | 25.56 | 966168 | 80.514 | 80.514 | 99.9469 | 52.1263 | 1240606.0832 | 103.3838 | 103.3838 | 183.8978 | 0.9 | 81.38 | 26.38 | 997164 | 83.097 | 83.097 | 104.6126 | 56.792 | 1351648.8686 | 112.6374 | 112.6374 | 195.7344 | 1 | 82.2 | 27.2 | 1028160 | 85.68 | 85.68 | 109.2783 | 61.4576 | 1462691.654 | 121.891 | 121.891 | 207.571 | 80 | 65 | 36.8784 | 36 | 65.8
7/23/20XX 5:00:00 PM | 0.70833 | 1 | 82.5 | 64.7 | 100.4018 | 117.5792 | 17.1774 | 60 | 82.5 |  | 82.5 | 108.4752 | 0.1 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 67.207 | 19.3864 | 461395.2798 | 38.4496 | 38.4496 | 100.9771 | 0.2 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 71.7923 | 23.9717 | 570526.7597 | 47.5439 | 47.5439 | 112.7489 | 0.3 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 76.3777 | 28.5571 | 679658.2395 | 56.6382 | 56.6382 | 124.5207 | 0.4 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 80.9631 | 33.1424 | 788789.7194 | 65.7325 | 65.7325 | 136.2925 | 0.5 | 78.25 | 23.25 | 878850 | 73.2375 | 73.2375 | 85.5484 | 37.7278 | 897921.1992 | 74.8268 | 74.8268 | 148.0643 | 0.6 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 90.1338 | 42.3131 | 1007052.6791 | 83.9211 | 83.9211 | 159.8361 | 0.7 | 79.95 | 24.95 | 943110 | 78.5925 | 78.5925 | 94.7191 | 46.8985 | 1116184.1589 | 93.0153 | 93.0153 | 171.6078 | 0.8 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 99.3045 | 51.4839 | 1225315.6388 | 102.1096 | 102.1096 | 183.3796 | 0.9 | 81.65 | 26.65 | 1007370 | 83.9475 | 83.9475 | 103.8898 | 56.0692 | 1334447.1186 | 111.2039 | 111.2039 | 195.1514 | 1 | 82.5 | 27.5 | 1039500 | 86.625 | 86.625 | 108.4752 | 60.6546 | 1443578.5985 | 120.2982 | 120.2982 | 206.9232 | 80 | 65 | 36.8264 | 36 | 64.7
7/23/20XX 6:00:00 PM | 0.75 | 1 | 81.9 | 62.9 | 98.4363 | 115.2712 | 16.8349 | 60 | 81.9 |  | 81.9 | 103.3185 | 0.1 | 74.79 | 19.79 | 748062 | 62.3385 | 62.3385 | 66.6913 | 18.8707 | 449122.2686 | 37.4269 | 37.4269 | 99.7654 | 0.2 | 75.58 | 20.58 | 777924 | 64.827 | 64.827 | 70.761 | 22.9404 | 545980.7372 | 45.4984 | 45.4984 | 110.3254 | 0.3 | 76.37 | 21.37 | 807786 | 67.3155 | 67.3155 | 74.8307 | 27.0101 | 642839.2057 | 53.5699 | 53.5699 | 120.8854 | 0.4 | 77.16 | 22.16 | 837648 | 69.804 | 69.804 | 78.9004 | 31.0797 | 739697.6743 | 61.6415 | 61.6415 | 131.4455 | 0.5 | 77.95 | 22.95 | 867510 | 72.2925 | 72.2925 | 82.9701 | 35.1494 | 836556.1429 | 69.713 | 69.713 | 142.0055 | 0.6 | 78.74 | 23.74 | 897372 | 74.781 | 74.781 | 87.0397 | 39.2191 | 933414.6115 | 77.7846 | 77.7846 | 152.5656 | 0.7 | 79.53 | 24.53 | 927234 | 77.2695 | 77.2695 | 91.1094 | 43.2888 | 1030273.08 | 85.8561 | 85.8561 | 163.1256 | 0.8 | 80.32 | 25.32 | 957096 | 79.758 | 79.758 | 95.1791 | 47.3585 | 1127131.5486 | 93.9276 | 93.9276 | 173.6856 | 0.9 | 81.11 | 26.11 | 986958 | 82.2465 | 82.2465 | 99.2488 | 51.4282 | 1223990.0172 | 101.9992 | 101.9992 | 184.2457 | 1 | 81.9 | 26.9 | 1016820 | 84.735 | 84.735 | 103.3185 | 55.4978 | 1320848.4858 | 110.0707 | 110.0707 | 194.8057 | 80 | 65 | 35.869 | 36 | 62.9
7/23/20XX 7:00:00 PM | 0.79167 | 1 | 81.3 | 62.6 | 96.5026 | 113.0005 | 16.4979 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/23/20XX 8:00:00 PM | 0.83333 | 1 | 78.4 | 70 | 102.5387 | 117.6073 | 15.0686 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/23/20XX 9:00:00 PM | 0.875 | 1 | 77.2 | 72.7 | 98.452 | 112.9035 | 14.4515 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/23/20XX 10:00:00 PM | 0.91667 | 1 | 76.9 | 73.1 | 97.452 | 111.7526 | 14.3007 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/23/20XX 11:00:00 PM | 0.95833 | 1 | 76.5 | 72.7 | 96.1318 | 110.2335 | 14.1017 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/23/20XX 12:00:00 AM | 0 | 2 | 76.4 | 72.5 | 95.8042 | 109.8565 | 14.0523 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/24/20XX 1:00:00 AM | 0.041667 | 2 | 75.8 | 73.4 | 93.8579 | 107.6171 | 13.7592 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/24/20XX 2:00:00 AM | 0.083333 | 2 | 75.7 | 73.8 | 93.5368 | 107.2477 | 13.7109 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/24/20XX 3:00:00 AM | 0.125 | 2 | 75.2 | 73.9 | 91.9451 | 105.4166 | 13.4714 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/24/20XX 4:00:00 AM | 0.16667 | 2 | 74.8 | 74.9 | 90.6884 | 103.9709 | 13.2825 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/24/20XX 5:00:00 AM | 0.20833 | 2 | 74.1 | 76.6 | 88.5243 | 101.4817 | 12.9575 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/24/20XX 6:00:00 AM | 0.25 | 2 | 74.6 | 76.1 | 90.0655 | 103.2545 | 13.1889 | 70 | 74.6 |  | 74.6 | 98.1108 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 66.1705 | 18.3499 | 436727.9466 | 36.394 | 36.394 | 96.433 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 69.7195 | 21.8988 | 521192.0932 | 43.4327 | 43.4327 | 103.6607 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 73.2684 | 25.4477 | 605656.2398 | 50.4714 | 50.4714 | 110.8884 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 76.8173 | 28.9967 | 690120.3864 | 57.51 | 57.51 | 118.116 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 80.3662 | 32.5456 | 774584.5331 | 64.5487 | 64.5487 | 125.3437 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 83.9151 | 36.0945 | 859048.6797 | 71.5874 | 71.5874 | 132.5714 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 87.464 | 39.6434 | 943512.8263 | 78.6261 | 78.6261 | 139.7991 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 91.0129 | 43.1923 | 1027976.9729 | 85.6647 | 85.6647 | 147.0267 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 94.5619 | 46.7412 | 1112441.1195 | 92.7034 | 92.7034 | 154.2544 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 98.1108 | 50.2901 | 1196905.2661 | 99.7421 | 99.7421 | 161.4821 | 75 | 75 | 33.2544 | 34 | 76.1
7/24/20XX 7:00:00 AM | 0.29167 | 2 | 75.3 | 74.8 | 92.2616 | 105.7806 | 13.519 | 70 | 75.3 |  | 75.3 | 98.7507 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 66.2345 | 18.4139 | 438251.0692 | 36.5209 | 36.5209 | 96.7804 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 69.8475 | 22.0268 | 524238.3383 | 43.6865 | 43.6865 | 104.3555 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 73.4604 | 25.6397 | 610225.6075 | 50.8521 | 50.8521 | 111.9306 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 77.0733 | 29.2526 | 696212.8766 | 58.0177 | 58.0177 | 119.5057 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 80.6862 | 32.8656 | 782200.1458 | 65.1833 | 65.1833 | 127.0808 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 84.2991 | 36.4785 | 868187.4149 | 72.349 | 72.349 | 134.656 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 87.912 | 40.0914 | 954174.6841 | 79.5146 | 79.5146 | 142.2311 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 91.5249 | 43.7043 | 1040161.9532 | 86.6802 | 86.6802 | 149.8062 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 95.1378 | 47.3172 | 1126149.2224 | 93.8458 | 93.8458 | 157.3813 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 98.7507 | 50.9301 | 1212136.4915 | 101.0114 | 101.0114 | 164.9564 | 75 | 75 | 33.5269 | 34 | 74.8
7/24/20XX 8:00:00 AM | 0.33333 | 2 | 77 | 69.9 | 83.5433 | 97.7844 | 14.241 | 60 | 77 |  | 77 | 97.642 | 0.1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 66.1237 | 18.303 | 435612.1743 | 36.301 | 36.301 | 97.096 | 0.2 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 69.6257 | 21.8051 | 518960.5486 | 43.2467 | 43.2467 | 104.9867 | 0.3 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 73.1277 | 25.3071 | 602308.9229 | 50.1924 | 50.1924 | 112.8774 | 0.4 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 76.6298 | 28.8091 | 685657.2972 | 57.1381 | 57.1381 | 120.7681 | 0.5 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 80.1318 | 32.3112 | 769005.6715 | 64.0838 | 64.0838 | 128.6588 | 0.6 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 83.6338 | 35.8132 | 852354.0458 | 71.0295 | 71.0295 | 136.5495 | 0.7 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 87.1359 | 39.3152 | 935702.4201 | 77.9752 | 77.9752 | 144.4402 | 0.8 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 90.6379 | 42.8173 | 1019050.7944 | 84.9209 | 84.9209 | 152.3309 | 0.9 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 94.1399 | 46.3193 | 1102399.1687 | 91.8666 | 91.8666 | 160.2216 | 1 | 77 | 22 | 831600 | 69.3 | 69.3 | 97.642 | 49.8213 | 1185747.5429 | 98.8123 | 98.8123 | 168.1123 | 75 | 70 | 33.7719 | 34 | 69.9
7/24/20XX 9:00:00 AM | 0.375 | 2 | 78 | 66.6 | 86.4193 | 101.161 | 14.7417 | 60 | 78 |  | 78 | 96.1488 | 0.1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 65.9744 | 18.1537 | 432058.5729 | 36.0049 | 36.0049 | 97.1149 | 0.2 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 69.3271 | 21.5064 | 511853.3458 | 42.6544 | 42.6544 | 105.0244 | 0.3 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 72.6798 | 24.8592 | 591648.1186 | 49.304 | 49.304 | 112.934 | 0.4 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 76.0325 | 28.2119 | 671442.8915 | 55.9536 | 55.9536 | 120.8436 | 0.5 | 76 | 21 | 793800 | 66.15 | 66.15 | 79.3852 | 31.5646 | 751237.6644 | 62.6031 | 62.6031 | 128.7531 | 0.6 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 82.738 | 34.9173 | 831032.4373 | 69.2527 | 69.2527 | 136.6627 | 0.7 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 86.0907 | 38.2701 | 910827.2101 | 75.9023 | 75.9023 | 144.5723 | 0.8 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 89.4434 | 41.6228 | 990621.983 | 82.5518 | 82.5518 | 152.4818 | 0.9 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 92.7961 | 44.9755 | 1070416.7559 | 89.2014 | 89.2014 | 160.3914 | 1 | 78 | 23 | 869400 | 72.45 | 72.45 | 96.1488 | 48.3282 | 1150211.5288 | 95.851 | 95.851 | 168.301 | 80 | 65 | 33.7842 | 34 | 66.6
7/24/20XX 10:00:00 AM | 0.41667 | 2 | 79.8 | 62.7 | 91.8048 | 107.4842 | 15.6795 | 60 | 79.8 |  | 79.8 | 96.0382 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 65.9633 | 18.1427 | 431795.2819 | 35.9829 | 35.9829 | 97.6599 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 69.305 | 21.4843 | 511326.7637 | 42.6106 | 42.6106 | 106.1146 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 72.6466 | 24.826 | 590858.2456 | 49.2382 | 49.2382 | 114.5692 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 75.9883 | 28.1676 | 670389.7274 | 55.8658 | 55.8658 | 123.0238 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 79.3299 | 31.5093 | 749921.2093 | 62.4934 | 62.4934 | 131.4784 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 82.6716 | 34.851 | 829452.6911 | 69.1211 | 69.1211 | 139.9331 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 86.0132 | 38.1926 | 908984.173 | 75.7487 | 75.7487 | 148.3877 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 89.3549 | 41.5343 | 988515.6548 | 82.3763 | 82.3763 | 156.8423 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 92.6966 | 44.8759 | 1068047.1367 | 89.0039 | 89.0039 | 165.2969 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 96.0382 | 48.2176 | 1147578.6185 | 95.6316 | 95.6316 | 173.7516 | 80 | 65 | 34.2098 | 34 | 62.7
7/24/20XX 11:00:00 AM | 0.45833 | 2 | 81 | 58.6 | 79.313 | 95.5475 | 16.2344 | 50 | 81 |  | 81 | 93.2747 | 0.1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 65.6869 | 17.8663 | 425218.023 | 35.4348 | 35.4348 | 97.4898 | 0.2 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 68.7522 | 20.9316 | 498172.2459 | 41.5144 | 41.5144 | 105.7744 | 0.3 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 71.8175 | 23.9969 | 571126.4689 | 47.5939 | 47.5939 | 114.0589 | 0.4 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 74.8828 | 27.0622 | 644080.6918 | 53.6734 | 53.6734 | 122.3434 | 0.5 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 77.9481 | 30.1275 | 717034.9148 | 59.7529 | 59.7529 | 130.6279 | 0.6 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 81.0135 | 33.1928 | 789989.1377 | 65.8324 | 65.8324 | 138.9124 | 0.7 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 84.0788 | 36.2581 | 862943.3607 | 71.9119 | 71.9119 | 147.1969 | 0.8 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 87.1441 | 39.3234 | 935897.5837 | 77.9915 | 77.9915 | 155.4815 | 0.9 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 90.2094 | 42.3887 | 1008851.8066 | 84.071 | 84.071 | 163.766 | 1 | 81 | 26 | 982800 | 81.9 | 81.9 | 93.2747 | 45.454 | 1081806.0296 | 90.1505 | 90.1505 | 172.0505 | 80 | 60 | 34.0716 | 34 | 58.6
7/24/20XX 12:00:00 PM | 0.5 | 2 | 82 | 56.8 | 81.9738 | 98.7617 | 16.7879 | 50 | 82 |  | 82 | 93.3896 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 65.6984 | 17.8778 | 425491.5235 | 35.4576 | 35.4576 | 97.8276 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 68.7752 | 20.9546 | 498719.247 | 41.5599 | 41.5599 | 106.4499 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 71.852 | 24.0314 | 571946.9704 | 47.6622 | 47.6622 | 115.0722 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 74.9288 | 27.1082 | 645174.6939 | 53.7646 | 53.7646 | 123.6946 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 78.0056 | 30.185 | 718402.4174 | 59.8669 | 59.8669 | 132.3169 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 81.0824 | 33.2618 | 791630.1409 | 65.9692 | 65.9692 | 140.9392 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 84.1592 | 36.3386 | 864857.8643 | 72.0715 | 72.0715 | 149.5615 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 87.236 | 39.4154 | 938085.5878 | 78.1738 | 78.1738 | 158.1838 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 90.3128 | 42.4922 | 1011313.3113 | 84.2761 | 84.2761 | 166.8061 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 93.3896 | 45.569 | 1084541.0348 | 90.3784 | 90.3784 | 175.4284 | 80 | 55 | 34.3356 | 34 | 56.8
7/24/20XX 1:00:00 PM | 0.54167 | 2 | 82.6 | 55.5 | 83.605 | 100.7325 | 17.1274 | 50 | 82.6 |  | 82.6 | 93.0251 | 0.1 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 65.662 | 17.8413 | 424624.1235 | 35.3853 | 35.3853 | 97.9443 | 0.2 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 68.7023 | 20.8817 | 496984.4471 | 41.4154 | 41.4154 | 106.6834 | 0.3 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 71.7427 | 23.922 | 569344.7706 | 47.4454 | 47.4454 | 115.4224 | 0.4 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 74.783 | 26.9624 | 641705.0942 | 53.4754 | 53.4754 | 124.1614 | 0.5 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 77.8234 | 30.0027 | 714065.4177 | 59.5055 | 59.5055 | 132.9005 | 0.6 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 80.8637 | 33.0431 | 786425.7413 | 65.5355 | 65.5355 | 141.6395 | 0.7 | 80.02 | 25.02 | 945756 | 78.813 | 78.813 | 83.9041 | 36.0834 | 858786.0648 | 71.5655 | 71.5655 | 150.3785 | 0.8 | 80.88 | 25.88 | 978264 | 81.522 | 81.522 | 86.9444 | 39.1238 | 931146.3884 | 77.5955 | 77.5955 | 159.1175 | 0.9 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 89.9848 | 42.1641 | 1003506.7119 | 83.6256 | 83.6256 | 167.8566 | 1 | 82.6 | 27.6 | 1043280 | 86.94 | 86.94 | 93.0251 | 45.2045 | 1075867.0355 | 89.6556 | 89.6556 | 176.5956 | 85 | 55 | 34.4259 | 34 | 55.5
7/24/20XX 2:00:00 PM | 0.58333 | 2 | 83.4 | 52.1 | 85.8211 | 103.4101 | 17.5889 | 50 | 83.4 |  | 83.4 | 89.5148 | 0.1 | 74.94 | 19.94 | 753732 | 62.811 | 62.811 | 65.3109 | 17.4903 | 416269.551 | 34.6891 | 34.6891 | 97.5001 | 0.2 | 75.88 | 20.88 | 789264 | 65.772 | 65.772 | 68.0003 | 20.1796 | 480275.302 | 40.0229 | 40.0229 | 105.7949 | 0.3 | 76.82 | 21.82 | 824796 | 68.733 | 68.733 | 70.6896 | 22.869 | 544281.053 | 45.3568 | 45.3568 | 114.0898 | 0.4 | 77.76 | 22.76 | 860328 | 71.694 | 71.694 | 73.3789 | 25.5583 | 608286.804 | 50.6906 | 50.6906 | 122.3846 | 0.5 | 78.7 | 23.7 | 895860 | 74.655 | 74.655 | 76.0682 | 28.2476 | 672292.555 | 56.0244 | 56.0244 | 130.6794 | 0.6 | 79.64 | 24.64 | 931392 | 77.616 | 77.616 | 78.7575 | 30.9369 | 736298.306 | 61.3582 | 61.3582 | 138.9742 | 0.7 | 80.58 | 25.58 | 966924 | 80.577 | 80.577 | 81.4469 | 33.6262 | 800304.057 | 66.692 | 66.692 | 147.269 | 0.8 | 81.52 | 26.52 | 1002456 | 83.538 | 83.538 | 84.1362 | 36.3155 | 864309.808 | 72.0258 | 72.0258 | 155.5638 | 0.9 | 82.46 | 27.46 | 1037988 | 86.499 | 86.499 | 86.8255 | 39.0049 | 928315.559 | 77.3596 | 77.3596 | 163.8586 | 1 | 83.4 | 28.4 | 1073520 | 89.46 | 89.46 | 89.5148 | 41.6942 | 992321.31 | 82.6934 | 82.6934 | 172.1534 | 85 | 50 | 34.0715 | 34 | 52.1
7/24/20XX 3:00:00 PM | 0.625 | 2 | 82.7 | 54.8 | 83.8795 | 101.064 | 17.1846 | 50 | 82.7 |  | 82.7 | 92.1281 | 0.1 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 65.5723 | 17.7516 | 422489.1133 | 35.2074 | 35.2074 | 97.7979 | 0.2 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 68.5229 | 20.7023 | 492714.4267 | 41.0595 | 41.0595 | 106.3905 | 0.3 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 71.4736 | 23.6529 | 562939.74 | 46.9116 | 46.9116 | 114.9831 | 0.4 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 74.4242 | 26.6036 | 633165.0533 | 52.7638 | 52.7638 | 123.5758 | 0.5 | 78.35 | 23.35 | 882630 | 73.5525 | 73.5525 | 77.3748 | 29.5542 | 703390.3666 | 58.6159 | 58.6159 | 132.1684 | 0.6 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 80.3255 | 32.5049 | 773615.68 | 64.468 | 64.468 | 140.761 | 0.7 | 80.09 | 25.09 | 948402 | 79.0335 | 79.0335 | 83.2761 | 35.4555 | 843840.9933 | 70.3201 | 70.3201 | 149.3536 | 0.8 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 86.2268 | 38.4061 | 914066.3066 | 76.1722 | 76.1722 | 157.9462 | 0.9 | 81.83 | 26.83 | 1014174 | 84.5145 | 84.5145 | 89.1774 | 41.3568 | 984291.62 | 82.0243 | 82.0243 | 166.5388 | 1 | 82.7 | 27.7 | 1047060 | 87.255 | 87.255 | 92.1281 | 44.3074 | 1054516.9333 | 87.8764 | 87.8764 | 175.1314 | 85 | 55 | 34.3097 | 34 | 54.8
7/24/20XX 4:00:00 PM | 0.66667 | 2 | 82.2 | 54 | 82.5146 | 99.4151 | 16.9005 | 50 | 82.2 |  | 82.2 | 89.2748 | 0.1 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 65.287 | 17.4663 | 415698.3802 | 34.6415 | 34.6415 | 97.0745 | 0.2 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 67.9523 | 20.1316 | 479132.9603 | 39.9277 | 39.9277 | 104.9437 | 0.3 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 70.6176 | 22.797 | 542567.5405 | 45.214 | 45.214 | 112.813 | 0.4 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 73.2829 | 25.4623 | 606002.1207 | 50.5002 | 50.5002 | 120.6822 | 0.5 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 75.9482 | 28.1276 | 669436.7008 | 55.7864 | 55.7864 | 128.5514 | 0.6 | 78.92 | 23.92 | 904176 | 75.348 | 75.348 | 78.6135 | 30.7929 | 732871.281 | 61.0726 | 61.0726 | 136.4206 | 0.7 | 79.74 | 24.74 | 935172 | 77.931 | 77.931 | 81.2789 | 33.4582 | 796305.8612 | 66.3588 | 66.3588 | 144.2898 | 0.8 | 80.56 | 25.56 | 966168 | 80.514 | 80.514 | 83.9442 | 36.1235 | 859740.4413 | 71.645 | 71.645 | 152.159 | 0.9 | 81.38 | 26.38 | 997164 | 83.097 | 83.097 | 86.6095 | 38.7889 | 923175.0215 | 76.9313 | 76.9313 | 160.0283 | 1 | 82.2 | 27.2 | 1028160 | 85.68 | 85.68 | 89.2748 | 41.4542 | 986609.6017 | 82.2175 | 82.2175 | 167.8975 | 80 | 55 | 33.739 | 34 | 54
7/24/20XX 5:00:00 PM | 0.70833 | 2 | 81.5 | 56.3 | 80.6344 | 97.1437 | 16.5092 | 50 | 81.5 |  | 81.5 | 91.0352 | 0.1 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 65.463 | 17.6424 | 419888.2087 | 34.9907 | 34.9907 | 97.2032 | 0.2 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 68.3044 | 20.4837 | 487512.6175 | 40.6261 | 40.6261 | 105.2011 | 0.3 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 71.1457 | 23.3251 | 555137.0262 | 46.2614 | 46.2614 | 113.1989 | 0.4 | 77 | 22 | 831600 | 69.3 | 69.3 | 73.9871 | 26.1664 | 622761.4349 | 51.8968 | 51.8968 | 121.1968 | 0.5 | 77.75 | 22.75 | 859950 | 71.6625 | 71.6625 | 76.8284 | 29.0078 | 690385.8436 | 57.5322 | 57.5322 | 129.1947 | 0.6 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 79.6698 | 31.8492 | 758010.2524 | 63.1675 | 63.1675 | 137.1925 | 0.7 | 79.25 | 24.25 | 916650 | 76.3875 | 76.3875 | 82.5112 | 34.6905 | 825634.6611 | 68.8029 | 68.8029 | 145.1904 | 0.8 | 80 | 25 | 945000 | 78.75 | 78.75 | 85.3525 | 37.5319 | 893259.0698 | 74.4383 | 74.4383 | 153.1883 | 0.9 | 80.75 | 25.75 | 973350 | 81.1125 | 81.1125 | 88.1939 | 40.3733 | 960883.4786 | 80.0736 | 80.0736 | 161.1861 | 1 | 81.5 | 26.5 | 1001700 | 83.475 | 83.475 | 91.0352 | 43.2146 | 1028507.8873 | 85.709 | 85.709 | 169.184 | 80 | 55 | 33.8432 | 34 | 56.3
7/24/20XX 6:00:00 PM | 0.75 | 2 | 80.2 | 59.1 | 77.2359 | 93.0386 | 15.8027 | 50 | 80.2 |  | 80.2 | 91.6164 | 0.1 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 65.5211 | 17.7005 | 421271.2851 | 35.1059 | 35.1059 | 96.9089 | 0.2 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 68.4206 | 20.5999 | 490278.7701 | 40.8566 | 40.8566 | 104.6126 | 0.3 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 71.3201 | 23.4994 | 559286.2552 | 46.6072 | 46.6072 | 112.3162 | 0.4 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 74.2195 | 26.3989 | 628293.7403 | 52.3578 | 52.3578 | 120.0198 | 0.5 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 77.119 | 29.2984 | 697301.2253 | 58.1084 | 58.1084 | 127.7234 | 0.6 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 80.0185 | 32.1978 | 766308.7104 | 63.8591 | 63.8591 | 135.4271 | 0.7 | 78.34 | 23.34 | 882252 | 73.521 | 73.521 | 82.918 | 35.0973 | 835316.1955 | 69.6097 | 69.6097 | 143.1307 | 0.8 | 78.96 | 23.96 | 905688 | 75.474 | 75.474 | 85.8174 | 37.9968 | 904323.6805 | 75.3603 | 75.3603 | 150.8343 | 0.9 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 88.7169 | 40.8963 | 973331.1656 | 81.1109 | 81.1109 | 158.5379 | 1 | 80.2 | 25.2 | 952560 | 79.38 | 79.38 | 91.6164 | 43.7957 | 1042338.6506 | 86.8616 | 86.8616 | 166.2416 | 80 | 60 | 33.6148 | 34 | 59.1
7/24/20XX 7:00:00 PM | 0.79167 | 2 | 79.5 | 59.5 | 75.4555 | 90.8883 | 15.4328 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/24/20XX 8:00:00 PM | 0.83333 | 2 | 78.2 | 61.9 | 87.0044 | 101.8479 | 14.8435 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/24/20XX 9:00:00 PM | 0.875 | 2 | 77.2 | 63.8 | 84.112 | 98.452 | 14.34 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/24/20XX 10:00:00 PM | 0.91667 | 2 | 76.5 | 65.4 | 82.1358 | 96.1318 | 13.9961 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/24/20XX 11:00:00 PM | 0.95833 | 2 | 75.8 | 64.8 | 80.1988 | 93.8579 | 13.6591 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/24/20XX 12:00:00 AM | 0 | 3 | 75.1 | 66.1 | 78.3007 | 91.6296 | 13.3289 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/25/20XX 1:00:00 AM | 0.041667 | 3 | 74 | 67.9 | 75.3952 | 88.2187 | 12.8236 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/25/20XX 2:00:00 AM | 0.083333 | 3 | 73.4 | 67.9 | 73.8495 | 86.4044 | 12.5549 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/25/20XX 3:00:00 AM | 0.125 | 3 | 72.4 | 67.9 | 71.3339 | 83.4515 | 12.1177 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/25/20XX 4:00:00 AM | 0.16667 | 3 | 71.8 | 69.6 | 69.8602 | 81.7218 | 11.8616 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/25/20XX 5:00:00 AM | 0.20833 | 3 | 71.3 | 69.4 | 68.6524 | 80.3042 | 11.6518 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/25/20XX 6:00:00 AM | 0.25 | 3 | 71.1 | 70.4 | 79.7432 | 91.3858 | 11.6426 | 70 | 71.1 |  | 71.1 | 80.2089 | 0.1 | 73.71 | 18.71 | 707238 | 58.9365 | 58.9365 | 64.3804 | 16.5597 | 394121.4486 | 32.8435 | 32.8435 | 91.78 | 0.2 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 66.1391 | 18.3184 | 435979.0972 | 36.3316 | 36.3316 | 94.3546 | 0.3 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 67.8978 | 20.0772 | 477836.7458 | 39.8197 | 39.8197 | 96.9292 | 0.4 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 69.6565 | 21.8359 | 519694.3943 | 43.3079 | 43.3079 | 99.5039 | 0.5 | 72.55 | 17.55 | 663390 | 55.2825 | 55.2825 | 71.4153 | 23.5946 | 561552.0429 | 46.796 | 46.796 | 102.0785 | 0.6 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 73.174 | 25.3533 | 603409.6915 | 50.2841 | 50.2841 | 104.6531 | 0.7 | 71.97 | 16.97 | 641466 | 53.4555 | 53.4555 | 74.9327 | 27.1121 | 645267.3401 | 53.7723 | 53.7723 | 107.2278 | 0.8 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 76.6914 | 28.8708 | 687124.9887 | 57.2604 | 57.2604 | 109.8024 | 0.9 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 78.4502 | 30.6295 | 728982.6373 | 60.7486 | 60.7486 | 112.3771 | 1 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 80.2089 | 32.3882 | 770840.2859 | 64.2367 | 64.2367 | 114.9517 | 70 | 70 | 29.5956 | 30 | 70.4
7/25/20XX 7:00:00 AM | 0.29167 | 3 | 72.2 | 69.1 | 70.8397 | 82.8715 | 12.0318 | 60 | 72.2 |  | 72.2 | 81.7886 | 0.1 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 64.5383 | 16.7177 | 397881.2234 | 33.1568 | 33.1568 | 92.4398 | 0.2 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 66.455 | 18.6344 | 443498.6469 | 36.9582 | 36.9582 | 95.6742 | 0.3 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 68.3717 | 20.5511 | 489116.0703 | 40.7597 | 40.7597 | 98.9087 | 0.4 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 70.2884 | 22.4678 | 534733.4938 | 44.5611 | 44.5611 | 102.1431 | 0.5 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 72.2051 | 24.3845 | 580350.9172 | 48.3626 | 48.3626 | 105.3776 | 0.6 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 74.1218 | 26.3012 | 625968.3407 | 52.164 | 52.164 | 108.612 | 0.7 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 76.0385 | 28.2179 | 671585.7641 | 55.9655 | 55.9655 | 111.8465 | 0.8 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 77.9552 | 30.1346 | 717203.1876 | 59.7669 | 59.7669 | 115.0809 | 0.9 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 79.8719 | 32.0513 | 762820.611 | 63.5684 | 63.5684 | 118.3154 | 1 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 81.7886 | 33.968 | 808438.0345 | 67.3698 | 67.3698 | 121.5498 | 70 | 70 | 30.1121 | 30 | 69.1
7/25/20XX 8:00:00 AM | 0.33333 | 3 | 73.7 | 66.3 | 74.6189 | 87.3075 | 12.6886 | 60 | 73.7 |  | 73.7 | 82.6127 | 0.1 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 64.6207 | 16.8001 | 399842.607 | 33.3202 | 33.3202 | 93.0757 | 0.2 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 66.6199 | 18.7992 | 447421.4139 | 37.2851 | 37.2851 | 96.9461 | 0.3 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 68.619 | 20.7983 | 495000.2209 | 41.25 | 41.25 | 100.8165 | 0.4 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 70.6181 | 22.7974 | 542579.0278 | 45.2149 | 45.2149 | 104.6869 | 0.5 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 72.6172 | 24.7965 | 590157.8348 | 49.1798 | 49.1798 | 108.5573 | 0.6 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 74.6163 | 26.7957 | 637736.6418 | 53.1447 | 53.1447 | 112.4277 | 0.7 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 76.6154 | 28.7948 | 685315.4487 | 57.1096 | 57.1096 | 116.2981 | 0.8 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 78.6145 | 30.7939 | 732894.2557 | 61.0745 | 61.0745 | 120.1685 | 0.9 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 80.6136 | 32.793 | 780473.0626 | 65.0394 | 65.0394 | 124.0389 | 1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 82.6127 | 34.7921 | 828051.8696 | 69.0043 | 69.0043 | 127.9093 | 75 | 65 | 30.6088 | 30 | 66.3
7/25/20XX 9:00:00 AM | 0.375 | 3 | 74.5 | 63.7 | 76.7042 | 89.7555 | 13.0512 | 60 | 74.5 |  | 74.5 | 81.5332 | 0.1 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 64.5128 | 16.6922 | 397273.3207 | 33.1061 | 33.1061 | 93.1136 | 0.2 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 66.4039 | 18.5833 | 442282.8413 | 36.8569 | 36.8569 | 97.0219 | 0.3 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 68.2951 | 20.4745 | 487292.362 | 40.6077 | 40.6077 | 100.9302 | 0.4 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 70.1863 | 22.3656 | 532301.8827 | 44.3585 | 44.3585 | 104.8385 | 0.5 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 72.0774 | 24.2568 | 577311.4034 | 48.1093 | 48.1093 | 108.7468 | 0.6 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 73.9686 | 26.1479 | 622320.924 | 51.8601 | 51.8601 | 112.6551 | 0.7 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 75.8597 | 28.0391 | 667330.4447 | 55.6109 | 55.6109 | 116.5634 | 0.8 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 77.7509 | 29.9303 | 712339.9654 | 59.3617 | 59.3617 | 120.4717 | 0.9 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 79.642 | 31.8214 | 757349.486 | 63.1125 | 63.1125 | 124.38 | 1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 81.5332 | 33.7126 | 802359.0067 | 66.8633 | 66.8633 | 128.2883 | 75 | 65 | 30.6361 | 30 | 63.7
7/25/20XX 10:00:00 AM | 0.41667 | 3 | 76.1 | 60.6 | 81.0242 | 94.8268 | 13.8027 | 60 | 76.1 |  | 76.1 | 81.8523 | 0.1 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 64.5447 | 16.7241 | 398032.8399 | 33.1694 | 33.1694 | 93.6809 | 0.2 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 66.4678 | 18.6471 | 443801.8798 | 36.9835 | 36.9835 | 98.1565 | 0.3 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 68.3908 | 20.5702 | 489570.9198 | 40.7976 | 40.7976 | 102.6321 | 0.4 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 70.3139 | 22.4933 | 535339.9597 | 44.6117 | 44.6117 | 107.1077 | 0.5 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 72.237 | 24.4163 | 581108.9996 | 48.4257 | 48.4257 | 111.5832 | 0.6 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 74.16 | 26.3394 | 626878.0395 | 52.2398 | 52.2398 | 116.0588 | 0.7 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 76.0831 | 28.2625 | 672647.0794 | 56.0539 | 56.0539 | 120.5344 | 0.8 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 78.0062 | 30.1856 | 718416.1193 | 59.868 | 59.868 | 125.01 | 0.9 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 79.9293 | 32.1086 | 764185.1593 | 63.6821 | 63.6821 | 129.4856 | 1 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 81.8523 | 34.0317 | 809954.1992 | 67.4962 | 67.4962 | 133.9612 | 75 | 60 | 31.0784 | 32 | 60.6
7/25/20XX 11:00:00 AM | 0.45833 | 3 | 78.4 | 57.5 | 72.7264 | 87.5927 | 14.8663 | 50 | 78.4 |  | 78.4 | 83.8762 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 64.7471 | 16.9265 | 402849.5794 | 33.5708 | 33.5708 | 94.8068 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 66.8725 | 19.0519 | 453435.3587 | 37.7863 | 37.7863 | 100.4083 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 68.998 | 21.1774 | 504021.1381 | 42.0018 | 42.0018 | 106.0098 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 71.1234 | 23.3028 | 554606.9174 | 46.2172 | 46.2172 | 111.6112 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 73.2489 | 25.4283 | 605192.6968 | 50.4327 | 50.4327 | 117.2127 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 75.3743 | 27.5537 | 655778.4761 | 54.6482 | 54.6482 | 122.8142 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 77.4998 | 29.6792 | 706364.2555 | 58.8637 | 58.8637 | 128.4157 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 79.6253 | 31.8046 | 756950.0348 | 63.0792 | 63.0792 | 134.0172 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 81.7507 | 33.9301 | 807535.8142 | 67.2947 | 67.2947 | 139.6187 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 83.8762 | 36.0555 | 858121.5935 | 71.5101 | 71.5101 | 145.2201 | 80 | 55 | 31.9595 | 32 | 57.5
7/25/20XX 12:00:00 PM | 0.5 | 3 | 79.2 | 56.1 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 84.0216 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 64.7616 | 16.941 | 403195.6955 | 33.5996 | 33.5996 | 95.0876 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 66.9016 | 19.081 | 454127.5911 | 37.844 | 37.844 | 100.97 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 69.0416 | 21.221 | 505059.4866 | 42.0883 | 42.0883 | 106.8523 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 71.1816 | 23.361 | 555991.3821 | 46.3326 | 46.3326 | 112.7346 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 73.3216 | 25.501 | 606923.2777 | 50.5769 | 50.5769 | 118.6169 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 75.4616 | 27.641 | 657855.1732 | 54.8213 | 54.8213 | 124.4993 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 77.6016 | 29.781 | 708787.0688 | 59.0656 | 59.0656 | 130.3816 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 79.7416 | 31.921 | 759718.9643 | 63.3099 | 63.3099 | 136.2639 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 81.8816 | 34.061 | 810650.8598 | 67.5542 | 67.5542 | 142.1462 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 84.0216 | 36.201 | 861582.7554 | 71.7986 | 71.7986 | 148.0286 | 80 | 55 | 32.1785 | 32 | 56.1
7/25/20XX 1:00:00 PM | 0.54167 | 3 | 80.1 | 55.1 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 85.0117 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 64.8606 | 17.04 | 405552.0765 | 33.796 | 33.796 | 95.5675 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 67.0996 | 19.279 | 458840.3529 | 38.2367 | 38.2367 | 101.9297 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 69.3386 | 21.518 | 512128.6294 | 42.6774 | 42.6774 | 108.2919 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 71.5776 | 23.757 | 565416.9059 | 47.1181 | 47.1181 | 114.6541 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 73.8166 | 25.996 | 618705.1823 | 51.5588 | 51.5588 | 121.0163 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 76.0557 | 28.235 | 671993.4588 | 55.9995 | 55.9995 | 127.3785 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 78.2947 | 30.474 | 725281.7353 | 60.4401 | 60.4401 | 133.7406 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 80.5337 | 32.713 | 778570.0117 | 64.8808 | 64.8808 | 140.1028 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 82.7727 | 34.952 | 831858.2882 | 69.3215 | 69.3215 | 146.465 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 85.0117 | 37.191 | 885146.5647 | 73.7622 | 73.7622 | 152.8272 | 80 | 55 | 32.5546 | 32 | 55.1
7/25/20XX 2:00:00 PM | 0.58333 | 3 | 79.6 | 58 | 75.7077 | 91.1929 | 15.4852 | 50 | 79.6 |  | 79.6 | 88.0959 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.1691 | 17.3484 | 412892.5446 | 34.4077 | 34.4077 | 96.0217 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 67.7165 | 19.8959 | 473521.2891 | 39.4601 | 39.4601 | 102.8381 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 70.2639 | 22.4433 | 534150.0337 | 44.5125 | 44.5125 | 109.6545 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 72.8113 | 24.9907 | 594778.7783 | 49.5649 | 49.5649 | 116.4709 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 75.3588 | 27.5381 | 655407.5229 | 54.6173 | 54.6173 | 123.2873 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 77.9062 | 30.0856 | 716036.2674 | 59.6697 | 59.6697 | 130.1037 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 80.4536 | 32.633 | 776665.012 | 64.7221 | 64.7221 | 136.9201 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 83.001 | 35.1804 | 837293.7566 | 69.7745 | 69.7745 | 143.7365 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 85.5485 | 37.7278 | 897922.5011 | 74.8269 | 74.8269 | 150.5529 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 88.0959 | 40.2753 | 958551.2457 | 79.8793 | 79.8793 | 157.3693 | 80 | 60 | 32.9154 | 32 | 58
7/25/20XX 3:00:00 PM | 0.625 | 3 | 77.3 | 64.5 | 84.3976 | 98.7873 | 14.3897 | 60 | 77.3 |  | 77.3 | 90.8729 | 0.1 | 74.33 | 19.33 | 730674 | 60.8895 | 60.8895 | 65.4468 | 17.6261 | 419501.9252 | 34.9585 | 34.9585 | 95.848 | 0.2 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 68.2719 | 20.4513 | 486740.0504 | 40.5617 | 40.5617 | 102.4907 | 0.3 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 71.097 | 23.2764 | 553978.1756 | 46.1648 | 46.1648 | 109.1333 | 0.4 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 73.9222 | 26.1015 | 621216.3008 | 51.768 | 51.768 | 115.776 | 0.5 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 76.7473 | 28.9267 | 688454.426 | 57.3712 | 57.3712 | 122.4187 | 0.6 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 79.5724 | 31.7518 | 755692.5512 | 62.9744 | 62.9744 | 129.0614 | 0.7 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 82.3976 | 34.5769 | 822930.6764 | 68.5776 | 68.5776 | 135.7041 | 0.8 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 85.2227 | 37.4021 | 890168.8016 | 74.1807 | 74.1807 | 142.3467 | 0.9 | 76.97 | 21.97 | 830466 | 69.2055 | 69.2055 | 88.0478 | 40.2272 | 957406.9267 | 79.7839 | 79.7839 | 148.9894 | 1 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 90.8729 | 43.0523 | 1024645.0519 | 85.3871 | 85.3871 | 155.6321 | 75 | 65 | 32.7855 | 32 | 64.5
7/25/20XX 4:00:00 PM | 0.66667 | 3 | 76 | 70.3 | 94.5029 | 108.3592 | 13.8563 | 70 | 76 |  | 76 | 94.9186 | 0.1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 65.8513 | 18.0307 | 429130.5631 | 35.7609 | 35.7609 | 96.2409 | 0.2 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 69.081 | 21.2604 | 505997.3263 | 42.1664 | 42.1664 | 103.2764 | 0.3 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 72.3107 | 24.4901 | 582864.0894 | 48.572 | 48.572 | 110.312 | 0.4 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 75.5404 | 27.7198 | 659730.8525 | 54.9776 | 54.9776 | 117.3476 | 0.5 | 75 | 20 | 756000 | 63 | 63 | 78.7701 | 30.9495 | 736597.6157 | 61.3831 | 61.3831 | 124.3831 | 0.6 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 81.9998 | 34.1792 | 813464.3788 | 67.7887 | 67.7887 | 131.4187 | 0.7 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 85.2295 | 37.4089 | 890331.1419 | 74.1943 | 74.1943 | 138.4543 | 0.8 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 88.4592 | 40.6386 | 967197.9051 | 80.5998 | 80.5998 | 145.4898 | 0.9 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 91.6889 | 43.8683 | 1044064.6682 | 87.0054 | 87.0054 | 152.5254 | 1 | 76 | 21 | 793800 | 66.15 | 66.15 | 94.9186 | 47.098 | 1120931.4313 | 93.411 | 93.411 | 159.561 | 75 | 70 | 33.0994 | 34 | 70.3
7/25/20XX 5:00:00 PM | 0.70833 | 3 | 74.9 | 70.8 | 91.0012 | 104.3307 | 13.3295 | 70 | 74.9 |  | 74.9 | 92.0676 | 0.1 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 65.5662 | 17.7456 | 422345.1108 | 35.1954 | 35.1954 | 95.3289 | 0.2 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 68.5108 | 20.6902 | 492426.4216 | 41.0355 | 41.0355 | 101.4525 | 0.3 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 71.4554 | 23.6348 | 562507.7324 | 46.8756 | 46.8756 | 107.5761 | 0.4 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 74.4 | 26.5794 | 632589.0432 | 52.7158 | 52.7158 | 113.6998 | 0.5 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 77.3446 | 29.524 | 702670.354 | 58.5559 | 58.5559 | 119.8234 | 0.6 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 80.2892 | 32.4686 | 772751.6648 | 64.396 | 64.396 | 125.947 | 0.7 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 83.2338 | 35.4132 | 842832.9756 | 70.2361 | 70.2361 | 132.0706 | 0.8 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 86.1784 | 38.3577 | 912914.2864 | 76.0762 | 76.0762 | 138.1942 | 0.9 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 89.123 | 41.3023 | 982995.5972 | 81.9163 | 81.9163 | 144.3178 | 1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 92.0676 | 44.2469 | 1053076.908 | 87.7564 | 87.7564 | 150.4414 | 75 | 70 | 32.3826 | 32 | 70.8
7/25/20XX 6:00:00 PM | 0.75 | 3 | 74.3 | 72.4 | 89.138 | 102.1877 | 13.0496 | 70 | 74.3 |  | 74.3 | 92.27 | 0.1 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 65.5865 | 17.7658 | 422826.8174 | 35.2356 | 35.2356 | 95.1801 | 0.2 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 68.5513 | 20.7307 | 493389.8348 | 41.1158 | 41.1158 | 101.1548 | 0.3 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 71.5161 | 23.6955 | 563952.8523 | 46.9961 | 46.9961 | 107.1296 | 0.4 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 74.481 | 26.6603 | 634515.8697 | 52.8763 | 52.8763 | 113.1043 | 0.5 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 77.4458 | 29.6252 | 705078.8871 | 58.7566 | 58.7566 | 119.0791 | 0.6 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 80.4106 | 32.59 | 775641.9045 | 64.6368 | 64.6368 | 125.0538 | 0.7 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 83.3755 | 35.5548 | 846204.9219 | 70.5171 | 70.5171 | 131.0286 | 0.8 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 86.3403 | 38.5197 | 916767.9393 | 76.3973 | 76.3973 | 137.0033 | 0.9 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 89.3051 | 41.4845 | 987330.9568 | 82.2776 | 82.2776 | 142.9781 | 1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 92.27 | 44.4493 | 1057893.9742 | 88.1578 | 88.1578 | 148.9528 | 75 | 70 | 32.2668 | 32 | 72.4
7/25/20XX 7:00:00 PM | 0.79167 | 3 | 73.5 | 74.8 | 86.7045 | 99.389 | 12.6844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/25/20XX 8:00:00 PM | 0.83333 | 3 | 73.3 | 73.4 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/25/20XX 9:00:00 PM | 0.875 | 3 | 72.6 | 75.5 | 84.035 | 96.3195 | 12.2844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/25/20XX 10:00:00 PM | 0.91667 | 3 | 72.8 | 75.7 | 84.6221 | 96.9944 | 12.3723 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/25/20XX 11:00:00 PM | 0.95833 | 3 | 72.1 | 76.3 | 82.5828 | 94.6498 | 12.0671 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/25/20XX 12:00:00 AM | 0 | 4 | 72 | 74.5 | 82.2949 | 94.3189 | 12.024 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/26/20XX 1:00:00 AM | 0.041667 | 4 | 71.6 | 74 | 81.1522 | 93.0054 | 11.8531 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/26/20XX 2:00:00 AM | 0.083333 | 4 | 71.3 | 74 | 80.3042 | 92.0306 | 11.7264 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/26/20XX 3:00:00 AM | 0.125 | 4 | 70.7 | 75 | 78.6313 | 90.1079 | 11.4766 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/26/20XX 4:00:00 AM | 0.16667 | 4 | 70.4 | 77.3 | 77.8062 | 89.1597 | 11.3535 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/26/20XX 5:00:00 AM | 0.20833 | 4 | 70.3 | 77.2 | 77.5329 | 88.8456 | 11.3127 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/26/20XX 6:00:00 AM | 0.25 | 4 | 70.8 | 75.9 | 78.908 | 90.4259 | 11.5179 | 70 | 70.8 |  | 70.8 | 85.7035 | 0.1 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 64.9298 | 17.1092 | 407198.7447 | 33.9332 | 33.9332 | 92.7752 | 0.2 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 67.238 | 19.4174 | 462133.6894 | 38.5111 | 38.5111 | 96.3451 | 0.3 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 69.5462 | 21.7256 | 517068.6341 | 43.0891 | 43.0891 | 99.9151 | 0.4 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 71.8544 | 24.0338 | 572003.5788 | 47.667 | 47.667 | 103.485 | 0.5 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 74.1626 | 26.342 | 626938.5234 | 52.2449 | 52.2449 | 107.0549 | 0.6 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 76.4708 | 28.6501 | 681873.4681 | 56.8228 | 56.8228 | 110.6248 | 0.7 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 78.779 | 30.9583 | 736808.4128 | 61.4007 | 61.4007 | 114.1947 | 0.8 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 81.0872 | 33.2665 | 791743.3575 | 65.9786 | 65.9786 | 117.7646 | 0.9 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 83.3954 | 35.5747 | 846678.3022 | 70.5565 | 70.5565 | 121.3345 | 1 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 85.7035 | 37.8829 | 901613.2469 | 75.1344 | 75.1344 | 124.9044 | 70 | 75 | 30.3805 | 30 | 75.9
7/26/20XX 7:00:00 AM | 0.29167 | 4 | 71.4 | 75.2 | 80.586 | 92.3545 | 11.7685 | 70 | 71.4 |  | 71.4 | 86.7057 | 0.1 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 65.03 | 17.2094 | 409583.7871 | 34.132 | 34.132 | 93.163 | 0.2 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 67.4384 | 19.6178 | 466903.7743 | 38.9086 | 38.9086 | 97.1206 | 0.3 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 69.8468 | 22.0262 | 524223.7614 | 43.6853 | 43.6853 | 101.0783 | 0.4 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 72.2552 | 24.4346 | 581543.7486 | 48.462 | 48.462 | 105.036 | 0.5 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 74.6636 | 26.843 | 638863.7357 | 53.2386 | 53.2386 | 108.9936 | 0.6 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 77.072 | 29.2514 | 696183.7229 | 58.0153 | 58.0153 | 112.9513 | 0.7 | 72.18 | 17.18 | 649404 | 54.117 | 54.117 | 79.4805 | 31.6598 | 753503.71 | 62.792 | 62.792 | 116.909 | 0.8 | 71.92 | 16.92 | 639576 | 53.298 | 53.298 | 81.8889 | 34.0682 | 810823.6971 | 67.5686 | 67.5686 | 120.8666 | 0.9 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 84.2973 | 36.4766 | 868143.6843 | 72.3453 | 72.3453 | 124.8243 | 1 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 86.7057 | 38.885 | 925463.6714 | 77.122 | 77.122 | 128.782 | 70 | 75 | 30.6843 | 30 | 75.2
7/26/20XX 8:00:00 AM | 0.33333 | 4 | 73.3 | 72.6 | 86.1051 | 98.6997 | 12.5946 | 70 | 73.3 |  | 73.3 | 89.3797 | 0.1 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 65.2974 | 17.4768 | 415947.9757 | 34.6623 | 34.6623 | 94.2918 | 0.2 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 67.9732 | 20.1526 | 479632.1514 | 39.9693 | 39.9693 | 99.3783 | 0.3 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 70.649 | 22.8284 | 543316.3271 | 45.2764 | 45.2764 | 104.4649 | 0.4 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 73.3249 | 25.5042 | 607000.5028 | 50.5834 | 50.5834 | 109.5514 | 0.5 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 76.0007 | 28.18 | 670684.6785 | 55.8904 | 55.8904 | 114.6379 | 0.6 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 78.6765 | 30.8558 | 734368.8542 | 61.1974 | 61.1974 | 119.7244 | 0.7 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 81.3523 | 33.5316 | 798053.0299 | 66.5044 | 66.5044 | 124.8109 | 0.8 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 84.0281 | 36.2074 | 861737.2057 | 71.8114 | 71.8114 | 129.8974 | 0.9 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 86.7039 | 38.8833 | 925421.3814 | 77.1184 | 77.1184 | 134.9839 | 1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 89.3797 | 41.5591 | 989105.5571 | 82.4255 | 82.4255 | 140.0705 | 75 | 75 | 31.5689 | 32 | 72.6
7/26/20XX 9:00:00 AM | 0.375 | 4 | 74.2 | 70.5 | 88.8307 | 101.8342 | 13.0035 | 70 | 74.2 |  | 74.2 | 89.4809 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 65.3076 | 17.4869 | 416188.8068 | 34.6824 | 34.6824 | 94.5954 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 67.9935 | 20.1728 | 480113.8137 | 40.0095 | 40.0095 | 99.9855 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 70.6794 | 22.8588 | 544038.8205 | 45.3366 | 45.3366 | 105.3756 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 73.3653 | 25.5447 | 607963.8273 | 50.6637 | 50.6637 | 110.7657 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 76.0513 | 28.2306 | 671888.8342 | 55.9907 | 55.9907 | 116.1557 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 78.7372 | 30.9165 | 735813.841 | 61.3178 | 61.3178 | 121.5458 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 81.4231 | 33.6025 | 799738.8478 | 66.6449 | 66.6449 | 126.9359 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 84.109 | 36.2884 | 863663.8547 | 71.972 | 71.972 | 132.326 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 86.795 | 38.9743 | 927588.8615 | 77.2991 | 77.2991 | 137.7161 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 89.4809 | 41.6602 | 991513.8683 | 82.6262 | 82.6262 | 143.1062 | 75 | 70 | 31.8059 | 32 | 70.5
7/26/20XX 10:00:00 AM | 0.41667 | 4 | 77.1 | 65.4 | 83.8273 | 98.1177 | 14.2905 | 60 | 77.1 |  | 77.1 | 91.5441 | 0.1 | 74.31 | 19.31 | 729918 | 60.8265 | 60.8265 | 65.5139 | 17.6932 | 421099.3026 | 35.0916 | 35.0916 | 95.9181 | 0.2 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 68.4061 | 20.5855 | 489934.8053 | 40.8279 | 40.8279 | 102.6309 | 0.3 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 71.2984 | 23.4777 | 558770.3079 | 46.5642 | 46.5642 | 109.3437 | 0.4 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 74.1906 | 26.37 | 627605.8106 | 52.3005 | 52.3005 | 116.0565 | 0.5 | 75.55 | 20.55 | 776790 | 64.7325 | 64.7325 | 77.0829 | 29.2622 | 696441.3132 | 58.0368 | 58.0368 | 122.7693 | 0.6 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 79.9751 | 32.1545 | 765276.8158 | 63.7731 | 63.7731 | 129.4821 | 0.7 | 76.17 | 21.17 | 800226 | 66.6855 | 66.6855 | 82.8674 | 35.0467 | 834112.3185 | 69.5094 | 69.5094 | 136.1949 | 0.8 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 85.7596 | 37.939 | 902947.8211 | 75.2457 | 75.2457 | 142.9077 | 0.9 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 88.6519 | 40.8312 | 971783.3238 | 80.9819 | 80.9819 | 149.6204 | 1 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 91.5441 | 43.7235 | 1040618.8264 | 86.7182 | 86.7182 | 156.3332 | 75 | 65 | 32.8415 | 32 | 65.4
7/26/20XX 11:00:00 AM | 0.45833 | 4 | 79.7 | 59.4 | 75.9607 | 91.4984 | 15.5378 | 50 | 79.7 |  | 79.7 | 90.5662 | 0.1 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 65.4161 | 17.5955 | 418771.776 | 34.8976 | 34.8976 | 96.5431 | 0.2 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 68.2105 | 20.3899 | 485279.752 | 40.44 | 40.44 | 103.881 | 0.3 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 71.005 | 23.1844 | 551787.728 | 45.9823 | 45.9823 | 111.2188 | 0.4 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 73.7994 | 25.9788 | 618295.704 | 51.5246 | 51.5246 | 118.5566 | 0.5 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 76.5939 | 28.7733 | 684803.6801 | 57.067 | 57.067 | 125.8945 | 0.6 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 79.3883 | 31.5677 | 751311.6561 | 62.6093 | 62.6093 | 133.2323 | 0.7 | 77.99 | 22.99 | 869022 | 72.4185 | 72.4185 | 82.1828 | 34.3622 | 817819.6321 | 68.1516 | 68.1516 | 140.5701 | 0.8 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 84.9773 | 37.1566 | 884327.6081 | 73.694 | 73.694 | 147.908 | 0.9 | 79.13 | 24.13 | 912114 | 76.0095 | 76.0095 | 87.7717 | 39.9511 | 950835.5841 | 79.2363 | 79.2363 | 155.2458 | 1 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 90.5662 | 42.7455 | 1017343.5601 | 84.7786 | 84.7786 | 162.5836 | 80 | 60 | 33.3273 | 34 | 59.4
7/26/20XX 12:00:00 PM | 0.5 | 4 | 81.3 | 57 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 91.5829 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 65.5178 | 17.6971 | 421191.6781 | 35.0993 | 35.0993 | 97.2488 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 68.4139 | 20.5933 | 490119.5562 | 40.8433 | 40.8433 | 105.2923 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 71.31 | 23.4894 | 559047.4343 | 46.5873 | 46.5873 | 113.3358 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 74.2061 | 26.3855 | 627975.3124 | 52.3313 | 52.3313 | 121.3793 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 77.1023 | 29.2816 | 696903.1906 | 58.0753 | 58.0753 | 129.4228 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 79.9984 | 32.1778 | 765831.0687 | 63.8193 | 63.8193 | 137.4663 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 82.8945 | 35.0739 | 834758.9468 | 69.5632 | 69.5632 | 145.5097 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 85.7907 | 37.97 | 903686.8249 | 75.3072 | 75.3072 | 153.5532 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 88.6868 | 40.8662 | 972614.703 | 81.0512 | 81.0512 | 161.5967 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 91.5829 | 43.7623 | 1041542.5811 | 86.7952 | 86.7952 | 169.6402 | 80 | 55 | 33.88 | 34 | 57
7/26/20XX 1:00:00 PM | 0.54167 | 4 | 82.6 | 52.8 | 83.605 | 100.7325 | 17.1274 | 50 | 82.6 |  | 82.6 | 88.4007 | 0.1 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 65.1995 | 17.3789 | 413618.0356 | 34.4682 | 34.4682 | 97.0272 | 0.2 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 67.7775 | 19.9568 | 474972.2711 | 39.581 | 39.581 | 104.849 | 0.3 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 70.3554 | 22.5347 | 536326.5067 | 44.6939 | 44.6939 | 112.6709 | 0.4 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 72.9333 | 25.1126 | 597680.7422 | 49.8067 | 49.8067 | 120.4927 | 0.5 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 75.5112 | 27.6905 | 659034.9778 | 54.9196 | 54.9196 | 128.3146 | 0.6 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 78.0891 | 30.2685 | 720389.2133 | 60.0324 | 60.0324 | 136.1364 | 0.7 | 80.02 | 25.02 | 945756 | 78.813 | 78.813 | 80.667 | 32.8464 | 781743.4489 | 65.1453 | 65.1453 | 143.9583 | 0.8 | 80.88 | 25.88 | 978264 | 81.522 | 81.522 | 83.2449 | 35.4243 | 843097.6844 | 70.2581 | 70.2581 | 151.7801 | 0.9 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 85.8228 | 38.0022 | 904451.92 | 75.371 | 75.371 | 159.602 | 1 | 82.6 | 27.6 | 1043280 | 86.94 | 86.94 | 88.4007 | 40.5801 | 965806.1555 | 80.4838 | 80.4838 | 167.4238 | 85 | 55 | 33.7 | 34 | 52.8
7/26/20XX 2:00:00 PM | 0.58333 | 4 | 83.8 | 50.9 | 86.947 | 104.7705 | 17.8235 | 50 | 83.8 |  | 83.8 | 88.5511 | 0.1 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 65.2146 | 17.3939 | 413975.8698 | 34.498 | 34.498 | 97.435 | 0.2 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 67.8075 | 19.9869 | 475687.9397 | 39.6407 | 39.6407 | 105.6647 | 0.3 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 70.4005 | 22.5798 | 537400.0095 | 44.7833 | 44.7833 | 113.8943 | 0.4 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 72.9934 | 25.1728 | 599112.0793 | 49.926 | 49.926 | 122.124 | 0.5 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 75.5864 | 27.7657 | 660824.1492 | 55.0687 | 55.0687 | 130.3537 | 0.6 | 79.88 | 24.88 | 940464 | 78.372 | 78.372 | 78.1793 | 30.3587 | 722536.219 | 60.2114 | 60.2114 | 138.5834 | 0.7 | 80.86 | 25.86 | 977508 | 81.459 | 81.459 | 80.7722 | 32.9516 | 784248.2888 | 65.354 | 65.354 | 146.813 | 0.8 | 81.84 | 26.84 | 1014552 | 84.546 | 84.546 | 83.3652 | 35.5446 | 845960.3587 | 70.4967 | 70.4967 | 155.0427 | 0.9 | 82.82 | 27.82 | 1051596 | 87.633 | 87.633 | 85.9581 | 38.1375 | 907672.4285 | 75.6394 | 75.6394 | 163.2724 | 1 | 83.8 | 28.8 | 1088640 | 90.72 | 90.72 | 88.5511 | 40.7304 | 969384.4983 | 80.782 | 80.782 | 171.502 | 85 | 50 | 34.0184 | 34 | 50.9
7/26/20XX 3:00:00 PM | 0.625 | 4 | 83.1 | 52 | 84.9846 | 102.3992 | 17.4147 | 50 | 83.1 |  | 83.1 | 88.4675 | 0.1 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 65.2062 | 17.3856 | 413776.9542 | 34.4814 | 34.4814 | 97.1979 | 0.2 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 67.7908 | 19.9702 | 475290.1084 | 39.6075 | 39.6075 | 105.1905 | 0.3 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 70.3754 | 22.5548 | 536803.2626 | 44.7336 | 44.7336 | 113.1831 | 0.4 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 72.96 | 25.1393 | 598316.4167 | 49.8597 | 49.8597 | 121.1757 | 0.5 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 75.5446 | 27.7239 | 659829.5709 | 54.9858 | 54.9858 | 129.1683 | 0.6 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 78.1292 | 30.3085 | 721342.7251 | 60.1119 | 60.1119 | 137.1609 | 0.7 | 80.37 | 25.37 | 958986 | 79.9155 | 79.9155 | 80.7137 | 32.8931 | 782855.8793 | 65.238 | 65.238 | 145.1535 | 0.8 | 81.28 | 26.28 | 993384 | 82.782 | 82.782 | 83.2983 | 35.4777 | 844369.0335 | 70.3641 | 70.3641 | 153.1461 | 0.9 | 82.19 | 27.19 | 1027782 | 85.6485 | 85.6485 | 85.8829 | 38.0623 | 905882.1877 | 75.4902 | 75.4902 | 161.1387 | 1 | 83.1 | 28.1 | 1062180 | 88.515 | 88.515 | 88.4675 | 40.6469 | 967395.3419 | 80.6163 | 80.6163 | 169.1313 | 85 | 50 | 33.8333 | 34 | 52
7/26/20XX 4:00:00 PM | 0.66667 | 4 | 83 | 51.6 | 84.7072 | 102.0641 | 17.3569 | 50 | 83 |  | 83 | 87.4843 | 0.1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 65.1079 | 17.2873 | 411436.9218 | 34.2864 | 34.2864 | 96.9714 | 0.2 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 67.5942 | 19.7735 | 470610.0435 | 39.2175 | 39.2175 | 104.7375 | 0.3 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 70.0804 | 22.2598 | 529783.1653 | 44.1486 | 44.1486 | 112.5036 | 0.4 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 72.5667 | 24.7461 | 588956.2871 | 49.0797 | 49.0797 | 120.2697 | 0.5 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 75.053 | 27.2323 | 648129.4088 | 54.0108 | 54.0108 | 128.0358 | 0.6 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 77.5392 | 29.7186 | 707302.5306 | 58.9419 | 58.9419 | 135.8019 | 0.7 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 80.0255 | 32.2049 | 766475.6524 | 63.873 | 63.873 | 143.568 | 0.8 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 82.5118 | 34.6911 | 825648.7741 | 68.8041 | 68.8041 | 151.3341 | 0.9 | 82.1 | 27.1 | 1024380 | 85.365 | 85.365 | 84.998 | 37.1774 | 884821.8959 | 73.7352 | 73.7352 | 159.1002 | 1 | 83 | 28 | 1058400 | 88.2 | 88.2 | 87.4843 | 39.6637 | 943995.0177 | 78.6663 | 78.6663 | 166.8663 | 85 | 50 | 33.6544 | 34 | 51.6
7/26/20XX 5:00:00 PM | 0.70833 | 4 | 82.2 | 53.1 | 82.5146 | 99.4151 | 16.9005 | 50 | 82.2 |  | 82.2 | 87.7538 | 0.1 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 65.1348 | 17.3142 | 412078.3021 | 34.3399 | 34.3399 | 96.7729 | 0.2 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 67.6481 | 19.8274 | 471892.8041 | 39.3244 | 39.3244 | 104.3404 | 0.3 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 70.1613 | 22.3406 | 531707.3062 | 44.3089 | 44.3089 | 111.9079 | 0.4 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 72.6745 | 24.8539 | 591521.8082 | 49.2935 | 49.2935 | 119.4755 | 0.5 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 75.1877 | 27.3671 | 651336.3103 | 54.278 | 54.278 | 127.043 | 0.6 | 78.92 | 23.92 | 904176 | 75.348 | 75.348 | 77.7009 | 29.8803 | 711150.8123 | 59.2626 | 59.2626 | 134.6106 | 0.7 | 79.74 | 24.74 | 935172 | 77.931 | 77.931 | 80.2141 | 32.3935 | 770965.3144 | 64.2471 | 64.2471 | 142.1781 | 0.8 | 80.56 | 25.56 | 966168 | 80.514 | 80.514 | 82.7273 | 34.9067 | 830779.8164 | 69.2317 | 69.2317 | 149.7457 | 0.9 | 81.38 | 26.38 | 997164 | 83.097 | 83.097 | 85.2406 | 37.4199 | 890594.3185 | 74.2162 | 74.2162 | 157.3132 | 1 | 82.2 | 27.2 | 1028160 | 85.68 | 85.68 | 87.7538 | 39.9331 | 950408.8205 | 79.2007 | 79.2007 | 164.8807 | 80 | 55 | 33.5003 | 34 | 53.1
7/26/20XX 6:00:00 PM | 0.75 | 4 | 80.7 | 56.7 | 78.5288 | 94.6002 | 16.0714 | 50 | 80.7 |  | 80.7 | 89.2966 | 0.1 | 74.67 | 19.67 | 743526 | 61.9605 | 61.9605 | 65.2891 | 17.4685 | 415750.3097 | 34.6459 | 34.6459 | 96.6064 | 0.2 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 67.9566 | 20.136 | 479236.8195 | 39.9364 | 39.9364 | 104.0074 | 0.3 | 76.01 | 21.01 | 794178 | 66.1815 | 66.1815 | 70.6241 | 22.8035 | 542723.3292 | 45.2269 | 45.2269 | 111.4084 | 0.4 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 73.2916 | 25.471 | 606209.8389 | 50.5175 | 50.5175 | 118.8095 | 0.5 | 77.35 | 22.35 | 844830 | 70.4025 | 70.4025 | 75.9591 | 28.1385 | 669696.3487 | 55.808 | 55.808 | 126.2105 | 0.6 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 78.6266 | 30.806 | 733182.8584 | 61.0986 | 61.0986 | 133.6116 | 0.7 | 78.69 | 23.69 | 895482 | 74.6235 | 74.6235 | 81.2941 | 33.4735 | 796669.3681 | 66.3891 | 66.3891 | 141.0126 | 0.8 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 83.9616 | 36.141 | 860155.8779 | 71.6797 | 71.6797 | 148.4137 | 0.9 | 80.03 | 25.03 | 946134 | 78.8445 | 78.8445 | 86.6291 | 38.8085 | 923642.3876 | 76.9702 | 76.9702 | 155.8147 | 1 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 89.2966 | 41.476 | 987128.8974 | 82.2607 | 82.2607 | 163.2157 | 80 | 55 | 33.3739 | 34 | 56.7
7/26/20XX 7:00:00 PM | 0.79167 | 4 | 79 | 59.6 | 74.2046 | 89.3778 | 15.1731 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/26/20XX 8:00:00 PM | 0.83333 | 4 | 76.6 | 64.4 | 82.4157 | 96.4605 | 14.0448 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/26/20XX 9:00:00 PM | 0.875 | 4 | 75.9 | 67.4 | 80.4731 | 94.1799 | 13.7068 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/26/20XX 10:00:00 PM | 0.91667 | 4 | 75.1 | 68.8 | 78.3007 | 91.6296 | 13.3289 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/26/20XX 11:00:00 PM | 0.95833 | 4 | 74.3 | 70.9 | 89.138 | 102.1877 | 13.0496 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/26/20XX 12:00:00 AM | 0 | 5 | 74 | 72.2 | 88.2187 | 101.1303 | 12.9116 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/27/20XX 1:00:00 AM | 0.041667 | 5 | 73.3 | 73.1 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/27/20XX 2:00:00 AM | 0.083333 | 5 | 72.5 | 74.6 | 83.7428 | 95.9835 | 12.2407 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/27/20XX 3:00:00 AM | 0.125 | 5 | 71.8 | 77.9 | 81.7218 | 93.6601 | 11.9383 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/27/20XX 4:00:00 AM | 0.16667 | 5 | 71.6 | 78.9 | 81.1522 | 93.0054 | 11.8531 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/27/20XX 5:00:00 AM | 0.20833 | 5 | 71.5 | 79.5 | 80.8687 | 92.6795 | 11.8108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/27/20XX 6:00:00 AM | 0.25 | 5 | 71.7 | 80.3 | 93.3322 | 105.2414 | 11.9091 | 80 | 71.7 |  | 71.7 | 93.6895 | 0.1 | 73.77 | 18.77 | 709506 | 59.1255 | 59.1255 | 65.7284 | 17.9078 | 426205.3801 | 35.5171 | 35.5171 | 94.6426 | 0.2 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 68.8352 | 21.0146 | 500146.9602 | 41.6789 | 41.6789 | 100.0799 | 0.3 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 71.942 | 24.1214 | 574088.5402 | 47.8407 | 47.8407 | 105.5172 | 0.4 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 75.0488 | 27.2282 | 648030.1203 | 54.0025 | 54.0025 | 110.9545 | 0.5 | 72.85 | 17.85 | 674730 | 56.2275 | 56.2275 | 78.1556 | 30.3349 | 721971.7004 | 60.1643 | 60.1643 | 116.3918 | 0.6 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 81.2624 | 33.4417 | 795913.2805 | 66.3261 | 66.3261 | 121.8291 | 0.7 | 72.39 | 17.39 | 657342 | 54.7785 | 54.7785 | 84.3692 | 36.5485 | 869854.8605 | 72.4879 | 72.4879 | 127.2664 | 0.8 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 87.4759 | 39.6553 | 943796.4406 | 78.6497 | 78.6497 | 132.7037 | 0.9 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 90.5827 | 42.7621 | 1017738.0207 | 84.8115 | 84.8115 | 138.141 | 1 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 93.6895 | 45.8689 | 1091679.6008 | 90.9733 | 90.9733 | 143.5783 | 70 | 80 | 31.8494 | 32 | 80.3
7/27/20XX 7:00:00 AM | 0.29167 | 5 | 73.4 | 75.8 | 86.4044 | 99.0438 | 12.6394 | 70 | 73.4 |  | 73.4 | 93.7352 | 0.1 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 65.733 | 17.9124 | 426314.1914 | 35.5262 | 35.5262 | 95.1872 | 0.2 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 68.8444 | 21.0237 | 500364.5827 | 41.697 | 41.697 | 101.169 | 0.3 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 71.9557 | 24.1351 | 574414.9741 | 47.8679 | 47.8679 | 107.1509 | 0.4 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 75.0671 | 27.2464 | 648465.3655 | 54.0388 | 54.0388 | 113.1328 | 0.5 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 78.1784 | 30.3578 | 722515.7569 | 60.2096 | 60.2096 | 119.1146 | 0.6 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 81.2898 | 33.4692 | 796566.1482 | 66.3805 | 66.3805 | 125.0965 | 0.7 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 84.4012 | 36.5805 | 870616.5396 | 72.5514 | 72.5514 | 131.0784 | 0.8 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 87.5125 | 39.6919 | 944666.931 | 78.7222 | 78.7222 | 137.0602 | 0.9 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 90.6239 | 42.8032 | 1018717.3224 | 84.8931 | 84.8931 | 143.0421 | 1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 93.7352 | 45.9146 | 1092767.7137 | 91.064 | 91.064 | 149.024 | 75 | 75 | 32.2746 | 32 | 75.8
7/27/20XX 8:00:00 AM | 0.33333 | 5 | 75 | 72.1 | 91.3149 | 104.6916 | 13.3767 | 70 | 75 |  | 75 | 94.124 | 0.1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 65.7719 | 17.9512 | 427239.4945 | 35.6033 | 35.6033 | 95.7683 | 0.2 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 68.9221 | 21.1015 | 502215.189 | 41.8513 | 41.8513 | 102.3313 | 0.3 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 72.0724 | 24.2517 | 577190.8835 | 48.0992 | 48.0992 | 108.8942 | 0.4 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 75.2226 | 27.402 | 652166.5781 | 54.3472 | 54.3472 | 115.4572 | 0.5 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 78.3728 | 30.5522 | 727142.2726 | 60.5952 | 60.5952 | 122.0202 | 0.6 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 81.5231 | 33.7024 | 802117.9671 | 66.8432 | 66.8432 | 128.5832 | 0.7 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 84.6733 | 36.8527 | 877093.6616 | 73.0911 | 73.0911 | 135.1461 | 0.8 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 87.8235 | 40.0029 | 952069.3561 | 79.3391 | 79.3391 | 141.7091 | 0.9 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 90.9738 | 43.1532 | 1027045.0506 | 85.5871 | 85.5871 | 148.2721 | 1 | 75 | 20 | 756000 | 63 | 63 | 94.124 | 46.3034 | 1102020.7452 | 91.8351 | 91.8351 | 154.8351 | 75 | 70 | 32.729 | 32 | 72.1
7/27/20XX 9:00:00 AM | 0.375 | 5 | 76.6 | 68.9 | 82.4157 | 96.4605 | 14.0448 | 60 | 76.6 |  | 76.6 | 94.9155 | 0.1 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 65.851 | 18.0304 | 429123.2729 | 35.7603 | 35.7603 | 96.4293 | 0.2 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 69.0804 | 21.2598 | 505982.7459 | 42.1652 | 42.1652 | 103.6532 | 0.3 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 72.3098 | 24.4892 | 582842.2188 | 48.5702 | 48.5702 | 110.8772 | 0.4 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 75.5392 | 27.7186 | 659701.6917 | 54.9751 | 54.9751 | 118.1011 | 0.5 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 78.7686 | 30.9479 | 736561.1647 | 61.3801 | 61.3801 | 125.3251 | 0.6 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 81.998 | 34.1773 | 813420.6376 | 67.7851 | 67.7851 | 132.5491 | 0.7 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 85.2274 | 37.4067 | 890280.1105 | 74.19 | 74.19 | 139.773 | 0.8 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 88.4567 | 40.6361 | 967139.5834 | 80.595 | 80.595 | 146.997 | 0.9 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 91.6861 | 43.8655 | 1043999.0564 | 86.9999 | 86.9999 | 154.2209 | 1 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 94.9155 | 47.0949 | 1120858.5293 | 93.4049 | 93.4049 | 161.4449 | 75 | 70 | 33.2465 | 34 | 68.9
7/27/20XX 10:00:00 AM | 0.41667 | 5 | 79 | 64 | 89.3778 | 104.6345 | 15.2568 | 60 | 79 |  | 79 | 95.4805 | 0.1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 65.9075 | 18.0869 | 430467.8217 | 35.8723 | 35.8723 | 97.2973 | 0.2 | 75 | 20 | 756000 | 63 | 63 | 69.1934 | 21.3728 | 508671.8435 | 42.3893 | 42.3893 | 105.3893 | 0.3 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 72.4793 | 24.6586 | 586875.8652 | 48.9063 | 48.9063 | 113.4813 | 0.4 | 76 | 21 | 793800 | 66.15 | 66.15 | 75.7652 | 27.9445 | 665079.8869 | 55.4233 | 55.4233 | 121.5733 | 0.5 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 79.051 | 31.2304 | 743283.9087 | 61.9403 | 61.9403 | 129.6653 | 0.6 | 77 | 22 | 831600 | 69.3 | 69.3 | 82.3369 | 34.5163 | 821487.9304 | 68.4573 | 68.4573 | 137.7573 | 0.7 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 85.6228 | 37.8022 | 899691.9521 | 74.9743 | 74.9743 | 145.8493 | 0.8 | 78 | 23 | 869400 | 72.45 | 72.45 | 88.9087 | 41.0881 | 977895.9738 | 81.4913 | 81.4913 | 153.9413 | 0.9 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 92.1946 | 44.3739 | 1056099.9956 | 88.0083 | 88.0083 | 162.0333 | 1 | 79 | 24 | 907200 | 75.6 | 75.6 | 95.4805 | 47.6598 | 1134304.0173 | 94.5253 | 94.5253 | 170.1253 | 80 | 65 | 33.9255 | 34 | 64
7/27/20XX 11:00:00 AM | 0.45833 | 5 | 82 | 58.8 | 81.9738 | 98.7617 | 16.7879 | 50 | 82 |  | 82 | 96.7472 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 66.0342 | 18.2136 | 433482.5677 | 36.1235 | 36.1235 | 98.4935 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 69.4467 | 21.6261 | 514701.3354 | 42.8918 | 42.8918 | 107.7818 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 72.8593 | 25.0387 | 595920.103 | 49.66 | 49.66 | 117.07 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 76.2718 | 28.4512 | 677138.8707 | 56.4282 | 56.4282 | 126.3582 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 79.6844 | 31.8638 | 758357.6384 | 63.1965 | 63.1965 | 135.6465 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 83.097 | 35.2763 | 839576.4061 | 69.9647 | 69.9647 | 144.9347 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 86.5095 | 38.6889 | 920795.1738 | 76.7329 | 76.7329 | 154.2229 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 89.9221 | 42.1014 | 1002013.9415 | 83.5012 | 83.5012 | 163.5112 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 93.3346 | 45.514 | 1083232.7091 | 90.2694 | 90.2694 | 172.7994 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 96.7472 | 48.9265 | 1164451.4768 | 97.0376 | 97.0376 | 182.0876 | 80 | 60 | 34.8625 | 34 | 58.8
7/27/20XX 12:00:00 PM | 0.5 | 5 | 82.8 | 56.3 | 84.1546 | 101.3965 | 17.2419 | 50 | 82.8 |  | 82.8 | 95.017 | 0.1 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 65.8612 | 18.0405 | 429364.8052 | 35.7804 | 35.7804 | 98.4024 | 0.2 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 69.1007 | 21.2801 | 506465.8105 | 42.2055 | 42.2055 | 107.5995 | 0.3 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 72.3402 | 24.5196 | 583566.8157 | 48.6306 | 48.6306 | 116.7966 | 0.4 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 75.5798 | 27.7592 | 660667.8209 | 55.0557 | 55.0557 | 125.9937 | 0.5 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 78.8193 | 30.9987 | 737768.8262 | 61.4807 | 61.4807 | 135.1907 | 0.6 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 82.0589 | 34.2382 | 814869.8314 | 67.9058 | 67.9058 | 144.3878 | 0.7 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 85.2984 | 37.4778 | 891970.8366 | 74.3309 | 74.3309 | 153.5849 | 0.8 | 81.04 | 26.04 | 984312 | 82.026 | 82.026 | 88.5379 | 40.7173 | 969071.8419 | 80.756 | 80.756 | 162.782 | 0.9 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 91.7775 | 43.9568 | 1046172.8471 | 87.1811 | 87.1811 | 171.9791 | 1 | 82.8 | 27.8 | 1050840 | 87.57 | 87.57 | 95.017 | 47.1964 | 1123273.8523 | 93.6062 | 93.6062 | 181.1762 | 85 | 55 | 34.7878 | 34 | 56.3
7/27/20XX 1:00:00 PM | 0.54167 | 5 | 82.9 | 56.6 | 84.4305 | 101.7299 | 17.2993 | 50 | 82.9 |  | 82.9 | 95.8481 | 0.1 | 74.89 | 19.89 | 751842 | 62.6535 | 62.6535 | 65.9443 | 18.1236 | 431342.7642 | 35.9452 | 35.9452 | 98.5987 | 0.2 | 75.78 | 20.78 | 785484 | 65.457 | 65.457 | 69.2669 | 21.4463 | 510421.7285 | 42.5351 | 42.5351 | 107.9921 | 0.3 | 76.67 | 21.67 | 819126 | 68.2605 | 68.2605 | 72.5896 | 24.7689 | 589500.6927 | 49.1251 | 49.1251 | 117.3856 | 0.4 | 77.56 | 22.56 | 852768 | 71.064 | 71.064 | 75.9122 | 28.0916 | 668579.6569 | 55.715 | 55.715 | 126.779 | 0.5 | 78.45 | 23.45 | 886410 | 73.8675 | 73.8675 | 79.2349 | 31.4142 | 747658.6212 | 62.3049 | 62.3049 | 136.1724 | 0.6 | 79.34 | 24.34 | 920052 | 76.671 | 76.671 | 82.5575 | 34.7369 | 826737.5854 | 68.8948 | 68.8948 | 145.5658 | 0.7 | 80.23 | 25.23 | 953694 | 79.4745 | 79.4745 | 85.8802 | 38.0595 | 905816.5496 | 75.4847 | 75.4847 | 154.9592 | 0.8 | 81.12 | 26.12 | 987336 | 82.278 | 82.278 | 89.2028 | 41.3822 | 984895.5138 | 82.0746 | 82.0746 | 164.3526 | 0.9 | 82.01 | 27.01 | 1020978 | 85.0815 | 85.0815 | 92.5254 | 44.7048 | 1063974.4781 | 88.6645 | 88.6645 | 173.746 | 1 | 82.9 | 27.9 | 1054620 | 87.885 | 87.885 | 95.8481 | 48.0275 | 1143053.4423 | 95.2545 | 95.2545 | 183.1395 | 85 | 55 | 34.9429 | 34 | 56.6
7/27/20XX 2:00:00 PM | 0.58333 | 5 | 83 | 57.1 | 84.7072 | 102.0641 | 17.3569 | 50 | 83 |  | 83 | 97.0306 | 0.1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 66.0625 | 18.2419 | 434157.1293 | 36.1798 | 36.1798 | 98.8648 | 0.2 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 69.5034 | 21.6828 | 516050.4585 | 43.0042 | 43.0042 | 108.5242 | 0.3 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 72.9443 | 25.1237 | 597943.7878 | 49.8286 | 49.8286 | 118.1836 | 0.4 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 76.3852 | 28.5646 | 679837.117 | 56.6531 | 56.6531 | 127.8431 | 0.5 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 79.8261 | 32.0055 | 761730.4463 | 63.4775 | 63.4775 | 137.5025 | 0.6 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 83.267 | 35.4464 | 843623.7756 | 70.302 | 70.302 | 147.162 | 0.7 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 86.7079 | 38.8873 | 925517.1048 | 77.1264 | 77.1264 | 156.8214 | 0.8 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 90.1488 | 42.3282 | 1007410.4341 | 83.9509 | 83.9509 | 166.4809 | 0.9 | 82.1 | 27.1 | 1024380 | 85.365 | 85.365 | 93.5897 | 45.7691 | 1089303.7633 | 90.7753 | 90.7753 | 176.1403 | 1 | 83 | 28 | 1058400 | 88.2 | 88.2 | 97.0306 | 49.21 | 1171197.0926 | 97.5998 | 97.5998 | 185.7998 | 85 | 55 | 35.1531 | 36 | 57.1
7/27/20XX 3:00:00 PM | 0.625 | 5 | 81.5 | 60.7 | 97.1437 | 113.7533 | 16.6096 | 60 | 81.5 |  | 81.5 | 98.3063 | 0.1 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 66.1901 | 18.3695 | 437193.4177 | 36.4328 | 36.4328 | 98.6453 | 0.2 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 69.7586 | 21.9379 | 522123.0354 | 43.5103 | 43.5103 | 108.0853 | 0.3 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 73.327 | 25.5064 | 607052.6531 | 50.5877 | 50.5877 | 117.5252 | 0.4 | 77 | 22 | 831600 | 69.3 | 69.3 | 76.8955 | 29.0749 | 691982.2707 | 57.6652 | 57.6652 | 126.9652 | 0.5 | 77.75 | 22.75 | 859950 | 71.6625 | 71.6625 | 80.464 | 32.6434 | 776911.8884 | 64.7427 | 64.7427 | 136.4052 | 0.6 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 84.0325 | 36.2118 | 861841.5061 | 71.8201 | 71.8201 | 145.8451 | 0.7 | 79.25 | 24.25 | 916650 | 76.3875 | 76.3875 | 87.6009 | 39.7803 | 946771.1238 | 78.8976 | 78.8976 | 155.2851 | 0.8 | 80 | 25 | 945000 | 78.75 | 78.75 | 91.1694 | 43.3488 | 1031700.7415 | 85.9751 | 85.9751 | 164.7251 | 0.9 | 80.75 | 25.75 | 973350 | 81.1125 | 81.1125 | 94.7379 | 46.9172 | 1116630.3592 | 93.0525 | 93.0525 | 174.165 | 1 | 81.5 | 26.5 | 1001700 | 83.475 | 83.475 | 98.3063 | 50.4857 | 1201559.9769 | 100.13 | 100.13 | 183.605 | 80 | 60 | 34.984 | 34 | 60.7
7/27/20XX 4:00:00 PM | 0.66667 | 5 | 82 | 59 | 81.9738 | 98.7617 | 16.7879 | 50 | 82 |  | 82 | 97.0829 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 66.0678 | 18.2471 | 434281.6721 | 36.1901 | 36.1901 | 98.5601 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 69.5139 | 21.6933 | 516299.5442 | 43.025 | 43.025 | 107.915 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 72.96 | 25.1394 | 598317.4163 | 49.8598 | 49.8598 | 117.2698 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 76.4061 | 28.5855 | 680335.2884 | 56.6946 | 56.6946 | 126.6246 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 79.8523 | 32.0316 | 762353.1605 | 63.5294 | 63.5294 | 135.9794 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 83.2984 | 35.4778 | 844371.0326 | 70.3643 | 70.3643 | 145.3343 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 86.7445 | 38.9239 | 926388.9047 | 77.1991 | 77.1991 | 154.6891 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 90.1907 | 42.37 | 1008406.7768 | 84.0339 | 84.0339 | 164.0439 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 93.6368 | 45.8162 | 1090424.6489 | 90.8687 | 90.8687 | 173.3987 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 97.0829 | 49.2623 | 1172442.521 | 97.7035 | 97.7035 | 182.7535 | 80 | 60 | 34.9152 | 34 | 59
7/27/20XX 5:00:00 PM | 0.70833 | 5 | 80.7 | 62.2 | 94.6002 | 110.7667 | 16.1665 | 60 | 80.7 |  | 80.7 | 98.1568 | 0.1 | 74.67 | 19.67 | 743526 | 61.9605 | 61.9605 | 66.1752 | 18.3545 | 436837.5418 | 36.4031 | 36.4031 | 98.3636 | 0.2 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 69.7287 | 21.908 | 521411.2837 | 43.4509 | 43.4509 | 107.5219 | 0.3 | 76.01 | 21.01 | 794178 | 66.1815 | 66.1815 | 73.2822 | 25.4616 | 605985.0255 | 50.4988 | 50.4988 | 116.6803 | 0.4 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 76.8357 | 29.0151 | 690558.7673 | 57.5466 | 57.5466 | 125.8386 | 0.5 | 77.35 | 22.35 | 844830 | 70.4025 | 70.4025 | 80.3892 | 32.5686 | 775132.5091 | 64.5944 | 64.5944 | 134.9969 | 0.6 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 83.9427 | 36.1221 | 859706.251 | 71.6422 | 71.6422 | 144.1552 | 0.7 | 78.69 | 23.69 | 895482 | 74.6235 | 74.6235 | 87.4963 | 39.6756 | 944279.9928 | 78.69 | 78.69 | 153.3135 | 0.8 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 91.0498 | 43.2291 | 1028853.7346 | 85.7378 | 85.7378 | 162.4718 | 0.9 | 80.03 | 25.03 | 946134 | 78.8445 | 78.8445 | 94.6033 | 46.7827 | 1113427.4765 | 92.7856 | 92.7856 | 171.6301 | 1 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 98.1568 | 50.3362 | 1198001.2183 | 99.8334 | 99.8334 | 180.7884 | 80 | 60 | 34.7636 | 34 | 62.2
7/27/20XX 6:00:00 PM | 0.75 | 5 | 79.9 | 62.8 | 92.1119 | 107.8449 | 15.733 | 60 | 79.9 |  | 79.9 | 96.5172 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 66.0112 | 18.1906 | 432935.2119 | 36.0779 | 36.0779 | 97.7864 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 69.4007 | 21.5801 | 513606.6238 | 42.8006 | 42.8006 | 106.3676 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 72.7903 | 24.9697 | 594278.0358 | 49.5232 | 49.5232 | 114.9487 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 76.1799 | 28.3592 | 674949.4477 | 56.2458 | 56.2458 | 123.5298 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 79.5694 | 31.7488 | 755620.8596 | 62.9684 | 62.9684 | 132.1109 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 82.959 | 35.1383 | 836292.2715 | 69.691 | 69.691 | 140.692 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 86.3485 | 38.5279 | 916963.6835 | 76.4136 | 76.4136 | 149.2731 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 89.7381 | 41.9174 | 997635.0954 | 83.1363 | 83.1363 | 157.8543 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 93.1276 | 45.307 | 1078306.5073 | 89.8589 | 89.8589 | 166.4354 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 96.5172 | 48.6966 | 1158977.9192 | 96.5815 | 96.5815 | 175.0165 | 80 | 65 | 34.3095 | 34 | 62.8
7/27/20XX 7:00:00 PM | 0.79167 | 5 | 78.8 | 64.7 | 88.7794 | 103.932 | 15.1526 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/27/20XX 8:00:00 PM | 0.83333 | 5 | 78.2 | 65.8 | 87.0044 | 101.8479 | 14.8435 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/27/20XX 9:00:00 PM | 0.875 | 5 | 77.7 | 68.2 | 85.548 | 100.1379 | 14.59 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/27/20XX 10:00:00 PM | 0.91667 | 5 | 76.7 | 68.8 | 82.6964 | 96.79 | 14.0936 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/27/20XX 11:00:00 PM | 0.95833 | 5 | 76.2 | 72.7 | 95.1517 | 109.1057 | 13.954 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/27/20XX 12:00:00 AM | 0 | 6 | 75.8 | 74 | 93.8579 | 107.6171 | 13.7592 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/28/20XX 1:00:00 AM | 0.041667 | 6 | 75 | 78 | 91.3149 | 104.6916 | 13.3767 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/28/20XX 2:00:00 AM | 0.083333 | 6 | 74.2 | 81.1 | 101.8342 | 114.8661 | 13.0319 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/28/20XX 3:00:00 AM | 0.125 | 6 | 73.3 | 81.6 | 98.6997 | 111.3171 | 12.6175 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/28/20XX 4:00:00 AM | 0.16667 | 6 | 72.7 | 83.2 | 96.6564 | 109.004 | 12.3476 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/28/20XX 5:00:00 AM | 0.20833 | 6 | 72.7 | 83.8 | 96.6564 | 109.004 | 12.3476 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/28/20XX 6:00:00 AM | 0.25 | 6 | 73.6 | 83 | 99.7352 | 112.4895 | 12.7543 | 80 | 73.6 |  | 73.6 | 103.5615 | 0.1 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 66.7156 | 18.895 | 449700.6091 | 37.4751 | 37.4751 | 97.1991 | 0.2 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 70.8096 | 22.989 | 547137.4183 | 45.5948 | 45.5948 | 105.1928 | 0.3 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 74.9036 | 27.083 | 644574.2274 | 53.7145 | 53.7145 | 113.1865 | 0.4 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 78.9976 | 31.1769 | 742011.0366 | 61.8343 | 61.8343 | 121.1803 | 0.5 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 83.0916 | 35.2709 | 839447.8457 | 69.954 | 69.954 | 129.174 | 0.6 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 87.1855 | 39.3649 | 936884.6548 | 78.0737 | 78.0737 | 137.1677 | 0.7 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 91.2795 | 43.4589 | 1034321.464 | 86.1935 | 86.1935 | 145.1615 | 0.8 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 95.3735 | 47.5529 | 1131758.2731 | 94.3132 | 94.3132 | 153.1552 | 0.9 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 99.4675 | 51.6469 | 1229195.0823 | 102.4329 | 102.4329 | 161.1489 | 1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 103.5615 | 55.7408 | 1326631.8914 | 110.5527 | 110.5527 | 169.1427 | 75 | 85 | 33.8606 | 34 | 83
7/28/20XX 7:00:00 AM | 0.29167 | 6 | 74.9 | 79.6 | 91.0012 | 104.3307 | 13.3295 | 70 | 74.9 |  | 74.9 | 103.7975 | 0.1 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 66.7392 | 18.9186 | 450262.4777 | 37.5219 | 37.5219 | 97.6554 | 0.2 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 70.8568 | 23.0362 | 548261.1555 | 45.6884 | 45.6884 | 106.1054 | 0.3 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 74.9744 | 27.1538 | 646259.8332 | 53.855 | 53.855 | 114.5555 | 0.4 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 79.092 | 31.2714 | 744258.511 | 62.0215 | 62.0215 | 123.0055 | 0.5 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 83.2096 | 35.389 | 842257.1887 | 70.1881 | 70.1881 | 131.4556 | 0.6 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 87.3272 | 39.5065 | 940255.8665 | 78.3547 | 78.3547 | 139.9057 | 0.7 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 91.4448 | 43.6241 | 1038254.5442 | 86.5212 | 86.5212 | 148.3557 | 0.8 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 95.5624 | 47.7417 | 1136253.222 | 94.6878 | 94.6878 | 156.8058 | 0.9 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 99.68 | 51.8593 | 1234251.8997 | 102.8543 | 102.8543 | 165.2558 | 1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 103.7975 | 55.9769 | 1332250.5774 | 111.0209 | 111.0209 | 173.7059 | 75 | 80 | 34.2181 | 34 | 79.6
7/28/20XX 8:00:00 AM | 0.33333 | 6 | 76.5 | 75.2 | 96.1318 | 110.2335 | 14.1017 | 70 | 76.5 |  | 76.5 | 103.4647 | 0.1 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 66.7059 | 18.8853 | 449470.3489 | 37.4559 | 37.4559 | 98.0934 | 0.2 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 70.7902 | 22.9696 | 546676.8978 | 45.5564 | 45.5564 | 106.9814 | 0.3 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 74.8746 | 27.0539 | 643883.4467 | 53.657 | 53.657 | 115.8695 | 0.4 | 75 | 20 | 756000 | 63 | 63 | 78.9589 | 31.1382 | 741089.9956 | 61.7575 | 61.7575 | 124.7575 | 0.5 | 75.25 | 20.25 | 765450 | 63.7875 | 63.7875 | 83.0432 | 35.2225 | 838296.5445 | 69.858 | 69.858 | 133.6455 | 0.6 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 87.1275 | 39.3069 | 935503.0934 | 77.9586 | 77.9586 | 142.5336 | 0.7 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 91.2118 | 43.3912 | 1032709.6423 | 86.0591 | 86.0591 | 151.4216 | 0.8 | 76 | 21 | 793800 | 66.15 | 66.15 | 95.2961 | 47.4755 | 1129916.1912 | 94.1597 | 94.1597 | 160.3097 | 0.9 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 99.3804 | 51.5598 | 1227122.7401 | 102.2602 | 102.2602 | 169.1977 | 1 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 103.4647 | 55.6441 | 1324329.289 | 110.3608 | 110.3608 | 178.0858 | 75 | 75 | 34.5605 | 34 | 75.2
7/28/20XX 9:00:00 AM | 0.375 | 6 | 77.9 | 70.3 | 100.819 | 115.6278 | 14.8088 | 70 | 77.9 |  | 77.9 | 101.2633 | 0.1 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 66.4858 | 18.6652 | 444230.9238 | 37.0192 | 37.0192 | 98.0977 | 0.2 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 70.35 | 22.5293 | 536198.0476 | 44.6832 | 44.6832 | 106.9902 | 0.3 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 74.2141 | 26.3935 | 628165.1714 | 52.3471 | 52.3471 | 115.8826 | 0.4 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 78.0783 | 30.2577 | 720132.2952 | 60.011 | 60.011 | 124.775 | 0.5 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 81.9425 | 34.1218 | 812099.419 | 67.675 | 67.675 | 133.6675 | 0.6 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 85.8066 | 37.986 | 904066.5428 | 75.3389 | 75.3389 | 142.5599 | 0.7 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 89.6708 | 41.8502 | 996033.6666 | 83.0028 | 83.0028 | 151.4523 | 0.8 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 93.535 | 45.7143 | 1088000.7904 | 90.6667 | 90.6667 | 160.3447 | 0.9 | 77.51 | 22.51 | 850878 | 70.9065 | 70.9065 | 97.3991 | 49.5785 | 1179967.9142 | 98.3307 | 98.3307 | 169.2372 | 1 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 101.2633 | 53.4426 | 1271935.038 | 105.9946 | 105.9946 | 178.1296 | 80 | 70 | 34.5608 | 34 | 70.3
7/28/20XX 10:00:00 AM | 0.41667 | 6 | 79.6 | 66.1 | 91.1929 | 106.7659 | 15.5729 | 60 | 79.6 |  | 79.6 | 100.6924 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 66.4287 | 18.6081 | 442872.2689 | 36.906 | 36.906 | 98.52 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 70.2358 | 22.4152 | 533480.7377 | 44.4567 | 44.4567 | 107.8347 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 74.0429 | 26.2222 | 624089.2066 | 52.0074 | 52.0074 | 117.1494 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 77.8499 | 30.0293 | 714697.6754 | 59.5581 | 59.5581 | 126.4641 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 81.657 | 33.8364 | 805306.1443 | 67.1088 | 67.1088 | 135.7788 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 85.4641 | 37.6435 | 895914.6131 | 74.6596 | 74.6596 | 145.0936 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 89.2712 | 41.4505 | 986523.082 | 82.2103 | 82.2103 | 154.4083 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 93.0783 | 45.2576 | 1077131.5508 | 89.761 | 89.761 | 163.723 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 96.8853 | 49.0647 | 1167740.0197 | 97.3117 | 97.3117 | 173.0377 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 100.6924 | 52.8718 | 1258348.4885 | 104.8624 | 104.8624 | 182.3524 | 80 | 65 | 34.8903 | 34 | 66.1
7/28/20XX 11:00:00 AM | 0.45833 | 6 | 81.5 | 62.6 | 97.1437 | 113.7533 | 16.6096 | 60 | 81.5 |  | 81.5 | 101.4622 | 0.1 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 66.5057 | 18.6851 | 444704.2917 | 37.0587 | 37.0587 | 99.2712 | 0.2 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 70.3897 | 22.5691 | 537144.7835 | 44.7621 | 44.7621 | 109.3371 | 0.3 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 74.2738 | 26.4532 | 629585.2752 | 52.4654 | 52.4654 | 119.4029 | 0.4 | 77 | 22 | 831600 | 69.3 | 69.3 | 78.1578 | 30.3372 | 722025.7669 | 60.1688 | 60.1688 | 129.4688 | 0.5 | 77.75 | 22.75 | 859950 | 71.6625 | 71.6625 | 82.0419 | 34.2213 | 814466.2587 | 67.8722 | 67.8722 | 139.5347 | 0.6 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 85.926 | 38.1053 | 906906.7504 | 75.5756 | 75.5756 | 149.6006 | 0.7 | 79.25 | 24.25 | 916650 | 76.3875 | 76.3875 | 89.81 | 41.9894 | 999347.2421 | 83.2789 | 83.2789 | 159.6664 | 0.8 | 80 | 25 | 945000 | 78.75 | 78.75 | 93.6941 | 45.8734 | 1091787.7339 | 90.9823 | 90.9823 | 169.7323 | 0.9 | 80.75 | 25.75 | 973350 | 81.1125 | 81.1125 | 97.5781 | 49.7575 | 1184228.2256 | 98.6857 | 98.6857 | 179.7982 | 1 | 81.5 | 26.5 | 1001700 | 83.475 | 83.475 | 101.4622 | 53.6415 | 1276668.7173 | 106.3891 | 106.3891 | 189.8641 | 80 | 65 | 35.4792 | 36 | 62.6
7/28/20XX 12:00:00 PM | 0.5 | 6 | 83.5 | 56.5 | 86.1015 | 103.7488 | 17.6473 | 50 | 83.5 |  | 83.5 | 97.5722 | 0.1 | 74.95 | 19.95 | 754110 | 62.8425 | 62.8425 | 66.1167 | 18.2961 | 435446.2423 | 36.2872 | 36.2872 | 99.1297 | 0.2 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 69.6118 | 21.7911 | 518628.6847 | 43.2191 | 43.2191 | 109.0541 | 0.3 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 73.1068 | 25.2862 | 601811.127 | 50.1509 | 50.1509 | 118.9784 | 0.4 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 76.6019 | 28.7812 | 684993.5694 | 57.0828 | 57.0828 | 128.9028 | 0.5 | 78.75 | 23.75 | 897750 | 74.8125 | 74.8125 | 80.0969 | 32.2763 | 768176.0117 | 64.0147 | 64.0147 | 138.8272 | 0.6 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 83.592 | 35.7714 | 851358.454 | 70.9465 | 70.9465 | 148.7515 | 0.7 | 80.65 | 25.65 | 969570 | 80.7975 | 80.7975 | 87.0871 | 39.2664 | 934540.8964 | 77.8784 | 77.8784 | 158.6759 | 0.8 | 81.6 | 26.6 | 1005480 | 83.79 | 83.79 | 90.5821 | 42.7615 | 1017723.3387 | 84.8103 | 84.8103 | 168.6003 | 0.9 | 82.55 | 27.55 | 1041390 | 86.7825 | 86.7825 | 94.0772 | 46.2565 | 1100905.781 | 91.7421 | 91.7421 | 178.5246 | 1 | 83.5 | 28.5 | 1077300 | 89.775 | 89.775 | 97.5722 | 49.7516 | 1184088.2234 | 98.674 | 98.674 | 188.449 | 85 | 55 | 35.3612 | 36 | 56.5
7/28/20XX 1:00:00 PM | 0.54167 | 6 | 83.9 | 55.7 | 87.2303 | 105.1128 | 17.8825 | 50 | 83.9 |  | 83.9 | 97.4233 | 0.1 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 66.1018 | 18.2812 | 435091.8389 | 36.2577 | 36.2577 | 99.2262 | 0.2 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 69.582 | 21.7613 | 517919.8779 | 43.16 | 43.16 | 109.247 | 0.3 | 76.97 | 21.97 | 830466 | 69.2055 | 69.2055 | 73.0621 | 25.2415 | 600747.9168 | 50.0623 | 50.0623 | 119.2678 | 0.4 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 76.5423 | 28.7217 | 683575.9558 | 56.9647 | 56.9647 | 129.2887 | 0.5 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 80.0225 | 32.2018 | 766403.9947 | 63.867 | 63.867 | 139.3095 | 0.6 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 83.5027 | 35.682 | 849232.0336 | 70.7693 | 70.7693 | 149.3303 | 0.7 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 86.9828 | 39.1622 | 932060.0726 | 77.6717 | 77.6717 | 159.3512 | 0.8 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 90.463 | 42.6424 | 1014888.1115 | 84.574 | 84.574 | 169.372 | 0.9 | 82.91 | 27.91 | 1054998 | 87.9165 | 87.9165 | 93.9432 | 46.1225 | 1097716.1504 | 91.4763 | 91.4763 | 179.3928 | 1 | 83.9 | 28.9 | 1092420 | 91.035 | 91.035 | 97.4233 | 49.6027 | 1180544.1894 | 98.3787 | 98.3787 | 189.4137 | 85 | 55 | 35.4363 | 36 | 55.7
7/28/20XX 2:00:00 PM | 0.58333 | 6 | 83.7 | 58.3 | 86.6644 | 104.429 | 17.7646 | 50 | 83.7 |  | 83.7 | 101.409 | 0.1 | 74.97 | 19.97 | 754866 | 62.9055 | 62.9055 | 66.5004 | 18.6797 | 444577.7742 | 37.0481 | 37.0481 | 99.9536 | 0.2 | 75.94 | 20.94 | 791532 | 65.961 | 65.961 | 70.3791 | 22.5585 | 536891.7484 | 44.741 | 44.741 | 110.702 | 0.3 | 76.91 | 21.91 | 828198 | 69.0165 | 69.0165 | 74.2578 | 26.4372 | 629205.7226 | 52.4338 | 52.4338 | 121.4503 | 0.4 | 77.88 | 22.88 | 864864 | 72.072 | 72.072 | 78.1366 | 30.316 | 721519.6969 | 60.1266 | 60.1266 | 132.1986 | 0.5 | 78.85 | 23.85 | 901530 | 75.1275 | 75.1275 | 82.0153 | 34.1947 | 813833.6711 | 67.8195 | 67.8195 | 142.947 | 0.6 | 79.82 | 24.82 | 938196 | 78.183 | 78.183 | 85.8941 | 38.0734 | 906147.6453 | 75.5123 | 75.5123 | 153.6953 | 0.7 | 80.79 | 25.79 | 974862 | 81.2385 | 81.2385 | 89.7728 | 41.9522 | 998461.6195 | 83.2051 | 83.2051 | 164.4436 | 0.8 | 81.76 | 26.76 | 1011528 | 84.294 | 84.294 | 93.6515 | 45.8309 | 1090775.5937 | 90.898 | 90.898 | 175.192 | 0.9 | 82.73 | 27.73 | 1048194 | 87.3495 | 87.3495 | 97.5303 | 49.7096 | 1183089.5679 | 98.5908 | 98.5908 | 185.9403 | 1 | 83.7 | 28.7 | 1084860 | 90.405 | 90.405 | 101.409 | 53.5884 | 1275403.5421 | 106.2836 | 106.2836 | 196.6886 | 85 | 60 | 36.013 | 36 | 58.3
7/28/20XX 3:00:00 PM | 0.625 | 6 | 82.9 | 60.9 | 101.7299 | 119.1388 | 17.4089 | 60 | 82.9 |  | 82.9 | 103.2967 | 0.1 | 74.89 | 19.89 | 751842 | 62.6535 | 62.6535 | 66.6891 | 18.8685 | 449070.3595 | 37.4225 | 37.4225 | 100.076 | 0.2 | 75.78 | 20.78 | 785484 | 65.457 | 65.457 | 70.7566 | 22.936 | 545876.919 | 45.4897 | 45.4897 | 110.9467 | 0.3 | 76.67 | 21.67 | 819126 | 68.2605 | 68.2605 | 74.8241 | 27.0035 | 642683.4785 | 53.557 | 53.557 | 121.8175 | 0.4 | 77.56 | 22.56 | 852768 | 71.064 | 71.064 | 78.8916 | 31.071 | 739490.038 | 61.6242 | 61.6242 | 132.6882 | 0.5 | 78.45 | 23.45 | 886410 | 73.8675 | 73.8675 | 82.9591 | 35.1385 | 836296.5975 | 69.6914 | 69.6914 | 143.5589 | 0.6 | 79.34 | 24.34 | 920052 | 76.671 | 76.671 | 87.0266 | 39.206 | 933103.157 | 77.7586 | 77.7586 | 154.4296 | 0.7 | 80.23 | 25.23 | 953694 | 79.4745 | 79.4745 | 91.0941 | 43.2735 | 1029909.7164 | 85.8258 | 85.8258 | 165.3003 | 0.8 | 81.12 | 26.12 | 987336 | 82.278 | 82.278 | 95.1617 | 47.341 | 1126716.2759 | 93.893 | 93.893 | 176.171 | 0.9 | 82.01 | 27.01 | 1020978 | 85.0815 | 85.0815 | 99.2292 | 51.4085 | 1223522.8354 | 101.9602 | 101.9602 | 187.0417 | 1 | 82.9 | 27.9 | 1054620 | 87.885 | 87.885 | 103.2967 | 55.476 | 1320329.3949 | 110.0274 | 110.0274 | 197.9124 | 85 | 60 | 36.1122 | 36 | 60.9
7/28/20XX 4:00:00 PM | 0.66667 | 6 | 82 | 60.3 | 98.7617 | 115.6533 | 16.8916 | 60 | 82 |  | 82 | 99.2685 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 66.2863 | 18.4657 | 439483.2544 | 36.6236 | 36.6236 | 98.9936 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 69.951 | 22.1304 | 526702.7088 | 43.8919 | 43.8919 | 108.7819 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 73.6157 | 25.795 | 613922.1632 | 51.1602 | 51.1602 | 118.5702 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 77.2804 | 29.4597 | 701141.6175 | 58.4285 | 58.4285 | 128.3585 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 80.945 | 33.1244 | 788361.0719 | 65.6968 | 65.6968 | 138.1468 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 84.6097 | 36.7891 | 875580.5263 | 72.965 | 72.965 | 147.935 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 88.2744 | 40.4538 | 962799.9807 | 80.2333 | 80.2333 | 157.7233 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 91.9391 | 44.1185 | 1050019.4351 | 87.5016 | 87.5016 | 167.5116 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 95.6038 | 47.7831 | 1137238.8895 | 94.7699 | 94.7699 | 177.2999 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 99.2685 | 51.4478 | 1224458.3438 | 102.0382 | 102.0382 | 187.0882 | 80 | 60 | 35.2581 | 36 | 60.3
7/28/20XX 5:00:00 PM | 0.70833 | 6 | 80.7 | 64 | 94.6002 | 110.7667 | 16.1665 | 60 | 80.7 |  | 80.7 | 101.0668 | 0.1 | 74.67 | 19.67 | 743526 | 61.9605 | 61.9605 | 66.4661 | 18.6455 | 443763.2512 | 36.9803 | 36.9803 | 98.9408 | 0.2 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 70.3107 | 22.49 | 535262.7024 | 44.6052 | 44.6052 | 108.6762 | 0.3 | 76.01 | 21.01 | 794178 | 66.1815 | 66.1815 | 74.1552 | 26.3345 | 626762.1536 | 52.2302 | 52.2302 | 118.4117 | 0.4 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 77.9997 | 30.1791 | 718261.6049 | 59.8551 | 59.8551 | 128.1471 | 0.5 | 77.35 | 22.35 | 844830 | 70.4025 | 70.4025 | 81.8442 | 34.0236 | 809761.0561 | 67.4801 | 67.4801 | 137.8826 | 0.6 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 85.6887 | 37.8681 | 901260.5073 | 75.105 | 75.105 | 147.618 | 0.7 | 78.69 | 23.69 | 895482 | 74.6235 | 74.6235 | 89.5332 | 41.7126 | 992759.9585 | 82.73 | 82.73 | 157.3535 | 0.8 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 93.3778 | 45.5571 | 1084259.4097 | 90.355 | 90.355 | 167.089 | 0.9 | 80.03 | 25.03 | 946134 | 78.8445 | 78.8445 | 97.2223 | 49.4016 | 1175758.8609 | 97.9799 | 97.9799 | 176.8244 | 1 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 101.0668 | 53.2461 | 1267258.3121 | 105.6049 | 105.6049 | 186.5599 | 80 | 65 | 35.22 | 36 | 64
7/28/20XX 6:00:00 PM | 0.75 | 6 | 79.3 | 67 | 90.2816 | 105.6957 | 15.4142 | 60 | 79.3 |  | 79.3 | 101.0715 | 0.1 | 74.53 | 19.53 | 738234 | 61.5195 | 61.5195 | 66.4666 | 18.646 | 443774.4417 | 36.9812 | 36.9812 | 98.5007 | 0.2 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 70.3116 | 22.491 | 535285.0834 | 44.6071 | 44.6071 | 107.7961 | 0.3 | 75.59 | 20.59 | 778302 | 64.8585 | 64.8585 | 74.1566 | 26.336 | 626795.725 | 52.233 | 52.233 | 117.0915 | 0.4 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 78.0016 | 30.1809 | 718306.3667 | 59.8589 | 59.8589 | 126.3869 | 0.5 | 76.65 | 21.65 | 818370 | 68.1975 | 68.1975 | 81.8466 | 34.0259 | 809817.0084 | 67.4848 | 67.4848 | 135.6823 | 0.6 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 85.6915 | 37.8709 | 901327.6501 | 75.1106 | 75.1106 | 144.9776 | 0.7 | 77.71 | 22.71 | 858438 | 71.5365 | 71.5365 | 89.5365 | 41.7159 | 992838.2918 | 82.7365 | 82.7365 | 154.273 | 0.8 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 93.3815 | 45.5609 | 1084348.9335 | 90.3624 | 90.3624 | 163.5684 | 0.9 | 78.77 | 23.77 | 898506 | 74.8755 | 74.8755 | 97.2265 | 49.4059 | 1175859.5751 | 97.9883 | 97.9883 | 172.8638 | 1 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 101.0715 | 53.2508 | 1267370.2168 | 105.6142 | 105.6142 | 182.1592 | 80 | 65 | 34.8758 | 34 | 67
7/28/20XX 7:00:00 PM | 0.79167 | 6 | 77.9 | 69.6 | 86.1281 | 100.819 | 14.691 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/28/20XX 8:00:00 PM | 0.83333 | 6 | 77.2 | 69.8 | 84.112 | 98.452 | 14.34 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/28/20XX 9:00:00 PM | 0.875 | 6 | 77.2 | 70.3 | 98.452 | 112.9035 | 14.4515 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/28/20XX 10:00:00 PM | 0.91667 | 6 | 76.5 | 72.7 | 96.1318 | 110.2335 | 14.1017 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/28/20XX 11:00:00 PM | 0.95833 | 6 | 75.8 | 72.7 | 93.8579 | 107.6171 | 13.7592 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/28/20XX 12:00:00 AM | 0 | 7 | 75 | 74.6 | 91.3149 | 104.6916 | 13.3767 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/29/20XX 1:00:00 AM | 0.041667 | 7 | 74.3 | 75.7 | 89.138 | 102.1877 | 13.0496 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/29/20XX 2:00:00 AM | 0.083333 | 7 | 73.5 | 76.2 | 86.7045 | 99.389 | 12.6844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/29/20XX 3:00:00 AM | 0.125 | 7 | 72.8 | 77.5 | 84.6221 | 96.9944 | 12.3723 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/29/20XX 4:00:00 AM | 0.16667 | 7 | 72.3 | 79.5 | 83.1611 | 95.3147 | 12.1536 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/29/20XX 5:00:00 AM | 0.20833 | 7 | 71.5 | 80.4 | 92.6795 | 104.5026 | 11.8231 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/29/20XX 6:00:00 AM | 0.25 | 7 | 71.9 | 79.5 | 82.008 | 93.989 | 11.9811 | 70 | 71.9 |  | 71.9 | 93.39 | 0.1 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 65.6985 | 17.8778 | 425492.476 | 35.4577 | 35.4577 | 94.6462 | 0.2 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 68.7753 | 20.9547 | 498721.152 | 41.5601 | 41.5601 | 100.0871 | 0.3 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 71.8521 | 24.0315 | 571949.828 | 47.6625 | 47.6625 | 105.528 | 0.4 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 74.929 | 27.1083 | 645178.5041 | 53.7649 | 53.7649 | 110.9689 | 0.5 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 78.0058 | 30.1852 | 718407.1801 | 59.8673 | 59.8673 | 116.4098 | 0.6 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 81.0826 | 33.262 | 791635.8561 | 65.9697 | 65.9697 | 121.8507 | 0.7 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 84.1595 | 36.3388 | 864864.5321 | 72.072 | 72.072 | 127.2915 | 0.8 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 87.2363 | 39.4157 | 938093.2081 | 78.1744 | 78.1744 | 132.7324 | 0.9 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 90.3131 | 42.4925 | 1011321.8841 | 84.2768 | 84.2768 | 138.1733 | 1 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 93.39 | 45.5694 | 1084550.5601 | 90.3792 | 90.3792 | 143.6142 | 70 | 80 | 31.8517 | 32 | 79.5
7/29/20XX 7:00:00 AM | 0.29167 | 7 | 71.7 | 81.1 | 93.3322 | 105.2414 | 11.9091 | 80 | 71.7 |  | 71.7 | 94.6423 | 0.1 | 73.77 | 18.77 | 709506 | 59.1255 | 59.1255 | 65.8237 | 18.0031 | 428472.8773 | 35.7061 | 35.7061 | 94.8316 | 0.2 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 69.0258 | 21.2051 | 504681.9545 | 42.0568 | 42.0568 | 100.4578 | 0.3 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 72.2278 | 24.4072 | 580891.0318 | 48.4076 | 48.4076 | 106.0841 | 0.4 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 75.4299 | 27.6092 | 657100.109 | 54.7583 | 54.7583 | 111.7103 | 0.5 | 72.85 | 17.85 | 674730 | 56.2275 | 56.2275 | 78.6319 | 30.8113 | 733309.1863 | 61.1091 | 61.1091 | 117.3366 | 0.6 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 81.834 | 34.0134 | 809518.2635 | 67.4599 | 67.4599 | 122.9629 | 0.7 | 72.39 | 17.39 | 657342 | 54.7785 | 54.7785 | 85.0361 | 37.2154 | 885727.3408 | 73.8106 | 73.8106 | 128.5891 | 0.8 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 88.2381 | 40.4175 | 961936.418 | 80.1614 | 80.1614 | 134.2154 | 0.9 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 91.4402 | 43.6196 | 1038145.4953 | 86.5121 | 86.5121 | 139.8416 | 1 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 94.6423 | 46.8216 | 1114354.5725 | 92.8629 | 92.8629 | 145.4679 | 70 | 80 | 31.9983 | 32 | 81.1
7/29/20XX 8:00:00 AM | 0.33333 | 7 | 72.8 | 77 | 84.6221 | 96.9944 | 12.3723 | 70 | 72.8 |  | 72.8 | 93.2827 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.6877 | 17.8671 | 425237.1712 | 35.4364 | 35.4364 | 94.9084 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 68.7538 | 20.9332 | 498210.5423 | 41.5175 | 41.5175 | 100.6115 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 71.82 | 23.9993 | 571183.9135 | 47.5987 | 47.5987 | 106.3147 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 74.8861 | 27.0654 | 644157.2847 | 53.6798 | 53.6798 | 112.0178 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 77.9522 | 30.1315 | 717130.6559 | 59.7609 | 59.7609 | 117.7209 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 81.0183 | 33.1976 | 790104.027 | 65.842 | 65.842 | 123.424 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 84.0844 | 36.2638 | 863077.3982 | 71.9231 | 71.9231 | 129.1271 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 87.1505 | 39.3299 | 936050.7694 | 78.0042 | 78.0042 | 134.8302 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 90.2166 | 42.396 | 1009024.1406 | 84.0853 | 84.0853 | 140.5333 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 93.2827 | 45.4621 | 1081997.5117 | 90.1665 | 90.1665 | 146.2365 | 75 | 75 | 32.0563 | 32 | 77
7/29/20XX 9:00:00 AM | 0.375 | 7 | 74.2 | 73.4 | 88.8307 | 101.8342 | 13.0035 | 70 | 74.2 |  | 74.2 | 93.2519 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 65.6847 | 17.864 | 425163.8076 | 35.4303 | 35.4303 | 95.3433 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 68.7477 | 20.9271 | 498063.8153 | 41.5053 | 41.5053 | 101.4813 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 71.8107 | 23.9901 | 570963.8229 | 47.5803 | 47.5803 | 107.6193 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 74.8737 | 27.0531 | 643863.8305 | 53.6553 | 53.6553 | 113.7573 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 77.9368 | 30.1161 | 716763.8381 | 59.7303 | 59.7303 | 119.8953 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 80.9998 | 33.1792 | 789663.8458 | 65.8053 | 65.8053 | 126.0333 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 84.0628 | 36.2422 | 862563.8534 | 71.8803 | 71.8803 | 132.1713 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 87.1258 | 39.3052 | 935463.861 | 77.9553 | 77.9553 | 138.3093 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 90.1889 | 42.3682 | 1008363.8686 | 84.0303 | 84.0303 | 144.4473 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 93.2519 | 45.4313 | 1081263.8763 | 90.1053 | 90.1053 | 150.5853 | 75 | 75 | 32.3958 | 32 | 73.4
7/29/20XX 10:00:00 AM | 0.41667 | 7 | 75.9 | 68.9 | 80.4731 | 94.1799 | 13.7068 | 60 | 75.9 |  | 75.9 | 92.6722 | 0.1 | 74.19 | 19.19 | 725382 | 60.4485 | 60.4485 | 65.6267 | 17.8061 | 423784.1016 | 35.3153 | 35.3153 | 95.7638 | 0.2 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 68.6317 | 20.8111 | 495304.4031 | 41.2754 | 41.2754 | 102.3224 | 0.3 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 71.6368 | 23.8162 | 566824.7047 | 47.2354 | 47.2354 | 108.8809 | 0.4 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 74.6419 | 26.8212 | 638345.0062 | 53.1954 | 53.1954 | 115.4394 | 0.5 | 74.95 | 19.95 | 754110 | 62.8425 | 62.8425 | 77.6469 | 29.8263 | 709865.3078 | 59.1554 | 59.1554 | 121.9979 | 0.6 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 80.652 | 32.8313 | 781385.6094 | 65.1155 | 65.1155 | 128.5565 | 0.7 | 75.33 | 20.33 | 768474 | 64.0395 | 64.0395 | 83.657 | 35.8364 | 852905.9109 | 71.0755 | 71.0755 | 135.115 | 0.8 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 86.6621 | 38.8414 | 924426.2125 | 77.0355 | 77.0355 | 141.6735 | 0.9 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 89.6671 | 41.8465 | 995946.5141 | 82.9955 | 82.9955 | 148.232 | 1 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 92.6722 | 44.8515 | 1067466.8156 | 88.9556 | 88.9556 | 154.7906 | 75 | 70 | 32.7231 | 32 | 68.9
7/29/20XX 11:00:00 AM | 0.45833 | 7 | 77.9 | 64.1 | 86.1281 | 100.819 | 14.691 | 60 | 77.9 |  | 77.9 | 92.1514 | 0.1 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 65.5746 | 17.754 | 422544.5392 | 35.212 | 35.212 | 96.2905 | 0.2 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 68.5276 | 20.7069 | 492825.2784 | 41.0688 | 41.0688 | 103.3758 | 0.3 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 71.4805 | 23.6599 | 563106.0177 | 46.9255 | 46.9255 | 110.461 | 0.4 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 74.4335 | 26.6129 | 633386.7569 | 52.7822 | 52.7822 | 117.5462 | 0.5 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 77.3865 | 29.5659 | 703667.4961 | 58.639 | 58.639 | 124.6315 | 0.6 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 80.3395 | 32.5188 | 773948.2353 | 64.4957 | 64.4957 | 131.7167 | 0.7 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 83.2924 | 35.4718 | 844228.9745 | 70.3524 | 70.3524 | 138.8019 | 0.8 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 86.2454 | 38.4248 | 914509.7138 | 76.2091 | 76.2091 | 145.8871 | 0.9 | 77.51 | 22.51 | 850878 | 70.9065 | 70.9065 | 89.1984 | 41.3778 | 984790.453 | 82.0659 | 82.0659 | 152.9724 | 1 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 92.1514 | 44.3307 | 1055071.1922 | 87.9226 | 87.9226 | 160.0576 | 80 | 65 | 33.1333 | 34 | 64.1
7/29/20XX 12:00:00 PM | 0.5 | 7 | 79.1 | 61.3 | 89.6782 | 104.9873 | 15.3091 | 60 | 79.1 |  | 79.1 | 91.6684 | 0.1 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 65.5263 | 17.7057 | 421395.0152 | 35.1163 | 35.1163 | 96.5728 | 0.2 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 68.431 | 20.6103 | 490526.2304 | 40.8772 | 40.8772 | 103.9402 | 0.3 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 71.3357 | 23.515 | 559657.4456 | 46.6381 | 46.6381 | 111.3076 | 0.4 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 74.2403 | 26.4197 | 628788.6608 | 52.3991 | 52.3991 | 118.6751 | 0.5 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 77.145 | 29.3244 | 697919.876 | 58.16 | 58.16 | 126.0425 | 0.6 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 80.0497 | 32.229 | 767051.0912 | 63.9209 | 63.9209 | 133.4099 | 0.7 | 77.57 | 22.57 | 853146 | 71.0955 | 71.0955 | 82.9543 | 35.1337 | 836182.3064 | 69.6819 | 69.6819 | 140.7774 | 0.8 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 85.859 | 38.0384 | 905313.5217 | 75.4428 | 75.4428 | 148.1448 | 0.9 | 78.59 | 23.59 | 891702 | 74.3085 | 74.3085 | 88.7637 | 40.9431 | 974444.7369 | 81.2037 | 81.2037 | 155.5122 | 1 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 91.6684 | 43.8477 | 1043575.9521 | 86.9647 | 86.9647 | 162.8797 | 80 | 60 | 33.3526 | 34 | 61.3
7/29/20XX 1:00:00 PM | 0.54167 | 7 | 79.8 | 61.3 | 91.8048 | 107.4842 | 15.6795 | 60 | 79.8 |  | 79.8 | 93.8431 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 65.7438 | 17.9231 | 426570.8782 | 35.5476 | 35.5476 | 97.2246 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 68.8659 | 21.0453 | 500877.9563 | 41.7398 | 41.7398 | 105.2438 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 71.9881 | 24.1674 | 575185.0345 | 47.9321 | 47.9321 | 113.2631 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 75.1102 | 27.2896 | 649492.1126 | 54.1243 | 54.1243 | 121.2823 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 78.2324 | 30.4117 | 723799.1908 | 60.3166 | 60.3166 | 129.3016 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 81.3545 | 33.5339 | 798106.2689 | 66.5089 | 66.5089 | 137.3209 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 84.4767 | 36.656 | 872413.3471 | 72.7011 | 72.7011 | 145.3401 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 87.5988 | 39.7782 | 946720.4252 | 78.8934 | 78.8934 | 153.3594 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 90.7209 | 42.9003 | 1021027.5034 | 85.0856 | 85.0856 | 161.3786 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 93.8431 | 46.0225 | 1095334.5815 | 91.2779 | 91.2779 | 169.3979 | 80 | 60 | 33.8656 | 34 | 61.3
7/29/20XX 2:00:00 PM | 0.58333 | 7 | 80 | 61.5 | 92.42 | 108.2066 | 15.7866 | 60 | 80 |  | 80 | 94.788 | 0.1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 65.8383 | 18.0176 | 428819.7077 | 35.735 | 35.735 | 97.475 | 0.2 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 69.0549 | 21.2343 | 505375.6154 | 42.1146 | 42.1146 | 105.7446 | 0.3 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 72.2715 | 24.4509 | 581931.5231 | 48.4943 | 48.4943 | 114.0143 | 0.4 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 75.4882 | 27.6675 | 658487.4308 | 54.874 | 54.874 | 122.284 | 0.5 | 77 | 22 | 831600 | 69.3 | 69.3 | 78.7048 | 30.8842 | 735043.3385 | 61.2536 | 61.2536 | 130.5536 | 0.6 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 81.9214 | 34.1008 | 811599.2462 | 67.6333 | 67.6333 | 138.8233 | 0.7 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 85.1381 | 37.3174 | 888155.1539 | 74.0129 | 74.0129 | 147.0929 | 0.8 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 88.3547 | 40.5341 | 964711.0616 | 80.3926 | 80.3926 | 155.3626 | 0.9 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 91.5713 | 43.7507 | 1041266.9693 | 86.7722 | 86.7722 | 163.6322 | 1 | 80 | 25 | 945000 | 78.75 | 78.75 | 94.788 | 46.9673 | 1117822.877 | 93.1519 | 93.1519 | 171.9019 | 80 | 60 | 34.063 | 34 | 61.5
7/29/20XX 3:00:00 PM | 0.625 | 7 | 80.9 | 57.2 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 90.7005 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 65.4295 | 17.6089 | 419091.4484 | 34.9243 | 34.9243 | 96.9478 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 68.2374 | 20.4168 | 485919.0967 | 40.4933 | 40.4933 | 104.6903 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 71.0453 | 23.2247 | 552746.7451 | 46.0622 | 46.0622 | 112.4327 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 73.8532 | 26.0325 | 619574.3935 | 51.6312 | 51.6312 | 120.1752 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 76.6611 | 28.8404 | 686402.0419 | 57.2002 | 57.2002 | 127.9177 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 79.4689 | 31.6483 | 753229.6902 | 62.7691 | 62.7691 | 135.6601 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 82.2768 | 34.4562 | 820057.3386 | 68.3381 | 68.3381 | 143.4026 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 85.0847 | 37.2641 | 886884.987 | 73.9071 | 73.9071 | 151.1451 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 87.8926 | 40.072 | 953712.6354 | 79.4761 | 79.4761 | 158.8876 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 90.7005 | 42.8798 | 1020540.2837 | 85.045 | 85.045 | 166.63 | 80 | 55 | 33.6432 | 34 | 57.2
7/29/20XX 4:00:00 PM | 0.66667 | 7 | 80 | 60.8 | 92.42 | 108.2066 | 15.7866 | 60 | 80 |  | 80 | 93.6829 | 0.1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 65.7278 | 17.9071 | 426189.6524 | 35.5158 | 35.5158 | 97.2558 | 0.2 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 68.8339 | 21.0133 | 500115.5048 | 41.6763 | 41.6763 | 105.3063 | 0.3 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 71.94 | 24.1194 | 574041.3572 | 47.8368 | 47.8368 | 113.3568 | 0.4 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 75.0461 | 27.2255 | 647967.2096 | 53.9973 | 53.9973 | 121.4073 | 0.5 | 77 | 22 | 831600 | 69.3 | 69.3 | 78.1523 | 30.3316 | 721893.062 | 60.1578 | 60.1578 | 129.4578 | 0.6 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 81.2584 | 33.4378 | 795818.9144 | 66.3182 | 66.3182 | 137.5082 | 0.7 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 84.3645 | 36.5439 | 869744.7668 | 72.4787 | 72.4787 | 145.5587 | 0.8 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 87.4707 | 39.65 | 943670.6192 | 78.6392 | 78.6392 | 153.6092 | 0.9 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 90.5768 | 42.7562 | 1017596.4716 | 84.7997 | 84.7997 | 161.6597 | 1 | 80 | 25 | 945000 | 78.75 | 78.75 | 93.6829 | 45.8623 | 1091522.324 | 90.9602 | 90.9602 | 169.7102 | 80 | 60 | 33.8897 | 34 | 60.8
7/29/20XX 5:00:00 PM | 0.70833 | 7 | 80.1 | 58.3 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 90.0515 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 65.3646 | 17.544 | 417546.8228 | 34.7956 | 34.7956 | 96.5671 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 68.1076 | 20.287 | 482829.8457 | 40.2358 | 40.2358 | 103.9288 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 70.8506 | 23.03 | 548112.8685 | 45.6761 | 45.6761 | 111.2906 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 73.5936 | 25.7729 | 613395.8913 | 51.1163 | 51.1163 | 118.6523 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 76.3366 | 28.5159 | 678678.9142 | 56.5566 | 56.5566 | 126.0141 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 79.0795 | 31.2589 | 743961.937 | 61.9968 | 61.9968 | 133.3758 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 81.8225 | 34.0019 | 809244.9598 | 67.4371 | 67.4371 | 140.7376 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 84.5655 | 36.7449 | 874527.9827 | 72.8773 | 72.8773 | 148.0993 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 87.3085 | 39.4879 | 939811.0055 | 78.3176 | 78.3176 | 155.4611 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 90.0515 | 42.2308 | 1005094.0284 | 83.7578 | 83.7578 | 162.8228 | 80 | 60 | 33.3449 | 34 | 58.3
7/29/20XX 6:00:00 PM | 0.75 | 7 | 78.8 | 59.3 | 73.7091 | 88.7794 | 15.0703 | 50 | 78.8 |  | 78.8 | 87.7245 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 65.1319 | 17.3113 | 412008.6056 | 34.3341 | 34.3341 | 95.6961 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 67.6422 | 19.8216 | 471753.4112 | 39.3128 | 39.3128 | 102.1868 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 70.1525 | 22.3319 | 531498.2168 | 44.2915 | 44.2915 | 108.6775 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 72.6628 | 24.8421 | 591243.0224 | 49.2703 | 49.2703 | 115.1683 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 75.1731 | 27.3524 | 650987.828 | 54.249 | 54.249 | 121.659 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 77.6833 | 29.8627 | 710732.6336 | 59.2277 | 59.2277 | 128.1497 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 80.1936 | 32.373 | 770477.4392 | 64.2065 | 64.2065 | 134.6405 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 82.7039 | 34.8833 | 830222.2448 | 69.1852 | 69.1852 | 141.1312 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 85.2142 | 37.3936 | 889967.0503 | 74.1639 | 74.1639 | 147.6219 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 87.7245 | 39.9039 | 949711.8559 | 79.1427 | 79.1427 | 154.1127 | 80 | 60 | 32.6607 | 32 | 59.3
7/29/20XX 7:00:00 PM | 0.79167 | 7 | 77.4 | 62.3 | 84.6839 | 99.1235 | 14.4396 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/29/20XX 8:00:00 PM | 0.83333 | 7 | 76.6 | 63.2 | 82.4157 | 96.4605 | 14.0448 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/29/20XX 9:00:00 PM | 0.875 | 7 | 75.8 | 64.7 | 80.1988 | 93.8579 | 13.6591 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/29/20XX 10:00:00 PM | 0.91667 | 7 | 74.9 | 65.9 | 77.7654 | 91.0012 | 13.2358 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/29/20XX 11:00:00 PM | 0.95833 | 7 | 74.4 | 65.9 | 76.4409 | 89.4463 | 13.0054 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/29/20XX 12:00:00 AM | 0 | 1 | 73.4 | 69.1 | 73.8495 | 86.4044 | 12.5549 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/30/20XX 1:00:00 AM | 0.041667 | 1 | 72.8 | 69.9 | 72.3311 | 84.6221 | 12.291 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/30/20XX 2:00:00 AM | 0.083333 | 1 | 71.9 | 71.1 | 82.008 | 93.989 | 11.9811 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/30/20XX 3:00:00 AM | 0.125 | 1 | 71.3 | 73.3 | 80.3042 | 92.0306 | 11.7264 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/30/20XX 4:00:00 AM | 0.16667 | 1 | 70.8 | 71.3 | 78.908 | 90.4259 | 11.5179 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/30/20XX 5:00:00 AM | 0.20833 | 1 | 70 | 73.9 | 76.7179 | 87.9091 | 11.1912 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/30/20XX 6:00:00 AM | 0.25 | 1 | 70.6 | 73 | 78.3554 | 89.7909 | 11.4354 | 70 | 70.6 |  | 70.6 | 81.7861 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 64.5381 | 16.7174 | 397875.1235 | 33.1563 | 33.1563 | 91.9353 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 66.4545 | 18.6339 | 443486.4469 | 36.9572 | 36.9572 | 94.6652 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 68.371 | 20.5503 | 489097.7704 | 40.7581 | 40.7581 | 97.3951 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 70.2874 | 22.4668 | 534709.0939 | 44.5591 | 44.5591 | 100.1251 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 72.2038 | 24.3832 | 580320.4173 | 48.36 | 48.36 | 102.855 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 74.1203 | 26.2997 | 625931.7408 | 52.161 | 52.161 | 105.585 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 76.0367 | 28.2161 | 671543.0642 | 55.9619 | 55.9619 | 108.3149 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 77.9532 | 30.1325 | 717154.3877 | 59.7629 | 59.7629 | 111.0449 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 79.8696 | 32.049 | 762765.7112 | 63.5638 | 63.5638 | 113.7748 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 81.7861 | 33.9654 | 808377.0346 | 67.3648 | 67.3648 | 116.5048 | 70 | 75 | 29.7194 | 30 | 73
7/30/20XX 7:00:00 AM | 0.29167 | 1 | 71.8 | 71.4 | 81.7218 | 93.6601 | 11.9383 | 70 | 71.8 |  | 71.8 | 83.3932 | 0.1 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 64.6988 | 16.8782 | 401700.1499 | 33.475 | 33.475 | 92.632 | 0.2 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 66.7759 | 18.9553 | 451136.4998 | 37.5947 | 37.5947 | 96.0587 | 0.3 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 68.8531 | 21.0325 | 500572.8498 | 41.7144 | 41.7144 | 99.4854 | 0.4 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 70.9303 | 23.1096 | 550009.1997 | 45.8341 | 45.8341 | 102.9121 | 0.5 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 73.0074 | 25.1868 | 599445.5496 | 49.9538 | 49.9538 | 106.3388 | 0.6 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 75.0846 | 27.2639 | 648881.8995 | 54.0735 | 54.0735 | 109.7655 | 0.7 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 77.1617 | 29.3411 | 698318.2494 | 58.1932 | 58.1932 | 113.1922 | 0.8 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 79.2389 | 31.4183 | 747754.5993 | 62.3129 | 62.3129 | 116.6189 | 0.9 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 81.3161 | 33.4954 | 797190.9493 | 66.4326 | 66.4326 | 120.0456 | 1 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 83.3932 | 35.5726 | 846627.2992 | 70.5523 | 70.5523 | 123.4723 | 70 | 70 | 30.2648 | 30 | 71.4
7/30/20XX 8:00:00 AM | 0.33333 | 1 | 73.5 | 65.2 | 74.1052 | 86.7045 | 12.5993 | 60 | 73.5 |  | 73.5 | 80.6569 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 64.4252 | 16.6045 | 395187.6227 | 32.9323 | 32.9323 | 92.6248 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 66.2287 | 18.408 | 438111.4453 | 36.5093 | 36.5093 | 96.0443 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 68.0322 | 20.2116 | 481035.268 | 40.0863 | 40.0863 | 99.4638 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 69.8357 | 22.0151 | 523959.0906 | 43.6633 | 43.6633 | 102.8833 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 71.6392 | 23.8186 | 566882.9133 | 47.2402 | 47.2402 | 106.3027 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 73.4428 | 25.6221 | 609806.7359 | 50.8172 | 50.8172 | 109.7222 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 75.2463 | 27.4257 | 652730.5586 | 54.3942 | 54.3942 | 113.1417 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 77.0498 | 29.2292 | 695654.3812 | 57.9712 | 57.9712 | 116.5612 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 78.8533 | 31.0327 | 738578.2039 | 61.5482 | 61.5482 | 119.9807 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 80.6569 | 32.8362 | 781502.0265 | 65.1252 | 65.1252 | 123.4002 | 75 | 65 | 30.2539 | 30 | 65.2
7/30/20XX 9:00:00 AM | 0.375 | 1 | 75.3 | 61.8 | 78.8391 | 92.2616 | 13.4225 | 60 | 75.3 |  | 75.3 | 81.2551 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 64.485 | 16.6644 | 396611.5523 | 33.051 | 33.051 | 93.3105 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 66.3483 | 18.5277 | 440959.3045 | 36.7466 | 36.7466 | 97.4156 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 68.2117 | 20.3911 | 485307.0568 | 40.4423 | 40.4423 | 101.5208 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 70.075 | 22.2544 | 529654.809 | 44.1379 | 44.1379 | 105.6259 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 71.9384 | 24.1178 | 574002.5613 | 47.8335 | 47.8335 | 109.731 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 73.8017 | 25.9811 | 618350.3135 | 51.5292 | 51.5292 | 113.8362 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 75.6651 | 27.8445 | 662698.0658 | 55.2248 | 55.2248 | 117.9413 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 77.5284 | 29.7078 | 707045.8181 | 58.9205 | 58.9205 | 122.0465 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 79.3918 | 31.5712 | 751393.5703 | 62.6161 | 62.6161 | 126.1516 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 81.2551 | 33.4345 | 795741.3226 | 66.3118 | 66.3118 | 130.2568 | 75 | 60 | 30.7888 | 30 | 61.8
7/30/20XX 10:00:00 AM | 0.41667 | 1 | 77 | 57.6 | 69.3725 | 83.5433 | 14.1708 | 50 | 77 |  | 77 | 80.1423 | 0.1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 64.3737 | 16.5531 | 393963.0675 | 32.8303 | 32.8303 | 93.6253 | 0.2 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 66.1258 | 18.3051 | 435662.335 | 36.3052 | 36.3052 | 98.0452 | 0.3 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 67.8778 | 20.0572 | 477361.6024 | 39.7801 | 39.7801 | 102.4651 | 0.4 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 69.6299 | 21.8093 | 519060.8699 | 43.2551 | 43.2551 | 106.8851 | 0.5 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 71.382 | 23.5614 | 560760.1374 | 46.73 | 46.73 | 111.305 | 0.6 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 73.1341 | 25.3134 | 602459.4049 | 50.205 | 50.205 | 115.725 | 0.7 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 74.8861 | 27.0655 | 644158.6723 | 53.6799 | 53.6799 | 120.1449 | 0.8 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 76.6382 | 28.8176 | 685857.9398 | 57.1548 | 57.1548 | 124.5648 | 0.9 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 78.3903 | 30.5696 | 727557.2073 | 60.6298 | 60.6298 | 128.9848 | 1 | 77 | 22 | 831600 | 69.3 | 69.3 | 80.1423 | 32.3217 | 769256.4748 | 64.1047 | 64.1047 | 133.4047 | 75 | 60 | 31.0312 | 32 | 57.6
7/30/20XX 11:00:00 AM | 0.45833 | 1 | 79.9 | 52.7 | 76.4687 | 92.1119 | 15.6433 | 50 | 79.9 |  | 79.9 | 80.6924 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 64.4287 | 16.6081 | 395272.113 | 32.9393 | 32.9393 | 94.6478 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 66.2358 | 18.4151 | 438280.4261 | 36.5234 | 36.5234 | 100.0904 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 68.0428 | 20.2222 | 481288.7391 | 40.1074 | 40.1074 | 105.5329 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 69.8499 | 22.0293 | 524297.0522 | 43.6914 | 43.6914 | 110.9754 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 71.657 | 23.8364 | 567305.3652 | 47.2754 | 47.2754 | 116.4179 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 73.4641 | 25.6434 | 610313.6783 | 50.8595 | 50.8595 | 121.8605 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 75.2711 | 27.4505 | 653321.9913 | 54.4435 | 54.4435 | 127.303 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 77.0782 | 29.2576 | 696330.3044 | 58.0275 | 58.0275 | 132.7455 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 78.8853 | 31.0646 | 739338.6174 | 61.6116 | 61.6116 | 138.1881 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 80.6924 | 32.8717 | 782346.9305 | 65.1956 | 65.1956 | 143.6306 | 80 | 55 | 31.8282 | 32 | 52.7
7/30/20XX 12:00:00 PM | 0.5 | 1 | 80.5 | 51.6 | 78.0095 | 93.973 | 15.9635 | 50 | 80.5 |  | 80.5 | 80.5637 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 64.4158 | 16.5952 | 394965.8714 | 32.9138 | 32.9138 | 94.8113 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 66.21 | 18.3894 | 437667.9428 | 36.4723 | 36.4723 | 100.4173 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 68.0042 | 20.1836 | 480370.0142 | 40.0308 | 40.0308 | 106.0233 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 69.7985 | 21.9778 | 523072.0856 | 43.5893 | 43.5893 | 111.6293 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 71.5927 | 23.772 | 565774.157 | 47.1478 | 47.1478 | 117.2353 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 73.3869 | 25.5662 | 608476.2284 | 50.7064 | 50.7064 | 122.8414 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 75.1811 | 27.3604 | 651178.2998 | 54.2649 | 54.2649 | 128.4474 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 76.9753 | 29.1546 | 693880.3712 | 57.8234 | 57.8234 | 134.0534 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 78.7695 | 30.9488 | 736582.4426 | 61.3819 | 61.3819 | 139.6594 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 80.5637 | 32.743 | 779284.5141 | 64.9404 | 64.9404 | 145.2654 | 80 | 50 | 31.9551 | 32 | 51.6
7/30/20XX 1:00:00 PM | 0.54167 | 1 | 80.9 | 53.2 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 84.2285 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 64.7823 | 16.9617 | 403688.1423 | 33.6407 | 33.6407 | 95.6642 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 66.943 | 19.1224 | 455112.4847 | 37.926 | 37.926 | 102.123 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 69.1037 | 21.2831 | 506536.827 | 42.2114 | 42.2114 | 108.5819 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 71.2644 | 23.4437 | 557961.1694 | 46.4968 | 46.4968 | 115.0408 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 73.4251 | 25.6044 | 609385.5117 | 50.7821 | 50.7821 | 121.4996 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 75.5858 | 27.7651 | 660809.8541 | 55.0675 | 55.0675 | 127.9585 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 77.7464 | 29.9258 | 712234.1964 | 59.3528 | 59.3528 | 134.4173 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 79.9071 | 32.0865 | 763658.5388 | 63.6382 | 63.6382 | 140.8762 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 82.0678 | 34.2472 | 815082.8811 | 67.9236 | 67.9236 | 147.3351 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 84.2285 | 36.4079 | 866507.2235 | 72.2089 | 72.2089 | 153.7939 | 80 | 55 | 32.628 | 32 | 53.2
7/30/20XX 2:00:00 PM | 0.58333 | 1 | 80.2 | 54.2 | 77.2359 | 93.0386 | 15.8027 | 50 | 80.2 |  | 80.2 | 83.8731 | 0.1 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 64.7468 | 16.9261 | 402842.1854 | 33.5702 | 33.5702 | 95.3732 | 0.2 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 66.8719 | 19.0513 | 453420.5707 | 37.785 | 37.785 | 101.541 | 0.3 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 68.9971 | 21.1764 | 503998.9561 | 41.9999 | 41.9999 | 107.7089 | 0.4 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 71.1222 | 23.3016 | 554577.3415 | 46.2148 | 46.2148 | 113.8768 | 0.5 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 73.2473 | 25.4267 | 605155.7269 | 50.4296 | 50.4296 | 120.0446 | 0.6 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 75.3725 | 27.5519 | 655734.1122 | 54.6445 | 54.6445 | 126.2125 | 0.7 | 78.34 | 23.34 | 882252 | 73.521 | 73.521 | 77.4976 | 29.677 | 706312.4976 | 58.8594 | 58.8594 | 132.3804 | 0.8 | 78.96 | 23.96 | 905688 | 75.474 | 75.474 | 79.6228 | 31.8021 | 756890.883 | 63.0742 | 63.0742 | 138.5482 | 0.9 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 81.7479 | 33.9273 | 807469.2684 | 67.2891 | 67.2891 | 144.7161 | 1 | 80.2 | 25.2 | 952560 | 79.38 | 79.38 | 83.8731 | 36.0524 | 858047.6537 | 71.504 | 71.504 | 150.884 | 80 | 55 | 32.4006 | 32 | 54.2
7/30/20XX 3:00:00 PM | 0.625 | 1 | 80.2 | 54.1 | 77.2359 | 93.0386 | 15.8027 | 50 | 80.2 |  | 80.2 | 83.715 | 0.1 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 64.731 | 16.9103 | 402466.0813 | 33.5388 | 33.5388 | 95.3418 | 0.2 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 66.8403 | 19.0197 | 452668.3626 | 37.7224 | 37.7224 | 101.4784 | 0.3 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 68.9497 | 21.129 | 502870.6439 | 41.9059 | 41.9059 | 107.6149 | 0.4 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 71.059 | 23.2384 | 553072.9252 | 46.0894 | 46.0894 | 113.7514 | 0.5 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 73.1683 | 25.3477 | 603275.2065 | 50.2729 | 50.2729 | 119.8879 | 0.6 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 75.2777 | 27.457 | 653477.4878 | 54.4565 | 54.4565 | 126.0245 | 0.7 | 78.34 | 23.34 | 882252 | 73.521 | 73.521 | 77.387 | 29.5664 | 703679.7691 | 58.64 | 58.64 | 132.161 | 0.8 | 78.96 | 23.96 | 905688 | 75.474 | 75.474 | 79.4963 | 31.6757 | 753882.0504 | 62.8235 | 62.8235 | 138.2975 | 0.9 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 81.6057 | 33.7851 | 804084.3317 | 67.007 | 67.007 | 144.434 | 1 | 80.2 | 25.2 | 952560 | 79.38 | 79.38 | 83.715 | 35.8944 | 854286.613 | 71.1906 | 71.1906 | 150.5706 | 80 | 55 | 32.3758 | 32 | 54.1
7/30/20XX 4:00:00 PM | 0.66667 | 1 | 79.2 | 56.2 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 84.1744 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 64.7769 | 16.9563 | 403559.2775 | 33.6299 | 33.6299 | 95.1179 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 66.9322 | 19.1115 | 454854.7551 | 37.9046 | 37.9046 | 101.0306 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 69.0874 | 21.2668 | 506150.2326 | 42.1792 | 42.1792 | 106.9432 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 71.2427 | 23.4221 | 557445.7101 | 46.4538 | 46.4538 | 112.8558 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 73.398 | 25.5774 | 608741.1877 | 50.7284 | 50.7284 | 118.7684 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 75.5533 | 27.7326 | 660036.6652 | 55.0031 | 55.0031 | 124.6811 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 77.7085 | 29.8879 | 711332.1427 | 59.2777 | 59.2777 | 130.5937 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 79.8638 | 32.0432 | 762627.6203 | 63.5523 | 63.5523 | 136.5063 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 82.0191 | 34.1984 | 813923.0978 | 67.8269 | 67.8269 | 142.4189 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 84.1744 | 36.3537 | 865218.5753 | 72.1015 | 72.1015 | 148.3315 | 80 | 55 | 32.2025 | 32 | 56.2
7/30/20XX 5:00:00 PM | 0.70833 | 1 | 79.2 | 56.9 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 85.2437 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 64.8838 | 17.0632 | 406104.3515 | 33.842 | 33.842 | 95.33 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 67.146 | 19.3254 | 459944.903 | 38.3287 | 38.3287 | 101.4547 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 69.4083 | 21.5876 | 513785.4545 | 42.8155 | 42.8155 | 107.5795 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 71.6705 | 23.8498 | 567626.006 | 47.3022 | 47.3022 | 113.7042 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 73.9327 | 26.112 | 621466.5576 | 51.7889 | 51.7889 | 119.8289 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 76.1949 | 28.3742 | 675307.1091 | 56.2756 | 56.2756 | 125.9536 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 78.4571 | 30.6365 | 729147.6606 | 60.7623 | 60.7623 | 132.0783 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 80.7193 | 32.8987 | 782988.2121 | 65.249 | 65.249 | 138.203 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 82.9815 | 35.1609 | 836828.7636 | 69.7357 | 69.7357 | 144.3277 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 85.2437 | 37.4231 | 890669.3151 | 74.2224 | 74.2224 | 150.4524 | 80 | 55 | 32.3701 | 32 | 56.9
7/30/20XX 6:00:00 PM | 0.75 | 1 | 78.4 | 57.7 | 72.7264 | 87.5927 | 14.8663 | 50 | 78.4 |  | 78.4 | 84.1735 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 64.7768 | 16.9562 | 403557.2163 | 33.6298 | 33.6298 | 94.8658 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 66.932 | 19.1114 | 454850.6326 | 37.9042 | 37.9042 | 100.5262 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 69.0872 | 21.2666 | 506144.049 | 42.1787 | 42.1787 | 106.1867 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 71.2424 | 23.4217 | 557437.4653 | 46.4531 | 46.4531 | 111.8471 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 73.3976 | 25.5769 | 608730.8816 | 50.7276 | 50.7276 | 117.5076 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 75.5527 | 27.7321 | 660024.2979 | 55.002 | 55.002 | 123.168 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 77.7079 | 29.8873 | 711317.7142 | 59.2765 | 59.2765 | 128.8285 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 79.8631 | 32.0425 | 762611.1306 | 63.5509 | 63.5509 | 134.4889 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 82.0183 | 34.1977 | 813904.5469 | 67.8254 | 67.8254 | 140.1494 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 84.1735 | 36.3529 | 865197.9632 | 72.0998 | 72.0998 | 145.8098 | 80 | 60 | 32.0061 | 32 | 57.7
7/30/20XX 7:00:00 PM | 0.79167 | 1 | 76.9 | 60.9 | 83.2602 | 97.452 | 14.1918 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/30/20XX 8:00:00 PM | 0.83333 | 1 | 75.3 | 63.9 | 78.8391 | 92.2616 | 13.4225 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/30/20XX 9:00:00 PM | 0.875 | 1 | 74.8 | 65.1 | 77.499 | 90.6884 | 13.1894 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/30/20XX 10:00:00 PM | 0.91667 | 1 | 74.3 | 67 | 76.1783 | 89.138 | 12.9597 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/30/20XX 11:00:00 PM | 0.95833 | 1 | 73.5 | 69 | 74.1052 | 86.7045 | 12.5993 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/30/20XX 12:00:00 AM | 0 | 2 | 73.2 | 68.9 | 73.3404 | 85.8067 | 12.4664 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/31/20XX 1:00:00 AM | 0.041667 | 2 | 72.5 | 69.5 | 71.5821 | 83.7428 | 12.1608 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/31/20XX 2:00:00 AM | 0.083333 | 2 | 72.1 | 70.1 | 82.5828 | 94.6498 | 12.0671 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/31/20XX 3:00:00 AM | 0.125 | 2 | 70.8 | 72.2 | 78.908 | 90.4259 | 11.5179 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/31/20XX 4:00:00 AM | 0.16667 | 2 | 71.1 | 70.6 | 79.7432 | 91.3858 | 11.6426 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/31/20XX 5:00:00 AM | 0.20833 | 2 | 70.4 | 73.3 | 77.8062 | 89.1597 | 11.3535 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/31/20XX 6:00:00 AM | 0.25 | 2 | 70.4 | 74.7 | 77.8062 | 89.1597 | 11.3535 | 70 | 70.4 |  | 70.4 | 83.1424 | 0.1 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 64.6737 | 16.8531 | 401103.1825 | 33.4253 | 33.4253 | 92.1413 | 0.2 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 66.7258 | 18.9051 | 449942.5651 | 37.4952 | 37.4952 | 95.0772 | 0.3 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 68.7779 | 20.9572 | 498781.9476 | 41.5652 | 41.5652 | 98.0132 | 0.4 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 70.8299 | 23.0093 | 547621.3301 | 45.6351 | 45.6351 | 100.9491 | 0.5 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 72.882 | 25.0614 | 596460.7126 | 49.7051 | 49.7051 | 103.8851 | 0.6 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 74.9341 | 27.1134 | 645300.0952 | 53.775 | 53.775 | 106.821 | 0.7 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 76.9862 | 29.1655 | 694139.4777 | 57.845 | 57.845 | 109.757 | 0.8 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 79.0382 | 31.2176 | 742978.8602 | 61.9149 | 61.9149 | 112.6929 | 0.9 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 81.0903 | 33.2697 | 791818.2428 | 65.9849 | 65.9849 | 115.6289 | 1 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 83.1424 | 35.3217 | 840657.6253 | 70.0548 | 70.0548 | 118.5648 | 70 | 75 | 29.8822 | 30 | 74.7
7/31/20XX 7:00:00 AM | 0.29167 | 2 | 71.8 | 70.5 | 81.7218 | 93.6601 | 11.9383 | 70 | 71.8 |  | 71.8 | 82.3188 | 0.1 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 64.5913 | 16.7707 | 399142.9667 | 33.2619 | 33.2619 | 92.4189 | 0.2 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 66.5611 | 18.7404 | 446022.1333 | 37.1685 | 37.1685 | 95.6325 | 0.3 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 68.5308 | 20.7101 | 492901.3 | 41.0751 | 41.0751 | 98.8461 | 0.4 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 70.5005 | 22.6799 | 539780.4666 | 44.9817 | 44.9817 | 102.0597 | 0.5 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 72.4702 | 24.6496 | 586659.6333 | 48.8883 | 48.8883 | 105.2733 | 0.6 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 74.4399 | 26.6193 | 633538.7999 | 52.7949 | 52.7949 | 108.4869 | 0.7 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 76.4096 | 28.589 | 680417.9666 | 56.7015 | 56.7015 | 111.7005 | 0.8 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 78.3793 | 30.5587 | 727297.1332 | 60.6081 | 60.6081 | 114.9141 | 0.9 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 80.349 | 32.5284 | 774176.2999 | 64.5147 | 64.5147 | 118.1277 | 1 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 82.3188 | 34.4981 | 821055.4665 | 68.4213 | 68.4213 | 121.3413 | 70 | 70 | 30.0969 | 30 | 70.5
7/31/20XX 8:00:00 AM | 0.33333 | 2 | 73.4 | 68 | 73.8495 | 86.4044 | 12.5549 | 60 | 73.4 |  | 73.4 | 83.8934 | 0.1 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 64.7488 | 16.9282 | 402890.591 | 33.5742 | 33.5742 | 93.2352 | 0.2 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 66.876 | 19.0554 | 453517.3821 | 37.7931 | 37.7931 | 97.2651 | 0.3 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 69.0032 | 21.1825 | 504144.1731 | 42.012 | 42.012 | 101.295 | 0.4 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 71.1303 | 23.3097 | 554770.9642 | 46.2309 | 46.2309 | 105.3249 | 0.5 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 73.2575 | 25.4369 | 605397.7552 | 50.4498 | 50.4498 | 109.3548 | 0.6 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 75.3847 | 27.5641 | 656024.5463 | 54.6687 | 54.6687 | 113.3847 | 0.7 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 77.5119 | 29.6912 | 706651.3373 | 58.8876 | 58.8876 | 117.4146 | 0.8 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 79.639 | 31.8184 | 757278.1284 | 63.1065 | 63.1065 | 121.4445 | 0.9 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 81.7662 | 33.9456 | 807904.9194 | 67.3254 | 67.3254 | 125.4744 | 1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 83.8934 | 36.0728 | 858531.7104 | 71.5443 | 71.5443 | 129.5043 | 75 | 70 | 30.7355 | 30 | 68
7/31/20XX 9:00:00 AM | 0.375 | 2 | 75.5 | 63 | 79.3806 | 92.8973 | 13.5167 | 60 | 75.5 |  | 75.5 | 83.4356 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 64.703 | 16.8824 | 401801.1227 | 33.4834 | 33.4834 | 93.8059 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 66.7844 | 18.9638 | 451338.4453 | 37.6115 | 37.6115 | 98.4065 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 68.8658 | 21.0452 | 500875.768 | 41.7396 | 41.7396 | 103.0071 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 70.9472 | 23.1266 | 550413.0906 | 45.8678 | 45.8678 | 107.6078 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 73.0286 | 25.208 | 599950.4133 | 49.9959 | 49.9959 | 112.2084 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 75.11 | 27.2894 | 649487.7359 | 54.124 | 54.124 | 116.809 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 77.1914 | 29.3708 | 699025.0586 | 58.2521 | 58.2521 | 121.4096 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 79.2728 | 31.4522 | 748562.3812 | 62.3802 | 62.3802 | 126.0102 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 81.3542 | 33.5336 | 798099.7039 | 66.5083 | 66.5083 | 130.6108 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 83.4356 | 35.615 | 847637.0265 | 70.6364 | 70.6364 | 135.2114 | 75 | 65 | 31.1791 | 32 | 63
7/31/20XX 10:00:00 AM | 0.41667 | 2 | 77.5 | 59 | 70.5552 | 84.9711 | 14.416 | 50 | 77.5 |  | 77.5 | 83.5295 | 0.1 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 64.7124 | 16.8918 | 402024.6064 | 33.5021 | 33.5021 | 94.4546 | 0.2 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 66.8032 | 18.9826 | 451785.4128 | 37.6488 | 37.6488 | 99.7038 | 0.3 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 68.894 | 21.0734 | 501546.2192 | 41.7955 | 41.7955 | 104.953 | 0.4 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 70.9848 | 23.1642 | 551307.0256 | 45.9423 | 45.9423 | 110.2023 | 0.5 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 73.0756 | 25.255 | 601067.8319 | 50.089 | 50.089 | 115.4515 | 0.6 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 75.1664 | 27.3457 | 650828.6383 | 54.2357 | 54.2357 | 120.7007 | 0.7 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 77.2572 | 29.4365 | 700589.4447 | 58.3825 | 58.3825 | 125.95 | 0.8 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 79.348 | 31.5273 | 750350.2511 | 62.5292 | 62.5292 | 131.1992 | 0.9 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 81.4387 | 33.6181 | 800111.0575 | 66.6759 | 66.6759 | 136.4484 | 1 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 83.5295 | 35.7089 | 849871.8639 | 70.8227 | 70.8227 | 141.6977 | 75 | 60 | 31.6844 | 32 | 59
7/31/20XX 11:00:00 AM | 0.45833 | 2 | 79 | 57.5 | 74.2046 | 89.3778 | 15.1731 | 50 | 79 |  | 79 | 85.5845 | 0.1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 64.9179 | 17.0973 | 406915.3598 | 33.9096 | 33.9096 | 95.3346 | 0.2 | 75 | 20 | 756000 | 63 | 63 | 67.2142 | 19.3936 | 461566.9196 | 38.4639 | 38.4639 | 101.4639 | 0.3 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 69.5105 | 21.6899 | 516218.4794 | 43.0182 | 43.0182 | 107.5932 | 0.4 | 76 | 21 | 793800 | 66.15 | 66.15 | 71.8068 | 23.9861 | 570870.0392 | 47.5725 | 47.5725 | 113.7225 | 0.5 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 74.1031 | 26.2824 | 625521.599 | 52.1268 | 52.1268 | 119.8518 | 0.6 | 77 | 22 | 831600 | 69.3 | 69.3 | 76.3993 | 28.5787 | 680173.1588 | 56.6811 | 56.6811 | 125.9811 | 0.7 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 78.6956 | 30.875 | 734824.7186 | 61.2354 | 61.2354 | 132.1104 | 0.8 | 78 | 23 | 869400 | 72.45 | 72.45 | 80.9919 | 33.1713 | 789476.2784 | 65.7897 | 65.7897 | 138.2397 | 0.9 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 83.2882 | 35.4676 | 844127.8382 | 70.344 | 70.344 | 144.369 | 1 | 79 | 24 | 907200 | 75.6 | 75.6 | 85.5845 | 37.7638 | 898779.398 | 74.8983 | 74.8983 | 150.4983 | 80 | 55 | 32.3744 | 32 | 57.5
7/31/20XX 12:00:00 PM | 0.5 | 2 | 81.3 | 53.9 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 86.4993 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 65.0094 | 17.1888 | 409092.5943 | 34.091 | 34.091 | 96.2405 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 67.3972 | 19.5765 | 465921.3885 | 38.8268 | 38.8268 | 103.2758 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 69.7849 | 21.9643 | 522750.1828 | 43.5625 | 43.5625 | 110.311 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 72.1727 | 24.3521 | 579578.9771 | 48.2982 | 48.2982 | 117.3462 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 74.5605 | 26.7398 | 636407.7714 | 53.034 | 53.034 | 124.3815 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 76.9482 | 29.1276 | 693236.5656 | 57.7697 | 57.7697 | 131.4167 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 79.336 | 31.5154 | 750065.3599 | 62.5054 | 62.5054 | 138.4519 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 81.7237 | 33.9031 | 806894.1542 | 67.2412 | 67.2412 | 145.4872 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 84.1115 | 36.2909 | 863722.9485 | 71.9769 | 71.9769 | 152.5224 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 86.4993 | 38.6786 | 920551.7427 | 76.7126 | 76.7126 | 159.5576 | 80 | 55 | 33.0824 | 34 | 53.9
7/31/20XX 1:00:00 PM | 0.54167 | 2 | 82.5 | 50.5 | 83.3313 | 100.4018 | 17.0705 | 50 | 82.5 |  | 82.5 | 84.1849 | 0.1 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 64.778 | 16.9573 | 403584.2954 | 33.632 | 33.632 | 96.1595 | 0.2 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 66.9343 | 19.1136 | 454904.7908 | 37.9087 | 37.9087 | 103.1137 | 0.3 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 69.0906 | 21.27 | 506225.2862 | 42.1854 | 42.1854 | 110.0679 | 0.4 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 71.2469 | 23.4263 | 557545.7816 | 46.4621 | 46.4621 | 117.0221 | 0.5 | 78.25 | 23.25 | 878850 | 73.2375 | 73.2375 | 73.4032 | 25.5826 | 608866.2771 | 50.7389 | 50.7389 | 123.9764 | 0.6 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 75.5596 | 27.7389 | 660186.7725 | 55.0156 | 55.0156 | 130.9306 | 0.7 | 79.95 | 24.95 | 943110 | 78.5925 | 78.5925 | 77.7159 | 29.8953 | 711507.2679 | 59.2923 | 59.2923 | 137.8848 | 0.8 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 79.8722 | 32.0516 | 762827.7633 | 63.569 | 63.569 | 144.839 | 0.9 | 81.65 | 26.65 | 1007370 | 83.9475 | 83.9475 | 82.0285 | 34.2079 | 814148.2587 | 67.8457 | 67.8457 | 151.7932 | 1 | 82.5 | 27.5 | 1039500 | 86.625 | 86.625 | 84.1849 | 36.3642 | 865468.7541 | 72.1224 | 72.1224 | 158.7474 | 80 | 50 | 33.0137 | 34 | 50.5
7/31/20XX 2:00:00 PM | 0.58333 | 2 | 82.6 | 50.5 | 83.605 | 100.7325 | 17.1274 | 50 | 82.6 |  | 82.6 | 84.4614 | 0.1 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 64.8056 | 16.985 | 404242.4791 | 33.6869 | 33.6869 | 96.2459 | 0.2 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 66.9896 | 19.169 | 456221.1582 | 38.0184 | 38.0184 | 103.2864 | 0.3 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 69.1736 | 21.3529 | 508199.8373 | 42.35 | 42.35 | 110.327 | 0.4 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 71.3575 | 23.5369 | 560178.5164 | 46.6815 | 46.6815 | 117.3675 | 0.5 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 73.5415 | 25.7209 | 612157.1956 | 51.0131 | 51.0131 | 124.4081 | 0.6 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 75.7255 | 27.9049 | 664135.8747 | 55.3447 | 55.3447 | 131.4487 | 0.7 | 80.02 | 25.02 | 945756 | 78.813 | 78.813 | 77.9095 | 30.0888 | 716114.5538 | 59.6762 | 59.6762 | 138.4892 | 0.8 | 80.88 | 25.88 | 978264 | 81.522 | 81.522 | 80.0935 | 32.2728 | 768093.2329 | 64.0078 | 64.0078 | 145.5298 | 0.9 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 82.2774 | 34.4568 | 820071.912 | 68.3393 | 68.3393 | 152.5703 | 1 | 82.6 | 27.6 | 1043280 | 86.94 | 86.94 | 84.4614 | 36.6408 | 872050.5911 | 72.6709 | 72.6709 | 159.6109 | 85 | 50 | 33.0817 | 34 | 50.5
7/31/20XX 3:00:00 PM | 0.625 | 2 | 80.7 | 53.7 | 78.5288 | 94.6002 | 16.0714 | 50 | 80.7 |  | 80.7 | 84.4752 | 0.1 | 74.67 | 19.67 | 743526 | 61.9605 | 61.9605 | 64.807 | 16.9864 | 404275.3314 | 33.6896 | 33.6896 | 95.6501 | 0.2 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 66.9923 | 19.1717 | 456286.8628 | 38.0239 | 38.0239 | 102.0949 | 0.3 | 76.01 | 21.01 | 794178 | 66.1815 | 66.1815 | 69.1777 | 21.3571 | 508298.3942 | 42.3582 | 42.3582 | 108.5397 | 0.4 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 71.3631 | 23.5424 | 560309.9256 | 46.6925 | 46.6925 | 114.9845 | 0.5 | 77.35 | 22.35 | 844830 | 70.4025 | 70.4025 | 73.5484 | 25.7278 | 612321.457 | 51.0268 | 51.0268 | 121.4293 | 0.6 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 75.7338 | 27.9132 | 664332.9883 | 55.3611 | 55.3611 | 127.8741 | 0.7 | 78.69 | 23.69 | 895482 | 74.6235 | 74.6235 | 77.9191 | 30.0985 | 716344.5197 | 59.6954 | 59.6954 | 134.3189 | 0.8 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 80.1045 | 32.2839 | 768356.0511 | 64.0297 | 64.0297 | 140.7637 | 0.9 | 80.03 | 25.03 | 946134 | 78.8445 | 78.8445 | 82.2899 | 34.4692 | 820367.5825 | 68.364 | 68.364 | 147.2085 | 1 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 84.4752 | 36.6546 | 872379.1139 | 72.6983 | 72.6983 | 153.6533 | 80 | 55 | 32.6177 | 32 | 53.7
7/31/20XX 4:00:00 PM | 0.66667 | 2 | 80.7 | 55.9 | 78.5288 | 94.6002 | 16.0714 | 50 | 80.7 |  | 80.7 | 88.0109 | 0.1 | 74.67 | 19.67 | 743526 | 61.9605 | 61.9605 | 65.1606 | 17.3399 | 412690.3155 | 34.3909 | 34.3909 | 96.3514 | 0.2 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 67.6995 | 19.8789 | 473116.831 | 39.4264 | 39.4264 | 103.4974 | 0.3 | 76.01 | 21.01 | 794178 | 66.1815 | 66.1815 | 70.2384 | 22.4178 | 533543.3465 | 44.4619 | 44.4619 | 110.6434 | 0.4 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 72.7773 | 24.9567 | 593969.862 | 49.4975 | 49.4975 | 117.7895 | 0.5 | 77.35 | 22.35 | 844830 | 70.4025 | 70.4025 | 75.3163 | 27.4956 | 654396.3776 | 54.533 | 54.533 | 124.9355 | 0.6 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 77.8552 | 30.0346 | 714822.8931 | 59.5686 | 59.5686 | 132.0816 | 0.7 | 78.69 | 23.69 | 895482 | 74.6235 | 74.6235 | 80.3941 | 32.5735 | 775249.4086 | 64.6041 | 64.6041 | 139.2276 | 0.8 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 82.9331 | 35.1124 | 835675.9241 | 69.6397 | 69.6397 | 146.3737 | 0.9 | 80.03 | 25.03 | 946134 | 78.8445 | 78.8445 | 85.472 | 37.6514 | 896102.4396 | 74.6752 | 74.6752 | 153.5197 | 1 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 88.0109 | 40.1903 | 956528.9551 | 79.7107 | 79.7107 | 160.6657 | 80 | 55 | 33.1722 | 34 | 55.9
7/31/20XX 5:00:00 PM | 0.70833 | 2 | 79.2 | 58.6 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 87.8407 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 65.1435 | 17.3229 | 412285.2455 | 34.3571 | 34.3571 | 95.8451 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 67.6655 | 19.8448 | 472306.6909 | 39.3589 | 39.3589 | 102.4849 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 70.1874 | 22.3667 | 532328.1364 | 44.3607 | 44.3607 | 109.1247 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 72.7093 | 24.8886 | 592349.5818 | 49.3625 | 49.3625 | 115.7645 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 75.2312 | 27.4105 | 652371.0273 | 54.3643 | 54.3643 | 122.4043 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 77.7531 | 29.9325 | 712392.4728 | 59.366 | 59.366 | 129.044 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 80.275 | 32.4544 | 772413.9182 | 64.3678 | 64.3678 | 135.6838 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 82.7969 | 34.9763 | 832435.3637 | 69.3696 | 69.3696 | 142.3236 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 85.3188 | 37.4982 | 892456.8092 | 74.3714 | 74.3714 | 148.9634 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 87.8407 | 40.0201 | 952478.2546 | 79.3732 | 79.3732 | 155.6032 | 80 | 60 | 32.7772 | 32 | 58.6
7/31/20XX 6:00:00 PM | 0.75 | 2 | 77.5 | 61.6 | 84.9711 | 99.4607 | 14.4896 | 60 | 77.5 |  | 77.5 | 87.2895 | 0.1 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 65.0884 | 17.2678 | 410973.2319 | 34.2478 | 34.2478 | 95.2003 | 0.2 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 67.5552 | 19.7346 | 469682.6638 | 39.1402 | 39.1402 | 101.1952 | 0.3 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 70.022 | 22.2013 | 528392.0957 | 44.0327 | 44.0327 | 107.1902 | 0.4 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 72.4888 | 24.6681 | 587101.5275 | 48.9251 | 48.9251 | 113.1851 | 0.5 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 74.9555 | 27.1349 | 645810.9594 | 53.8176 | 53.8176 | 119.1801 | 0.6 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 77.4223 | 29.6017 | 704520.3913 | 58.71 | 58.71 | 125.175 | 0.7 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 79.8891 | 32.0685 | 763229.8232 | 63.6025 | 63.6025 | 131.17 | 0.8 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 82.3559 | 34.5353 | 821939.2551 | 68.4949 | 68.4949 | 137.1649 | 0.9 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 84.8227 | 37.002 | 880648.687 | 73.3874 | 73.3874 | 143.1599 | 1 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 87.2895 | 39.4688 | 939358.1188 | 78.2798 | 78.2798 | 149.1548 | 75 | 60 | 32.2733 | 32 | 61.6
7/31/20XX 7:00:00 PM | 0.79167 | 2 | 76 | 63.5 | 80.7483 | 94.5029 | 13.7546 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/31/20XX 8:00:00 PM | 0.83333 | 2 | 75.3 | 65.9 | 78.8391 | 92.2616 | 13.4225 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/31/20XX 9:00:00 PM | 0.875 | 2 | 74.2 | 68.2 | 75.9165 | 88.8307 | 12.9142 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/31/20XX 10:00:00 PM | 0.91667 | 2 | 74.2 | 69.4 | 75.9165 | 88.8307 | 12.9142 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/31/20XX 11:00:00 PM | 0.95833 | 2 | 74 | 70 | 88.2187 | 101.1303 | 12.9116 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7/31/20XX 12:00:00 AM | 0 | 1 | 73.2 | 73.9 | 85.8067 | 98.3566 | 12.5498 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/1/20XX 1:00:00 AM | 0.041667 | 1 | 72.9 | 77.3 | 84.9169 | 97.3334 | 12.4165 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/1/20XX 2:00:00 AM | 0.083333 | 1 | 72.5 | 78.5 | 83.7428 | 95.9835 | 12.2407 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/1/20XX 3:00:00 AM | 0.125 | 1 | 72.2 | 77.8 | 82.8715 | 94.9817 | 12.1103 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/1/20XX 4:00:00 AM | 0.16667 | 1 | 72.2 | 78.7 | 82.8715 | 94.9817 | 12.1103 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/1/20XX 5:00:00 AM | 0.20833 | 1 | 71.6 | 79.2 | 81.1522 | 93.0054 | 11.8531 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/1/20XX 6:00:00 AM | 0.25 | 1 | 71.9 | 78.2 | 82.008 | 93.989 | 11.9811 | 70 | 71.9 |  | 71.9 | 91.8324 | 0.1 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 65.5427 | 17.7221 | 421785.5289 | 35.1488 | 35.1488 | 94.3373 | 0.2 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 68.4638 | 20.6432 | 491307.2577 | 40.9423 | 40.9423 | 99.4693 | 0.3 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 71.3849 | 23.5642 | 560828.9866 | 46.7357 | 46.7357 | 104.6012 | 0.4 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 74.306 | 26.4853 | 630350.7154 | 52.5292 | 52.5292 | 109.7332 | 0.5 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 77.227 | 29.4064 | 699872.4443 | 58.3227 | 58.3227 | 114.8652 | 0.6 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 80.1481 | 32.3275 | 769394.1731 | 64.1162 | 64.1162 | 119.9972 | 0.7 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 83.0692 | 35.2486 | 838915.902 | 69.9097 | 69.9097 | 125.1292 | 0.8 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 85.9903 | 38.1696 | 908437.6308 | 75.7031 | 75.7031 | 130.2611 | 0.9 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 88.9114 | 41.0907 | 977959.3597 | 81.4966 | 81.4966 | 135.3931 | 1 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 91.8324 | 44.0118 | 1047481.0886 | 87.2901 | 87.2901 | 140.5251 | 70 | 80 | 31.6083 | 32 | 78.2
8/1/20XX 7:00:00 AM | 0.29167 | 1 | 72.8 | 76.9 | 84.6221 | 96.9944 | 12.3723 | 70 | 72.8 |  | 72.8 | 93.159 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.6754 | 17.8547 | 424942.7094 | 35.4119 | 35.4119 | 94.8839 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 68.7291 | 20.9085 | 497621.6187 | 41.4685 | 41.4685 | 100.5625 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 71.7828 | 23.9622 | 570300.5281 | 47.525 | 47.525 | 106.241 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 74.8366 | 27.0159 | 642979.4375 | 53.5816 | 53.5816 | 111.9196 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 77.8903 | 30.0697 | 715658.3469 | 59.6382 | 59.6382 | 117.5982 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 80.944 | 33.1234 | 788337.2562 | 65.6948 | 65.6948 | 123.2768 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 83.9978 | 36.1771 | 861016.1656 | 71.7513 | 71.7513 | 128.9553 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 87.0515 | 39.2309 | 933695.075 | 77.8079 | 77.8079 | 134.6339 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 90.1053 | 42.2846 | 1006373.9844 | 83.8645 | 83.8645 | 140.3125 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 93.159 | 45.3384 | 1079052.8937 | 89.9211 | 89.9211 | 145.9911 | 75 | 75 | 32.037 | 32 | 76.9
8/1/20XX 8:00:00 AM | 0.33333 | 1 | 74.6 | 73.4 | 90.0655 | 103.2545 | 13.1889 | 70 | 74.6 |  | 74.6 | 94.5498 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 65.8144 | 17.9938 | 428252.742 | 35.6877 | 35.6877 | 95.7267 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 69.0073 | 21.1866 | 504241.6839 | 42.0201 | 42.0201 | 102.2481 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 72.2001 | 24.3794 | 580230.6259 | 48.3526 | 48.3526 | 108.7696 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 75.3929 | 27.5723 | 656219.5679 | 54.685 | 54.685 | 115.291 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 78.5857 | 30.7651 | 732208.5098 | 61.0174 | 61.0174 | 121.8124 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 81.7785 | 33.9579 | 808197.4518 | 67.3498 | 67.3498 | 128.3338 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 84.9713 | 37.1507 | 884186.3938 | 73.6822 | 73.6822 | 134.8552 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 88.1641 | 40.3435 | 960175.3357 | 80.0146 | 80.0146 | 141.3766 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 91.3569 | 43.5363 | 1036164.2777 | 86.347 | 86.347 | 147.898 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 94.5498 | 46.7291 | 1112153.2197 | 92.6794 | 92.6794 | 154.4194 | 75 | 75 | 32.6972 | 32 | 73.4
8/1/20XX 9:00:00 AM | 0.375 | 1 | 76.1 | 72.2 | 94.8268 | 108.7319 | 13.9051 | 70 | 76.1 |  | 76.1 | 97.8859 | 0.1 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 66.1481 | 18.3274 | 436192.8398 | 36.3494 | 36.3494 | 96.8609 | 0.2 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 69.6745 | 21.8539 | 520121.8796 | 43.3435 | 43.3435 | 104.5165 | 0.3 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 73.2009 | 25.3803 | 604050.9194 | 50.3376 | 50.3376 | 112.1721 | 0.4 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 76.7274 | 28.9067 | 687979.9592 | 57.3317 | 57.3317 | 119.8277 | 0.5 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 80.2538 | 32.4332 | 771908.999 | 64.3257 | 64.3257 | 127.4832 | 0.6 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 83.7802 | 35.9596 | 855838.0388 | 71.3198 | 71.3198 | 135.1388 | 0.7 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 87.3066 | 39.486 | 939767.0786 | 78.3139 | 78.3139 | 142.7944 | 0.8 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 90.8331 | 43.0124 | 1023696.1184 | 85.308 | 85.308 | 150.45 | 0.9 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 94.3595 | 46.5389 | 1107625.1582 | 92.3021 | 92.3021 | 158.1056 | 1 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 97.8859 | 50.0653 | 1191554.198 | 99.2962 | 99.2962 | 165.7612 | 75 | 70 | 33.5885 | 34 | 72.2
8/1/20XX 10:00:00 AM | 0.41667 | 1 | 77.5 | 68.2 | 84.9711 | 99.4607 | 14.4896 | 60 | 77.5 |  | 77.5 | 96.8526 | 0.1 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 66.0447 | 18.2241 | 433733.426 | 36.1445 | 36.1445 | 97.097 | 0.2 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 69.4678 | 21.6472 | 515203.0519 | 42.9336 | 42.9336 | 104.9886 | 0.3 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 72.8909 | 25.0703 | 596672.6779 | 49.7227 | 49.7227 | 112.8802 | 0.4 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 76.314 | 28.4934 | 678142.3038 | 56.5119 | 56.5119 | 120.7719 | 0.5 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 79.7371 | 31.9165 | 759611.9298 | 63.301 | 63.301 | 128.6635 | 0.6 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 83.1602 | 35.3396 | 841081.5557 | 70.0901 | 70.0901 | 136.5551 | 0.7 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 86.5833 | 38.7627 | 922551.1817 | 76.8793 | 76.8793 | 144.4468 | 0.8 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 90.0064 | 42.1857 | 1004020.8077 | 83.6684 | 83.6684 | 152.3384 | 0.9 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 93.4295 | 45.6088 | 1085490.4336 | 90.4575 | 90.4575 | 160.23 | 1 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 96.8526 | 49.0319 | 1166960.0596 | 97.2467 | 97.2467 | 168.1217 | 75 | 70 | 33.7713 | 34 | 68.2
8/1/20XX 11:00:00 AM | 0.45833 | 1 | 79.7 | 64.4 | 91.4984 | 107.1246 | 15.6261 | 60 | 79.7 |  | 79.7 | 98.3739 | 0.1 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 66.1969 | 18.3762 | 437354.2459 | 36.4462 | 36.4462 | 98.0917 | 0.2 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 69.7721 | 21.9515 | 522444.6918 | 43.5371 | 43.5371 | 106.9781 | 0.3 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 73.3473 | 25.5267 | 607535.1378 | 50.6279 | 50.6279 | 115.8644 | 0.4 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 76.9225 | 29.1019 | 692625.5837 | 57.7188 | 57.7188 | 124.7508 | 0.5 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 80.4978 | 32.6771 | 777716.0296 | 64.8097 | 64.8097 | 133.6372 | 0.6 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 84.073 | 36.2524 | 862806.4755 | 71.9005 | 71.9005 | 142.5235 | 0.7 | 77.99 | 22.99 | 869022 | 72.4185 | 72.4185 | 87.6482 | 39.8276 | 947896.9215 | 78.9914 | 78.9914 | 151.4099 | 0.8 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 91.2235 | 43.4028 | 1032987.3674 | 86.0823 | 86.0823 | 160.2963 | 0.9 | 79.13 | 24.13 | 912114 | 76.0095 | 76.0095 | 94.7987 | 46.9781 | 1118077.8133 | 93.1732 | 93.1732 | 169.1827 | 1 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 98.3739 | 50.5533 | 1203168.2592 | 100.264 | 100.264 | 178.069 | 80 | 65 | 34.5514 | 34 | 64.4
8/1/20XX 12:00:00 PM | 0.5 | 1 | 79.8 | 63.1 | 91.8048 | 107.4842 | 15.6795 | 60 | 79.8 |  | 79.8 | 96.6654 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 66.026 | 18.2054 | 433287.9686 | 36.1073 | 36.1073 | 97.7843 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 69.4304 | 21.6098 | 514312.1372 | 42.8593 | 42.8593 | 106.3633 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 72.8348 | 25.0141 | 595336.3059 | 49.6114 | 49.6114 | 114.9424 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 76.2391 | 28.4185 | 676360.4745 | 56.3634 | 56.3634 | 123.5214 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 79.6435 | 31.8229 | 757384.6431 | 63.1154 | 63.1154 | 132.1004 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 83.0479 | 35.2273 | 838408.8117 | 69.8674 | 69.8674 | 140.6794 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 86.4523 | 38.6316 | 919432.9804 | 76.6194 | 76.6194 | 149.2584 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 89.8566 | 42.036 | 1000457.149 | 83.3714 | 83.3714 | 157.8374 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 93.261 | 45.4404 | 1081481.3176 | 90.1234 | 90.1234 | 166.4164 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 96.6654 | 48.8448 | 1162505.4862 | 96.8755 | 96.8755 | 174.9955 | 80 | 65 | 34.3081 | 34 | 63.1
8/1/20XX 1:00:00 PM | 0.54167 | 1 | 80.8 | 61.1 | 94.9151 | 111.1364 | 16.2213 | 60 | 80.8 |  | 80.8 | 96.6994 | 0.1 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 66.0294 | 18.2088 | 433368.9869 | 36.1141 | 36.1141 | 98.1061 | 0.2 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 69.4372 | 21.6166 | 514474.1737 | 42.8728 | 42.8728 | 107.0068 | 0.3 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 72.845 | 25.0243 | 595579.3606 | 49.6316 | 49.6316 | 115.9076 | 0.4 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 76.2528 | 28.4321 | 676684.5475 | 56.3904 | 56.3904 | 124.8084 | 0.5 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 79.6605 | 31.8399 | 757789.7343 | 63.1491 | 63.1491 | 133.7091 | 0.6 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 83.0683 | 35.2477 | 838894.9212 | 69.9079 | 69.9079 | 142.6099 | 0.7 | 78.76 | 23.76 | 898128 | 74.844 | 74.844 | 86.4761 | 38.6555 | 920000.1081 | 76.6667 | 76.6667 | 151.5107 | 0.8 | 79.44 | 24.44 | 923832 | 76.986 | 76.986 | 89.8839 | 42.0632 | 1001105.2949 | 83.4254 | 83.4254 | 160.4114 | 0.9 | 80.12 | 25.12 | 949536 | 79.128 | 79.128 | 93.2917 | 45.471 | 1082210.4818 | 90.1842 | 90.1842 | 169.3122 | 1 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 96.6994 | 48.8788 | 1163315.6687 | 96.943 | 96.943 | 178.213 | 80 | 60 | 34.5596 | 34 | 61.1
8/1/20XX 2:00:00 PM | 0.58333 | 1 | 80.3 | 64.6 | 93.3492 | 109.2977 | 15.9485 | 60 | 80.3 |  | 80.3 | 100.6855 | 0.1 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 66.428 | 18.6074 | 442855.8845 | 36.9047 | 36.9047 | 98.7392 | 0.2 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 70.2344 | 22.4138 | 533447.969 | 44.454 | 44.454 | 108.273 | 0.3 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 74.0408 | 26.2202 | 624040.0534 | 52.0033 | 52.0033 | 117.8068 | 0.4 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 77.8472 | 30.0266 | 714632.1379 | 59.5527 | 59.5527 | 127.3407 | 0.5 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 81.6536 | 33.833 | 805224.2224 | 67.102 | 67.102 | 136.8745 | 0.6 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 85.46 | 37.6393 | 895816.3069 | 74.6514 | 74.6514 | 146.4084 | 0.7 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 89.2664 | 41.4457 | 986408.3913 | 82.2007 | 82.2007 | 155.9422 | 0.8 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 93.0728 | 45.2521 | 1077000.4758 | 89.75 | 89.75 | 165.476 | 0.9 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 96.8791 | 49.0585 | 1167592.5603 | 97.2994 | 97.2994 | 175.0099 | 1 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 100.6855 | 52.8649 | 1258184.6448 | 104.8487 | 104.8487 | 184.5437 | 80 | 65 | 35.0616 | 36 | 64.6
8/1/20XX 3:00:00 PM | 0.625 | 1 | 79.9 | 63.7 | 92.1119 | 107.8449 | 15.733 | 60 | 79.9 |  | 79.9 | 97.9332 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 66.1528 | 18.3322 | 436305.2183 | 36.3588 | 36.3588 | 98.0673 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 69.6839 | 21.8633 | 520346.6367 | 43.3622 | 43.3622 | 106.9292 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 73.2151 | 25.3945 | 604388.055 | 50.3657 | 50.3657 | 115.7912 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 76.7462 | 28.9256 | 688429.4734 | 57.3691 | 57.3691 | 124.6531 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 80.2774 | 32.4568 | 772470.8917 | 64.3726 | 64.3726 | 133.5151 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 83.8085 | 35.9879 | 856512.3101 | 71.376 | 71.376 | 142.377 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 87.3397 | 39.5191 | 940553.7284 | 78.3795 | 78.3795 | 151.239 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 90.8708 | 43.0502 | 1024595.1468 | 85.3829 | 85.3829 | 160.1009 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 94.402 | 46.5814 | 1108636.5651 | 92.3864 | 92.3864 | 168.9629 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 97.9332 | 50.1125 | 1192677.9835 | 99.3898 | 99.3898 | 177.8248 | 80 | 65 | 34.5315 | 34 | 63.7
8/1/20XX 4:00:00 PM | 0.66667 | 1 | 78.6 | 64.9 | 88.1844 | 103.2334 | 15.049 | 60 | 78.6 |  | 78.6 | 95.5584 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 65.9153 | 18.0947 | 430653.3372 | 35.8878 | 35.8878 | 97.1868 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 69.209 | 21.3884 | 509042.8743 | 42.4202 | 42.4202 | 105.1682 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 72.5027 | 24.682 | 587432.4115 | 48.9527 | 48.9527 | 113.1497 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 75.7963 | 27.9757 | 665821.9486 | 55.4852 | 55.4852 | 121.1312 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 79.09 | 31.2694 | 744211.4858 | 62.0176 | 62.0176 | 129.1126 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 82.3837 | 34.5631 | 822601.0229 | 68.5501 | 68.5501 | 137.0941 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 85.6774 | 37.8567 | 900990.5601 | 75.0825 | 75.0825 | 145.0755 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 88.9711 | 41.1504 | 979380.0972 | 81.615 | 81.615 | 153.057 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 92.2647 | 44.4441 | 1057769.6344 | 88.1475 | 88.1475 | 161.0385 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 95.5584 | 47.7378 | 1136159.1715 | 94.6799 | 94.6799 | 169.0199 | 80 | 65 | 33.8393 | 34 | 64.9
8/1/20XX 5:00:00 PM | 0.70833 | 1 | 78.6 | 66.1 | 88.1844 | 103.2334 | 15.049 | 60 | 78.6 |  | 78.6 | 97.3643 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 66.0959 | 18.2753 | 434951.3266 | 36.2459 | 36.2459 | 97.5449 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 69.5702 | 21.7495 | 517638.8532 | 43.1366 | 43.1366 | 105.8846 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 73.0444 | 25.2238 | 600326.3798 | 50.0272 | 50.0272 | 114.2242 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 76.5187 | 28.6981 | 683013.9064 | 56.9178 | 56.9178 | 122.5638 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 79.993 | 32.1723 | 765701.433 | 63.8085 | 63.8085 | 130.9035 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 83.4672 | 35.6466 | 848388.9596 | 70.6991 | 70.6991 | 139.2431 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 86.9415 | 39.1209 | 931076.4862 | 77.5897 | 77.5897 | 147.5827 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 90.4158 | 42.5951 | 1013764.0128 | 84.4803 | 84.4803 | 155.9223 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 93.89 | 46.0694 | 1096451.5395 | 91.371 | 91.371 | 164.262 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 97.3643 | 49.5437 | 1179139.0661 | 98.2616 | 98.2616 | 172.6016 | 80 | 65 | 34.1223 | 34 | 66.1
8/1/20XX 6:00:00 PM | 0.75 | 1 | 78.3 | 63.9 | 87.2982 | 102.1928 | 14.8947 | 60 | 78.3 |  | 78.3 | 93.1071 | 0.1 | 74.43 | 19.43 | 734454 | 61.2045 | 61.2045 | 65.6702 | 17.8495 | 424819.1505 | 35.4016 | 35.4016 | 96.6061 | 0.2 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 68.7187 | 20.8981 | 497374.5011 | 41.4479 | 41.4479 | 104.0069 | 0.3 | 75.29 | 20.29 | 766962 | 63.9135 | 63.9135 | 71.7673 | 23.9466 | 569929.8516 | 47.4942 | 47.4942 | 111.4077 | 0.4 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 74.8158 | 26.9952 | 642485.2021 | 53.5404 | 53.5404 | 118.8084 | 0.5 | 76.15 | 21.15 | 799470 | 66.6225 | 66.6225 | 77.8644 | 30.0437 | 715040.5526 | 59.5867 | 59.5867 | 126.2092 | 0.6 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 80.9129 | 33.0923 | 787595.9032 | 65.633 | 65.633 | 133.61 | 0.7 | 77.01 | 22.01 | 831978 | 69.3315 | 69.3315 | 83.9614 | 36.1408 | 860151.2537 | 71.6793 | 71.6793 | 141.0108 | 0.8 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 87.01 | 39.1894 | 932706.6042 | 77.7256 | 77.7256 | 148.4116 | 0.9 | 77.87 | 22.87 | 864486 | 72.0405 | 72.0405 | 90.0585 | 42.2379 | 1005261.9548 | 83.7718 | 83.7718 | 155.8123 | 1 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 93.1071 | 45.2864 | 1077817.3053 | 89.8181 | 89.8181 | 163.2131 | 80 | 65 | 33.3814 | 34 | 63.9
8/1/20XX 7:00:00 PM | 0.79167 | 1 | 77 | 67.7 | 83.5433 | 97.7844 | 14.241 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/1/20XX 8:00:00 PM | 0.83333 | 1 | 76.2 | 69.7 | 81.3009 | 95.1517 | 13.8508 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/1/20XX 9:00:00 PM | 0.875 | 1 | 76.1 | 68.9 | 81.0242 | 94.8268 | 13.8027 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/1/20XX 10:00:00 PM | 0.91667 | 1 | 74.8 | 72.4 | 90.6884 | 103.9709 | 13.2825 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/1/20XX 11:00:00 PM | 0.95833 | 1 | 74.4 | 72.9 | 89.4463 | 102.5422 | 13.0959 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/1/20XX 12:00:00 AM | 0 | 2 | 73.9 | 75.8 | 87.9141 | 100.78 | 12.8659 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/2/20XX 1:00:00 AM | 0.041667 | 2 | 73.8 | 75 | 87.6104 | 100.4307 | 12.8203 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/2/20XX 2:00:00 AM | 0.083333 | 2 | 73.3 | 74 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/2/20XX 3:00:00 AM | 0.125 | 2 | 72.7 | 76 | 84.3281 | 96.6564 | 12.3283 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/2/20XX 4:00:00 AM | 0.16667 | 2 | 72.1 | 79 | 82.5828 | 94.6498 | 12.0671 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/2/20XX 5:00:00 AM | 0.20833 | 2 | 71.6 | 79.7 | 81.1522 | 93.0054 | 11.8531 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/2/20XX 6:00:00 AM | 0.25 | 2 | 71.4 | 80 | 92.3545 | 104.1348 | 11.7803 | 80 | 71.4 |  | 71.4 | 92.3545 | 0.1 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 65.5949 | 17.7743 | 423028.1384 | 35.2523 | 35.2523 | 94.2833 | 0.2 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 68.5682 | 20.7476 | 493792.4767 | 41.1494 | 41.1494 | 99.3614 | 0.3 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 71.5415 | 23.7209 | 564556.8151 | 47.0464 | 47.0464 | 104.4394 | 0.4 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 74.5148 | 26.6942 | 635321.1535 | 52.9434 | 52.9434 | 109.5174 | 0.5 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 77.4881 | 29.6675 | 706085.4918 | 58.8405 | 58.8405 | 114.5955 | 0.6 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 80.4614 | 32.6407 | 776849.8302 | 64.7375 | 64.7375 | 119.6735 | 0.7 | 72.18 | 17.18 | 649404 | 54.117 | 54.117 | 83.4347 | 35.614 | 847614.1686 | 70.6345 | 70.6345 | 124.7515 | 0.8 | 71.92 | 16.92 | 639576 | 53.298 | 53.298 | 86.408 | 38.5873 | 918378.5069 | 76.5315 | 76.5315 | 129.8295 | 0.9 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 89.3813 | 41.5606 | 989142.8453 | 82.4286 | 82.4286 | 134.9076 | 1 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 92.3545 | 44.5339 | 1059907.1836 | 88.3256 | 88.3256 | 139.9856 | 70 | 80 | 31.567 | 32 | 80
8/2/20XX 7:00:00 AM | 0.29167 | 2 | 72.7 | 77.2 | 84.3281 | 96.6564 | 12.3283 | 70 | 72.7 |  | 72.7 | 93.2045 | 0.1 | 73.87 | 18.87 | 713286 | 59.4405 | 59.4405 | 65.6799 | 17.8593 | 425051.0322 | 35.4209 | 35.4209 | 94.8614 | 0.2 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 68.7382 | 20.9176 | 497838.2644 | 41.4865 | 41.4865 | 100.5175 | 0.3 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 71.7965 | 23.9759 | 570625.4967 | 47.5521 | 47.5521 | 106.1736 | 0.4 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 74.8548 | 27.0341 | 643412.7289 | 53.6177 | 53.6177 | 111.8297 | 0.5 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 77.9131 | 30.0924 | 716199.9611 | 59.6833 | 59.6833 | 117.4858 | 0.6 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 80.9714 | 33.1507 | 788987.1933 | 65.7489 | 65.7489 | 123.1419 | 0.7 | 73.09 | 18.09 | 683802 | 56.9835 | 56.9835 | 84.0296 | 36.209 | 861774.4256 | 71.8145 | 71.8145 | 128.798 | 0.8 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 87.0879 | 39.2673 | 934561.6578 | 77.8801 | 77.8801 | 134.4541 | 0.9 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 90.1462 | 42.3256 | 1007348.89 | 83.9457 | 83.9457 | 140.1102 | 1 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 93.2045 | 45.3839 | 1080136.1222 | 90.0113 | 90.0113 | 145.7663 | 75 | 75 | 32.0195 | 32 | 77.2
8/2/20XX 8:00:00 AM | 0.33333 | 2 | 73.9 | 74.3 | 87.9141 | 100.78 | 12.8659 | 70 | 73.9 |  | 73.9 | 93.4464 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 65.7041 | 17.8835 | 425626.8138 | 35.4689 | 35.4689 | 95.2874 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 68.7866 | 20.966 | 498989.8276 | 41.5825 | 41.5825 | 101.3695 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 71.8691 | 24.0484 | 572352.8415 | 47.6961 | 47.6961 | 107.4516 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 74.9516 | 27.1309 | 645715.8553 | 53.8097 | 53.8097 | 113.5337 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 78.034 | 30.2134 | 719078.8691 | 59.9232 | 59.9232 | 119.6157 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 81.1165 | 33.2959 | 792441.8829 | 66.0368 | 66.0368 | 125.6978 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 84.199 | 36.3784 | 865804.8967 | 72.1504 | 72.1504 | 131.7799 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 87.2815 | 39.4608 | 939167.9105 | 78.264 | 78.264 | 137.862 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 90.3639 | 42.5433 | 1012530.9244 | 84.3776 | 84.3776 | 143.9441 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 93.4464 | 45.6258 | 1085893.9382 | 90.4912 | 90.4912 | 150.0262 | 75 | 75 | 32.3524 | 32 | 74.3
8/2/20XX 9:00:00 AM | 0.375 | 2 | 75.6 | 70.7 | 93.2166 | 106.8793 | 13.6627 | 70 | 75.6 |  | 75.6 | 94.173 | 0.1 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 65.7768 | 17.9561 | 427355.9964 | 35.613 | 35.613 | 95.967 | 0.2 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 68.9319 | 21.1113 | 502448.1929 | 41.8707 | 41.8707 | 102.7287 | 0.3 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 72.087 | 24.2664 | 577540.3893 | 48.1284 | 48.1284 | 109.4904 | 0.4 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 75.2422 | 27.4215 | 652632.5857 | 54.386 | 54.386 | 116.252 | 0.5 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 78.3973 | 30.5767 | 727724.7822 | 60.6437 | 60.6437 | 123.0137 | 0.6 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 81.5524 | 33.7318 | 802816.9786 | 66.9014 | 66.9014 | 129.7754 | 0.7 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 84.7076 | 36.8869 | 877909.1751 | 73.1591 | 73.1591 | 136.5371 | 0.8 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 87.8627 | 40.0421 | 953001.3715 | 79.4168 | 79.4168 | 143.2988 | 0.9 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 91.0178 | 43.1972 | 1028093.5679 | 85.6745 | 85.6745 | 150.0605 | 1 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 94.173 | 46.3523 | 1103185.7644 | 91.9321 | 91.9321 | 156.8221 | 75 | 70 | 32.8842 | 32 | 70.7
8/2/20XX 10:00:00 AM | 0.41667 | 2 | 77.7 | 64.1 | 85.548 | 100.1379 | 14.59 | 60 | 77.7 |  | 77.7 | 91.5298 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 65.5125 | 17.6918 | 421065.3461 | 35.0888 | 35.0888 | 96.1043 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 68.4033 | 20.5826 | 489866.8922 | 40.8222 | 40.8222 | 103.0032 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 71.2941 | 23.4735 | 558668.4384 | 46.5557 | 46.5557 | 109.9022 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 74.1849 | 26.3643 | 627469.9845 | 52.2892 | 52.2892 | 116.8012 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 77.0757 | 29.2551 | 696271.5306 | 58.0226 | 58.0226 | 123.7001 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 79.9666 | 32.1459 | 765073.0767 | 63.7561 | 63.7561 | 130.5991 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 82.8574 | 35.0367 | 833874.6228 | 69.4896 | 69.4896 | 137.4981 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 85.7482 | 37.9276 | 902676.169 | 75.223 | 75.223 | 144.397 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 88.639 | 40.8184 | 971477.7151 | 80.9565 | 80.9565 | 151.296 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 91.5298 | 43.7092 | 1040279.2612 | 86.6899 | 86.6899 | 158.1949 | 80 | 65 | 32.9867 | 32 | 64.1
8/2/20XX 11:00:00 AM | 0.45833 | 2 | 80.7 | 58.2 | 78.5288 | 94.6002 | 16.0714 | 50 | 80.7 |  | 80.7 | 91.7073 | 0.1 | 74.67 | 19.67 | 743526 | 61.9605 | 61.9605 | 65.5302 | 17.7096 | 421487.7989 | 35.124 | 35.124 | 97.0845 | 0.2 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 68.4388 | 20.6181 | 490711.7978 | 40.8926 | 40.8926 | 104.9636 | 0.3 | 76.01 | 21.01 | 794178 | 66.1815 | 66.1815 | 71.3473 | 23.5267 | 559935.7967 | 46.6613 | 46.6613 | 112.8428 | 0.4 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 74.2559 | 26.4353 | 629159.7956 | 52.43 | 52.43 | 120.722 | 0.5 | 77.35 | 22.35 | 844830 | 70.4025 | 70.4025 | 77.1645 | 29.3439 | 698383.7945 | 58.1986 | 58.1986 | 128.6011 | 0.6 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 80.0731 | 32.2524 | 767607.7934 | 63.9673 | 63.9673 | 136.4803 | 0.7 | 78.69 | 23.69 | 895482 | 74.6235 | 74.6235 | 82.9816 | 35.161 | 836831.7924 | 69.736 | 69.736 | 144.3595 | 0.8 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 85.8902 | 38.0696 | 906055.7913 | 75.5046 | 75.5046 | 152.2386 | 0.9 | 80.03 | 25.03 | 946134 | 78.8445 | 78.8445 | 88.7988 | 40.9781 | 975279.7902 | 81.2733 | 81.2733 | 160.1178 | 1 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 91.7073 | 43.8867 | 1044503.7891 | 87.042 | 87.042 | 167.997 | 80 | 60 | 33.752 | 34 | 58.2
8/2/20XX 12:00:00 PM | 0.5 | 2 | 81.3 | 56.7 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 91.091 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 65.4686 | 17.6479 | 420020.799 | 35.0017 | 35.0017 | 97.1512 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 68.3155 | 20.4949 | 487777.7981 | 40.6481 | 40.6481 | 105.0971 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 71.1624 | 23.3418 | 555534.7971 | 46.2946 | 46.2946 | 113.0431 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 74.0094 | 26.1887 | 623291.7961 | 51.941 | 51.941 | 120.989 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 76.8563 | 29.0357 | 691048.7951 | 57.5874 | 57.5874 | 128.9349 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 79.7032 | 31.8826 | 758805.7942 | 63.2338 | 63.2338 | 136.8808 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 82.5502 | 34.7295 | 826562.7932 | 68.8802 | 68.8802 | 144.8267 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 85.3971 | 37.5765 | 894319.7922 | 74.5266 | 74.5266 | 152.7726 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 88.244 | 40.4234 | 962076.7913 | 80.1731 | 80.1731 | 160.7186 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 91.091 | 43.2703 | 1029833.7903 | 85.8195 | 85.8195 | 168.6645 | 80 | 55 | 33.8028 | 34 | 56.7
8/2/20XX 1:00:00 PM | 0.54167 | 2 | 80.5 | 57.2 | 78.0095 | 93.973 | 15.9635 | 50 | 80.5 |  | 80.5 | 89.5032 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 65.3098 | 17.4892 | 416241.9728 | 34.6868 | 34.6868 | 96.5843 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 67.9979 | 20.1773 | 480220.1457 | 40.0183 | 40.0183 | 103.9633 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 70.6861 | 22.8655 | 544198.3185 | 45.3499 | 45.3499 | 111.3424 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 73.3743 | 25.5536 | 608176.4914 | 50.6814 | 50.6814 | 118.7214 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 76.0624 | 28.2418 | 672154.6642 | 56.0129 | 56.0129 | 126.1004 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 78.7506 | 30.93 | 736132.8371 | 61.3444 | 61.3444 | 133.4794 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 81.4387 | 33.6181 | 800111.0099 | 66.6759 | 66.6759 | 140.8584 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 84.1269 | 36.3063 | 864089.1827 | 72.0074 | 72.0074 | 148.2374 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 86.8151 | 38.9944 | 928067.3556 | 77.3389 | 77.3389 | 155.6164 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 89.5032 | 41.6826 | 992045.5284 | 82.6705 | 82.6705 | 162.9955 | 80 | 55 | 33.3572 | 34 | 57.2
8/2/20XX 2:00:00 PM | 0.58333 | 2 | 81.3 | 56.9 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 91.4189 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 65.5014 | 17.6807 | 420801.3851 | 35.0668 | 35.0668 | 97.2163 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 68.3811 | 20.5605 | 489338.9702 | 40.7782 | 40.7782 | 105.2272 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 71.2608 | 23.4402 | 557876.5552 | 46.4897 | 46.4897 | 113.2382 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 74.1406 | 26.3199 | 626414.1403 | 52.2012 | 52.2012 | 121.2492 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 77.0203 | 29.1997 | 694951.7254 | 57.9126 | 57.9126 | 129.2601 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 79.9 | 32.0794 | 763489.3105 | 63.6241 | 63.6241 | 137.2711 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 82.7797 | 34.9591 | 832026.8956 | 69.3356 | 69.3356 | 145.2821 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 85.6595 | 37.8388 | 900564.4807 | 75.047 | 75.047 | 153.293 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 88.5392 | 40.7186 | 969102.0657 | 80.7585 | 80.7585 | 161.304 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 91.4189 | 43.5983 | 1037639.6508 | 86.47 | 86.47 | 169.315 | 80 | 55 | 33.8543 | 34 | 56.9
8/2/20XX 3:00:00 PM | 0.625 | 2 | 80.6 | 57.9 | 78.2688 | 94.2862 | 16.0174 | 50 | 80.6 |  | 80.6 | 90.9225 | 0.1 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 65.4517 | 17.6311 | 419619.9062 | 34.9683 | 34.9683 | 96.8973 | 0.2 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 68.2818 | 20.4612 | 486976.0123 | 40.5813 | 40.5813 | 104.5893 | 0.3 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 71.1119 | 23.2913 | 554332.1185 | 46.1943 | 46.1943 | 112.2813 | 0.4 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 73.942 | 26.1214 | 621688.2247 | 51.8074 | 51.8074 | 119.9734 | 0.5 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 76.7721 | 28.9514 | 689044.3308 | 57.4204 | 57.4204 | 127.6654 | 0.6 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 79.6022 | 31.7815 | 756400.437 | 63.0334 | 63.0334 | 135.3574 | 0.7 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 82.4323 | 34.6116 | 823756.5431 | 68.6464 | 68.6464 | 143.0494 | 0.8 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 85.2623 | 37.4417 | 891112.6493 | 74.2594 | 74.2594 | 150.7414 | 0.9 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 88.0924 | 40.2718 | 958468.7555 | 79.8724 | 79.8724 | 158.4334 | 1 | 80.6 | 25.6 | 967680 | 80.64 | 80.64 | 90.9225 | 43.1019 | 1025824.8616 | 85.4854 | 85.4854 | 166.1254 | 80 | 60 | 33.6043 | 34 | 57.9
8/2/20XX 4:00:00 PM | 0.66667 | 2 | 79.8 | 57.8 | 76.2143 | 91.8048 | 15.5904 | 50 | 79.8 |  | 79.8 | 88.3749 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 65.197 | 17.3763 | 413556.4904 | 34.463 | 34.463 | 96.14 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 67.7723 | 19.9516 | 474849.1807 | 39.5708 | 39.5708 | 103.0748 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 70.3476 | 22.527 | 536141.8711 | 44.6785 | 44.6785 | 110.0095 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 72.9229 | 25.1023 | 597434.5614 | 49.7862 | 49.7862 | 116.9442 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 75.4982 | 27.6776 | 658727.2518 | 54.8939 | 54.8939 | 123.8789 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 78.0736 | 30.2529 | 720019.9421 | 60.0017 | 60.0017 | 130.8137 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 80.6489 | 32.8283 | 781312.6325 | 65.1094 | 65.1094 | 137.7484 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 83.2242 | 35.4036 | 842605.3228 | 70.2171 | 70.2171 | 144.6831 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 85.7995 | 37.9789 | 903898.0132 | 75.3248 | 75.3248 | 151.6178 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 88.3749 | 40.5542 | 965190.7035 | 80.4326 | 80.4326 | 158.5526 | 80 | 60 | 33.0083 | 34 | 57.8
8/2/20XX 5:00:00 PM | 0.70833 | 2 | 78.8 | 60.8 | 88.7794 | 103.932 | 15.1526 | 60 | 78.8 |  | 78.8 | 89.9916 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 65.3586 | 17.538 | 417404.3644 | 34.7837 | 34.7837 | 96.1457 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 68.0956 | 20.275 | 482544.9288 | 40.2121 | 40.2121 | 103.0861 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 70.8326 | 23.012 | 547685.4932 | 45.6405 | 45.6405 | 110.0265 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 73.5696 | 25.749 | 612826.0577 | 51.0688 | 51.0688 | 116.9668 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 76.3066 | 28.486 | 677966.6221 | 56.4972 | 56.4972 | 123.9072 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 79.0436 | 31.223 | 743107.1865 | 61.9256 | 61.9256 | 130.8476 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 81.7806 | 33.96 | 808247.7509 | 67.354 | 67.354 | 137.788 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 84.5176 | 36.697 | 873388.3153 | 72.7824 | 72.7824 | 144.7284 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 87.2546 | 39.434 | 938528.8797 | 78.2107 | 78.2107 | 151.6687 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 89.9916 | 42.171 | 1003669.4441 | 83.6391 | 83.6391 | 158.6091 | 80 | 60 | 33.016 | 34 | 60.8
8/2/20XX 6:00:00 PM | 0.75 | 2 | 78.1 | 61.3 | 86.7115 | 101.504 | 14.7925 | 60 | 78.1 |  | 78.1 | 88.6345 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 65.2229 | 17.4023 | 414174.3899 | 34.5145 | 34.5145 | 95.656 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 67.8242 | 20.0036 | 476084.9797 | 39.6737 | 39.6737 | 102.1067 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 70.4255 | 22.6049 | 537995.5696 | 44.833 | 44.833 | 108.5575 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 73.0268 | 25.2061 | 599906.1594 | 49.9922 | 49.9922 | 115.0082 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 75.6281 | 27.8074 | 661816.7493 | 55.1514 | 55.1514 | 121.4589 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 78.2293 | 30.4087 | 723727.3392 | 60.3106 | 60.3106 | 127.9096 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 80.8306 | 33.01 | 785637.929 | 65.4698 | 65.4698 | 134.3603 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 83.4319 | 35.6113 | 847548.5189 | 70.629 | 70.629 | 140.811 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 86.0332 | 38.2126 | 909459.1087 | 75.7883 | 75.7883 | 147.2618 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 88.6345 | 40.8139 | 971369.6986 | 80.9475 | 80.9475 | 153.7125 | 80 | 60 | 32.6314 | 32 | 61.3
8/2/20XX 7:00:00 PM | 0.79167 | 2 | 76.5 | 65.6 | 82.1358 | 96.1318 | 13.9961 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/2/20XX 8:00:00 PM | 0.83333 | 2 | 75.6 | 68 | 79.6526 | 93.2166 | 13.564 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/2/20XX 9:00:00 PM | 0.875 | 2 | 74.8 | 70.1 | 90.6884 | 103.9709 | 13.2825 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/2/20XX 10:00:00 PM | 0.91667 | 2 | 74.4 | 70.2 | 89.4463 | 102.5422 | 13.0959 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/2/20XX 11:00:00 PM | 0.95833 | 2 | 74.3 | 69.7 | 76.1783 | 89.138 | 12.9597 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/2/20XX 12:00:00 AM | 0 | 3 | 73.6 | 70.7 | 87.0056 | 99.7352 | 12.7296 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/3/20XX 1:00:00 AM | 0.041667 | 3 | 73.3 | 70.9 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/3/20XX 2:00:00 AM | 0.083333 | 3 | 72.6 | 73.9 | 84.035 | 96.3195 | 12.2844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/3/20XX 3:00:00 AM | 0.125 | 3 | 72.1 | 75.9 | 82.5828 | 94.6498 | 12.0671 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/3/20XX 4:00:00 AM | 0.16667 | 3 | 71.7 | 77.2 | 81.4366 | 93.3322 | 11.8956 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/3/20XX 5:00:00 AM | 0.20833 | 3 | 71.5 | 77.4 | 80.8687 | 92.6795 | 11.8108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/3/20XX 6:00:00 AM | 0.25 | 3 | 71.8 | 78 | 81.7218 | 93.6601 | 11.9383 | 70 | 71.8 |  | 71.8 | 91.2725 | 0.1 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 65.4867 | 17.6661 | 420452.8272 | 35.0377 | 35.0377 | 94.1947 | 0.2 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 68.3518 | 20.5312 | 488641.8544 | 40.7202 | 40.7202 | 99.1842 | 0.3 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 71.2169 | 23.3963 | 556830.8816 | 46.4026 | 46.4026 | 104.1736 | 0.4 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 74.082 | 26.2613 | 625019.9088 | 52.085 | 52.085 | 109.163 | 0.5 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 76.9471 | 29.1264 | 693208.936 | 57.7674 | 57.7674 | 114.1524 | 0.6 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 79.8121 | 31.9915 | 761397.9632 | 63.4498 | 63.4498 | 119.1418 | 0.7 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 82.6772 | 34.8566 | 829586.9904 | 69.1322 | 69.1322 | 124.1312 | 0.8 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 85.5423 | 37.7217 | 897776.0177 | 74.8147 | 74.8147 | 129.1207 | 0.9 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 88.4074 | 40.5868 | 965965.0449 | 80.4971 | 80.4971 | 134.1101 | 1 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 91.2725 | 43.4519 | 1034154.0721 | 86.1795 | 86.1795 | 139.0995 | 70 | 80 | 31.4962 | 32 | 78
8/3/20XX 7:00:00 AM | 0.29167 | 3 | 72.7 | 76.9 | 84.3281 | 96.6564 | 12.3283 | 70 | 72.7 |  | 72.7 | 92.8347 | 0.1 | 73.87 | 18.87 | 713286 | 59.4405 | 59.4405 | 65.6429 | 17.8223 | 424170.7903 | 35.3476 | 35.3476 | 94.7881 | 0.2 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 68.6642 | 20.8436 | 496077.7807 | 41.3398 | 41.3398 | 100.3708 | 0.3 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 71.6855 | 23.8649 | 567984.771 | 47.3321 | 47.3321 | 105.9536 | 0.4 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 74.7068 | 26.8862 | 639891.7613 | 53.3243 | 53.3243 | 111.5363 | 0.5 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 77.7281 | 29.9075 | 711798.7517 | 59.3166 | 59.3166 | 117.1191 | 0.6 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 80.7494 | 32.9288 | 783705.742 | 65.3088 | 65.3088 | 122.7018 | 0.7 | 73.09 | 18.09 | 683802 | 56.9835 | 56.9835 | 83.7707 | 35.9501 | 855612.7324 | 71.3011 | 71.3011 | 128.2846 | 0.8 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 86.792 | 38.9714 | 927519.7227 | 77.2933 | 77.2933 | 133.8673 | 0.9 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 89.8134 | 41.9927 | 999426.713 | 83.2856 | 83.2856 | 139.4501 | 1 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 92.8347 | 45.014 | 1071333.7034 | 89.2778 | 89.2778 | 145.0328 | 75 | 75 | 31.9617 | 32 | 76.9
8/3/20XX 8:00:00 AM | 0.33333 | 3 | 73.7 | 73.2 | 87.3075 | 100.0824 | 12.7749 | 70 | 73.7 |  | 73.7 | 91.3955 | 0.1 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 65.499 | 17.6784 | 420745.5589 | 35.0621 | 35.0621 | 94.8176 | 0.2 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 68.3764 | 20.5558 | 489227.3177 | 40.7689 | 40.7689 | 100.4299 | 0.3 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 71.2538 | 23.4332 | 557709.0766 | 46.4758 | 46.4758 | 106.0423 | 0.4 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 74.1312 | 26.3105 | 626190.8354 | 52.1826 | 52.1826 | 111.6546 | 0.5 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 77.0086 | 29.1879 | 694672.5943 | 57.8894 | 57.8894 | 117.2669 | 0.6 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 79.8859 | 32.0653 | 763154.3531 | 63.5962 | 63.5962 | 122.8792 | 0.7 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 82.7633 | 34.9427 | 831636.112 | 69.303 | 69.303 | 128.4915 | 0.8 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 85.6407 | 37.8201 | 900117.8708 | 75.0098 | 75.0098 | 134.1038 | 0.9 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 88.5181 | 40.6975 | 968599.6297 | 80.7166 | 80.7166 | 139.7161 | 1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 91.3955 | 43.5748 | 1037081.3885 | 86.4234 | 86.4234 | 145.3284 | 75 | 75 | 31.9825 | 32 | 73.2
8/3/20XX 9:00:00 AM | 0.375 | 3 | 75.6 | 69.7 | 79.6526 | 93.2166 | 13.564 | 60 | 75.6 |  | 75.6 | 92.8097 | 0.1 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 65.6404 | 17.8198 | 424111.3193 | 35.3426 | 35.3426 | 95.6966 | 0.2 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 68.6592 | 20.8386 | 495958.8386 | 41.3299 | 41.3299 | 102.1879 | 0.3 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 71.678 | 23.8574 | 567806.358 | 47.3172 | 47.3172 | 108.6792 | 0.4 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 74.6968 | 26.8762 | 639653.8773 | 53.3045 | 53.3045 | 115.1705 | 0.5 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 77.7156 | 29.895 | 711501.3966 | 59.2918 | 59.2918 | 121.6618 | 0.6 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 80.7345 | 32.9138 | 783348.9159 | 65.2791 | 65.2791 | 128.1531 | 0.7 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 83.7533 | 35.9326 | 855196.4352 | 71.2664 | 71.2664 | 134.6444 | 0.8 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 86.7721 | 38.9514 | 927043.9546 | 77.2537 | 77.2537 | 141.1357 | 0.9 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 89.7909 | 41.9702 | 998891.4739 | 83.241 | 83.241 | 147.627 | 1 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 92.8097 | 44.989 | 1070738.9932 | 89.2282 | 89.2282 | 154.1182 | 75 | 70 | 32.6708 | 32 | 69.7
8/3/20XX 10:00:00 AM | 0.41667 | 3 | 77.7 | 64.3 | 85.548 | 100.1379 | 14.59 | 60 | 77.7 |  | 77.7 | 91.8216 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 65.5416 | 17.721 | 421759.8286 | 35.1467 | 35.1467 | 96.1622 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 68.4616 | 20.641 | 491255.8571 | 40.938 | 40.938 | 103.119 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 71.3816 | 23.561 | 560751.8857 | 46.7293 | 46.7293 | 110.0758 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 74.3016 | 26.481 | 630247.9142 | 52.5207 | 52.5207 | 117.0327 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 77.2216 | 29.401 | 699743.9428 | 58.312 | 58.312 | 123.9895 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 80.1416 | 32.321 | 769239.9713 | 64.1033 | 64.1033 | 130.9463 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 83.0616 | 35.241 | 838735.9999 | 69.8947 | 69.8947 | 137.9032 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 85.9816 | 38.161 | 908232.0284 | 75.686 | 75.686 | 144.86 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 88.9016 | 41.081 | 977728.057 | 81.4773 | 81.4773 | 151.8168 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 91.8216 | 44.001 | 1047224.0855 | 87.2687 | 87.2687 | 158.7737 | 80 | 65 | 33.0324 | 34 | 64.3
8/3/20XX 11:00:00 AM | 0.45833 | 3 | 80.2 | 61.4 | 93.0386 | 108.933 | 15.8944 | 60 | 80.2 |  | 80.2 | 95.2638 | 0.1 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 65.8859 | 18.0652 | 429952.2391 | 35.8294 | 35.8294 | 97.6324 | 0.2 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 69.1501 | 21.3294 | 507640.6782 | 42.3034 | 42.3034 | 106.0594 | 0.3 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 72.4143 | 24.5937 | 585329.1173 | 48.7774 | 48.7774 | 114.4864 | 0.4 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 75.6785 | 27.8579 | 663017.5564 | 55.2515 | 55.2515 | 122.9135 | 0.5 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 78.9427 | 31.1221 | 740705.9955 | 61.7255 | 61.7255 | 131.3405 | 0.6 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 82.207 | 34.3863 | 818394.4346 | 68.1995 | 68.1995 | 139.7675 | 0.7 | 78.34 | 23.34 | 882252 | 73.521 | 73.521 | 85.4712 | 37.6505 | 896082.8737 | 74.6736 | 74.6736 | 148.1946 | 0.8 | 78.96 | 23.96 | 905688 | 75.474 | 75.474 | 88.7354 | 40.9148 | 973771.3128 | 81.1476 | 81.1476 | 156.6216 | 0.9 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 91.9996 | 44.179 | 1051459.7519 | 87.6216 | 87.6216 | 165.0486 | 1 | 80.2 | 25.2 | 952560 | 79.38 | 79.38 | 95.2638 | 47.4432 | 1129148.191 | 94.0957 | 94.0957 | 173.4757 | 80 | 60 | 34.1868 | 34 | 61.4
8/3/20XX 12:00:00 PM | 0.5 | 3 | 80.3 | 62.3 | 93.3492 | 109.2977 | 15.9485 | 60 | 80.3 |  | 80.3 | 97.0174 | 0.1 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 66.0612 | 18.2406 | 434125.6663 | 36.1771 | 36.1771 | 98.0116 | 0.2 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 69.5008 | 21.6801 | 515987.5325 | 42.999 | 42.999 | 106.818 | 0.3 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 72.9404 | 25.1197 | 597849.3988 | 49.8208 | 49.8208 | 115.6243 | 0.4 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 76.3799 | 28.5593 | 679711.265 | 56.6426 | 56.6426 | 124.4306 | 0.5 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 79.8195 | 31.9989 | 761573.1313 | 63.4644 | 63.4644 | 133.2369 | 0.6 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 83.2591 | 35.4384 | 843434.9975 | 70.2862 | 70.2862 | 142.0432 | 0.7 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 86.6987 | 38.878 | 925296.8638 | 77.1081 | 77.1081 | 150.8496 | 0.8 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 90.1382 | 42.3176 | 1007158.7301 | 83.9299 | 83.9299 | 159.6559 | 0.9 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 93.5778 | 45.7572 | 1089020.5963 | 90.7517 | 90.7517 | 168.4622 | 1 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 97.0174 | 49.1967 | 1170882.4626 | 97.5735 | 97.5735 | 177.2685 | 80 | 60 | 34.4864 | 34 | 62.3
8/3/20XX 1:00:00 PM | 0.54167 | 3 | 80.6 | 62.1 | 94.2862 | 110.3979 | 16.1117 | 60 | 80.6 |  | 80.6 | 97.6696 | 0.1 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 66.1264 | 18.3058 | 435678.0292 | 36.3065 | 36.3065 | 98.2355 | 0.2 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 69.6312 | 21.8106 | 519092.2583 | 43.2577 | 43.2577 | 107.2657 | 0.3 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 73.136 | 25.3154 | 602506.4875 | 50.2089 | 50.2089 | 116.2959 | 0.4 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 76.6408 | 28.8202 | 685920.7167 | 57.1601 | 57.1601 | 125.3261 | 0.5 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 80.1456 | 32.325 | 769334.9459 | 64.1112 | 64.1112 | 134.3562 | 0.6 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 83.6504 | 35.8298 | 852749.175 | 71.0624 | 71.0624 | 143.3864 | 0.7 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 87.1552 | 39.3346 | 936163.4042 | 78.0136 | 78.0136 | 152.4166 | 0.8 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 90.66 | 42.8394 | 1019577.6334 | 84.9648 | 84.9648 | 161.4468 | 0.9 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 94.1648 | 46.3442 | 1102991.8625 | 91.916 | 91.916 | 170.477 | 1 | 80.6 | 25.6 | 967680 | 80.64 | 80.64 | 97.6696 | 49.849 | 1186406.0917 | 98.8672 | 98.8672 | 179.5072 | 80 | 60 | 34.6625 | 34 | 62.1
8/3/20XX 2:00:00 PM | 0.58333 | 3 | 81.1 | 60.1 | 95.865 | 112.2518 | 16.3868 | 60 | 81.1 |  | 81.1 | 96.0289 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 65.9624 | 18.1417 | 431772.9874 | 35.9811 | 35.9811 | 98.0676 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 69.3031 | 21.4824 | 511282.1748 | 42.6068 | 42.6068 | 106.9298 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 72.6438 | 24.8232 | 590791.3623 | 49.2326 | 49.2326 | 115.7921 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 75.9845 | 28.1639 | 670300.5497 | 55.8584 | 55.8584 | 124.6544 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 79.3252 | 31.5046 | 749809.7371 | 62.4841 | 62.4841 | 133.5166 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 82.666 | 34.8453 | 829318.9245 | 69.1099 | 69.1099 | 142.3789 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 86.0067 | 38.1861 | 908828.1119 | 75.7357 | 75.7357 | 151.2412 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 89.3474 | 41.5268 | 988337.2994 | 82.3614 | 82.3614 | 160.1034 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 92.6881 | 44.8675 | 1067846.4868 | 88.9872 | 88.9872 | 168.9657 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 96.0289 | 48.2082 | 1147355.6742 | 95.613 | 95.613 | 177.828 | 80 | 60 | 34.5283 | 34 | 60.1
8/3/20XX 3:00:00 PM | 0.625 | 3 | 80.2 | 61.5 | 93.0386 | 108.933 | 15.8944 | 60 | 80.2 |  | 80.2 | 95.4228 | 0.1 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 65.9017 | 18.0811 | 430330.5261 | 35.8609 | 35.8609 | 97.6639 | 0.2 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 69.1819 | 21.3612 | 508397.2521 | 42.3664 | 42.3664 | 106.1224 | 0.3 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 72.462 | 24.6413 | 586463.9782 | 48.872 | 48.872 | 114.581 | 0.4 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 75.7421 | 27.9215 | 664530.7042 | 55.3776 | 55.3776 | 123.0396 | 0.5 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 79.0222 | 31.2016 | 742597.4303 | 61.8831 | 61.8831 | 131.4981 | 0.6 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 82.3023 | 34.4817 | 820664.1563 | 68.3887 | 68.3887 | 139.9567 | 0.7 | 78.34 | 23.34 | 882252 | 73.521 | 73.521 | 85.5824 | 37.7618 | 898730.8824 | 74.8942 | 74.8942 | 148.4152 | 0.8 | 78.96 | 23.96 | 905688 | 75.474 | 75.474 | 88.8625 | 41.0419 | 976797.6084 | 81.3998 | 81.3998 | 156.8738 | 0.9 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 92.1427 | 44.322 | 1054864.3345 | 87.9054 | 87.9054 | 165.3324 | 1 | 80.2 | 25.2 | 952560 | 79.38 | 79.38 | 95.4228 | 47.6021 | 1132931.0605 | 94.4109 | 94.4109 | 173.7909 | 80 | 60 | 34.2117 | 34 | 61.5
8/3/20XX 4:00:00 PM | 0.66667 | 3 | 79.3 | 63.5 | 90.2816 | 105.6957 | 15.4142 | 60 | 79.3 |  | 79.3 | 95.6765 | 0.1 | 74.53 | 19.53 | 738234 | 61.5195 | 61.5195 | 65.9271 | 18.1065 | 430934.4261 | 35.9112 | 35.9112 | 97.4307 | 0.2 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 69.2326 | 21.412 | 509605.0521 | 42.4671 | 42.4671 | 105.6561 | 0.3 | 75.59 | 20.59 | 778302 | 64.8585 | 64.8585 | 72.5381 | 24.7175 | 588275.6782 | 49.023 | 49.023 | 113.8815 | 0.4 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 75.8436 | 28.023 | 666946.3042 | 55.5789 | 55.5789 | 122.1069 | 0.5 | 76.65 | 21.65 | 818370 | 68.1975 | 68.1975 | 79.1491 | 31.3284 | 745616.9303 | 62.1347 | 62.1347 | 130.3322 | 0.6 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 82.4546 | 34.6339 | 824287.5563 | 68.6906 | 68.6906 | 138.5576 | 0.7 | 77.71 | 22.71 | 858438 | 71.5365 | 71.5365 | 85.7601 | 37.9394 | 902958.1824 | 75.2465 | 75.2465 | 146.783 | 0.8 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 89.0655 | 41.2449 | 981628.8085 | 81.8024 | 81.8024 | 155.0084 | 0.9 | 78.77 | 23.77 | 898506 | 74.8755 | 74.8755 | 92.371 | 44.5504 | 1060299.4345 | 88.3583 | 88.3583 | 163.2338 | 1 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 95.6765 | 47.8559 | 1138970.0606 | 94.9142 | 94.9142 | 171.4592 | 80 | 65 | 34.0301 | 34 | 63.5
8/3/20XX 5:00:00 PM | 0.70833 | 3 | 78.8 | 63.5 | 88.7794 | 103.932 | 15.1526 | 60 | 78.8 |  | 78.8 | 94.0828 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 65.7678 | 17.9471 | 427141.4189 | 35.5951 | 35.5951 | 96.9571 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 68.9139 | 21.0932 | 502019.0378 | 41.8349 | 41.8349 | 104.7089 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 72.06 | 24.2394 | 576896.6567 | 48.0747 | 48.0747 | 112.4607 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 75.2061 | 27.3855 | 651774.2755 | 54.3145 | 54.3145 | 120.2125 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 78.3522 | 30.5316 | 726651.8944 | 60.5543 | 60.5543 | 127.9643 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 81.4983 | 33.6777 | 801529.5133 | 66.7941 | 66.7941 | 135.7161 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 84.6445 | 36.8238 | 876407.1322 | 73.0339 | 73.0339 | 143.4679 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 87.7906 | 39.9699 | 951284.7511 | 79.2737 | 79.2737 | 151.2197 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 90.9367 | 43.1161 | 1026162.37 | 85.5135 | 85.5135 | 158.9715 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 94.0828 | 46.2622 | 1101039.9889 | 91.7533 | 91.7533 | 166.7233 | 80 | 65 | 33.6572 | 34 | 63.5
8/3/20XX 6:00:00 PM | 0.75 | 3 | 77.8 | 67.1 | 85.8376 | 100.478 | 14.6404 | 60 | 77.8 |  | 77.8 | 96.2323 | 0.1 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 65.9827 | 18.1621 | 432257.1329 | 36.0214 | 36.0214 | 97.0684 | 0.2 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 69.3438 | 21.5231 | 512250.4658 | 42.6875 | 42.6875 | 104.9315 | 0.3 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 72.7048 | 24.8842 | 592243.7988 | 49.3536 | 49.3536 | 112.7946 | 0.4 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 76.0659 | 28.2453 | 672237.1317 | 56.0198 | 56.0198 | 120.6578 | 0.5 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 79.427 | 31.6063 | 752230.4646 | 62.6859 | 62.6859 | 128.5209 | 0.6 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 82.788 | 34.9674 | 832223.7975 | 69.352 | 69.352 | 136.384 | 0.7 | 76.66 | 21.66 | 818748 | 68.229 | 68.229 | 86.1491 | 38.3285 | 912217.1304 | 76.0181 | 76.0181 | 144.2471 | 0.8 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 89.5101 | 41.6895 | 992210.4633 | 82.6842 | 82.6842 | 152.1102 | 0.9 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 92.8712 | 45.0506 | 1072203.7963 | 89.3503 | 89.3503 | 159.9733 | 1 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 96.2323 | 48.4116 | 1152197.1292 | 96.0164 | 96.0164 | 167.8364 | 80 | 65 | 33.748 | 34 | 67.1
8/3/20XX 7:00:00 PM | 0.79167 | 3 | 76.9 | 67.5 | 83.2602 | 97.452 | 14.1918 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/3/20XX 8:00:00 PM | 0.83333 | 3 | 76.4 | 68.1 | 81.8567 | 95.8042 | 13.9475 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/3/20XX 9:00:00 PM | 0.875 | 3 | 75.8 | 69.7 | 80.1988 | 93.8579 | 13.6591 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/3/20XX 10:00:00 PM | 0.91667 | 3 | 74.9 | 72.1 | 91.0012 | 104.3307 | 13.3295 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/3/20XX 11:00:00 PM | 0.95833 | 3 | 74.7 | 72.2 | 90.3765 | 103.6122 | 13.2356 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/3/20XX 12:00:00 AM | 0 | 4 | 74.1 | 73.4 | 88.5243 | 101.4817 | 12.9575 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/4/20XX 1:00:00 AM | 0.041667 | 4 | 73.5 | 76.6 | 86.7045 | 99.389 | 12.6844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/4/20XX 2:00:00 AM | 0.083333 | 4 | 73.2 | 77.8 | 85.8067 | 98.3566 | 12.5498 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/4/20XX 3:00:00 AM | 0.125 | 4 | 72.5 | 79.1 | 83.7428 | 95.9835 | 12.2407 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/4/20XX 4:00:00 AM | 0.16667 | 4 | 71.7 | 80.8 | 93.3322 | 105.2414 | 11.9091 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/4/20XX 5:00:00 AM | 0.20833 | 4 | 71.3 | 82.3 | 92.0306 | 103.7683 | 11.7376 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/4/20XX 6:00:00 AM | 0.25 | 4 | 72 | 81.8 | 94.3189 | 106.3581 | 12.0392 | 80 | 72 |  | 72 | 96.486 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 66.0081 | 18.1874 | 432860.9715 | 36.0717 | 36.0717 | 95.2917 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 69.3945 | 21.5739 | 513458.1429 | 42.7882 | 42.7882 | 101.3782 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 72.7809 | 24.9603 | 594055.3144 | 49.5046 | 49.5046 | 107.4646 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 76.1674 | 28.3467 | 674652.4858 | 56.221 | 56.221 | 113.551 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 79.5538 | 31.7332 | 755249.6573 | 62.9375 | 62.9375 | 119.6375 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 82.9402 | 35.1196 | 835846.8287 | 69.6539 | 69.6539 | 125.7239 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 86.3267 | 38.5061 | 916444.0002 | 76.3703 | 76.3703 | 131.8103 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 89.7131 | 41.8925 | 997041.1716 | 83.0868 | 83.0868 | 137.8968 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 93.0996 | 45.2789 | 1077638.3431 | 89.8032 | 89.8032 | 143.9832 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 96.486 | 48.6654 | 1158235.5145 | 96.5196 | 96.5196 | 150.0696 | 70 | 80 | 32.3602 | 32 | 81.8
8/4/20XX 7:00:00 AM | 0.29167 | 4 | 72.2 | 80.9 | 94.9817 | 107.1084 | 12.1266 | 80 | 72.2 |  | 72.2 | 96.0731 | 0.1 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 65.9668 | 18.1462 | 431878.3787 | 35.9899 | 35.9899 | 95.2729 | 0.2 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 69.3119 | 21.4913 | 511492.9574 | 42.6244 | 42.6244 | 101.3404 | 0.3 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 72.6571 | 24.8365 | 591107.536 | 49.259 | 49.259 | 107.408 | 0.4 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 76.0022 | 28.1816 | 670722.1147 | 55.8935 | 55.8935 | 113.4755 | 0.5 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 79.3474 | 31.5268 | 750336.6934 | 62.5281 | 62.5281 | 119.5431 | 0.6 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 82.6925 | 34.8719 | 829951.2721 | 69.1626 | 69.1626 | 125.6106 | 0.7 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 86.0377 | 38.2171 | 909565.8508 | 75.7972 | 75.7972 | 131.6782 | 0.8 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 89.3828 | 41.5622 | 989180.4294 | 82.4317 | 82.4317 | 137.7457 | 0.9 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 92.728 | 44.9074 | 1068795.0081 | 89.0663 | 89.0663 | 143.8133 | 1 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 96.0731 | 48.2525 | 1148409.5868 | 95.7008 | 95.7008 | 149.8808 | 70 | 80 | 32.3449 | 32 | 80.9
8/4/20XX 8:00:00 AM | 0.33333 | 4 | 74 | 75.8 | 88.2187 | 101.1303 | 12.9116 | 70 | 74 |  | 74 | 95.7075 | 0.1 | 74 | 19 | 718200 | 59.85 | 59.85 | 65.9302 | 18.1096 | 431008.0816 | 35.9173 | 35.9173 | 95.7673 | 0.2 | 74 | 19 | 718200 | 59.85 | 59.85 | 69.2388 | 21.4182 | 509752.3632 | 42.4794 | 42.4794 | 102.3294 | 0.3 | 74 | 19 | 718200 | 59.85 | 59.85 | 72.5474 | 24.7267 | 588496.6448 | 49.0414 | 49.0414 | 108.8914 | 0.4 | 74 | 19 | 718200 | 59.85 | 59.85 | 75.856 | 28.0353 | 667240.9264 | 55.6034 | 55.6034 | 115.4534 | 0.5 | 74 | 19 | 718200 | 59.85 | 59.85 | 79.1645 | 31.3439 | 745985.2079 | 62.1654 | 62.1654 | 122.0154 | 0.6 | 74 | 19 | 718200 | 59.85 | 59.85 | 82.4731 | 34.6525 | 824729.4895 | 68.7275 | 68.7275 | 128.5775 | 0.7 | 74 | 19 | 718200 | 59.85 | 59.85 | 85.7817 | 37.9611 | 903473.7711 | 75.2895 | 75.2895 | 135.1395 | 0.8 | 74 | 19 | 718200 | 59.85 | 59.85 | 89.0903 | 41.2697 | 982218.0527 | 81.8515 | 81.8515 | 141.7015 | 0.9 | 74 | 19 | 718200 | 59.85 | 59.85 | 92.3989 | 44.5782 | 1060962.3343 | 88.4135 | 88.4135 | 148.2635 | 1 | 74 | 19 | 718200 | 59.85 | 59.85 | 95.7075 | 47.8868 | 1139706.6159 | 94.9756 | 94.9756 | 154.8256 | 75 | 75 | 32.7307 | 32 | 75.8
8/4/20XX 9:00:00 AM | 0.375 | 4 | 75.8 | 72.3 | 93.8579 | 107.6171 | 13.7592 | 70 | 75.8 |  | 75.8 | 97.0225 | 0.1 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 66.0617 | 18.2411 | 434137.8667 | 36.1782 | 36.1782 | 96.5952 | 0.2 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 69.5018 | 21.6812 | 516011.9333 | 43.001 | 43.001 | 103.985 | 0.3 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 72.9419 | 25.1213 | 597886 | 49.8238 | 49.8238 | 111.3748 | 0.4 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 76.382 | 28.5613 | 679760.0666 | 56.6467 | 56.6467 | 118.7647 | 0.5 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 79.8221 | 32.0014 | 761634.1333 | 63.4695 | 63.4695 | 126.1545 | 0.6 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 83.2622 | 35.4415 | 843508.2 | 70.2923 | 70.2923 | 133.5443 | 0.7 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 86.7022 | 38.8816 | 925382.2666 | 77.1152 | 77.1152 | 140.9342 | 0.8 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 90.1423 | 42.3217 | 1007256.3333 | 83.938 | 83.938 | 148.324 | 0.9 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 93.5824 | 45.7618 | 1089130.3999 | 90.7609 | 90.7609 | 155.7139 | 1 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 97.0225 | 49.2019 | 1171004.4666 | 97.5837 | 97.5837 | 163.1037 | 75 | 70 | 33.3795 | 34 | 72.3
8/4/20XX 10:00:00 AM | 0.41667 | 4 | 78 | 68.9 | 86.4193 | 101.161 | 14.7417 | 60 | 78 |  | 78 | 99.5394 | 0.1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 66.3134 | 18.4928 | 440128.1608 | 36.6773 | 36.6773 | 97.7873 | 0.2 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 70.0052 | 22.1846 | 527992.5216 | 43.9994 | 43.9994 | 106.3694 | 0.3 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 73.697 | 25.8763 | 615856.8824 | 51.3214 | 51.3214 | 114.9514 | 0.4 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 77.3888 | 29.5681 | 703721.2432 | 58.6434 | 58.6434 | 123.5334 | 0.5 | 76 | 21 | 793800 | 66.15 | 66.15 | 81.0805 | 33.2599 | 791585.6039 | 65.9655 | 65.9655 | 132.1155 | 0.6 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 84.7723 | 36.9517 | 879449.9647 | 73.2875 | 73.2875 | 140.6975 | 0.7 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 88.4641 | 40.6435 | 967314.3255 | 80.6095 | 80.6095 | 149.2795 | 0.8 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 92.1559 | 44.3352 | 1055178.6863 | 87.9316 | 87.9316 | 157.8616 | 0.9 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 95.8477 | 48.027 | 1143043.0471 | 95.2536 | 95.2536 | 166.4436 | 1 | 78 | 23 | 869400 | 72.45 | 72.45 | 99.5394 | 51.7188 | 1230907.4079 | 102.5756 | 102.5756 | 175.0256 | 80 | 70 | 34.3154 | 34 | 68.9
8/4/20XX 11:00:00 AM | 0.45833 | 4 | 80.3 | 63.8 | 93.3492 | 109.2977 | 15.9485 | 60 | 80.3 |  | 80.3 | 99.4097 | 0.1 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 66.3004 | 18.4798 | 439819.2868 | 36.6516 | 36.6516 | 98.4861 | 0.2 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 69.9792 | 22.1586 | 527374.7737 | 43.9479 | 43.9479 | 107.7669 | 0.3 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 73.658 | 25.8374 | 614930.2605 | 51.2442 | 51.2442 | 117.0477 | 0.4 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 77.3368 | 29.5162 | 702485.7473 | 58.5405 | 58.5405 | 126.3285 | 0.5 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 81.0156 | 33.195 | 790041.2342 | 65.8368 | 65.8368 | 135.6093 | 0.6 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 84.6944 | 36.8738 | 877596.721 | 73.1331 | 73.1331 | 144.8901 | 0.7 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 88.3732 | 40.5526 | 965152.2079 | 80.4294 | 80.4294 | 154.1709 | 0.8 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 92.052 | 44.2314 | 1052707.6947 | 87.7256 | 87.7256 | 163.4516 | 0.9 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 95.7309 | 47.9102 | 1140263.1815 | 95.0219 | 95.0219 | 172.7324 | 1 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 99.4097 | 51.589 | 1227818.6684 | 102.3182 | 102.3182 | 182.0132 | 80 | 65 | 34.8616 | 34 | 63.8
8/4/20XX 12:00:00 PM | 0.5 | 4 | 82.2 | 59.3 | 82.5146 | 99.4151 | 16.9005 | 50 | 82.2 |  | 82.2 | 98.2321 | 0.1 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 66.1827 | 18.362 | 437016.618 | 36.4181 | 36.4181 | 98.8511 | 0.2 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 69.7437 | 21.9231 | 521769.4359 | 43.4808 | 43.4808 | 108.4968 | 0.3 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 73.3048 | 25.4841 | 606522.2539 | 50.5435 | 50.5435 | 118.1425 | 0.4 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 76.8658 | 29.0452 | 691275.0718 | 57.6063 | 57.6063 | 127.7883 | 0.5 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 80.4268 | 32.6062 | 776027.8898 | 64.669 | 64.669 | 137.434 | 0.6 | 78.92 | 23.92 | 904176 | 75.348 | 75.348 | 83.9879 | 36.1673 | 860780.7077 | 71.7317 | 71.7317 | 147.0797 | 0.7 | 79.74 | 24.74 | 935172 | 77.931 | 77.931 | 87.5489 | 39.7283 | 945533.5257 | 78.7945 | 78.7945 | 156.7255 | 0.8 | 80.56 | 25.56 | 966168 | 80.514 | 80.514 | 91.11 | 43.2893 | 1030286.3436 | 85.8572 | 85.8572 | 166.3712 | 0.9 | 81.38 | 26.38 | 997164 | 83.097 | 83.097 | 94.671 | 46.8504 | 1115039.1616 | 92.9199 | 92.9199 | 176.0169 | 1 | 82.2 | 27.2 | 1028160 | 85.68 | 85.68 | 98.2321 | 50.4114 | 1199791.9795 | 99.9827 | 99.9827 | 185.6627 | 80 | 60 | 35.1447 | 36 | 59.3
8/4/20XX 1:00:00 PM | 0.54167 | 4 | 82.9 | 54 | 84.4305 | 101.7299 | 17.2993 | 50 | 82.9 |  | 82.9 | 91.3503 | 0.1 | 74.89 | 19.89 | 751842 | 62.6535 | 62.6535 | 65.4945 | 17.6739 | 420637.9505 | 35.0532 | 35.0532 | 97.7067 | 0.2 | 75.78 | 20.78 | 785484 | 65.457 | 65.457 | 68.3674 | 20.5467 | 489012.101 | 40.751 | 40.751 | 106.208 | 0.3 | 76.67 | 21.67 | 819126 | 68.2605 | 68.2605 | 71.2402 | 23.4196 | 557386.2515 | 46.4489 | 46.4489 | 114.7094 | 0.4 | 77.56 | 22.56 | 852768 | 71.064 | 71.064 | 74.1131 | 26.2925 | 625760.402 | 52.1467 | 52.1467 | 123.2107 | 0.5 | 78.45 | 23.45 | 886410 | 73.8675 | 73.8675 | 76.9859 | 29.1653 | 694134.5525 | 57.8445 | 57.8445 | 131.712 | 0.6 | 79.34 | 24.34 | 920052 | 76.671 | 76.671 | 79.8588 | 32.0382 | 762508.703 | 63.5424 | 63.5424 | 140.2134 | 0.7 | 80.23 | 25.23 | 953694 | 79.4745 | 79.4745 | 82.7317 | 34.911 | 830882.8535 | 69.2402 | 69.2402 | 148.7147 | 0.8 | 81.12 | 26.12 | 987336 | 82.278 | 82.278 | 85.6045 | 37.7839 | 899257.004 | 74.9381 | 74.9381 | 157.2161 | 0.9 | 82.01 | 27.01 | 1020978 | 85.0815 | 85.0815 | 88.4774 | 40.6568 | 967631.1545 | 80.6359 | 80.6359 | 165.7174 | 1 | 82.9 | 27.9 | 1054620 | 87.885 | 87.885 | 91.3503 | 43.5296 | 1036005.305 | 86.3338 | 86.3338 | 174.2188 | 85 | 55 | 34.2368 | 34 | 54
8/4/20XX 2:00:00 PM | 0.58333 | 4 | 83.8 | 51.1 | 86.947 | 104.7705 | 17.8235 | 50 | 83.8 |  | 83.8 | 88.9075 | 0.1 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 65.2502 | 17.4296 | 414824.2684 | 34.5687 | 34.5687 | 97.5057 | 0.2 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 67.8788 | 20.0582 | 477384.7368 | 39.7821 | 39.7821 | 105.8061 | 0.3 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 70.5074 | 22.6868 | 539945.2052 | 44.9954 | 44.9954 | 114.1064 | 0.4 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 73.136 | 25.3154 | 602505.6736 | 50.2088 | 50.2088 | 122.4068 | 0.5 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 75.7646 | 27.944 | 665066.142 | 55.4222 | 55.4222 | 130.7072 | 0.6 | 79.88 | 24.88 | 940464 | 78.372 | 78.372 | 78.3932 | 30.5725 | 727626.6104 | 60.6356 | 60.6356 | 139.0076 | 0.7 | 80.86 | 25.86 | 977508 | 81.459 | 81.459 | 81.0218 | 33.2011 | 790187.0788 | 65.8489 | 65.8489 | 147.3079 | 0.8 | 81.84 | 26.84 | 1014552 | 84.546 | 84.546 | 83.6504 | 35.8297 | 852747.5472 | 71.0623 | 71.0623 | 155.6083 | 0.9 | 82.82 | 27.82 | 1051596 | 87.633 | 87.633 | 86.279 | 38.4583 | 915308.0156 | 76.2757 | 76.2757 | 163.9087 | 1 | 83.8 | 28.8 | 1088640 | 90.72 | 90.72 | 88.9075 | 41.0869 | 977868.484 | 81.489 | 81.489 | 172.209 | 85 | 50 | 34.0744 | 34 | 51.1
8/4/20XX 3:00:00 PM | 0.625 | 4 | 82.5 | 52.8 | 83.3313 | 100.4018 | 17.0705 | 50 | 82.5 |  | 82.5 | 88.1111 | 0.1 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 65.1706 | 17.3499 | 412928.6618 | 34.4107 | 34.4107 | 96.9382 | 0.2 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 67.7195 | 19.8989 | 473593.5237 | 39.4661 | 39.4661 | 104.6711 | 0.3 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 70.2685 | 22.4478 | 534258.3855 | 44.5215 | 44.5215 | 112.404 | 0.4 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 72.8174 | 24.9968 | 594923.2473 | 49.5769 | 49.5769 | 120.1369 | 0.5 | 78.25 | 23.25 | 878850 | 73.2375 | 73.2375 | 75.3664 | 27.5457 | 655588.1091 | 54.6323 | 54.6323 | 127.8698 | 0.6 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 77.9153 | 30.0947 | 716252.971 | 59.6877 | 59.6877 | 135.6027 | 0.7 | 79.95 | 24.95 | 943110 | 78.5925 | 78.5925 | 80.4642 | 32.6436 | 776917.8328 | 64.7432 | 64.7432 | 143.3357 | 0.8 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 83.0132 | 35.1926 | 837582.6946 | 69.7986 | 69.7986 | 151.0686 | 0.9 | 81.65 | 26.65 | 1007370 | 83.9475 | 83.9475 | 85.5621 | 37.7415 | 898247.5564 | 74.854 | 74.854 | 158.8015 | 1 | 82.5 | 27.5 | 1039500 | 86.625 | 86.625 | 88.1111 | 40.2904 | 958912.4183 | 79.9094 | 79.9094 | 166.5344 | 80 | 55 | 33.63 | 34 | 52.8
8/4/20XX 4:00:00 PM | 0.66667 | 4 | 82.3 | 54.7 | 82.7861 | 99.7431 | 16.957 | 50 | 82.3 |  | 82.3 | 90.7559 | 0.1 | 74.83 | 19.83 | 749574 | 62.4645 | 62.4645 | 65.4351 | 17.6144 | 419223.3922 | 34.9353 | 34.9353 | 97.3998 | 0.2 | 75.66 | 20.66 | 780948 | 65.079 | 65.079 | 68.2485 | 20.4279 | 486182.9843 | 40.5152 | 40.5152 | 105.5942 | 0.3 | 76.49 | 21.49 | 812322 | 67.6935 | 67.6935 | 71.0619 | 23.2413 | 553142.5765 | 46.0952 | 46.0952 | 113.7887 | 0.4 | 77.32 | 22.32 | 843696 | 70.308 | 70.308 | 73.8753 | 26.0547 | 620102.1687 | 51.6752 | 51.6752 | 121.9832 | 0.5 | 78.15 | 23.15 | 875070 | 72.9225 | 72.9225 | 76.6888 | 28.8681 | 687061.7608 | 57.2551 | 57.2551 | 130.1776 | 0.6 | 78.98 | 23.98 | 906444 | 75.537 | 75.537 | 79.5022 | 31.6816 | 754021.353 | 62.8351 | 62.8351 | 138.3721 | 0.7 | 79.81 | 24.81 | 937818 | 78.1515 | 78.1515 | 82.3156 | 34.495 | 820980.9452 | 68.4151 | 68.4151 | 146.5666 | 0.8 | 80.64 | 25.64 | 969192 | 80.766 | 80.766 | 85.1291 | 37.3084 | 887940.5373 | 73.995 | 73.995 | 154.761 | 0.9 | 81.47 | 26.47 | 1000566 | 83.3805 | 83.3805 | 87.9425 | 40.1219 | 954900.1295 | 79.575 | 79.575 | 162.9555 | 1 | 82.3 | 27.3 | 1031940 | 85.995 | 85.995 | 90.7559 | 42.9353 | 1021859.7217 | 85.155 | 85.155 | 171.15 | 80 | 55 | 33.996 | 34 | 54.7
8/4/20XX 5:00:00 PM | 0.70833 | 4 | 81.1 | 58 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 92.6072 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 65.6202 | 17.7996 | 423629.3701 | 35.3024 | 35.3024 | 97.3889 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 68.6187 | 20.7981 | 494994.9402 | 41.2496 | 41.2496 | 105.5726 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 71.6173 | 23.7967 | 566360.5103 | 47.1967 | 47.1967 | 113.7562 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 74.6158 | 26.7952 | 637726.0804 | 53.1438 | 53.1438 | 121.9398 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 77.6144 | 29.7938 | 709091.6504 | 59.091 | 59.091 | 130.1235 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 80.613 | 32.7923 | 780457.2205 | 65.0381 | 65.0381 | 138.3071 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 83.6115 | 35.7909 | 851822.7906 | 70.9852 | 70.9852 | 146.4907 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 86.6101 | 38.7894 | 923188.3607 | 76.9324 | 76.9324 | 154.6744 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 89.6086 | 41.788 | 994553.9308 | 82.8795 | 82.8795 | 162.858 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 92.6072 | 44.7865 | 1065919.5009 | 88.8266 | 88.8266 | 171.0416 | 80 | 60 | 33.9915 | 34 | 58
8/4/20XX 6:00:00 PM | 0.75 | 4 | 80.1 | 60.7 | 92.7289 | 108.5693 | 15.8405 | 60 | 80.1 |  | 80.1 | 93.8377 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 65.7432 | 17.9226 | 426558.0513 | 35.5465 | 35.5465 | 97.318 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 68.8648 | 21.0442 | 500852.3027 | 41.7377 | 41.7377 | 105.4307 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 71.9865 | 24.1658 | 575146.554 | 47.9289 | 47.9289 | 113.5434 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 75.1081 | 27.2874 | 649440.8053 | 54.1201 | 54.1201 | 121.6561 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 78.2297 | 30.409 | 723735.0566 | 60.3113 | 60.3113 | 129.7688 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 81.3513 | 33.5306 | 798029.308 | 66.5024 | 66.5024 | 137.8814 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 84.4729 | 36.6523 | 872323.5593 | 72.6936 | 72.6936 | 145.9941 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 87.5945 | 39.7739 | 946617.8106 | 78.8848 | 78.8848 | 154.1068 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 90.7161 | 42.8955 | 1020912.0619 | 85.076 | 85.076 | 162.2195 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 93.8377 | 46.0171 | 1095206.3133 | 91.2672 | 91.2672 | 170.3322 | 80 | 60 | 33.9386 | 34 | 60.7
8/4/20XX 7:00:00 PM | 0.79167 | 4 | 79 | 63.1 | 89.3778 | 104.6345 | 15.2568 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/4/20XX 8:00:00 PM | 0.83333 | 4 | 77.7 | 64.7 | 85.548 | 100.1379 | 14.59 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/4/20XX 9:00:00 PM | 0.875 | 4 | 77.5 | 65 | 84.9711 | 99.4607 | 14.4896 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/4/20XX 10:00:00 PM | 0.91667 | 4 | 76.6 | 67.9 | 82.4157 | 96.4605 | 14.0448 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/4/20XX 11:00:00 PM | 0.95833 | 4 | 76.1 | 69.3 | 81.0242 | 94.8268 | 13.8027 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/4/20XX 12:00:00 AM | 0 | 5 | 74.9 | 72.3 | 91.0012 | 104.3307 | 13.3295 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/5/20XX 1:00:00 AM | 0.041667 | 5 | 74.5 | 72.3 | 89.7555 | 102.8978 | 13.1423 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/5/20XX 2:00:00 AM | 0.083333 | 5 | 74.3 | 72.9 | 89.138 | 102.1877 | 13.0496 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/5/20XX 3:00:00 AM | 0.125 | 5 | 73.5 | 74.2 | 86.7045 | 99.389 | 12.6844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/5/20XX 4:00:00 AM | 0.16667 | 5 | 73.3 | 75.7 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/5/20XX 5:00:00 AM | 0.20833 | 5 | 72.4 | 79.6 | 83.4515 | 95.6486 | 12.1971 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/5/20XX 6:00:00 AM | 0.25 | 5 | 71.9 | 80.2 | 93.989 | 105.9847 | 11.9957 | 80 | 71.9 |  | 71.9 | 94.229 | 0.1 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 65.7824 | 17.9617 | 427489.2204 | 35.6241 | 35.6241 | 94.8126 | 0.2 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 68.9431 | 21.1225 | 502714.6407 | 41.8929 | 41.8929 | 100.4199 | 0.3 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 72.1038 | 24.2832 | 577940.0611 | 48.1617 | 48.1617 | 106.0272 | 0.4 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 75.2646 | 27.4439 | 653165.4814 | 54.4305 | 54.4305 | 111.6345 | 0.5 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 78.4253 | 30.6047 | 728390.9018 | 60.6992 | 60.6992 | 117.2417 | 0.6 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 81.586 | 33.7654 | 803616.3221 | 66.968 | 66.968 | 122.849 | 0.7 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 84.7468 | 36.9261 | 878841.7425 | 73.2368 | 73.2368 | 128.4563 | 0.8 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 87.9075 | 40.0869 | 954067.1629 | 79.5056 | 79.5056 | 134.0636 | 0.9 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 91.0682 | 43.2476 | 1029292.5832 | 85.7744 | 85.7744 | 139.6709 | 1 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 94.229 | 46.4083 | 1104518.0036 | 92.0432 | 92.0432 | 145.2782 | 70 | 80 | 31.9829 | 32 | 80.2
8/5/20XX 7:00:00 AM | 0.29167 | 5 | 73.6 | 76.2 | 87.0056 | 99.7352 | 12.7296 | 70 | 73.6 |  | 73.6 | 94.8979 | 0.1 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 65.8493 | 18.0286 | 429081.3733 | 35.7568 | 35.7568 | 95.4808 | 0.2 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 69.0769 | 21.2563 | 505898.9466 | 42.1582 | 42.1582 | 101.7562 | 0.3 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 72.3045 | 24.4839 | 582716.5198 | 48.5597 | 48.5597 | 108.0317 | 0.4 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 75.5321 | 27.7115 | 659534.0931 | 54.9612 | 54.9612 | 114.3072 | 0.5 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 78.7598 | 30.9391 | 736351.6664 | 61.3626 | 61.3626 | 120.5826 | 0.6 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 81.9874 | 34.1668 | 813169.2397 | 67.7641 | 67.7641 | 126.8581 | 0.7 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 85.215 | 37.3944 | 889986.813 | 74.1656 | 74.1656 | 133.1336 | 0.8 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 88.4427 | 40.622 | 966804.3862 | 80.567 | 80.567 | 139.409 | 0.9 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 91.6703 | 43.8497 | 1043621.9595 | 86.9685 | 86.9685 | 145.6845 | 1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 94.8979 | 47.0773 | 1120439.5328 | 93.37 | 93.37 | 151.96 | 75 | 75 | 32.5057 | 32 | 76.2
8/5/20XX 8:00:00 AM | 0.33333 | 5 | 75.2 | 71.9 | 91.9451 | 105.4166 | 13.4714 | 70 | 75.2 |  | 75.2 | 94.5047 | 0.1 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.8099 | 17.9893 | 428145.4847 | 35.6788 | 35.6788 | 95.9068 | 0.2 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 68.9982 | 21.1776 | 504027.1694 | 42.0023 | 42.0023 | 102.6083 | 0.3 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 72.1866 | 24.3659 | 579908.854 | 48.3257 | 48.3257 | 109.3097 | 0.4 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 75.3749 | 27.5542 | 655790.5387 | 54.6492 | 54.6492 | 116.0112 | 0.5 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 78.5632 | 30.7425 | 731672.2234 | 60.9727 | 60.9727 | 122.7127 | 0.6 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 81.7515 | 33.9308 | 807553.9081 | 67.2962 | 67.2962 | 129.4142 | 0.7 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 84.9398 | 37.1191 | 883435.5928 | 73.6196 | 73.6196 | 136.1156 | 0.8 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 88.1281 | 40.3074 | 959317.2775 | 79.9431 | 79.9431 | 142.8171 | 0.9 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 91.3164 | 43.4958 | 1035198.9621 | 86.2666 | 86.2666 | 149.5186 | 1 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 94.5047 | 46.6841 | 1111080.6468 | 92.5901 | 92.5901 | 156.2201 | 75 | 70 | 32.8378 | 32 | 71.9
8/5/20XX 9:00:00 AM | 0.375 | 5 | 77.4 | 66.8 | 84.6839 | 99.1235 | 14.4396 | 60 | 77.4 |  | 77.4 | 94.5028 | 0.1 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 65.8098 | 17.9891 | 428141.0955 | 35.6784 | 35.6784 | 96.5994 | 0.2 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 68.9979 | 21.1772 | 504018.3911 | 42.0015 | 42.0015 | 103.9935 | 0.3 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 72.186 | 24.3654 | 579895.6866 | 48.3246 | 48.3246 | 111.3876 | 0.4 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 75.3741 | 27.5535 | 655772.9822 | 54.6477 | 54.6477 | 118.7817 | 0.5 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 78.5622 | 30.7416 | 731650.2777 | 60.9709 | 60.9709 | 126.1759 | 0.6 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 81.7504 | 33.9297 | 807527.5733 | 67.294 | 67.294 | 133.57 | 0.7 | 76.38 | 21.38 | 808164 | 67.347 | 67.347 | 84.9385 | 37.1179 | 883404.8688 | 73.6171 | 73.6171 | 140.9641 | 0.8 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 88.1266 | 40.306 | 959282.1643 | 79.9402 | 79.9402 | 148.3582 | 0.9 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 91.3147 | 43.4941 | 1035159.4599 | 86.2633 | 86.2633 | 155.7523 | 1 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 94.5028 | 46.6822 | 1111036.7554 | 92.5864 | 92.5864 | 163.1464 | 75 | 65 | 33.3787 | 34 | 66.8
8/5/20XX 10:00:00 AM | 0.41667 | 5 | 79.8 | 59.7 | 76.2143 | 91.8048 | 15.5904 | 50 | 79.8 |  | 79.8 | 91.337 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 65.4932 | 17.6725 | 420606.4885 | 35.0505 | 35.0505 | 96.7275 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 68.3647 | 20.5441 | 488949.1771 | 40.7458 | 40.7458 | 104.2498 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 71.2363 | 23.4156 | 557291.8656 | 46.441 | 46.441 | 111.772 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 74.1078 | 26.2872 | 625634.5542 | 52.1362 | 52.1362 | 119.2942 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 76.9793 | 29.1587 | 693977.2427 | 57.8314 | 57.8314 | 126.8164 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 79.8509 | 32.0302 | 762319.9312 | 63.5267 | 63.5267 | 134.3387 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 82.7224 | 34.9018 | 830662.6198 | 69.2219 | 69.2219 | 141.8609 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 85.594 | 37.7733 | 899005.3083 | 74.9171 | 74.9171 | 149.3831 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 88.4655 | 40.6449 | 967347.9969 | 80.6123 | 80.6123 | 156.9053 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 91.337 | 43.5164 | 1035690.6854 | 86.3076 | 86.3076 | 164.4276 | 80 | 60 | 33.4727 | 34 | 59.7
8/5/20XX 11:00:00 AM | 0.45833 | 5 | 82.6 | 53.7 | 83.605 | 100.7325 | 17.1274 | 50 | 82.6 |  | 82.6 | 89.9422 | 0.1 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 65.3537 | 17.5331 | 417286.7315 | 34.7739 | 34.7739 | 97.3329 | 0.2 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 68.0857 | 20.2651 | 482309.6631 | 40.1925 | 40.1925 | 105.4605 | 0.3 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 70.8178 | 22.9972 | 547332.5946 | 45.611 | 45.611 | 113.588 | 0.4 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 73.5499 | 25.7292 | 612355.5262 | 51.0296 | 51.0296 | 121.7156 | 0.5 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 76.2819 | 28.4613 | 677378.4577 | 56.4482 | 56.4482 | 129.8432 | 0.6 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 79.014 | 31.1933 | 742401.3893 | 61.8668 | 61.8668 | 137.9708 | 0.7 | 80.02 | 25.02 | 945756 | 78.813 | 78.813 | 81.746 | 33.9254 | 807424.3208 | 67.2854 | 67.2854 | 146.0984 | 0.8 | 80.88 | 25.88 | 978264 | 81.522 | 81.522 | 84.4781 | 36.6574 | 872447.2524 | 72.7039 | 72.7039 | 154.2259 | 0.9 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 87.2101 | 39.3895 | 937470.1839 | 78.1225 | 78.1225 | 162.3535 | 1 | 82.6 | 27.6 | 1043280 | 86.94 | 86.94 | 89.9422 | 42.1216 | 1002493.1155 | 83.5411 | 83.5411 | 170.4811 | 85 | 55 | 33.942 | 34 | 53.7
8/5/20XX 12:00:00 PM | 0.5 | 5 | 83.8 | 51.7 | 86.947 | 104.7705 | 17.8235 | 50 | 83.8 |  | 83.8 | 89.977 | 0.1 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 65.3572 | 17.5365 | 417369.4641 | 34.7808 | 34.7808 | 97.7178 | 0.2 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 68.0927 | 20.2721 | 482475.1282 | 40.2063 | 40.2063 | 106.2303 | 0.3 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 70.8282 | 23.0076 | 547580.7923 | 45.6317 | 45.6317 | 114.7427 | 0.4 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 73.5638 | 25.7431 | 612686.4564 | 51.0572 | 51.0572 | 123.2552 | 0.5 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 76.2993 | 28.4787 | 677792.1205 | 56.4827 | 56.4827 | 131.7677 | 0.6 | 79.88 | 24.88 | 940464 | 78.372 | 78.372 | 79.0348 | 31.2142 | 742897.7846 | 61.9081 | 61.9081 | 140.2801 | 0.7 | 80.86 | 25.86 | 977508 | 81.459 | 81.459 | 81.7704 | 33.9497 | 808003.4487 | 67.3336 | 67.3336 | 148.7926 | 0.8 | 81.84 | 26.84 | 1014552 | 84.546 | 84.546 | 84.5059 | 36.6853 | 873109.1128 | 72.7591 | 72.7591 | 157.3051 | 0.9 | 82.82 | 27.82 | 1051596 | 87.633 | 87.633 | 87.2414 | 39.4208 | 938214.7769 | 78.1846 | 78.1846 | 165.8176 | 1 | 83.8 | 28.8 | 1088640 | 90.72 | 90.72 | 89.977 | 42.1563 | 1003320.441 | 83.61 | 83.61 | 174.33 | 85 | 50 | 34.2423 | 34 | 51.7
8/5/20XX 1:00:00 PM | 0.54167 | 5 | 84.3 | 49.5 | 70.3706 | 88.3711 | 18.0005 | 40 | 84.3 |  | 84.3 | 87.471 | 0.1 | 75.03 | 20.03 | 757134 | 63.0945 | 63.0945 | 65.1066 | 17.2859 | 411405.4047 | 34.2838 | 34.2838 | 97.3783 | 0.2 | 76.06 | 21.06 | 796068 | 66.339 | 66.339 | 67.5915 | 19.7709 | 470547.0094 | 39.2123 | 39.2123 | 105.5513 | 0.3 | 77.09 | 22.09 | 835002 | 69.5835 | 69.5835 | 70.0765 | 22.2558 | 529688.614 | 44.1407 | 44.1407 | 113.7242 | 0.4 | 78.12 | 23.12 | 873936 | 72.828 | 72.828 | 72.5614 | 24.7408 | 588830.2187 | 49.0692 | 49.0692 | 121.8972 | 0.5 | 79.15 | 24.15 | 912870 | 76.0725 | 76.0725 | 75.0463 | 27.2257 | 647971.8234 | 53.9977 | 53.9977 | 130.0702 | 0.6 | 80.18 | 25.18 | 951804 | 79.317 | 79.317 | 77.5313 | 29.7106 | 707113.4281 | 58.9261 | 58.9261 | 138.2431 | 0.7 | 81.21 | 26.21 | 990738 | 82.5615 | 82.5615 | 80.0162 | 32.1956 | 766255.0327 | 63.8546 | 63.8546 | 146.4161 | 0.8 | 82.24 | 27.24 | 1029672 | 85.806 | 85.806 | 82.5012 | 34.6805 | 825396.6374 | 68.7831 | 68.7831 | 154.5891 | 0.9 | 83.27 | 28.27 | 1068606 | 89.0505 | 89.0505 | 84.9861 | 37.1655 | 884538.2421 | 73.7115 | 73.7115 | 162.762 | 1 | 84.3 | 29.3 | 1107540 | 92.295 | 92.295 | 87.471 | 39.6504 | 943679.8468 | 78.64 | 78.64 | 170.935 | 85 | 50 | 33.9715 | 34 | 49.5
8/5/20XX 2:00:00 PM | 0.58333 | 5 | 84.4 | 48.5 | 70.5978 | 88.6581 | 18.0604 | 40 | 84.4 |  | 84.4 | 85.9491 | 0.1 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 64.9544 | 17.1337 | 407783.1544 | 33.9819 | 33.9819 | 97.1079 | 0.2 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 67.2871 | 19.4665 | 463302.5088 | 38.6085 | 38.6085 | 105.0105 | 0.3 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 69.6199 | 21.7992 | 518821.8633 | 43.2352 | 43.2352 | 112.9132 | 0.4 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 71.9526 | 24.132 | 574341.2177 | 47.8618 | 47.8618 | 120.8158 | 0.5 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 74.2854 | 26.4647 | 629860.5721 | 52.4884 | 52.4884 | 128.7184 | 0.6 | 80.24 | 25.24 | 954072 | 79.506 | 79.506 | 76.6181 | 28.7975 | 685379.9265 | 57.115 | 57.115 | 136.621 | 0.7 | 81.28 | 26.28 | 993384 | 82.782 | 82.782 | 78.9509 | 31.1302 | 740899.2809 | 61.7416 | 61.7416 | 144.5236 | 0.8 | 82.32 | 27.32 | 1032696 | 86.058 | 86.058 | 81.2836 | 33.463 | 796418.6353 | 66.3682 | 66.3682 | 152.4262 | 0.9 | 83.36 | 28.36 | 1072008 | 89.334 | 89.334 | 83.6163 | 35.7957 | 851937.9898 | 70.9948 | 70.9948 | 160.3288 | 1 | 84.4 | 29.4 | 1111320 | 92.61 | 92.61 | 85.9491 | 38.1285 | 907457.3442 | 75.6214 | 75.6214 | 168.2314 | 85 | 50 | 33.757 | 34 | 48.5
8/5/20XX 3:00:00 PM | 0.625 | 5 | 83.5 | 51.2 | 86.1015 | 103.7488 | 17.6473 | 50 | 83.5 |  | 83.5 | 88.2191 | 0.1 | 74.95 | 19.95 | 754110 | 62.8425 | 62.8425 | 65.1814 | 17.3608 | 413185.8908 | 34.4322 | 34.4322 | 97.2747 | 0.2 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 67.7411 | 19.9205 | 474107.9815 | 39.509 | 39.509 | 105.344 | 0.3 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 70.3009 | 22.4803 | 535030.0723 | 44.5858 | 44.5858 | 113.4133 | 0.4 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 72.8606 | 25.04 | 595952.1631 | 49.6627 | 49.6627 | 121.4827 | 0.5 | 78.75 | 23.75 | 897750 | 74.8125 | 74.8125 | 75.4204 | 27.5998 | 656874.2538 | 54.7395 | 54.7395 | 129.552 | 0.6 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 77.9801 | 30.1595 | 717796.3446 | 59.8164 | 59.8164 | 137.6214 | 0.7 | 80.65 | 25.65 | 969570 | 80.7975 | 80.7975 | 80.5399 | 32.7193 | 778718.4354 | 64.8932 | 64.8932 | 145.6907 | 0.8 | 81.6 | 26.6 | 1005480 | 83.79 | 83.79 | 83.0996 | 35.279 | 839640.5261 | 69.97 | 69.97 | 153.76 | 0.9 | 82.55 | 27.55 | 1041390 | 86.7825 | 86.7825 | 85.6594 | 37.8388 | 900562.6169 | 75.0469 | 75.0469 | 161.8294 | 1 | 83.5 | 28.5 | 1077300 | 89.775 | 89.775 | 88.2191 | 40.3985 | 961484.7077 | 80.1237 | 80.1237 | 169.8987 | 85 | 50 | 33.8926 | 34 | 51.2
8/5/20XX 4:00:00 PM | 0.66667 | 5 | 82.6 | 51.4 | 83.605 | 100.7325 | 17.1274 | 50 | 82.6 |  | 82.6 | 86.0029 | 0.1 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 64.9598 | 17.1391 | 407911.1751 | 33.9926 | 33.9926 | 96.5516 | 0.2 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 67.2979 | 19.4773 | 463558.5502 | 38.6299 | 38.6299 | 103.8979 | 0.3 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 69.636 | 21.8154 | 519205.9253 | 43.2672 | 43.2672 | 111.2442 | 0.4 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 71.9741 | 24.1535 | 574853.3004 | 47.9044 | 47.9044 | 118.5904 | 0.5 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 74.3123 | 26.4916 | 630500.6755 | 52.5417 | 52.5417 | 125.9367 | 0.6 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 76.6504 | 28.8298 | 686148.0507 | 57.179 | 57.179 | 133.283 | 0.7 | 80.02 | 25.02 | 945756 | 78.813 | 78.813 | 78.9885 | 31.1679 | 741795.4258 | 61.8163 | 61.8163 | 140.6293 | 0.8 | 80.88 | 25.88 | 978264 | 81.522 | 81.522 | 81.3266 | 33.506 | 797442.8009 | 66.4536 | 66.4536 | 147.9756 | 0.9 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 83.6648 | 35.8441 | 853090.176 | 71.0908 | 71.0908 | 155.3218 | 1 | 82.6 | 27.6 | 1043280 | 86.94 | 86.94 | 86.0029 | 38.1823 | 908737.5511 | 75.7281 | 75.7281 | 162.6681 | 85 | 50 | 33.3237 | 34 | 51.4
8/5/20XX 5:00:00 PM | 0.70833 | 5 | 81.8 | 53.2 | 81.4359 | 98.1119 | 16.676 | 50 | 81.8 |  | 81.8 | 86.7722 | 0.1 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 65.0367 | 17.2161 | 409742.1414 | 34.1452 | 34.1452 | 96.4522 | 0.2 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 67.4517 | 19.6311 | 467220.4828 | 38.935 | 38.935 | 103.699 | 0.3 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 69.8668 | 22.0462 | 524698.8242 | 43.7249 | 43.7249 | 110.9459 | 0.4 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 72.2819 | 24.4612 | 582177.1656 | 48.5148 | 48.5148 | 118.1928 | 0.5 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 74.6969 | 26.8763 | 639655.507 | 53.3046 | 53.3046 | 125.4396 | 0.6 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 77.112 | 29.2913 | 697133.8484 | 58.0945 | 58.0945 | 132.6865 | 0.7 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 79.527 | 31.7064 | 754612.1898 | 62.8843 | 62.8843 | 139.9333 | 0.8 | 80.24 | 25.24 | 954072 | 79.506 | 79.506 | 81.9421 | 34.1215 | 812090.5311 | 67.6742 | 67.6742 | 147.1802 | 0.9 | 81.02 | 26.02 | 983556 | 81.963 | 81.963 | 84.3571 | 36.5365 | 869568.8725 | 72.4641 | 72.4641 | 154.4271 | 1 | 81.8 | 26.8 | 1013040 | 84.42 | 84.42 | 86.7722 | 38.9516 | 927047.2139 | 77.2539 | 77.2539 | 161.6739 | 80 | 55 | 33.248 | 34 | 53.2
8/5/20XX 6:00:00 PM | 0.75 | 5 | 80.5 | 55.4 | 78.0095 | 93.973 | 15.9635 | 50 | 80.5 |  | 80.5 | 86.6298 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 65.0224 | 17.2018 | 409403.226 | 34.1169 | 34.1169 | 96.0144 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 67.4233 | 19.6026 | 466542.6519 | 38.8786 | 38.8786 | 102.8236 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 69.8241 | 22.0034 | 523682.0779 | 43.6402 | 43.6402 | 109.6327 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 72.2249 | 24.4043 | 580821.5038 | 48.4018 | 48.4018 | 116.4418 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 74.6257 | 26.8051 | 637960.9298 | 53.1634 | 53.1634 | 123.2509 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 77.0265 | 29.2059 | 695100.3557 | 57.925 | 57.925 | 130.06 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 79.4273 | 31.6067 | 752239.7817 | 62.6866 | 62.6866 | 136.8691 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 81.8282 | 34.0075 | 809379.2076 | 67.4483 | 67.4483 | 143.6783 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 84.229 | 36.4083 | 866518.6336 | 72.2099 | 72.2099 | 150.4874 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 86.6298 | 38.8092 | 923658.0595 | 76.9715 | 76.9715 | 157.2965 | 80 | 55 | 32.9065 | 32 | 55.4
8/5/20XX 7:00:00 PM | 0.79167 | 5 | 79.5 | 54.3 | 75.4555 | 90.8883 | 15.4328 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/5/20XX 8:00:00 PM | 0.83333 | 5 | 77.9 | 58.8 | 71.5134 | 86.1281 | 14.6147 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/5/20XX 9:00:00 PM | 0.875 | 5 | 77.2 | 60.7 | 84.112 | 98.452 | 14.34 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/5/20XX 10:00:00 PM | 0.91667 | 5 | 76.5 | 61.6 | 82.1358 | 96.1318 | 13.9961 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/5/20XX 11:00:00 PM | 0.95833 | 5 | 75.8 | 62.2 | 80.1988 | 93.8579 | 13.6591 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/5/20XX 12:00:00 AM | 0 | 6 | 75 | 63.9 | 78.0327 | 91.3149 | 13.2822 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/6/20XX 1:00:00 AM | 0.041667 | 6 | 74 | 67 | 75.3952 | 88.2187 | 12.8236 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/6/20XX 2:00:00 AM | 0.083333 | 6 | 73.1 | 68.2 | 73.0869 | 85.5092 | 12.4223 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/6/20XX 3:00:00 AM | 0.125 | 6 | 72.4 | 70 | 83.4515 | 95.6486 | 12.1971 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/6/20XX 4:00:00 AM | 0.16667 | 6 | 71.7 | 71.2 | 81.4366 | 93.3322 | 11.8956 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/6/20XX 5:00:00 AM | 0.20833 | 6 | 71.3 | 72.6 | 80.3042 | 92.0306 | 11.7264 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/6/20XX 6:00:00 AM | 0.25 | 6 | 71.5 | 73.3 | 80.8687 | 92.6795 | 11.8108 | 70 | 71.5 |  | 71.5 | 84.7662 | 0.1 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 64.8361 | 17.0155 | 404967.9816 | 33.7473 | 33.7473 | 92.8098 | 0.2 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 67.0506 | 19.2299 | 457672.1631 | 38.1393 | 38.1393 | 96.4143 | 0.3 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 69.265 | 21.4444 | 510376.3447 | 42.5314 | 42.5314 | 100.0189 | 0.4 | 73 | 18 | 680400 | 56.7 | 56.7 | 71.4795 | 23.6588 | 563080.5263 | 46.9234 | 46.9234 | 103.6234 | 0.5 | 72.75 | 17.75 | 670950 | 55.9125 | 55.9125 | 73.6939 | 25.8733 | 615784.7079 | 51.3154 | 51.3154 | 107.2279 | 0.6 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 75.9084 | 28.0878 | 668488.8894 | 55.7074 | 55.7074 | 110.8324 | 0.7 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 78.1229 | 30.3022 | 721193.071 | 60.0994 | 60.0994 | 114.4369 | 0.8 | 72 | 17 | 642600 | 53.55 | 53.55 | 80.3373 | 32.5167 | 773897.2526 | 64.4914 | 64.4914 | 118.0414 | 0.9 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 82.5518 | 34.7312 | 826601.4342 | 68.8835 | 68.8835 | 121.646 | 1 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 84.7662 | 36.9456 | 879305.6157 | 73.2755 | 73.2755 | 125.2505 | 70 | 75 | 30.4058 | 30 | 73.3
8/6/20XX 7:00:00 AM | 0.29167 | 6 | 72 | 73.3 | 82.2949 | 94.3189 | 12.024 | 70 | 72 |  | 72 | 86.2629 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.9858 | 17.1651 | 408529.8981 | 34.0442 | 34.0442 | 93.2642 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 67.3499 | 19.5292 | 464795.9962 | 38.733 | 38.733 | 97.323 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 69.714 | 21.8934 | 521062.0942 | 43.4218 | 43.4218 | 101.3818 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 72.0781 | 24.2575 | 577328.1923 | 48.1107 | 48.1107 | 105.4407 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 74.4422 | 26.6216 | 633594.2904 | 52.7995 | 52.7995 | 109.4995 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 76.8064 | 28.9857 | 689860.3885 | 57.4884 | 57.4884 | 113.5584 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 79.1705 | 31.3499 | 746126.4865 | 62.1772 | 62.1772 | 117.6172 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 81.5346 | 33.714 | 802392.5846 | 66.866 | 66.866 | 121.676 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 83.8987 | 36.0781 | 858658.6827 | 71.5549 | 71.5549 | 125.7349 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 86.2629 | 38.4422 | 914924.7808 | 76.2437 | 76.2437 | 129.7937 | 70 | 75 | 30.7624 | 30 | 73.3
8/6/20XX 8:00:00 AM | 0.33333 | 6 | 73.8 | 67.8 | 74.8769 | 87.6104 | 12.7335 | 60 | 73.8 |  | 73.8 | 84.809 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 64.8404 | 17.0197 | 405069.7163 | 33.7558 | 33.7558 | 93.5428 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 67.0591 | 19.2385 | 457875.6325 | 38.1563 | 38.1563 | 97.8803 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 69.2778 | 21.4572 | 510681.5488 | 42.5568 | 42.5568 | 102.2178 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 71.4966 | 23.6759 | 563487.4651 | 46.9573 | 46.9573 | 106.5553 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 73.7153 | 25.8947 | 616293.3814 | 51.3578 | 51.3578 | 110.8928 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 75.934 | 28.1134 | 669099.2976 | 55.7583 | 55.7583 | 115.2303 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 78.1528 | 30.3322 | 721905.2139 | 60.1588 | 60.1588 | 119.5678 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 80.3715 | 32.5509 | 774711.1302 | 64.5593 | 64.5593 | 123.9053 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 82.5903 | 34.7696 | 827517.0465 | 68.9598 | 68.9598 | 128.2428 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 84.809 | 36.9884 | 880322.9627 | 73.3602 | 73.3602 | 132.5802 | 75 | 70 | 30.9769 | 30 | 67.8
8/6/20XX 9:00:00 AM | 0.375 | 6 | 75.7 | 63.1 | 79.9253 | 93.5368 | 13.6115 | 60 | 75.7 |  | 75.7 | 84.1449 | 0.1 | 74.17 | 19.17 | 724626 | 60.3855 | 60.3855 | 64.774 | 16.9533 | 403489.0723 | 33.6241 | 33.6241 | 94.0096 | 0.2 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 66.9263 | 19.1056 | 454714.3447 | 37.8929 | 37.8929 | 98.8139 | 0.3 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 69.0786 | 21.258 | 505939.617 | 42.1616 | 42.1616 | 103.6181 | 0.4 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 71.2309 | 23.4103 | 557164.8894 | 46.4304 | 46.4304 | 108.4224 | 0.5 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 73.3832 | 25.5626 | 608390.1617 | 50.6992 | 50.6992 | 113.2267 | 0.6 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 75.5356 | 27.7149 | 659615.4341 | 54.968 | 54.968 | 118.031 | 0.7 | 75.19 | 20.19 | 763182 | 63.5985 | 63.5985 | 77.6879 | 29.8673 | 710840.7064 | 59.2367 | 59.2367 | 122.8352 | 0.8 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 79.8402 | 32.0196 | 762065.9788 | 63.5055 | 63.5055 | 127.6395 | 0.9 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 81.9925 | 34.1719 | 813291.2511 | 67.7743 | 67.7743 | 132.4438 | 1 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 84.1449 | 36.3242 | 864516.5234 | 72.043 | 72.043 | 137.248 | 75 | 65 | 31.3391 | 32 | 63.1
8/6/20XX 10:00:00 AM | 0.41667 | 6 | 77.6 | 58.2 | 70.7937 | 85.2591 | 14.4654 | 50 | 77.6 |  | 77.6 | 82.6554 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 64.625 | 16.8044 | 399944.0656 | 33.3287 | 33.3287 | 94.3127 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 66.6284 | 18.8077 | 447624.3312 | 37.302 | 37.302 | 99.42 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 68.6317 | 20.8111 | 495304.5968 | 41.2754 | 41.2754 | 104.5274 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 70.6351 | 22.8145 | 542984.8623 | 45.2487 | 45.2487 | 109.6347 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 72.6385 | 24.8179 | 590665.1279 | 49.2221 | 49.2221 | 114.7421 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 74.6419 | 26.8212 | 638345.3935 | 53.1954 | 53.1954 | 119.8494 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 76.6452 | 28.8246 | 686025.6591 | 57.1688 | 57.1688 | 124.9568 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 78.6486 | 30.828 | 733705.9247 | 61.1422 | 61.1422 | 130.0642 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 80.652 | 32.8314 | 781386.1903 | 65.1155 | 65.1155 | 135.1715 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 82.6554 | 34.8347 | 829066.4559 | 69.0889 | 69.0889 | 140.2789 | 80 | 60 | 31.572 | 32 | 58.2
8/6/20XX 11:00:00 AM | 0.45833 | 6 | 79.1 | 55.7 | 74.4534 | 89.6782 | 15.2248 | 50 | 79.1 |  | 79.1 | 83.1315 | 0.1 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 64.6726 | 16.852 | 401077.3592 | 33.4231 | 33.4231 | 94.8796 | 0.2 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 66.7236 | 18.903 | 449890.9185 | 37.4909 | 37.4909 | 100.5539 | 0.3 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 68.7746 | 20.954 | 498704.4777 | 41.5587 | 41.5587 | 106.2282 | 0.4 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 70.8256 | 23.005 | 547518.037 | 45.6265 | 45.6265 | 111.9025 | 0.5 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 72.8766 | 25.0559 | 596331.5962 | 49.6943 | 49.6943 | 117.5768 | 0.6 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 74.9276 | 27.1069 | 645145.1555 | 53.7621 | 53.7621 | 123.2511 | 0.7 | 77.57 | 22.57 | 853146 | 71.0955 | 71.0955 | 76.9786 | 29.1579 | 693958.7147 | 57.8299 | 57.8299 | 128.9254 | 0.8 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 79.0296 | 31.2089 | 742772.2739 | 61.8977 | 61.8977 | 134.5997 | 0.9 | 78.59 | 23.59 | 891702 | 74.3085 | 74.3085 | 81.0805 | 33.2599 | 791585.8332 | 65.9655 | 65.9655 | 140.274 | 1 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 83.1315 | 35.3109 | 840399.3924 | 70.0333 | 70.0333 | 145.9483 | 80 | 55 | 32.0145 | 32 | 55.7
8/6/20XX 12:00:00 PM | 0.5 | 6 | 80.4 | 52.3 | 77.751 | 93.6607 | 15.9097 | 50 | 80.4 |  | 80.4 | 81.4102 | 0.1 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 64.5005 | 16.6799 | 396980.5603 | 33.0817 | 33.0817 | 94.9477 | 0.2 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 66.3793 | 18.5587 | 441697.3207 | 36.8081 | 36.8081 | 100.6901 | 0.3 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 68.2582 | 20.4376 | 486414.081 | 40.5345 | 40.5345 | 106.4325 | 0.4 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 70.1371 | 22.3164 | 531130.8413 | 44.2609 | 44.2609 | 112.1749 | 0.5 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 72.0159 | 24.1953 | 575847.6017 | 47.9873 | 47.9873 | 117.9173 | 0.6 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 73.8948 | 26.0741 | 620564.362 | 51.7137 | 51.7137 | 123.6597 | 0.7 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 75.7736 | 27.953 | 665281.1223 | 55.4401 | 55.4401 | 129.4021 | 0.8 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 77.6525 | 29.8318 | 709997.8826 | 59.1665 | 59.1665 | 135.1445 | 0.9 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 79.5313 | 31.7107 | 754714.643 | 62.8929 | 62.8929 | 140.8869 | 1 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 81.4102 | 33.5896 | 799431.4033 | 66.6193 | 66.6193 | 146.6293 | 80 | 50 | 32.0634 | 32 | 52.3
8/6/20XX 1:00:00 PM | 0.54167 | 6 | 81.9 | 47.1 | 65.0926 | 81.7045 | 16.6119 | 40 | 81.9 |  | 81.9 | 76.887 | 0.1 | 74.79 | 19.79 | 748062 | 62.3385 | 62.3385 | 64.0482 | 16.2275 | 386215.4805 | 32.1846 | 32.1846 | 94.5231 | 0.2 | 75.58 | 20.58 | 777924 | 64.827 | 64.827 | 65.4747 | 17.6541 | 420167.161 | 35.0139 | 35.0139 | 99.8409 | 0.3 | 76.37 | 21.37 | 807786 | 67.3155 | 67.3155 | 66.9013 | 19.0806 | 454118.8415 | 37.8432 | 37.8432 | 105.1587 | 0.4 | 77.16 | 22.16 | 837648 | 69.804 | 69.804 | 68.3278 | 20.5072 | 488070.522 | 40.6725 | 40.6725 | 110.4765 | 0.5 | 77.95 | 22.95 | 867510 | 72.2925 | 72.2925 | 69.7543 | 21.9337 | 522022.2026 | 43.5019 | 43.5019 | 115.7944 | 0.6 | 78.74 | 23.74 | 897372 | 74.781 | 74.781 | 71.1809 | 23.3602 | 555973.8831 | 46.3312 | 46.3312 | 121.1122 | 0.7 | 79.53 | 24.53 | 927234 | 77.2695 | 77.2695 | 72.6074 | 24.7868 | 589925.5636 | 49.1605 | 49.1605 | 126.43 | 0.8 | 80.32 | 25.32 | 957096 | 79.758 | 79.758 | 74.034 | 26.2133 | 623877.2441 | 51.9898 | 51.9898 | 131.7478 | 0.9 | 81.11 | 26.11 | 986958 | 82.2465 | 82.2465 | 75.4605 | 27.6399 | 657828.9246 | 54.8191 | 54.8191 | 137.0656 | 1 | 81.9 | 26.9 | 1016820 | 84.735 | 84.735 | 76.887 | 29.0664 | 691780.6051 | 57.6484 | 57.6484 | 142.3834 | 80 | 45 | 31.7213 | 32 | 47.1
8/6/20XX 2:00:00 PM | 0.58333 | 6 | 81.7 | 46.6 | 64.6678 | 81.168 | 16.5002 | 40 | 81.7 |  | 81.7 | 75.5579 | 0.1 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 63.9153 | 16.0946 | 383052.1748 | 31.921 | 31.921 | 94.1965 | 0.2 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 65.2089 | 17.3883 | 413840.5496 | 34.4867 | 34.4867 | 99.1877 | 0.3 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 66.5025 | 18.6819 | 444628.9244 | 37.0524 | 37.0524 | 104.1789 | 0.4 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 67.7961 | 19.9755 | 475417.2993 | 39.6181 | 39.6181 | 109.1701 | 0.5 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 69.0898 | 21.2691 | 506205.6741 | 42.1838 | 42.1838 | 114.1613 | 0.6 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 70.3834 | 22.5628 | 536994.0489 | 44.7495 | 44.7495 | 119.1525 | 0.7 | 79.39 | 24.39 | 921942 | 76.8285 | 76.8285 | 71.677 | 23.8564 | 567782.4237 | 47.3152 | 47.3152 | 124.1437 | 0.8 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 72.9707 | 25.15 | 598570.7985 | 49.8809 | 49.8809 | 129.1349 | 0.9 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 74.2643 | 26.4437 | 629359.1733 | 52.4466 | 52.4466 | 134.1261 | 1 | 81.7 | 26.7 | 1009260 | 84.105 | 84.105 | 75.5579 | 27.7373 | 660147.5481 | 55.0123 | 55.0123 | 139.1173 | 80 | 45 | 31.4638 | 32 | 46.6
8/6/20XX 3:00:00 PM | 0.625 | 6 | 82.2 | 47.3 | 65.7342 | 82.5146 | 16.7804 | 40 | 82.2 |  | 82.2 | 77.9839 | 0.1 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 64.1579 | 16.3372 | 388826.0331 | 32.4022 | 32.4022 | 94.8352 | 0.2 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 65.6941 | 17.8735 | 425388.2663 | 35.449 | 35.449 | 100.465 | 0.3 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 67.2303 | 19.4097 | 461950.4994 | 38.4959 | 38.4959 | 106.0949 | 0.4 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 68.7665 | 20.9459 | 498512.7326 | 41.5427 | 41.5427 | 111.7247 | 0.5 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 70.3028 | 22.4821 | 535074.9657 | 44.5896 | 44.5896 | 117.3546 | 0.6 | 78.92 | 23.92 | 904176 | 75.348 | 75.348 | 71.839 | 24.0184 | 571637.1989 | 47.6364 | 47.6364 | 122.9844 | 0.7 | 79.74 | 24.74 | 935172 | 77.931 | 77.931 | 73.3752 | 25.5546 | 608199.432 | 50.6833 | 50.6833 | 128.6143 | 0.8 | 80.56 | 25.56 | 966168 | 80.514 | 80.514 | 74.9115 | 27.0908 | 644761.6652 | 53.7301 | 53.7301 | 134.2441 | 0.9 | 81.38 | 26.38 | 997164 | 83.097 | 83.097 | 76.4477 | 28.6271 | 681323.8983 | 56.777 | 56.777 | 139.874 | 1 | 82.2 | 27.2 | 1028160 | 85.68 | 85.68 | 77.9839 | 30.1633 | 717886.1315 | 59.8238 | 59.8238 | 145.5038 | 80 | 45 | 31.967 | 32 | 47.3
8/6/20XX 4:00:00 PM | 0.66667 | 6 | 80.8 | 49.2 | 62.7838 | 78.7895 | 16.0057 | 40 | 80.8 |  | 80.8 | 77.509 | 0.1 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 64.1104 | 16.2897 | 387695.8503 | 32.308 | 32.308 | 94.3 | 0.2 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 65.5991 | 17.7785 | 423127.9006 | 35.2607 | 35.2607 | 99.3947 | 0.3 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 67.0879 | 19.2672 | 458559.9509 | 38.2133 | 38.2133 | 104.4893 | 0.4 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 68.5766 | 20.756 | 493992.0012 | 41.166 | 41.166 | 109.584 | 0.5 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 70.0653 | 22.2447 | 529424.0514 | 44.1187 | 44.1187 | 114.6787 | 0.6 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 71.5541 | 23.7334 | 564856.1017 | 47.0713 | 47.0713 | 119.7733 | 0.7 | 78.76 | 23.76 | 898128 | 74.844 | 74.844 | 73.0428 | 25.2222 | 600288.152 | 50.024 | 50.024 | 124.868 | 0.8 | 79.44 | 24.44 | 923832 | 76.986 | 76.986 | 74.5316 | 26.7109 | 635720.2023 | 52.9767 | 52.9767 | 129.9627 | 0.9 | 80.12 | 25.12 | 949536 | 79.128 | 79.128 | 76.0203 | 28.1997 | 671152.2526 | 55.9294 | 55.9294 | 135.0574 | 1 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 77.509 | 29.6884 | 706584.3029 | 58.882 | 58.882 | 140.152 | 80 | 50 | 31.5495 | 32 | 49.2
8/6/20XX 5:00:00 PM | 0.70833 | 6 | 79.4 | 52.1 | 75.2039 | 90.5845 | 15.3806 | 50 | 79.4 |  | 79.4 | 78.4338 | 0.1 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 64.2029 | 16.3822 | 389896.8503 | 32.4914 | 32.4914 | 94.0424 | 0.2 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 65.7841 | 17.9634 | 427529.9006 | 35.6275 | 35.6275 | 98.8795 | 0.3 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 67.3653 | 19.5447 | 465162.9509 | 38.7636 | 38.7636 | 103.7166 | 0.4 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 68.9465 | 21.1259 | 502796.0013 | 41.8997 | 41.8997 | 108.5537 | 0.5 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 70.5277 | 22.7071 | 540429.0516 | 45.0358 | 45.0358 | 113.3908 | 0.6 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 72.109 | 24.2883 | 578062.1019 | 48.1718 | 48.1718 | 118.2278 | 0.7 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 73.6902 | 25.8695 | 615695.1522 | 51.3079 | 51.3079 | 123.0649 | 0.8 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 75.2714 | 27.4508 | 653328.2025 | 54.444 | 54.444 | 127.902 | 0.9 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 76.8526 | 29.032 | 690961.2528 | 57.5801 | 57.5801 | 132.7391 | 1 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 78.4338 | 30.6132 | 728594.3032 | 60.7162 | 60.7162 | 137.5762 | 80 | 50 | 31.3516 | 32 | 52.1
8/6/20XX 6:00:00 PM | 0.75 | 6 | 78.4 | 53.4 | 72.7264 | 87.5927 | 14.8663 | 50 | 78.4 |  | 78.4 | 77.781 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 64.1376 | 16.3169 | 388343.0215 | 32.3619 | 32.3619 | 93.5979 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 65.6535 | 17.8329 | 424422.243 | 35.3685 | 35.3685 | 97.9905 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 67.1694 | 19.3488 | 460501.4645 | 38.3751 | 38.3751 | 102.3831 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 68.6854 | 20.8647 | 496580.686 | 41.3817 | 41.3817 | 106.7757 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 70.2013 | 22.3807 | 532659.9076 | 44.3883 | 44.3883 | 111.1683 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 71.7172 | 23.8966 | 568739.1291 | 47.3949 | 47.3949 | 115.5609 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 73.2332 | 25.4125 | 604818.3506 | 50.4015 | 50.4015 | 119.9535 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 74.7491 | 26.9285 | 640897.5721 | 53.4081 | 53.4081 | 124.3461 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 76.265 | 28.4444 | 676976.7936 | 56.4147 | 56.4147 | 128.7387 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 77.781 | 29.9603 | 713056.0151 | 59.4213 | 59.4213 | 133.1313 | 80 | 55 | 31.0043 | 32 | 53.4
8/6/20XX 7:00:00 PM | 0.79167 | 6 | 77.1 | 55.8 | 69.6077 | 83.8273 | 14.2196 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/6/20XX 8:00:00 PM | 0.83333 | 6 | 75.8 | 58.5 | 66.6019 | 80.1988 | 13.5969 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/6/20XX 9:00:00 PM | 0.875 | 6 | 75.3 | 58.5 | 65.4753 | 78.8391 | 13.3637 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/6/20XX 10:00:00 PM | 0.91667 | 6 | 75 | 56.7 | 64.8072 | 78.0327 | 13.2255 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/6/20XX 11:00:00 PM | 0.95833 | 6 | 73.9 | 59.2 | 62.4066 | 75.1356 | 12.7291 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/6/20XX 12:00:00 AM | 0 | 7 | 73.5 | 59.7 | 61.5526 | 74.1052 | 12.5526 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/7/20XX 1:00:00 AM | 0.041667 | 7 | 72.3 | 63.9 | 71.0864 | 83.1611 | 12.0747 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/7/20XX 2:00:00 AM | 0.083333 | 7 | 71.6 | 65.2 | 69.3749 | 81.1522 | 11.7773 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/7/20XX 3:00:00 AM | 0.125 | 7 | 71.1 | 66.2 | 68.1744 | 79.7432 | 11.5688 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/7/20XX 4:00:00 AM | 0.16667 | 7 | 70.3 | 67.9 | 66.2911 | 77.5329 | 11.2418 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/7/20XX 5:00:00 AM | 0.20833 | 7 | 70.1 | 68.2 | 65.8275 | 76.9888 | 11.1613 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/7/20XX 6:00:00 AM | 0.25 | 7 | 70.3 | 68.4 | 66.2911 | 77.5329 | 11.2418 | 60 | 70.3 |  | 70.3 | 75.7342 | 0.1 | 73.63 | 18.63 | 704214 | 58.6845 | 58.6845 | 63.9329 | 16.1123 | 383471.7666 | 31.956 | 31.956 | 90.6405 | 0.2 | 73.26 | 18.26 | 690228 | 57.519 | 57.519 | 65.2442 | 17.4235 | 414679.7331 | 34.5566 | 34.5566 | 92.0756 | 0.3 | 72.89 | 17.89 | 676242 | 56.3535 | 56.3535 | 66.5554 | 18.7348 | 445887.6997 | 37.1573 | 37.1573 | 93.5108 | 0.4 | 72.52 | 17.52 | 662256 | 55.188 | 55.188 | 67.8667 | 20.046 | 477095.6662 | 39.758 | 39.758 | 94.946 | 0.5 | 72.15 | 17.15 | 648270 | 54.0225 | 54.0225 | 69.1779 | 21.3573 | 508303.6328 | 42.3586 | 42.3586 | 96.3811 | 0.6 | 71.78 | 16.78 | 634284 | 52.857 | 52.857 | 70.4892 | 22.6686 | 539511.5994 | 44.9593 | 44.9593 | 97.8163 | 0.7 | 71.41 | 16.41 | 620298 | 51.6915 | 51.6915 | 71.8004 | 23.9798 | 570719.5659 | 47.56 | 47.56 | 99.2515 | 0.8 | 71.04 | 16.04 | 606312 | 50.526 | 50.526 | 73.1117 | 25.2911 | 601927.5325 | 50.1606 | 50.1606 | 100.6866 | 0.9 | 70.67 | 15.67 | 592326 | 49.3605 | 49.3605 | 74.423 | 26.6023 | 633135.499 | 52.7613 | 52.7613 | 102.1218 | 1 | 70.3 | 15.3 | 578340 | 48.195 | 48.195 | 75.7342 | 27.9136 | 664343.4656 | 55.362 | 55.362 | 103.557 | 70 | 70 | 28.7007 | 28 | 68.4
8/7/20XX 7:00:00 AM | 0.29167 | 7 | 71.5 | 66.2 | 69.1333 | 80.8687 | 11.7354 | 60 | 71.5 |  | 71.5 | 76.4093 | 0.1 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 64.0004 | 16.1798 | 385078.3597 | 32.0899 | 32.0899 | 91.1524 | 0.2 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 65.3792 | 17.5585 | 417892.9194 | 34.8244 | 34.8244 | 93.0994 | 0.3 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 66.7579 | 18.9373 | 450707.4791 | 37.559 | 37.559 | 95.0465 | 0.4 | 73 | 18 | 680400 | 56.7 | 56.7 | 68.1367 | 20.3161 | 483522.0389 | 40.2935 | 40.2935 | 96.9935 | 0.5 | 72.75 | 17.75 | 670950 | 55.9125 | 55.9125 | 69.5154 | 21.6948 | 516336.5986 | 43.028 | 43.028 | 98.9405 | 0.6 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 70.8942 | 23.0736 | 549151.1583 | 45.7626 | 45.7626 | 100.8876 | 0.7 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 72.273 | 24.4523 | 581965.718 | 48.4971 | 48.4971 | 102.8346 | 0.8 | 72 | 17 | 642600 | 53.55 | 53.55 | 73.6517 | 25.8311 | 614780.2777 | 51.2317 | 51.2317 | 104.7817 | 0.9 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 75.0305 | 27.2099 | 647594.8374 | 53.9662 | 53.9662 | 106.7287 | 1 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 76.4093 | 28.5886 | 680409.3971 | 56.7008 | 56.7008 | 108.6758 | 70 | 65 | 29.0999 | 30 | 66.2
8/7/20XX 8:00:00 AM | 0.33333 | 7 | 72.8 | 65.2 | 72.3311 | 84.6221 | 12.291 | 60 | 72.8 |  | 72.8 | 78.7224 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 64.2317 | 16.4111 | 390583.6604 | 32.5486 | 32.5486 | 92.0206 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 65.8418 | 18.0212 | 428903.5208 | 35.742 | 35.742 | 94.836 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 67.4519 | 19.6312 | 467223.3813 | 38.9353 | 38.9353 | 97.6513 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 69.0619 | 21.2413 | 505543.2417 | 42.1286 | 42.1286 | 100.4666 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 70.672 | 22.8514 | 543863.1021 | 45.3219 | 45.3219 | 103.2819 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 72.2821 | 24.4615 | 582182.9625 | 48.5152 | 48.5152 | 106.0972 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 73.8922 | 26.0715 | 620502.8229 | 51.7086 | 51.7086 | 108.9126 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 75.5023 | 27.6816 | 658822.6834 | 54.9019 | 54.9019 | 111.7279 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 77.1123 | 29.2917 | 697142.5438 | 58.0952 | 58.0952 | 114.5432 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 78.7224 | 30.9018 | 735462.4042 | 61.2885 | 61.2885 | 117.3585 | 75 | 65 | 29.7799 | 30 | 65.2
8/7/20XX 9:00:00 AM | 0.375 | 7 | 74.2 | 65.3 | 75.9165 | 88.8307 | 12.9142 | 60 | 74.2 |  | 74.2 | 82.761 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 64.6356 | 16.8149 | 400195.5436 | 33.3496 | 33.3496 | 93.2626 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 66.6495 | 18.8289 | 448127.2872 | 37.3439 | 37.3439 | 97.3199 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 68.6634 | 20.8428 | 496059.0308 | 41.3383 | 41.3383 | 101.3773 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 70.6774 | 22.8568 | 543990.7744 | 45.3326 | 45.3326 | 105.4346 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 72.6913 | 24.8707 | 591922.518 | 49.3269 | 49.3269 | 109.4919 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 74.7053 | 26.8846 | 639854.2616 | 53.3212 | 53.3212 | 113.5492 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 76.7192 | 28.8986 | 687786.0053 | 57.3155 | 57.3155 | 117.6065 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 78.7331 | 30.9125 | 735717.7489 | 61.3098 | 61.3098 | 121.6638 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 80.7471 | 32.9264 | 783649.4925 | 65.3041 | 65.3041 | 125.7211 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 82.761 | 34.9404 | 831581.2361 | 69.2984 | 69.2984 | 129.7784 | 75 | 65 | 30.7546 | 30 | 65.3
8/7/20XX 10:00:00 AM | 0.41667 | 7 | 76.4 | 60.4 | 81.8567 | 95.8042 | 13.9475 | 60 | 76.4 |  | 76.4 | 82.4146 | 0.1 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 64.6009 | 16.7803 | 399370.9821 | 33.2809 | 33.2809 | 93.8869 | 0.2 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 66.5802 | 18.7596 | 446478.1642 | 37.2065 | 37.2065 | 98.5685 | 0.3 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 68.5595 | 20.7389 | 493585.3463 | 41.1321 | 41.1321 | 103.2501 | 0.4 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 70.5388 | 22.7182 | 540692.5283 | 45.0577 | 45.0577 | 107.9317 | 0.5 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 72.5181 | 24.6975 | 587799.7104 | 48.9833 | 48.9833 | 112.6133 | 0.6 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 74.4974 | 26.6768 | 634906.8925 | 52.9089 | 52.9089 | 117.2949 | 0.7 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 76.4767 | 28.6561 | 682014.0746 | 56.8345 | 56.8345 | 121.9765 | 0.8 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 78.456 | 30.6353 | 729121.2567 | 60.7601 | 60.7601 | 126.6581 | 0.9 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 80.4353 | 32.6146 | 776228.4388 | 64.6857 | 64.6857 | 131.3397 | 1 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 82.4146 | 34.5939 | 823335.6209 | 68.6113 | 68.6113 | 136.0213 | 75 | 60 | 31.24 | 32 | 60.4
8/7/20XX 11:00:00 AM | 0.45833 | 7 | 79.2 | 53.2 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 79.5914 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 64.3186 | 16.498 | 392651.8176 | 32.721 | 32.721 | 94.209 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 66.0156 | 18.195 | 433039.8352 | 36.0867 | 36.0867 | 99.2127 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 67.7126 | 19.8919 | 473427.8529 | 39.4523 | 39.4523 | 104.2163 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 69.4095 | 21.5889 | 513815.8705 | 42.818 | 42.818 | 109.22 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 71.1065 | 23.2859 | 554203.8881 | 46.1837 | 46.1837 | 114.2237 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 72.8035 | 24.9829 | 594591.9057 | 49.5493 | 49.5493 | 119.2273 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 74.5005 | 26.6798 | 634979.9234 | 52.915 | 52.915 | 124.231 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 76.1974 | 28.3768 | 675367.941 | 56.2807 | 56.2807 | 129.2347 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 77.8944 | 30.0738 | 715755.9586 | 59.6463 | 59.6463 | 134.2383 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 79.5914 | 31.7708 | 756143.9762 | 63.012 | 63.012 | 139.242 | 80 | 55 | 31.4841 | 32 | 53.2
8/7/20XX 12:00:00 PM | 0.5 | 7 | 80.4 | 52.1 | 77.751 | 93.6607 | 15.9097 | 50 | 80.4 |  | 80.4 | 81.092 | 0.1 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 64.4687 | 16.648 | 396223.2576 | 33.0186 | 33.0186 | 94.8846 | 0.2 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 66.3157 | 18.4951 | 440182.7153 | 36.6819 | 36.6819 | 100.5639 | 0.3 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 68.1627 | 20.3421 | 484142.1729 | 40.3452 | 40.3452 | 106.2432 | 0.4 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 70.0098 | 22.1891 | 528101.6305 | 44.0085 | 44.0085 | 111.9225 | 0.5 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 71.8568 | 24.0362 | 572061.0882 | 47.6718 | 47.6718 | 117.6018 | 0.6 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 73.7038 | 25.8832 | 616020.5458 | 51.335 | 51.335 | 123.281 | 0.7 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 75.5509 | 27.7303 | 659980.0034 | 54.9983 | 54.9983 | 128.9603 | 0.8 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 77.3979 | 29.5773 | 703939.4611 | 58.6616 | 58.6616 | 134.6396 | 0.9 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 79.245 | 31.4243 | 747898.9187 | 62.3249 | 62.3249 | 140.3189 | 1 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 81.092 | 33.2714 | 791858.3763 | 65.9882 | 65.9882 | 145.9982 | 80 | 50 | 32.0135 | 32 | 52.1
8/7/20XX 1:00:00 PM | 0.54167 | 7 | 81.5 | 49.8 | 64.2452 | 80.6344 | 16.3893 | 40 | 81.5 |  | 81.5 | 80.3066 | 0.1 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 64.3901 | 16.5695 | 394354.1119 | 32.8628 | 32.8628 | 95.0753 | 0.2 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 66.1586 | 18.338 | 436444.4239 | 36.3704 | 36.3704 | 100.9454 | 0.3 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 67.9271 | 20.1065 | 478534.7358 | 39.8779 | 39.8779 | 106.8154 | 0.4 | 77 | 22 | 831600 | 69.3 | 69.3 | 69.6956 | 21.875 | 520625.0477 | 43.3854 | 43.3854 | 112.6854 | 0.5 | 77.75 | 22.75 | 859950 | 71.6625 | 71.6625 | 71.4641 | 23.6435 | 562715.3596 | 46.8929 | 46.8929 | 118.5554 | 0.6 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 73.2326 | 25.412 | 604805.6716 | 50.4005 | 50.4005 | 124.4255 | 0.7 | 79.25 | 24.25 | 916650 | 76.3875 | 76.3875 | 75.0011 | 27.1805 | 646895.9835 | 53.908 | 53.908 | 130.2955 | 0.8 | 80 | 25 | 945000 | 78.75 | 78.75 | 76.7696 | 28.949 | 688986.2954 | 57.4155 | 57.4155 | 136.1655 | 0.9 | 80.75 | 25.75 | 973350 | 81.1125 | 81.1125 | 78.5381 | 30.7175 | 731076.6074 | 60.9231 | 60.9231 | 142.0356 | 1 | 81.5 | 26.5 | 1001700 | 83.475 | 83.475 | 80.3066 | 32.486 | 773166.9193 | 64.4306 | 64.4306 | 147.9056 | 80 | 50 | 32.1599 | 32 | 49.8
8/7/20XX 2:00:00 PM | 0.58333 | 7 | 81.6 | 50.1 | 80.9009 | 97.4655 | 16.5647 | 50 | 81.6 |  | 81.6 | 81.0665 | 0.1 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 64.4661 | 16.6455 | 396162.5866 | 33.0135 | 33.0135 | 95.2575 | 0.2 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 66.3106 | 18.49 | 440061.3733 | 36.6718 | 36.6718 | 101.3098 | 0.3 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 68.1551 | 20.3345 | 483960.1599 | 40.33 | 40.33 | 107.362 | 0.4 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 69.9996 | 22.1789 | 527858.9466 | 43.9882 | 43.9882 | 113.4142 | 0.5 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 71.8441 | 24.0234 | 571757.7332 | 47.6465 | 47.6465 | 119.4665 | 0.6 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 73.6886 | 25.8679 | 615656.5199 | 51.3047 | 51.3047 | 125.5187 | 0.7 | 79.32 | 24.32 | 919296 | 76.608 | 76.608 | 75.533 | 27.7124 | 659555.3065 | 54.9629 | 54.9629 | 131.5709 | 0.8 | 80.08 | 25.08 | 948024 | 79.002 | 79.002 | 77.3775 | 29.5569 | 703454.0932 | 58.6212 | 58.6212 | 137.6232 | 0.9 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 79.222 | 31.4014 | 747352.8798 | 62.2794 | 62.2794 | 143.6754 | 1 | 81.6 | 26.6 | 1005480 | 83.79 | 83.79 | 81.0665 | 33.2459 | 791251.6665 | 65.9376 | 65.9376 | 149.7276 | 80 | 50 | 32.3037 | 32 | 50.1
8/7/20XX 3:00:00 PM | 0.625 | 7 | 80.7 | 51.1 | 78.5288 | 94.6002 | 16.0714 | 50 | 80.7 |  | 80.7 | 80.2967 | 0.1 | 74.67 | 19.67 | 743526 | 61.9605 | 61.9605 | 64.3891 | 16.5685 | 394330.3502 | 32.8609 | 32.8609 | 94.8214 | 0.2 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 66.1566 | 18.336 | 436396.9003 | 36.3664 | 36.3664 | 100.4374 | 0.3 | 76.01 | 21.01 | 794178 | 66.1815 | 66.1815 | 67.9241 | 20.1035 | 478463.4505 | 39.872 | 39.872 | 106.0535 | 0.4 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 69.6916 | 21.871 | 520530.0006 | 43.3775 | 43.3775 | 111.6695 | 0.5 | 77.35 | 22.35 | 844830 | 70.4025 | 70.4025 | 71.4591 | 23.6385 | 562596.5508 | 46.883 | 46.883 | 117.2855 | 0.6 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 73.2266 | 25.406 | 604663.101 | 50.3886 | 50.3886 | 122.9016 | 0.7 | 78.69 | 23.69 | 895482 | 74.6235 | 74.6235 | 74.9941 | 27.1735 | 646729.6511 | 53.8941 | 53.8941 | 128.5176 | 0.8 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 76.7616 | 28.941 | 688796.2013 | 57.3997 | 57.3997 | 134.1337 | 0.9 | 80.03 | 25.03 | 946134 | 78.8445 | 78.8445 | 78.5292 | 30.7085 | 730862.7514 | 60.9052 | 60.9052 | 139.7497 | 1 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 80.2967 | 32.476 | 772929.3016 | 64.4108 | 64.4108 | 145.3658 | 80 | 50 | 31.9623 | 32 | 51.1
8/7/20XX 4:00:00 PM | 0.66667 | 7 | 80.3 | 51.6 | 77.4931 | 93.3492 | 15.8561 | 50 | 80.3 |  | 80.3 | 80.0301 | 0.1 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 64.3625 | 16.5418 | 393695.8712 | 32.808 | 32.808 | 94.6425 | 0.2 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 66.1033 | 18.2827 | 435127.9424 | 36.2607 | 36.2607 | 100.0797 | 0.3 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 67.8442 | 20.0235 | 476560.0136 | 39.7133 | 39.7133 | 105.5168 | 0.4 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 69.585 | 21.7644 | 517992.0848 | 43.166 | 43.166 | 110.954 | 0.5 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 71.3258 | 23.5052 | 559424.156 | 46.6187 | 46.6187 | 116.3912 | 0.6 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 73.0667 | 25.2461 | 600856.2272 | 50.0714 | 50.0714 | 121.8284 | 0.7 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 74.8075 | 26.9869 | 642288.2984 | 53.524 | 53.524 | 127.2655 | 0.8 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 76.5484 | 28.7277 | 683720.3696 | 56.9767 | 56.9767 | 132.7027 | 0.9 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 78.2892 | 30.4686 | 725152.4408 | 60.4294 | 60.4294 | 138.1399 | 1 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 80.0301 | 32.2094 | 766584.512 | 63.882 | 63.882 | 143.577 | 80 | 50 | 31.8224 | 32 | 51.6
8/7/20XX 5:00:00 PM | 0.70833 | 7 | 79.2 | 54.4 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 81.4246 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 64.5019 | 16.6813 | 397014.8016 | 33.0846 | 33.0846 | 94.5726 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 66.3822 | 18.5616 | 441765.8032 | 36.8138 | 36.8138 | 99.9398 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 68.2625 | 20.4419 | 486516.8048 | 40.5431 | 40.5431 | 105.3071 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 70.1428 | 22.3222 | 531267.8063 | 44.2723 | 44.2723 | 110.6743 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 72.0231 | 24.2025 | 576018.8079 | 48.0016 | 48.0016 | 116.0416 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 73.9034 | 26.0828 | 620769.8095 | 51.7308 | 51.7308 | 121.4088 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 75.7837 | 27.9631 | 665520.8111 | 55.4601 | 55.4601 | 126.7761 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 77.664 | 29.8434 | 710271.8127 | 59.1893 | 59.1893 | 132.1433 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 79.5443 | 31.7236 | 755022.8143 | 62.9186 | 62.9186 | 137.5106 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 81.4246 | 33.6039 | 799773.8159 | 66.6478 | 66.6478 | 142.8778 | 80 | 55 | 31.7714 | 32 | 54.4
8/7/20XX 6:00:00 PM | 0.75 | 7 | 78.3 | 58 | 72.4824 | 87.2982 | 14.8157 | 50 | 78.3 |  | 78.3 | 84.335 | 0.1 | 74.43 | 19.43 | 734454 | 61.2045 | 61.2045 | 64.793 | 16.9723 | 403941.6439 | 33.6618 | 33.6618 | 94.8663 | 0.2 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 66.9643 | 19.1437 | 455619.4878 | 37.9683 | 37.9683 | 100.5273 | 0.3 | 75.29 | 20.29 | 766962 | 63.9135 | 63.9135 | 69.1356 | 21.315 | 507297.3317 | 42.2748 | 42.2748 | 106.1883 | 0.4 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 71.307 | 23.4864 | 558975.1755 | 46.5813 | 46.5813 | 111.8493 | 0.5 | 76.15 | 21.15 | 799470 | 66.6225 | 66.6225 | 73.4783 | 25.6577 | 610653.0194 | 50.8878 | 50.8878 | 117.5103 | 0.6 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 75.6497 | 27.829 | 662330.8633 | 55.1942 | 55.1942 | 123.1712 | 0.7 | 77.01 | 22.01 | 831978 | 69.3315 | 69.3315 | 77.821 | 30.0004 | 714008.7072 | 59.5007 | 59.5007 | 128.8322 | 0.8 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 79.9923 | 32.1717 | 765686.5511 | 63.8072 | 63.8072 | 134.4932 | 0.9 | 77.87 | 22.87 | 864486 | 72.0405 | 72.0405 | 82.1637 | 34.343 | 817364.395 | 68.1137 | 68.1137 | 140.1542 | 1 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 84.335 | 36.5144 | 869042.2389 | 72.4202 | 72.4202 | 145.8152 | 80 | 60 | 32.0068 | 32 | 58
8/7/20XX 7:00:00 PM | 0.79167 | 7 | 76.7 | 59.8 | 68.6709 | 82.6964 | 14.0254 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/7/20XX 8:00:00 PM | 0.83333 | 7 | 75.5 | 64 | 79.3806 | 92.8973 | 13.5167 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/7/20XX 9:00:00 PM | 0.875 | 7 | 73.8 | 67.1 | 74.8769 | 87.6104 | 12.7335 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/7/20XX 10:00:00 PM | 0.91667 | 7 | 73.6 | 67.5 | 74.3617 | 87.0056 | 12.6439 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/7/20XX 11:00:00 PM | 0.95833 | 7 | 73.2 | 68.3 | 73.3404 | 85.8067 | 12.4664 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/7/20XX 12:00:00 AM | 0 | 1 | 72.7 | 70.1 | 84.3281 | 96.6564 | 12.3283 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/8/20XX 1:00:00 AM | 0.041667 | 1 | 72.4 | 69.8 | 71.3339 | 83.4515 | 12.1177 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/8/20XX 2:00:00 AM | 0.083333 | 1 | 71.8 | 72.3 | 81.7218 | 93.6601 | 11.9383 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/8/20XX 3:00:00 AM | 0.125 | 1 | 70.7 | 75.8 | 78.6313 | 90.1079 | 11.4766 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/8/20XX 4:00:00 AM | 0.16667 | 1 | 70.5 | 78.1 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/8/20XX 5:00:00 AM | 0.20833 | 1 | 70.1 | 77.9 | 76.9888 | 88.2203 | 11.2316 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/8/20XX 6:00:00 AM | 0.25 | 1 | 70.8 | 76.8 | 78.908 | 90.4259 | 11.5179 | 70 | 70.8 |  | 70.8 | 86.7402 | 0.1 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 65.0335 | 17.2129 | 409665.8776 | 34.1388 | 34.1388 | 92.9808 | 0.2 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 67.4453 | 19.6247 | 467067.9553 | 38.9223 | 38.9223 | 96.7563 | 0.3 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 69.8572 | 22.0366 | 524470.0329 | 43.7058 | 43.7058 | 100.5318 | 0.4 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 72.269 | 24.4484 | 581872.1105 | 48.4893 | 48.4893 | 104.3073 | 0.5 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 74.6809 | 26.8603 | 639274.1881 | 53.2728 | 53.2728 | 108.0828 | 0.6 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 77.0927 | 29.2721 | 696676.2658 | 58.0564 | 58.0564 | 111.8584 | 0.7 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 79.5046 | 31.684 | 754078.3434 | 62.8399 | 62.8399 | 115.6339 | 0.8 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 81.9164 | 34.0958 | 811480.421 | 67.6234 | 67.6234 | 119.4094 | 0.9 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 84.3283 | 36.5077 | 868882.4986 | 72.4069 | 72.4069 | 123.1849 | 1 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 86.7402 | 38.9195 | 926284.5763 | 77.1904 | 77.1904 | 126.9604 | 70 | 75 | 30.5424 | 30 | 76.8
8/8/20XX 7:00:00 AM | 0.29167 | 1 | 71.8 | 73.6 | 81.7218 | 93.6601 | 11.9383 | 70 | 71.8 |  | 71.8 | 86.0196 | 0.1 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 64.9614 | 17.1408 | 407951.0423 | 33.9959 | 33.9959 | 93.1529 | 0.2 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 67.3012 | 19.4806 | 463638.2847 | 38.6365 | 38.6365 | 97.1005 | 0.3 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 69.641 | 21.8204 | 519325.527 | 43.2771 | 43.2771 | 101.0481 | 0.4 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 71.9808 | 24.1602 | 575012.7694 | 47.9177 | 47.9177 | 104.9957 | 0.5 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 74.3206 | 26.5 | 630700.0117 | 52.5583 | 52.5583 | 108.9433 | 0.6 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 76.6604 | 28.8398 | 686387.2541 | 57.1989 | 57.1989 | 112.8909 | 0.7 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 79.0002 | 31.1796 | 742074.4964 | 61.8395 | 61.8395 | 116.8385 | 0.8 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 81.34 | 33.5194 | 797761.7388 | 66.4801 | 66.4801 | 120.7861 | 0.9 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 83.6798 | 35.8592 | 853448.9811 | 71.1207 | 71.1207 | 124.7337 | 1 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 86.0196 | 38.199 | 909136.2235 | 75.7614 | 75.7614 | 128.6814 | 70 | 75 | 30.6753 | 30 | 73.6
8/8/20XX 8:00:00 AM | 0.33333 | 1 | 73.2 | 71 | 85.8067 | 98.3566 | 12.5498 | 70 | 73.2 |  | 73.2 | 87.0617 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 65.0656 | 17.245 | 410431.1795 | 34.2026 | 34.2026 | 93.8006 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 67.5096 | 19.689 | 468598.559 | 39.0499 | 39.0499 | 98.3959 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 69.9537 | 22.133 | 526765.9385 | 43.8972 | 43.8972 | 102.9912 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 72.3977 | 24.577 | 584933.3181 | 48.7444 | 48.7444 | 107.5864 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 74.8417 | 27.021 | 643100.6976 | 53.5917 | 53.5917 | 112.1817 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 77.2857 | 29.465 | 701268.0771 | 58.439 | 58.439 | 116.777 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 79.7297 | 31.9091 | 759435.4566 | 63.2863 | 63.2863 | 121.3723 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 82.1737 | 34.3531 | 817602.8361 | 68.1336 | 68.1336 | 125.9676 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 84.6177 | 36.7971 | 875770.2156 | 72.9809 | 72.9809 | 130.5629 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 87.0617 | 39.2411 | 933937.5952 | 77.8281 | 77.8281 | 135.1581 | 75 | 70 | 31.1819 | 32 | 71
8/8/20XX 9:00:00 AM | 0.375 | 1 | 75.5 | 64.3 | 79.3806 | 92.8973 | 13.5167 | 60 | 75.5 |  | 75.5 | 85.1928 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 64.8787 | 17.0581 | 405983.1933 | 33.8319 | 33.8319 | 94.1544 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 67.1359 | 19.3152 | 459702.5866 | 38.3085 | 38.3085 | 99.1035 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 69.393 | 21.5724 | 513421.9799 | 42.7852 | 42.7852 | 104.0527 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 71.6501 | 23.8295 | 567141.3732 | 47.2618 | 47.2618 | 109.0018 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 73.9072 | 26.0866 | 620860.7665 | 51.7384 | 51.7384 | 113.9509 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 76.1643 | 28.3437 | 674580.1598 | 56.215 | 56.215 | 118.9 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 78.4215 | 30.6008 | 728299.5531 | 60.6916 | 60.6916 | 123.8491 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 80.6786 | 32.8579 | 782018.9463 | 65.1682 | 65.1682 | 128.7982 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 82.9357 | 35.1151 | 835738.3396 | 69.6449 | 69.6449 | 133.7474 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 85.1928 | 37.3722 | 889457.7329 | 74.1215 | 74.1215 | 138.6965 | 75 | 65 | 31.4541 | 32 | 64.3
8/8/20XX 10:00:00 AM | 0.41667 | 1 | 77.7 | 58.2 | 71.0329 | 85.548 | 14.515 | 50 | 77.7 |  | 77.7 | 82.9353 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 64.653 | 16.8324 | 400610.2123 | 33.3842 | 33.3842 | 94.3997 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 66.6844 | 18.8637 | 448956.6246 | 37.4131 | 37.4131 | 99.5941 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 68.7157 | 20.8951 | 497303.0369 | 41.4419 | 41.4419 | 104.7884 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 70.7471 | 22.9264 | 545649.4492 | 45.4708 | 45.4708 | 109.9828 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 72.7784 | 24.9578 | 593995.8615 | 49.4997 | 49.4997 | 115.1772 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 74.8098 | 26.9892 | 642342.2738 | 53.5285 | 53.5285 | 120.3715 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 76.8412 | 29.0205 | 690688.6861 | 57.5574 | 57.5574 | 125.5659 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 78.8725 | 31.0519 | 739035.0984 | 61.5863 | 61.5863 | 130.7603 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 80.9039 | 33.0833 | 787381.5107 | 65.6151 | 65.6151 | 135.9546 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 82.9353 | 35.1146 | 835727.923 | 69.644 | 69.644 | 141.149 | 80 | 60 | 31.6403 | 32 | 58.2
8/8/20XX 11:00:00 AM | 0.45833 | 1 | 80.5 | 53.4 | 78.0095 | 93.973 | 15.9635 | 50 | 80.5 |  | 80.5 | 83.4371 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 64.7032 | 16.8825 | 401804.6183 | 33.4837 | 33.4837 | 95.3812 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 66.7847 | 18.9641 | 451345.4366 | 37.6121 | 37.6121 | 101.5571 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 68.8663 | 21.0456 | 500886.2549 | 41.7405 | 41.7405 | 107.733 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 70.9478 | 23.1272 | 550427.0732 | 45.8689 | 45.8689 | 113.9089 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 73.0294 | 25.2087 | 599967.8915 | 49.9973 | 49.9973 | 120.0848 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 75.1109 | 27.2903 | 649508.7098 | 54.1257 | 54.1257 | 126.2607 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 77.1925 | 29.3718 | 699049.5281 | 58.2541 | 58.2541 | 132.4366 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 79.274 | 31.4534 | 748590.3464 | 62.3825 | 62.3825 | 138.6125 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 81.3556 | 33.5349 | 798131.1647 | 66.5109 | 66.5109 | 144.7884 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 83.4371 | 35.6165 | 847671.983 | 70.6393 | 70.6393 | 150.9643 | 80 | 55 | 32.4058 | 32 | 53.4
8/8/20XX 12:00:00 PM | 0.5 | 1 | 80.9 | 51.9 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 82.1251 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 64.572 | 16.7513 | 398682.0679 | 33.2235 | 33.2235 | 95.247 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 66.5223 | 18.7017 | 445100.3358 | 37.0917 | 37.0917 | 101.2887 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 68.4727 | 20.652 | 491518.6037 | 40.9599 | 40.9599 | 107.3304 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 70.423 | 22.6024 | 537936.8716 | 44.8281 | 44.8281 | 113.3721 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 72.3734 | 24.5527 | 584355.1394 | 48.6963 | 48.6963 | 119.4138 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 74.3237 | 26.5031 | 630773.4073 | 52.5645 | 52.5645 | 125.4555 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 76.2741 | 28.4534 | 677191.6752 | 56.4326 | 56.4326 | 131.4971 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 78.2244 | 30.4038 | 723609.9431 | 60.3008 | 60.3008 | 137.5388 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 80.1748 | 32.3541 | 770028.211 | 64.169 | 64.169 | 143.5805 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 82.1251 | 34.3045 | 816446.4789 | 68.0372 | 68.0372 | 149.6222 | 80 | 50 | 32.2981 | 32 | 51.9
8/8/20XX 1:00:00 PM | 0.54167 | 1 | 82.9 | 50.3 | 84.4305 | 101.7299 | 17.2993 | 50 | 82.9 |  | 82.9 | 84.9495 | 0.1 | 74.89 | 19.89 | 751842 | 62.6535 | 62.6535 | 64.8544 | 17.0338 | 405404.1771 | 33.7837 | 33.7837 | 96.4372 | 0.2 | 75.78 | 20.78 | 785484 | 65.457 | 65.457 | 67.0872 | 19.2666 | 458544.5543 | 38.212 | 38.212 | 103.669 | 0.3 | 76.67 | 21.67 | 819126 | 68.2605 | 68.2605 | 69.32 | 21.4994 | 511684.9314 | 42.6404 | 42.6404 | 110.9009 | 0.4 | 77.56 | 22.56 | 852768 | 71.064 | 71.064 | 71.5528 | 23.7322 | 564825.3085 | 47.0688 | 47.0688 | 118.1328 | 0.5 | 78.45 | 23.45 | 886410 | 73.8675 | 73.8675 | 73.7856 | 25.9649 | 617965.6856 | 51.4971 | 51.4971 | 125.3646 | 0.6 | 79.34 | 24.34 | 920052 | 76.671 | 76.671 | 76.0184 | 28.1977 | 671106.0628 | 55.9255 | 55.9255 | 132.5965 | 0.7 | 80.23 | 25.23 | 953694 | 79.4745 | 79.4745 | 78.2512 | 30.4305 | 724246.4399 | 60.3539 | 60.3539 | 139.8284 | 0.8 | 81.12 | 26.12 | 987336 | 82.278 | 82.278 | 80.4839 | 32.6633 | 777386.817 | 64.7822 | 64.7822 | 147.0602 | 0.9 | 82.01 | 27.01 | 1020978 | 85.0815 | 85.0815 | 82.7167 | 34.8961 | 830527.1941 | 69.2106 | 69.2106 | 154.2921 | 1 | 82.9 | 27.9 | 1054620 | 87.885 | 87.885 | 84.9495 | 37.1289 | 883667.5713 | 73.639 | 73.639 | 161.524 | 85 | 50 | 33.2319 | 34 | 50.3
8/8/20XX 2:00:00 PM | 0.58333 | 1 | 82.2 | 51.6 | 82.5146 | 99.4151 | 16.9005 | 50 | 82.2 |  | 82.2 | 85.2187 | 0.1 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 64.8813 | 17.0607 | 406044.8385 | 33.8371 | 33.8371 | 96.2701 | 0.2 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 67.141 | 19.3204 | 459825.8771 | 38.3188 | 38.3188 | 103.3348 | 0.3 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 69.4008 | 21.5801 | 513606.9156 | 42.8006 | 42.8006 | 110.3996 | 0.4 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 71.6605 | 23.8398 | 567387.9541 | 47.2823 | 47.2823 | 117.4643 | 0.5 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 73.9202 | 26.0995 | 621168.9926 | 51.7641 | 51.7641 | 124.5291 | 0.6 | 78.92 | 23.92 | 904176 | 75.348 | 75.348 | 76.1799 | 28.3592 | 674950.0312 | 56.2458 | 56.2458 | 131.5938 | 0.7 | 79.74 | 24.74 | 935172 | 77.931 | 77.931 | 78.4396 | 30.619 | 728731.0697 | 60.7276 | 60.7276 | 138.6586 | 0.8 | 80.56 | 25.56 | 966168 | 80.514 | 80.514 | 80.6993 | 32.8787 | 782512.1082 | 65.2093 | 65.2093 | 145.7233 | 0.9 | 81.38 | 26.38 | 997164 | 83.097 | 83.097 | 82.959 | 35.1384 | 836293.1468 | 69.6911 | 69.6911 | 152.7881 | 1 | 82.2 | 27.2 | 1028160 | 85.68 | 85.68 | 85.2187 | 37.3981 | 890074.1853 | 74.1728 | 74.1728 | 159.8528 | 80 | 50 | 33.1024 | 34 | 51.6
8/8/20XX 3:00:00 PM | 0.625 | 1 | 81.5 | 52.6 | 80.6344 | 97.1437 | 16.5092 | 50 | 81.5 |  | 81.5 | 84.9268 | 0.1 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 64.8522 | 17.0315 | 405350.1639 | 33.7792 | 33.7792 | 95.9917 | 0.2 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 67.0827 | 19.262 | 458436.5278 | 38.203 | 38.203 | 102.778 | 0.3 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 69.3132 | 21.4926 | 511522.8917 | 42.6269 | 42.6269 | 109.5644 | 0.4 | 77 | 22 | 831600 | 69.3 | 69.3 | 71.5437 | 23.7231 | 564609.2556 | 47.0508 | 47.0508 | 116.3508 | 0.5 | 77.75 | 22.75 | 859950 | 71.6625 | 71.6625 | 73.7742 | 25.9536 | 617695.6195 | 51.4746 | 51.4746 | 123.1371 | 0.6 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 76.0047 | 28.1841 | 670781.9834 | 55.8985 | 55.8985 | 129.9235 | 0.7 | 79.25 | 24.25 | 916650 | 76.3875 | 76.3875 | 78.2353 | 30.4146 | 723868.3473 | 60.3224 | 60.3224 | 136.7099 | 0.8 | 80 | 25 | 945000 | 78.75 | 78.75 | 80.4658 | 32.6452 | 776954.7112 | 64.7462 | 64.7462 | 143.4962 | 0.9 | 80.75 | 25.75 | 973350 | 81.1125 | 81.1125 | 82.6963 | 34.8757 | 830041.0751 | 69.1701 | 69.1701 | 150.2826 | 1 | 81.5 | 26.5 | 1001700 | 83.475 | 83.475 | 84.9268 | 37.1062 | 883127.4389 | 73.594 | 73.594 | 157.069 | 80 | 55 | 32.8848 | 32 | 52.6
8/8/20XX 4:00:00 PM | 0.66667 | 1 | 81.2 | 54.5 | 79.8394 | 96.1834 | 16.3439 | 50 | 81.2 |  | 81.2 | 87.1942 | 0.1 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 65.0789 | 17.2583 | 410746.5166 | 34.2289 | 34.2289 | 96.3469 | 0.2 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 67.5361 | 19.7155 | 469229.2333 | 39.1024 | 39.1024 | 103.4884 | 0.3 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 69.9934 | 22.1728 | 527711.9499 | 43.976 | 43.976 | 110.63 | 0.4 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 72.4507 | 24.63 | 586194.6665 | 48.8496 | 48.8496 | 117.7716 | 0.5 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 74.9079 | 27.0873 | 644677.3832 | 53.7231 | 53.7231 | 124.9131 | 0.6 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 77.3652 | 29.5445 | 703160.0998 | 58.5967 | 58.5967 | 132.0547 | 0.7 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 79.8224 | 32.0018 | 761642.8165 | 63.4702 | 63.4702 | 139.1962 | 0.8 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 82.2797 | 34.4591 | 820125.5331 | 68.3438 | 68.3438 | 146.3378 | 0.9 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 84.7369 | 36.9163 | 878608.2497 | 73.2174 | 73.2174 | 153.4794 | 1 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 87.1942 | 39.3736 | 937090.9664 | 78.0909 | 78.0909 | 160.6209 | 80 | 55 | 33.1669 | 34 | 54.5
8/8/20XX 5:00:00 PM | 0.70833 | 1 | 79.3 | 57.6 | 74.9531 | 90.2816 | 15.3285 | 50 | 79.3 |  | 79.3 | 86.6027 | 0.1 | 74.53 | 19.53 | 738234 | 61.5195 | 61.5195 | 65.0197 | 17.1991 | 409338.7728 | 34.1116 | 34.1116 | 95.6311 | 0.2 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 67.4178 | 19.5972 | 466413.7455 | 38.8678 | 38.8678 | 102.0568 | 0.3 | 75.59 | 20.59 | 778302 | 64.8585 | 64.8585 | 69.816 | 21.9953 | 523488.7183 | 43.6241 | 43.6241 | 108.4826 | 0.4 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 72.2141 | 24.3934 | 580563.691 | 48.3803 | 48.3803 | 114.9083 | 0.5 | 76.65 | 21.65 | 818370 | 68.1975 | 68.1975 | 74.6122 | 26.7915 | 637638.6638 | 53.1366 | 53.1366 | 121.3341 | 0.6 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 77.0103 | 29.1896 | 694713.6366 | 57.8928 | 57.8928 | 127.7598 | 0.7 | 77.71 | 22.71 | 858438 | 71.5365 | 71.5365 | 79.4084 | 31.5878 | 751788.6093 | 62.6491 | 62.6491 | 134.1856 | 0.8 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 81.8065 | 33.9859 | 808863.5821 | 67.4053 | 67.4053 | 140.6113 | 0.9 | 78.77 | 23.77 | 898506 | 74.8755 | 74.8755 | 84.2046 | 36.384 | 865938.5549 | 72.1615 | 72.1615 | 147.037 | 1 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 86.6027 | 38.7821 | 923013.5276 | 76.9178 | 76.9178 | 153.4628 | 80 | 60 | 32.6077 | 32 | 57.6
8/8/20XX 6:00:00 PM | 0.75 | 1 | 78.8 | 57.7 | 73.7091 | 88.7794 | 15.0703 | 50 | 78.8 |  | 78.8 | 85.3132 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 64.8908 | 17.0702 | 406269.8498 | 33.8558 | 33.8558 | 95.2178 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 67.16 | 19.3393 | 460275.8997 | 38.3563 | 38.3563 | 101.2303 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 69.4291 | 21.6085 | 514281.9495 | 42.8568 | 42.8568 | 107.2428 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 71.6983 | 23.8776 | 568287.9994 | 47.3573 | 47.3573 | 113.2553 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 73.9674 | 26.1468 | 622294.0492 | 51.8578 | 51.8578 | 119.2678 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 76.2366 | 28.416 | 676300.099 | 56.3583 | 56.3583 | 125.2803 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 78.5058 | 30.6851 | 730306.1489 | 60.8588 | 60.8588 | 131.2928 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 80.7749 | 32.9543 | 784312.1987 | 65.3593 | 65.3593 | 137.3053 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 83.0441 | 35.2235 | 838318.2486 | 69.8599 | 69.8599 | 143.3179 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 85.3132 | 37.4926 | 892324.2984 | 74.3604 | 74.3604 | 149.3304 | 80 | 60 | 32.2828 | 32 | 57.7
8/8/20XX 7:00:00 PM | 0.79167 | 1 | 77.4 | 63.7 | 84.6839 | 99.1235 | 14.4396 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/8/20XX 8:00:00 PM | 0.83333 | 1 | 76.4 | 66.6 | 81.8567 | 95.8042 | 13.9475 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/8/20XX 9:00:00 PM | 0.875 | 1 | 75.9 | 68.6 | 80.4731 | 94.1799 | 13.7068 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/8/20XX 10:00:00 PM | 0.91667 | 1 | 75.1 | 71.2 | 91.6296 | 105.0536 | 13.424 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/8/20XX 11:00:00 PM | 0.95833 | 1 | 74.8 | 70.3 | 90.6884 | 103.9709 | 13.2825 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/8/20XX 12:00:00 AM | 0 | 2 | 74.2 | 71.6 | 88.8307 | 101.8342 | 13.0035 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/9/20XX 1:00:00 AM | 0.041667 | 2 | 73.3 | 75.4 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/9/20XX 2:00:00 AM | 0.083333 | 2 | 72.6 | 76.6 | 84.035 | 96.3195 | 12.2844 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/9/20XX 3:00:00 AM | 0.125 | 2 | 72.2 | 77.2 | 82.8715 | 94.9817 | 12.1103 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/9/20XX 4:00:00 AM | 0.16667 | 2 | 71.5 | 80.9 | 92.6795 | 104.5026 | 11.8231 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/9/20XX 5:00:00 AM | 0.20833 | 2 | 71 | 81.5 | 91.0648 | 102.6753 | 11.6104 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/9/20XX 6:00:00 AM | 0.25 | 2 | 71.7 | 79.7 | 81.4366 | 93.3322 | 11.8956 | 70 | 71.7 |  | 71.7 | 92.9754 | 0.1 | 73.77 | 18.77 | 709506 | 59.1255 | 59.1255 | 65.657 | 17.8364 | 424505.7194 | 35.3755 | 35.3755 | 94.501 | 0.2 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 68.6924 | 20.8717 | 496747.6388 | 41.3956 | 41.3956 | 99.7966 | 0.3 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 71.7278 | 23.9071 | 568989.5582 | 47.4158 | 47.4158 | 105.0923 | 0.4 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 74.7631 | 26.9425 | 641231.4776 | 53.436 | 53.436 | 110.388 | 0.5 | 72.85 | 17.85 | 674730 | 56.2275 | 56.2275 | 77.7985 | 29.9779 | 713473.397 | 59.4561 | 59.4561 | 115.6836 | 0.6 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 80.8339 | 33.0132 | 785715.3163 | 65.4763 | 65.4763 | 120.9793 | 0.7 | 72.39 | 17.39 | 657342 | 54.7785 | 54.7785 | 83.8693 | 36.0486 | 857957.2357 | 71.4964 | 71.4964 | 126.2749 | 0.8 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 86.9046 | 39.084 | 930199.1551 | 77.5166 | 77.5166 | 131.5706 | 0.9 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 89.94 | 42.1194 | 1002441.0745 | 83.5368 | 83.5368 | 136.8663 | 1 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 92.9754 | 45.1547 | 1074682.9939 | 89.5569 | 89.5569 | 142.1619 | 70 | 80 | 31.7378 | 32 | 79.7
8/9/20XX 7:00:00 AM | 0.29167 | 2 | 73.2 | 75.9 | 85.8067 | 98.3566 | 12.5498 | 70 | 73.2 |  | 73.2 | 93.2111 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 65.6806 | 17.86 | 425066.8124 | 35.4222 | 35.4222 | 95.0202 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 68.7395 | 20.9189 | 497869.8247 | 41.4892 | 41.4892 | 100.8352 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 71.7985 | 23.9779 | 570672.8371 | 47.5561 | 47.5561 | 106.6501 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 74.8574 | 27.0368 | 643475.8495 | 53.623 | 53.623 | 112.465 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 77.9164 | 30.0958 | 716278.8618 | 59.6899 | 59.6899 | 118.2799 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 80.9753 | 33.1547 | 789081.8742 | 65.7568 | 65.7568 | 124.0948 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 84.0343 | 36.2137 | 861884.8866 | 71.8237 | 71.8237 | 129.9097 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 87.0932 | 39.2726 | 934687.8989 | 77.8907 | 77.8907 | 135.7247 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 90.1522 | 42.3316 | 1007490.9113 | 83.9576 | 83.9576 | 141.5396 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 93.2111 | 45.3905 | 1080293.9237 | 90.0245 | 90.0245 | 147.3545 | 75 | 75 | 32.1435 | 32 | 75.9
8/9/20XX 8:00:00 AM | 0.33333 | 2 | 75.3 | 72.1 | 92.2616 | 105.7806 | 13.519 | 70 | 75.3 |  | 75.3 | 95.1006 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 65.8695 | 18.0489 | 429563.737 | 35.797 | 35.797 | 96.0565 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 69.1174 | 21.2968 | 506863.6741 | 42.2386 | 42.2386 | 102.9076 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 72.3653 | 24.5447 | 584163.6111 | 48.6803 | 48.6803 | 109.7588 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 75.6132 | 27.7926 | 661463.5482 | 55.122 | 55.122 | 116.61 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 78.8611 | 31.0405 | 738763.4852 | 61.5636 | 61.5636 | 123.4611 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 82.109 | 34.2884 | 816063.4223 | 68.0053 | 68.0053 | 130.3123 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 85.3569 | 37.5363 | 893363.3593 | 74.4469 | 74.4469 | 137.1634 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 88.6048 | 40.7842 | 970663.2964 | 80.8886 | 80.8886 | 144.0146 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 91.8527 | 44.0321 | 1047963.2334 | 87.3303 | 87.3303 | 150.8658 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 95.1006 | 47.28 | 1125263.1705 | 93.7719 | 93.7719 | 157.7169 | 75 | 70 | 32.9556 | 32 | 72.1
8/9/20XX 9:00:00 AM | 0.375 | 2 | 77 | 67 | 83.5433 | 97.7844 | 14.241 | 60 | 77 |  | 77 | 93.5121 | 0.1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 65.7107 | 17.89 | 425783.0108 | 35.4819 | 35.4819 | 96.2769 | 0.2 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 68.7997 | 20.9791 | 499302.2217 | 41.6085 | 41.6085 | 103.3485 | 0.3 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 71.8888 | 24.0681 | 572821.4325 | 47.7351 | 47.7351 | 110.4201 | 0.4 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 74.9778 | 27.1572 | 646340.6433 | 53.8617 | 53.8617 | 117.4917 | 0.5 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 78.0668 | 30.2462 | 719859.8542 | 59.9883 | 59.9883 | 124.5633 | 0.6 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 81.1559 | 33.3353 | 793379.065 | 66.1149 | 66.1149 | 131.6349 | 0.7 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 84.2449 | 36.4243 | 866898.2758 | 72.2415 | 72.2415 | 138.7065 | 0.8 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 87.334 | 39.5133 | 940417.4867 | 78.3681 | 78.3681 | 145.7781 | 0.9 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 90.423 | 42.6024 | 1013936.6975 | 84.4947 | 84.4947 | 152.8497 | 1 | 77 | 22 | 831600 | 69.3 | 69.3 | 93.5121 | 45.6914 | 1087455.9083 | 90.6213 | 90.6213 | 159.9213 | 75 | 65 | 33.1251 | 34 | 67
8/9/20XX 10:00:00 AM | 0.41667 | 2 | 79.4 | 61.4 | 90.5845 | 106.0515 | 15.4669 | 60 | 79.4 |  | 79.4 | 92.7499 | 0.1 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 65.6345 | 17.8138 | 423969.0196 | 35.3308 | 35.3308 | 96.8818 | 0.2 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 68.6473 | 20.8266 | 495674.2391 | 41.3062 | 41.3062 | 104.5582 | 0.3 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 71.6601 | 23.8395 | 567379.4587 | 47.2816 | 47.2816 | 112.2346 | 0.4 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 74.6729 | 26.8523 | 639084.6783 | 53.2571 | 53.2571 | 119.9111 | 0.5 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 77.6858 | 29.8651 | 710789.8978 | 59.2325 | 59.2325 | 127.5875 | 0.6 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 80.6986 | 32.8779 | 782495.1174 | 65.2079 | 65.2079 | 135.2639 | 0.7 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 83.7114 | 35.8908 | 854200.337 | 71.1834 | 71.1834 | 142.9404 | 0.8 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 86.7242 | 38.9036 | 925905.5566 | 77.1588 | 77.1588 | 150.6168 | 0.9 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 89.7371 | 41.9164 | 997610.7761 | 83.1342 | 83.1342 | 158.2932 | 1 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 92.7499 | 44.9292 | 1069315.9957 | 89.1097 | 89.1097 | 165.9697 | 80 | 60 | 33.5959 | 34 | 61.4
8/9/20XX 11:00:00 AM | 0.45833 | 2 | 81.7 | 56.7 | 81.168 | 97.7883 | 16.6202 | 50 | 81.7 |  | 81.7 | 92.3036 | 0.1 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 65.5898 | 17.7692 | 422906.8195 | 35.2422 | 35.2422 | 97.5177 | 0.2 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 68.558 | 20.7374 | 493549.8389 | 41.1292 | 41.1292 | 105.8302 | 0.3 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 71.5262 | 23.7056 | 564192.8584 | 47.0161 | 47.0161 | 114.1426 | 0.4 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 74.4944 | 26.6738 | 634835.8778 | 52.903 | 52.903 | 122.455 | 0.5 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 77.4626 | 29.642 | 705478.8973 | 58.7899 | 58.7899 | 130.7674 | 0.6 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 80.4308 | 32.6102 | 776121.9167 | 64.6768 | 64.6768 | 139.0798 | 0.7 | 79.39 | 24.39 | 921942 | 76.8285 | 76.8285 | 83.399 | 35.5784 | 846764.9362 | 70.5637 | 70.5637 | 147.3922 | 0.8 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 86.3672 | 38.5466 | 917407.9556 | 76.4507 | 76.4507 | 155.7047 | 0.9 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 89.3354 | 41.5147 | 988050.9751 | 82.3376 | 82.3376 | 164.0171 | 1 | 81.7 | 26.7 | 1009260 | 84.105 | 84.105 | 92.3036 | 44.4829 | 1058693.9945 | 88.2245 | 88.2245 | 172.3295 | 80 | 55 | 34.0914 | 34 | 56.7
8/9/20XX 12:00:00 PM | 0.5 | 2 | 82.9 | 54.2 | 84.4305 | 101.7299 | 17.2993 | 50 | 82.9 |  | 82.9 | 91.6963 | 0.1 | 74.89 | 19.89 | 751842 | 62.6535 | 62.6535 | 65.5291 | 17.7085 | 421461.3977 | 35.1218 | 35.1218 | 97.7753 | 0.2 | 75.78 | 20.78 | 785484 | 65.457 | 65.457 | 68.4366 | 20.6159 | 490658.9954 | 40.8882 | 40.8882 | 106.3452 | 0.3 | 76.67 | 21.67 | 819126 | 68.2605 | 68.2605 | 71.344 | 23.5234 | 559856.5931 | 46.6547 | 46.6547 | 114.9152 | 0.4 | 77.56 | 22.56 | 852768 | 71.064 | 71.064 | 74.2515 | 26.4308 | 629054.1909 | 52.4212 | 52.4212 | 123.4852 | 0.5 | 78.45 | 23.45 | 886410 | 73.8675 | 73.8675 | 77.1589 | 29.3383 | 698251.7886 | 58.1876 | 58.1876 | 132.0551 | 0.6 | 79.34 | 24.34 | 920052 | 76.671 | 76.671 | 80.0664 | 32.2458 | 767449.3863 | 63.9541 | 63.9541 | 140.6251 | 0.7 | 80.23 | 25.23 | 953694 | 79.4745 | 79.4745 | 82.9739 | 35.1532 | 836646.984 | 69.7206 | 69.7206 | 149.1951 | 0.8 | 81.12 | 26.12 | 987336 | 82.278 | 82.278 | 85.8813 | 38.0607 | 905844.5817 | 75.487 | 75.487 | 157.765 | 0.9 | 82.01 | 27.01 | 1020978 | 85.0815 | 85.0815 | 88.7888 | 40.9682 | 975042.1794 | 81.2535 | 81.2535 | 166.335 | 1 | 82.9 | 27.9 | 1054620 | 87.885 | 87.885 | 91.6963 | 43.8756 | 1044239.7771 | 87.02 | 87.02 | 174.905 | 85 | 55 | 34.2911 | 34 | 54.2
8/9/20XX 1:00:00 PM | 0.54167 | 2 | 83.9 | 51.6 | 87.2303 | 105.1128 | 17.8825 | 50 | 83.9 |  | 83.9 | 90.0915 | 0.1 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 65.3686 | 17.548 | 417642.0565 | 34.8035 | 34.8035 | 97.772 | 0.2 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 68.1156 | 20.295 | 483020.313 | 40.2517 | 40.2517 | 106.3387 | 0.3 | 76.97 | 21.97 | 830466 | 69.2055 | 69.2055 | 70.8626 | 23.042 | 548398.5695 | 45.6999 | 45.6999 | 114.9054 | 0.4 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 73.6096 | 25.7889 | 613776.826 | 51.1481 | 51.1481 | 123.4721 | 0.5 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 76.3566 | 28.5359 | 679155.0825 | 56.5963 | 56.5963 | 132.0388 | 0.6 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 79.1035 | 31.2829 | 744533.339 | 62.0444 | 62.0444 | 140.6054 | 0.7 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 81.8505 | 34.0299 | 809911.5955 | 67.4926 | 67.4926 | 149.1721 | 0.8 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 84.5975 | 36.7769 | 875289.852 | 72.9408 | 72.9408 | 157.7388 | 0.9 | 82.91 | 27.91 | 1054998 | 87.9165 | 87.9165 | 87.3445 | 39.5239 | 940668.1085 | 78.389 | 78.389 | 166.3055 | 1 | 83.9 | 28.9 | 1092420 | 91.035 | 91.035 | 90.0915 | 42.2709 | 1006046.365 | 83.8372 | 83.8372 | 174.8722 | 85 | 50 | 34.2849 | 34 | 51.6
8/9/20XX 2:00:00 PM | 0.58333 | 2 | 83.8 | 54 | 86.947 | 104.7705 | 17.8235 | 50 | 83.8 |  | 83.8 | 94.0764 | 0.1 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 65.7671 | 17.9465 | 427126.0476 | 35.5938 | 35.5938 | 98.5308 | 0.2 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 68.9126 | 21.0919 | 501988.2952 | 41.8324 | 41.8324 | 107.8564 | 0.3 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 72.0581 | 24.2374 | 576850.5428 | 48.0709 | 48.0709 | 117.1819 | 0.4 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 75.2035 | 27.3829 | 651712.7904 | 54.3094 | 54.3094 | 126.5074 | 0.5 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 78.349 | 30.5284 | 726575.038 | 60.5479 | 60.5479 | 135.8329 | 0.6 | 79.88 | 24.88 | 940464 | 78.372 | 78.372 | 81.4945 | 33.6738 | 801437.2856 | 66.7864 | 66.7864 | 145.1584 | 0.7 | 80.86 | 25.86 | 977508 | 81.459 | 81.459 | 84.6399 | 36.8193 | 876299.5332 | 73.025 | 73.025 | 154.484 | 0.8 | 81.84 | 26.84 | 1014552 | 84.546 | 84.546 | 87.7854 | 39.9648 | 951161.7808 | 79.2635 | 79.2635 | 163.8095 | 0.9 | 82.82 | 27.82 | 1051596 | 87.633 | 87.633 | 90.9309 | 43.1103 | 1026024.0284 | 85.502 | 85.502 | 173.135 | 1 | 83.8 | 28.8 | 1088640 | 90.72 | 90.72 | 94.0764 | 46.2557 | 1100886.276 | 91.7405 | 91.7405 | 182.4605 | 85 | 55 | 34.8861 | 34 | 54
8/9/20XX 3:00:00 PM | 0.625 | 2 | 82.3 | 55.9 | 82.7861 | 99.7431 | 16.957 | 50 | 82.3 |  | 82.3 | 92.7908 | 0.1 | 74.83 | 19.83 | 749574 | 62.4645 | 62.4645 | 65.6385 | 17.8179 | 424066.3019 | 35.3389 | 35.3389 | 97.8034 | 0.2 | 75.66 | 20.66 | 780948 | 65.079 | 65.079 | 68.6555 | 20.8348 | 495868.8039 | 41.3224 | 41.3224 | 106.4014 | 0.3 | 76.49 | 21.49 | 812322 | 67.6935 | 67.6935 | 71.6724 | 23.8517 | 567671.3058 | 47.3059 | 47.3059 | 114.9994 | 0.4 | 77.32 | 22.32 | 843696 | 70.308 | 70.308 | 74.6893 | 26.8686 | 639473.8077 | 53.2895 | 53.2895 | 123.5975 | 0.5 | 78.15 | 23.15 | 875070 | 72.9225 | 72.9225 | 77.7062 | 29.8856 | 711276.3096 | 59.273 | 59.273 | 132.1955 | 0.6 | 78.98 | 23.98 | 906444 | 75.537 | 75.537 | 80.7231 | 32.9025 | 783078.8116 | 65.2566 | 65.2566 | 140.7936 | 0.7 | 79.81 | 24.81 | 937818 | 78.1515 | 78.1515 | 83.74 | 35.9194 | 854881.3135 | 71.2401 | 71.2401 | 149.3916 | 0.8 | 80.64 | 25.64 | 969192 | 80.766 | 80.766 | 86.7569 | 38.9363 | 926683.8154 | 77.2237 | 77.2237 | 157.9897 | 0.9 | 81.47 | 26.47 | 1000566 | 83.3805 | 83.3805 | 89.7738 | 41.9532 | 998486.3174 | 83.2072 | 83.2072 | 166.5877 | 1 | 82.3 | 27.3 | 1031940 | 85.995 | 85.995 | 92.7908 | 44.9701 | 1070288.8193 | 89.1907 | 89.1907 | 175.1857 | 80 | 55 | 34.3154 | 34 | 55.9
8/9/20XX 4:00:00 PM | 0.66667 | 2 | 81.2 | 59.4 | 79.8394 | 96.1834 | 16.3439 | 50 | 81.2 |  | 81.2 | 95.2027 | 0.1 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 65.8797 | 18.0591 | 429806.7798 | 35.8172 | 35.8172 | 97.9352 | 0.2 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 69.1378 | 21.3172 | 507349.7597 | 42.2791 | 42.2791 | 106.6651 | 0.3 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 72.396 | 24.5753 | 584892.7395 | 48.7411 | 48.7411 | 115.3951 | 0.4 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 75.6541 | 27.8334 | 662435.7194 | 55.203 | 55.203 | 124.125 | 0.5 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 78.9122 | 31.0915 | 739978.6992 | 61.6649 | 61.6649 | 132.8549 | 0.6 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 82.1703 | 34.3497 | 817521.6791 | 68.1268 | 68.1268 | 141.5848 | 0.7 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 85.4284 | 37.6078 | 895064.6589 | 74.5887 | 74.5887 | 150.3147 | 0.8 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 88.6865 | 40.8659 | 972607.6388 | 81.0506 | 81.0506 | 159.0446 | 0.9 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 91.9446 | 44.124 | 1050150.6186 | 87.5126 | 87.5126 | 167.7746 | 1 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 95.2027 | 47.3821 | 1127693.5984 | 93.9745 | 93.9745 | 176.5045 | 80 | 60 | 34.4233 | 34 | 59.4
8/9/20XX 5:00:00 PM | 0.70833 | 2 | 80.4 | 59.7 | 77.751 | 93.6607 | 15.9097 | 50 | 80.4 |  | 80.4 | 93.1834 | 0.1 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 65.6778 | 17.8572 | 425000.7601 | 35.4167 | 35.4167 | 97.2827 | 0.2 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 68.734 | 20.9133 | 497737.7202 | 41.4781 | 41.4781 | 105.3601 | 0.3 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 71.7902 | 23.9695 | 570474.6804 | 47.5396 | 47.5396 | 113.4376 | 0.4 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 74.8463 | 27.0257 | 643211.6405 | 53.601 | 53.601 | 121.515 | 0.5 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 77.9025 | 30.0819 | 715948.6006 | 59.6624 | 59.6624 | 129.5924 | 0.6 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 80.9587 | 33.138 | 788685.5607 | 65.7238 | 65.7238 | 137.6698 | 0.7 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 84.0149 | 36.1942 | 861422.5208 | 71.7852 | 71.7852 | 145.7472 | 0.8 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 87.071 | 39.2504 | 934159.481 | 77.8466 | 77.8466 | 153.8246 | 0.9 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 90.1272 | 42.3066 | 1006896.4411 | 83.908 | 83.908 | 161.902 | 1 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 93.1834 | 45.3627 | 1079633.4012 | 89.9695 | 89.9695 | 169.9795 | 80 | 60 | 33.9097 | 34 | 59.7
8/9/20XX 6:00:00 PM | 0.75 | 2 | 79.4 | 62.4 | 90.5845 | 106.0515 | 15.4669 | 60 | 79.4 |  | 79.4 | 94.2966 | 0.1 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 65.7891 | 17.9685 | 427650.1529 | 35.6375 | 35.6375 | 97.1885 | 0.2 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 68.9566 | 21.136 | 503036.5058 | 41.9197 | 41.9197 | 105.1717 | 0.3 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 72.1241 | 24.3035 | 578422.8587 | 48.2019 | 48.2019 | 113.1549 | 0.4 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 75.2916 | 27.471 | 653809.2116 | 54.4841 | 54.4841 | 121.1381 | 0.5 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 78.4591 | 30.6385 | 729195.5645 | 60.7663 | 60.7663 | 129.1213 | 0.6 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 81.6266 | 33.806 | 804581.9174 | 67.0485 | 67.0485 | 137.1045 | 0.7 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 84.7941 | 36.9735 | 879968.2703 | 73.3307 | 73.3307 | 145.0877 | 0.8 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 87.9616 | 40.141 | 955354.6232 | 79.6129 | 79.6129 | 153.0709 | 0.9 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 91.1291 | 43.3084 | 1030740.9761 | 85.8951 | 85.8951 | 161.0541 | 1 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 94.2966 | 46.4759 | 1106127.329 | 92.1773 | 92.1773 | 169.0373 | 80 | 60 | 33.8383 | 34 | 62.4
8/9/20XX 7:00:00 PM | 0.79167 | 2 | 78.3 | 63.5 | 87.2982 | 102.1928 | 14.8947 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/9/20XX 8:00:00 PM | 0.83333 | 2 | 77 | 68.3 | 83.5433 | 97.7844 | 14.241 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/9/20XX 9:00:00 PM | 0.875 | 2 | 77.1 | 68.5 | 83.8273 | 98.1177 | 14.2905 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/9/20XX 10:00:00 PM | 0.91667 | 2 | 76.4 | 71 | 95.8042 | 109.8565 | 14.0523 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/9/20XX 11:00:00 PM | 0.95833 | 2 | 75.9 | 71.8 | 94.1799 | 107.9876 | 13.8077 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/9/20XX 12:00:00 AM | 0 | 3 | 75.2 | 73.4 | 91.9451 | 105.4166 | 13.4714 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/10/20XX 1:00:00 AM | 0.041667 | 3 | 74.3 | 74.4 | 89.138 | 102.1877 | 13.0496 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/10/20XX 2:00:00 AM | 0.083333 | 3 | 73.8 | 75.3 | 87.6104 | 100.4307 | 12.8203 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/10/20XX 3:00:00 AM | 0.125 | 3 | 73.2 | 74.8 | 85.8067 | 98.3566 | 12.5498 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/10/20XX 4:00:00 AM | 0.16667 | 3 | 73 | 75.9 | 85.2126 | 97.6734 | 12.4608 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/10/20XX 5:00:00 AM | 0.20833 | 3 | 72.5 | 77.2 | 83.7428 | 95.9835 | 12.2407 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/10/20XX 6:00:00 AM | 0.25 | 3 | 72.9 | 77.8 | 84.9169 | 97.3334 | 12.4165 | 70 | 72.9 |  | 72.9 | 94.6018 | 0.1 | 73.89 | 18.89 | 714042 | 59.5035 | 59.5035 | 65.8196 | 17.999 | 428376.5696 | 35.698 | 35.698 | 95.2015 | 0.2 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 69.0177 | 21.197 | 504489.3392 | 42.0408 | 42.0408 | 101.1978 | 0.3 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 72.2157 | 24.395 | 580602.1088 | 48.3835 | 48.3835 | 107.194 | 0.4 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 75.4137 | 27.5931 | 656714.8784 | 54.7262 | 54.7262 | 113.1902 | 0.5 | 73.45 | 18.45 | 697410 | 58.1175 | 58.1175 | 78.6117 | 30.7911 | 732827.6479 | 61.069 | 61.069 | 119.1865 | 0.6 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 81.8097 | 33.9891 | 808940.4175 | 67.4117 | 67.4117 | 125.1827 | 0.7 | 73.23 | 18.23 | 689094 | 57.4245 | 57.4245 | 85.0077 | 37.1871 | 885053.1871 | 73.7544 | 73.7544 | 131.1789 | 0.8 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 88.2058 | 40.3851 | 961165.9567 | 80.0972 | 80.0972 | 137.1752 | 0.9 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 91.4038 | 43.5831 | 1037278.7263 | 86.4399 | 86.4399 | 143.1714 | 1 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 94.6018 | 46.7812 | 1113391.4959 | 92.7826 | 92.7826 | 149.1676 | 75 | 80 | 32.2871 | 32 | 77.8
8/10/20XX 7:00:00 AM | 0.29167 | 3 | 74.3 | 74.1 | 89.138 | 102.1877 | 13.0496 | 70 | 74.3 |  | 74.3 | 94.4884 | 0.1 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 65.8083 | 17.9877 | 428106.6957 | 35.6756 | 35.6756 | 95.6201 | 0.2 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 68.995 | 21.1744 | 503949.5913 | 41.9958 | 41.9958 | 102.0348 | 0.3 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 72.1817 | 24.361 | 579792.487 | 48.316 | 48.316 | 108.4495 | 0.4 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 75.3683 | 27.5477 | 655635.3827 | 54.6363 | 54.6363 | 114.8643 | 0.5 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 78.555 | 30.7344 | 731478.2783 | 60.9565 | 60.9565 | 121.279 | 0.6 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 81.7417 | 33.9211 | 807321.174 | 67.2768 | 67.2768 | 127.6938 | 0.7 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 84.9284 | 37.1077 | 883164.0696 | 73.597 | 73.597 | 134.1085 | 0.8 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 88.115 | 40.2944 | 959006.9653 | 79.9172 | 79.9172 | 140.5232 | 0.9 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 91.3017 | 43.4811 | 1034849.861 | 86.2375 | 86.2375 | 146.938 | 1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 94.4884 | 46.6678 | 1110692.7566 | 92.5577 | 92.5577 | 153.3527 | 75 | 75 | 32.6138 | 32 | 74.1
8/10/20XX 8:00:00 AM | 0.33333 | 3 | 75.8 | 69.4 | 80.1988 | 93.8579 | 13.6591 | 60 | 75.8 |  | 75.8 | 93.0383 | 0.1 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 65.6633 | 17.8427 | 424655.5594 | 35.388 | 35.388 | 95.805 | 0.2 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 68.705 | 20.8843 | 497047.3188 | 41.4206 | 41.4206 | 102.4046 | 0.3 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 71.7466 | 23.926 | 569439.0783 | 47.4533 | 47.4533 | 109.0043 | 0.4 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 74.7883 | 26.9677 | 641830.8377 | 53.4859 | 53.4859 | 115.6039 | 0.5 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 77.83 | 30.0094 | 714222.5971 | 59.5185 | 59.5185 | 122.2035 | 0.6 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 80.8717 | 33.051 | 786614.3565 | 65.5512 | 65.5512 | 128.8032 | 0.7 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 83.9133 | 36.0927 | 859006.1159 | 71.5838 | 71.5838 | 135.4028 | 0.8 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 86.955 | 39.1344 | 931397.8754 | 77.6165 | 77.6165 | 142.0025 | 0.9 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 89.9967 | 42.176 | 1003789.6348 | 83.6491 | 83.6491 | 148.6021 | 1 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 93.0383 | 45.2177 | 1076181.3942 | 89.6818 | 89.6818 | 155.2018 | 75 | 70 | 32.7558 | 32 | 69.4
8/10/20XX 9:00:00 AM | 0.375 | 3 | 78.1 | 64.4 | 86.7115 | 101.504 | 14.7925 | 60 | 78.1 |  | 78.1 | 93.2202 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 65.6815 | 17.8609 | 425088.3123 | 35.424 | 35.424 | 96.5655 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 68.7413 | 20.9207 | 497912.8247 | 41.4927 | 41.4927 | 103.9257 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 71.8012 | 23.9806 | 570737.337 | 47.5614 | 47.5614 | 111.2859 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 74.861 | 27.0404 | 643561.8493 | 53.6302 | 53.6302 | 118.6462 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 77.9209 | 30.1003 | 716386.3616 | 59.6989 | 59.6989 | 126.0064 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 80.9808 | 33.1601 | 789210.874 | 65.7676 | 65.7676 | 133.3666 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 84.0406 | 36.22 | 862035.3863 | 71.8363 | 71.8363 | 140.7268 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 87.1005 | 39.2798 | 934859.8986 | 77.905 | 77.905 | 148.087 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 90.1603 | 42.3397 | 1007684.411 | 83.9737 | 83.9737 | 155.4472 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 93.2202 | 45.3995 | 1080508.9233 | 90.0424 | 90.0424 | 162.8074 | 80 | 65 | 33.3499 | 34 | 64.4
8/10/20XX 10:00:00 AM | 0.41667 | 3 | 80.4 | 58.2 | 77.751 | 93.6607 | 15.9097 | 50 | 80.4 |  | 80.4 | 90.7969 | 0.1 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 65.4392 | 17.6185 | 419320.9899 | 34.9434 | 34.9434 | 96.8094 | 0.2 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 68.2567 | 20.4361 | 486378.1798 | 40.5315 | 40.5315 | 104.4135 | 0.3 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 71.0742 | 23.2536 | 553435.3697 | 46.1196 | 46.1196 | 112.0176 | 0.4 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 73.8917 | 26.0711 | 620492.5596 | 51.7077 | 51.7077 | 119.6217 | 0.5 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 76.7093 | 28.8886 | 687549.7495 | 57.2958 | 57.2958 | 127.2258 | 0.6 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 79.5268 | 31.7062 | 754606.9393 | 62.8839 | 62.8839 | 134.8299 | 0.7 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 82.3443 | 34.5237 | 821664.1292 | 68.472 | 68.472 | 142.434 | 0.8 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 85.1619 | 37.3412 | 888721.3191 | 74.0601 | 74.0601 | 150.0381 | 0.9 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 87.9794 | 40.1588 | 955778.509 | 79.6482 | 79.6482 | 157.6422 | 1 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 90.7969 | 42.9763 | 1022835.6989 | 85.2363 | 85.2363 | 165.2463 | 80 | 60 | 33.5355 | 34 | 58.2
8/10/20XX 11:00:00 AM | 0.45833 | 3 | 81.9 | 55.9 | 81.7045 | 98.4363 | 16.7319 | 50 | 81.9 |  | 81.9 | 91.5763 | 0.1 | 74.79 | 19.79 | 748062 | 62.3385 | 62.3385 | 65.5171 | 17.6965 | 421175.8681 | 35.098 | 35.098 | 97.4365 | 0.2 | 75.58 | 20.58 | 777924 | 64.827 | 64.827 | 68.4126 | 20.5919 | 490087.9363 | 40.8407 | 40.8407 | 105.6677 | 0.3 | 76.37 | 21.37 | 807786 | 67.3155 | 67.3155 | 71.308 | 23.4874 | 559000.0044 | 46.5833 | 46.5833 | 113.8988 | 0.4 | 77.16 | 22.16 | 837648 | 69.804 | 69.804 | 74.2035 | 26.3829 | 627912.0725 | 52.326 | 52.326 | 122.13 | 0.5 | 77.95 | 22.95 | 867510 | 72.2925 | 72.2925 | 77.099 | 29.2783 | 696824.1407 | 58.0687 | 58.0687 | 130.3612 | 0.6 | 78.74 | 23.74 | 897372 | 74.781 | 74.781 | 79.9944 | 32.1738 | 765736.2088 | 63.8114 | 63.8114 | 138.5924 | 0.7 | 79.53 | 24.53 | 927234 | 77.2695 | 77.2695 | 82.8899 | 35.0693 | 834648.277 | 69.554 | 69.554 | 146.8235 | 0.8 | 80.32 | 25.32 | 957096 | 79.758 | 79.758 | 85.7854 | 37.9647 | 903560.3451 | 75.2967 | 75.2967 | 155.0547 | 0.9 | 81.11 | 26.11 | 986958 | 82.2465 | 82.2465 | 88.6808 | 40.8602 | 972472.4132 | 81.0394 | 81.0394 | 163.2859 | 1 | 81.9 | 26.9 | 1016820 | 84.735 | 84.735 | 91.5763 | 43.7557 | 1041384.4814 | 86.782 | 86.782 | 171.517 | 80 | 55 | 34.0264 | 34 | 55.9
8/10/20XX 12:00:00 PM | 0.5 | 3 | 82.3 | 56.7 | 82.7861 | 99.7431 | 16.957 | 50 | 82.3 |  | 82.3 | 94.1473 | 0.1 | 74.83 | 19.83 | 749574 | 62.4645 | 62.4645 | 65.7742 | 17.9536 | 427294.9084 | 35.6079 | 35.6079 | 98.0724 | 0.2 | 75.66 | 20.66 | 780948 | 65.079 | 65.079 | 68.9268 | 21.1061 | 502326.0169 | 41.8605 | 41.8605 | 106.9395 | 0.3 | 76.49 | 21.49 | 812322 | 67.6935 | 67.6935 | 72.0793 | 24.2587 | 577357.1253 | 48.1131 | 48.1131 | 115.8066 | 0.4 | 77.32 | 22.32 | 843696 | 70.308 | 70.308 | 75.2319 | 27.4113 | 652388.2337 | 54.3657 | 54.3657 | 124.6737 | 0.5 | 78.15 | 23.15 | 875070 | 72.9225 | 72.9225 | 78.3845 | 30.5638 | 727419.3422 | 60.6183 | 60.6183 | 133.5408 | 0.6 | 78.98 | 23.98 | 906444 | 75.537 | 75.537 | 81.537 | 33.7164 | 802450.4506 | 66.8709 | 66.8709 | 142.4079 | 0.7 | 79.81 | 24.81 | 937818 | 78.1515 | 78.1515 | 84.6896 | 36.869 | 877481.5591 | 73.1235 | 73.1235 | 151.275 | 0.8 | 80.64 | 25.64 | 969192 | 80.766 | 80.766 | 87.8422 | 40.0215 | 952512.6675 | 79.3761 | 79.3761 | 160.1421 | 0.9 | 81.47 | 26.47 | 1000566 | 83.3805 | 83.3805 | 90.9947 | 43.1741 | 1027543.7759 | 85.6286 | 85.6286 | 169.0091 | 1 | 82.3 | 27.3 | 1031940 | 85.995 | 85.995 | 94.1473 | 46.3267 | 1102574.8844 | 91.8812 | 91.8812 | 177.8762 | 80 | 55 | 34.5283 | 34 | 56.7
8/10/20XX 1:00:00 PM | 0.54167 | 3 | 83.2 | 55.6 | 85.2627 | 102.7353 | 17.4726 | 50 | 83.2 |  | 83.2 | 95.0473 | 0.1 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 65.8642 | 18.0436 | 429436.9751 | 35.7864 | 35.7864 | 98.5344 | 0.2 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 69.1068 | 21.2861 | 506610.1502 | 42.2175 | 42.2175 | 107.8635 | 0.3 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 72.3493 | 24.5287 | 583783.3254 | 48.6486 | 48.6486 | 117.1926 | 0.4 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 75.5919 | 27.7713 | 660956.5005 | 55.0797 | 55.0797 | 126.5217 | 0.5 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 78.8345 | 31.0139 | 738129.6756 | 61.5108 | 61.5108 | 135.8508 | 0.6 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 82.0771 | 34.2564 | 815302.8507 | 67.9419 | 67.9419 | 145.1799 | 0.7 | 80.44 | 25.44 | 961632 | 80.136 | 80.136 | 85.3196 | 37.499 | 892476.0258 | 74.373 | 74.373 | 154.509 | 0.8 | 81.36 | 26.36 | 996408 | 83.034 | 83.034 | 88.5622 | 40.7416 | 969649.201 | 80.8041 | 80.8041 | 163.8381 | 0.9 | 82.28 | 27.28 | 1031184 | 85.932 | 85.932 | 91.8048 | 43.9841 | 1046822.3761 | 87.2352 | 87.2352 | 173.1672 | 1 | 83.2 | 28.2 | 1065960 | 88.83 | 88.83 | 95.0473 | 47.2267 | 1123995.5512 | 93.6663 | 93.6663 | 182.4963 | 85 | 55 | 34.891 | 34 | 55.6
8/10/20XX 2:00:00 PM | 0.58333 | 3 | 83.9 | 53.4 | 87.2303 | 105.1128 | 17.8825 | 50 | 83.9 |  | 83.9 | 93.3103 | 0.1 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 65.6905 | 17.8699 | 425302.9366 | 35.4419 | 35.4419 | 98.4104 | 0.2 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 68.7594 | 20.9387 | 498342.0732 | 41.5285 | 41.5285 | 107.6155 | 0.3 | 76.97 | 21.97 | 830466 | 69.2055 | 69.2055 | 71.8282 | 24.0076 | 571381.2098 | 47.6151 | 47.6151 | 116.8206 | 0.4 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 74.8971 | 27.0765 | 644420.3464 | 53.7017 | 53.7017 | 126.0257 | 0.5 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 77.966 | 30.1454 | 717459.483 | 59.7883 | 59.7883 | 135.2308 | 0.6 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 81.0349 | 33.2142 | 790498.6196 | 65.8749 | 65.8749 | 144.4359 | 0.7 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 84.1037 | 36.2831 | 863537.7561 | 71.9615 | 71.9615 | 153.641 | 0.8 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 87.1726 | 39.352 | 936576.8927 | 78.0481 | 78.0481 | 162.8461 | 0.9 | 82.91 | 27.91 | 1054998 | 87.9165 | 87.9165 | 90.2415 | 42.4208 | 1009616.0293 | 84.1347 | 84.1347 | 172.0512 | 1 | 83.9 | 28.9 | 1092420 | 91.035 | 91.035 | 93.3103 | 45.4897 | 1082655.1659 | 90.2213 | 90.2213 | 181.2563 | 85 | 55 | 34.7904 | 34 | 53.4
8/10/20XX 3:00:00 PM | 0.625 | 3 | 83.2 | 54.2 | 85.2627 | 102.7353 | 17.4726 | 50 | 83.2 |  | 83.2 | 92.6012 | 0.1 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 65.6196 | 17.799 | 423615.1013 | 35.3013 | 35.3013 | 98.0493 | 0.2 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 68.6175 | 20.7969 | 494966.4026 | 41.2472 | 41.2472 | 106.8932 | 0.3 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 71.6155 | 23.7949 | 566317.7039 | 47.1931 | 47.1931 | 115.7371 | 0.4 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 74.6134 | 26.7928 | 637669.0052 | 53.1391 | 53.1391 | 124.5811 | 0.5 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 77.6114 | 29.7908 | 709020.3065 | 59.085 | 59.085 | 133.425 | 0.6 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 80.6094 | 32.7887 | 780371.6078 | 65.031 | 65.031 | 142.269 | 0.7 | 80.44 | 25.44 | 961632 | 80.136 | 80.136 | 83.6073 | 35.7867 | 851722.9091 | 70.9769 | 70.9769 | 151.1129 | 0.8 | 81.36 | 26.36 | 996408 | 83.034 | 83.034 | 86.6053 | 38.7846 | 923074.2104 | 76.9229 | 76.9229 | 159.9569 | 0.9 | 82.28 | 27.28 | 1031184 | 85.932 | 85.932 | 89.6032 | 41.7826 | 994425.5117 | 82.8688 | 82.8688 | 168.8008 | 1 | 83.2 | 28.2 | 1065960 | 88.83 | 88.83 | 92.6012 | 44.7805 | 1065776.813 | 88.8147 | 88.8147 | 177.6447 | 85 | 55 | 34.5069 | 34 | 54.2
8/10/20XX 4:00:00 PM | 0.66667 | 3 | 82.7 | 55.2 | 83.8795 | 101.064 | 17.1846 | 50 | 82.7 |  | 82.7 | 92.8154 | 0.1 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 65.641 | 17.8204 | 424125.0842 | 35.3438 | 35.3438 | 97.9343 | 0.2 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 68.6604 | 20.8398 | 495986.3684 | 41.3322 | 41.3322 | 106.6632 | 0.3 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 71.6798 | 23.8591 | 567847.6526 | 47.3206 | 47.3206 | 115.3921 | 0.4 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 74.6992 | 26.8785 | 639708.9367 | 53.3091 | 53.3091 | 124.1211 | 0.5 | 78.35 | 23.35 | 882630 | 73.5525 | 73.5525 | 77.7185 | 29.8979 | 711570.2209 | 59.2975 | 59.2975 | 132.85 | 0.6 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 80.7379 | 32.9173 | 783431.5051 | 65.286 | 65.286 | 141.579 | 0.7 | 80.09 | 25.09 | 948402 | 79.0335 | 79.0335 | 83.7573 | 35.9367 | 855292.7893 | 71.2744 | 71.2744 | 150.3079 | 0.8 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 86.7767 | 38.9561 | 927154.0735 | 77.2628 | 77.2628 | 159.0368 | 0.9 | 81.83 | 26.83 | 1014174 | 84.5145 | 84.5145 | 89.7961 | 41.9754 | 999015.3577 | 83.2513 | 83.2513 | 167.7658 | 1 | 82.7 | 27.7 | 1047060 | 87.255 | 87.255 | 92.8154 | 44.9948 | 1070876.6419 | 89.2397 | 89.2397 | 176.4947 | 85 | 55 | 34.4176 | 34 | 55.2
8/10/20XX 5:00:00 PM | 0.70833 | 3 | 82.6 | 54.3 | 83.605 | 100.7325 | 17.1274 | 50 | 82.6 |  | 82.6 | 90.9698 | 0.1 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 65.4565 | 17.6358 | 419732.5289 | 34.9777 | 34.9777 | 97.5367 | 0.2 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 68.2913 | 20.4706 | 487201.2578 | 40.6001 | 40.6001 | 105.8681 | 0.3 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 71.1261 | 23.3055 | 554669.9866 | 46.2225 | 46.2225 | 114.1995 | 0.4 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 73.9609 | 26.1403 | 622138.7155 | 51.8449 | 51.8449 | 122.5309 | 0.5 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 76.7957 | 28.9751 | 689607.4444 | 57.4673 | 57.4673 | 130.8623 | 0.6 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 79.6306 | 31.8099 | 757076.1733 | 63.0897 | 63.0897 | 139.1937 | 0.7 | 80.02 | 25.02 | 945756 | 78.813 | 78.813 | 82.4654 | 34.6447 | 824544.9022 | 68.7121 | 68.7121 | 147.5251 | 0.8 | 80.88 | 25.88 | 978264 | 81.522 | 81.522 | 85.3002 | 37.4796 | 892013.6311 | 74.3345 | 74.3345 | 155.8565 | 0.9 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 88.135 | 40.3144 | 959482.3599 | 79.9569 | 79.9569 | 164.1879 | 1 | 82.6 | 27.6 | 1043280 | 86.94 | 86.94 | 90.9698 | 43.1492 | 1026951.0888 | 85.5793 | 85.5793 | 172.5193 | 85 | 55 | 34.1033 | 34 | 54.3
8/10/20XX 6:00:00 PM | 0.75 | 3 | 81.3 | 56.9 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 91.4189 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 65.5014 | 17.6807 | 420801.3851 | 35.0668 | 35.0668 | 97.2163 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 68.3811 | 20.5605 | 489338.9702 | 40.7782 | 40.7782 | 105.2272 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 71.2608 | 23.4402 | 557876.5552 | 46.4897 | 46.4897 | 113.2382 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 74.1406 | 26.3199 | 626414.1403 | 52.2012 | 52.2012 | 121.2492 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 77.0203 | 29.1997 | 694951.7254 | 57.9126 | 57.9126 | 129.2601 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 79.9 | 32.0794 | 763489.3105 | 63.6241 | 63.6241 | 137.2711 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 82.7797 | 34.9591 | 832026.8956 | 69.3356 | 69.3356 | 145.2821 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 85.6595 | 37.8388 | 900564.4807 | 75.047 | 75.047 | 153.293 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 88.5392 | 40.7186 | 969102.0657 | 80.7585 | 80.7585 | 161.304 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 91.4189 | 43.5983 | 1037639.6508 | 86.47 | 86.47 | 169.315 | 80 | 55 | 33.8543 | 34 | 56.9
8/10/20XX 7:00:00 PM | 0.79167 | 3 | 80.5 | 57.6 | 78.0095 | 93.973 | 15.9635 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/10/20XX 8:00:00 PM | 0.83333 | 3 | 79.4 | 58.6 | 75.2039 | 90.5845 | 15.3806 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/10/20XX 9:00:00 PM | 0.875 | 3 | 78.3 | 59.2 | 72.4824 | 87.2982 | 14.8157 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/10/20XX 10:00:00 PM | 0.91667 | 3 | 77.7 | 61.5 | 85.548 | 100.1379 | 14.59 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/10/20XX 11:00:00 PM | 0.95833 | 3 | 77.3 | 62.7 | 84.3976 | 98.7873 | 14.3897 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/10/20XX 12:00:00 AM | 0 | 4 | 76.7 | 64 | 82.6964 | 96.79 | 14.0936 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/11/20XX 1:00:00 AM | 0.041667 | 4 | 76.5 | 65.1 | 82.1358 | 96.1318 | 13.9961 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/11/20XX 2:00:00 AM | 0.083333 | 4 | 75.3 | 68.3 | 78.8391 | 92.2616 | 13.4225 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/11/20XX 3:00:00 AM | 0.125 | 4 | 74.3 | 71 | 89.138 | 102.1877 | 13.0496 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/11/20XX 4:00:00 AM | 0.16667 | 4 | 73.8 | 71.7 | 87.6104 | 100.4307 | 12.8203 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/11/20XX 5:00:00 AM | 0.20833 | 4 | 73.4 | 73.4 | 86.4044 | 99.0438 | 12.6394 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/11/20XX 6:00:00 AM | 0.25 | 4 | 73.1 | 75.1 | 85.5092 | 98.0145 | 12.5053 | 70 | 73.1 |  | 73.1 | 91.8869 | 0.1 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 65.5482 | 17.7275 | 421915.1775 | 35.1596 | 35.1596 | 94.7261 | 0.2 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 68.4747 | 20.6541 | 491566.5551 | 40.9639 | 40.9639 | 100.2469 | 0.3 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 71.4012 | 23.5806 | 561217.9326 | 46.7682 | 46.7682 | 105.7677 | 0.4 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 74.3277 | 26.5071 | 630869.3101 | 52.5724 | 52.5724 | 111.2884 | 0.5 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 77.2543 | 29.4336 | 700520.6877 | 58.3767 | 58.3767 | 116.8092 | 0.6 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 80.1808 | 32.3602 | 770172.0652 | 64.181 | 64.181 | 122.33 | 0.7 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 83.1073 | 35.2867 | 839823.4427 | 69.9853 | 69.9853 | 127.8508 | 0.8 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 86.0339 | 38.2132 | 909474.8203 | 75.7896 | 75.7896 | 133.3716 | 0.9 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 88.9604 | 41.1398 | 979126.1978 | 81.5938 | 81.5938 | 138.8923 | 1 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 91.8869 | 44.0663 | 1048777.5753 | 87.3981 | 87.3981 | 144.4131 | 75 | 75 | 31.9118 | 32 | 75.1
8/11/20XX 7:00:00 AM | 0.29167 | 4 | 74.1 | 72.9 | 88.5243 | 101.4817 | 12.9575 | 70 | 74.1 |  | 74.1 | 92.2819 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 65.5877 | 17.767 | 422855.3158 | 35.2379 | 35.2379 | 95.1194 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 68.5537 | 20.7331 | 493446.8316 | 41.1206 | 41.1206 | 101.0336 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 71.5197 | 23.6991 | 564038.3475 | 47.0032 | 47.0032 | 106.9477 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 74.4858 | 26.6651 | 634629.8633 | 52.8858 | 52.8858 | 112.8618 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 77.4518 | 29.6312 | 705221.3791 | 58.7684 | 58.7684 | 118.7759 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 80.4178 | 32.5972 | 775812.8949 | 64.6511 | 64.6511 | 124.6901 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 83.3838 | 35.5632 | 846404.4107 | 70.5337 | 70.5337 | 130.6042 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 86.3499 | 38.5292 | 916995.9265 | 76.4163 | 76.4163 | 136.5183 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 89.3159 | 41.4953 | 987587.4424 | 82.299 | 82.299 | 142.4325 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 92.2819 | 44.4613 | 1058178.9582 | 88.1816 | 88.1816 | 148.3466 | 75 | 75 | 32.2195 | 32 | 72.9
8/11/20XX 8:00:00 AM | 0.33333 | 4 | 75.3 | 70.5 | 92.2616 | 105.7806 | 13.519 | 70 | 75.3 |  | 75.3 | 92.9376 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 65.6532 | 17.8326 | 424415.6884 | 35.368 | 35.368 | 95.6275 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 68.6848 | 20.8642 | 496567.5768 | 41.3806 | 41.3806 | 102.0496 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 71.7164 | 23.8958 | 568719.4652 | 47.3933 | 47.3933 | 108.4718 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 74.748 | 26.9274 | 640871.3536 | 53.4059 | 53.4059 | 114.8939 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 77.7796 | 29.959 | 713023.242 | 59.4186 | 59.4186 | 121.3161 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 80.8112 | 32.9906 | 785175.1303 | 65.4313 | 65.4313 | 127.7383 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 83.8428 | 36.0221 | 857327.0187 | 71.4439 | 71.4439 | 134.1604 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 86.8744 | 39.0537 | 929478.9071 | 77.4566 | 77.4566 | 140.5826 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 89.906 | 42.0853 | 1001630.7955 | 83.4692 | 83.4692 | 147.0047 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 92.9376 | 45.1169 | 1073782.6839 | 89.4819 | 89.4819 | 153.4269 | 75 | 70 | 32.6171 | 32 | 70.5
8/11/20XX 9:00:00 AM | 0.375 | 4 | 76.8 | 67.4 | 82.9779 | 97.1205 | 14.1426 | 60 | 76.8 |  | 76.8 | 93.4434 | 0.1 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 65.7038 | 17.8832 | 425619.6821 | 35.4683 | 35.4683 | 96.2003 | 0.2 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 68.786 | 20.9654 | 498975.5642 | 41.5813 | 41.5813 | 103.1953 | 0.3 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 71.8682 | 24.0475 | 572331.4463 | 47.6943 | 47.6943 | 110.1903 | 0.4 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 74.9504 | 27.1297 | 645687.3285 | 53.8073 | 53.8073 | 117.1853 | 0.5 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 78.0325 | 30.2119 | 719043.2106 | 59.9203 | 59.9203 | 124.1803 | 0.6 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 81.1147 | 33.2941 | 792399.0927 | 66.0333 | 66.0333 | 131.1753 | 0.7 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 84.1969 | 36.3763 | 865754.9748 | 72.1462 | 72.1462 | 138.1702 | 0.8 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 87.2791 | 39.4584 | 939110.8569 | 78.2592 | 78.2592 | 145.1652 | 0.9 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 90.3613 | 42.5406 | 1012466.739 | 84.3722 | 84.3722 | 152.1602 | 1 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 93.4434 | 45.6228 | 1085822.6212 | 90.4852 | 90.4852 | 159.1552 | 75 | 65 | 33.0652 | 34 | 67.4
8/11/20XX 10:00:00 AM | 0.41667 | 4 | 77.9 | 65.3 | 86.1281 | 100.819 | 14.691 | 60 | 77.9 |  | 77.9 | 93.9143 | 0.1 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 65.7509 | 17.9303 | 426740.276 | 35.5617 | 35.5617 | 96.6402 | 0.2 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 68.8802 | 21.0595 | 501216.752 | 41.7681 | 41.7681 | 104.0751 | 0.3 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 72.0094 | 24.1888 | 575693.228 | 47.9744 | 47.9744 | 111.5099 | 0.4 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 75.1387 | 27.3181 | 650169.7039 | 54.1808 | 54.1808 | 118.9448 | 0.5 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 78.268 | 30.4473 | 724646.1799 | 60.3872 | 60.3872 | 126.3797 | 0.6 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 81.3972 | 33.5766 | 799122.6559 | 66.5936 | 66.5936 | 133.8146 | 0.7 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 84.5265 | 36.7058 | 873599.1319 | 72.7999 | 72.7999 | 141.2494 | 0.8 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 87.6557 | 39.8351 | 948075.6079 | 79.0063 | 79.0063 | 148.6843 | 0.9 | 77.51 | 22.51 | 850878 | 70.9065 | 70.9065 | 90.785 | 42.9644 | 1022552.0839 | 85.2127 | 85.2127 | 156.1192 | 1 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 93.9143 | 46.0936 | 1097028.5599 | 91.419 | 91.419 | 163.554 | 80 | 65 | 33.4095 | 34 | 65.3
8/11/20XX 11:00:00 AM | 0.45833 | 4 | 81.1 | 57.9 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 92.4443 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 65.6039 | 17.7833 | 423241.6895 | 35.2701 | 35.2701 | 97.3566 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 68.5862 | 20.7655 | 494219.5791 | 41.185 | 41.185 | 105.508 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 71.5684 | 23.7478 | 565197.4686 | 47.0998 | 47.0998 | 113.6593 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 74.5507 | 26.7301 | 636175.3582 | 53.0146 | 53.0146 | 121.8106 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 77.533 | 29.7123 | 707153.2477 | 58.9294 | 58.9294 | 129.9619 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 80.5152 | 32.6946 | 778131.1372 | 64.8443 | 64.8443 | 138.1133 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 83.4975 | 35.6768 | 849109.0268 | 70.7591 | 70.7591 | 146.2646 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 86.4797 | 38.6591 | 920086.9163 | 76.6739 | 76.6739 | 154.4159 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 89.462 | 41.6414 | 991064.8059 | 82.5887 | 82.5887 | 162.5672 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 92.4443 | 44.6236 | 1062042.6954 | 88.5036 | 88.5036 | 170.7186 | 80 | 60 | 33.9659 | 34 | 57.9
8/11/20XX 12:00:00 PM | 0.5 | 4 | 82.1 | 56.1 | 82.2439 | 99.088 | 16.8441 | 50 | 82.1 |  | 82.1 | 92.5188 | 0.1 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 65.6113 | 17.7907 | 423418.965 | 35.2849 | 35.2849 | 97.6864 | 0.2 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 68.6011 | 20.7804 | 494574.13 | 41.2145 | 41.2145 | 106.1675 | 0.3 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 71.5908 | 23.7701 | 565729.2949 | 47.1441 | 47.1441 | 114.6486 | 0.4 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 74.5805 | 26.7599 | 636884.4599 | 53.0737 | 53.0737 | 123.1297 | 0.5 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 77.5702 | 29.7496 | 708039.6249 | 59.0033 | 59.0033 | 131.6108 | 0.6 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 80.5599 | 32.7393 | 779194.7899 | 64.9329 | 64.9329 | 140.0919 | 0.7 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 83.5496 | 35.729 | 850349.9549 | 70.8625 | 70.8625 | 148.573 | 0.8 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 86.5393 | 38.7187 | 921505.1198 | 76.7921 | 76.7921 | 157.0541 | 0.9 | 81.29 | 26.29 | 993762 | 82.8135 | 82.8135 | 89.529 | 41.7084 | 992660.2848 | 82.7217 | 82.7217 | 165.5352 | 1 | 82.1 | 27.1 | 1024380 | 85.365 | 85.365 | 92.5188 | 44.6981 | 1063815.4498 | 88.6513 | 88.6513 | 174.0163 | 80 | 55 | 34.2235 | 34 | 56.1
8/11/20XX 1:00:00 PM | 0.54167 | 4 | 82.9 | 55.2 | 84.4305 | 101.7299 | 17.2993 | 50 | 82.9 |  | 82.9 | 93.4262 | 0.1 | 74.89 | 19.89 | 751842 | 62.6535 | 62.6535 | 65.7021 | 17.8815 | 425578.6338 | 35.4649 | 35.4649 | 98.1184 | 0.2 | 75.78 | 20.78 | 785484 | 65.457 | 65.457 | 68.7825 | 20.9619 | 498893.4675 | 41.5745 | 41.5745 | 107.0315 | 0.3 | 76.67 | 21.67 | 819126 | 68.2605 | 68.2605 | 71.863 | 24.0424 | 572208.3013 | 47.684 | 47.684 | 115.9445 | 0.4 | 77.56 | 22.56 | 852768 | 71.064 | 71.064 | 74.9435 | 27.1228 | 645523.1351 | 53.7936 | 53.7936 | 124.8576 | 0.5 | 78.45 | 23.45 | 886410 | 73.8675 | 73.8675 | 78.0239 | 30.2033 | 718837.9688 | 59.9032 | 59.9032 | 133.7707 | 0.6 | 79.34 | 24.34 | 920052 | 76.671 | 76.671 | 81.1044 | 33.2837 | 792152.8026 | 66.0127 | 66.0127 | 142.6837 | 0.7 | 80.23 | 25.23 | 953694 | 79.4745 | 79.4745 | 84.1848 | 36.3642 | 865467.6363 | 72.1223 | 72.1223 | 151.5968 | 0.8 | 81.12 | 26.12 | 987336 | 82.278 | 82.278 | 87.2653 | 39.4446 | 938782.4701 | 78.2319 | 78.2319 | 160.5099 | 0.9 | 82.01 | 27.01 | 1020978 | 85.0815 | 85.0815 | 90.3457 | 42.5251 | 1012097.3039 | 84.3414 | 84.3414 | 169.4229 | 1 | 82.9 | 27.9 | 1054620 | 87.885 | 87.885 | 93.4262 | 45.6056 | 1085412.1376 | 90.451 | 90.451 | 178.336 | 85 | 55 | 34.5626 | 34 | 55.2
8/11/20XX 2:00:00 PM | 0.58333 | 4 | 82.6 | 55.9 | 83.605 | 100.7325 | 17.1274 | 50 | 82.6 |  | 82.6 | 93.7102 | 0.1 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 65.7305 | 17.9099 | 426254.6551 | 35.5212 | 35.5212 | 98.0802 | 0.2 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 68.8394 | 21.0187 | 500245.5102 | 41.6871 | 41.6871 | 106.9551 | 0.3 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 71.9482 | 24.1276 | 574236.3653 | 47.853 | 47.853 | 115.83 | 0.4 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 75.0571 | 27.2364 | 648227.2204 | 54.0189 | 54.0189 | 124.7049 | 0.5 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 78.1659 | 30.3453 | 722218.0755 | 60.1848 | 60.1848 | 133.5798 | 0.6 | 79.16 | 24.16 | 913248 | 76.104 | 76.104 | 81.2748 | 33.4542 | 796208.9306 | 66.3507 | 66.3507 | 142.4547 | 0.7 | 80.02 | 25.02 | 945756 | 78.813 | 78.813 | 84.3836 | 36.563 | 870199.7857 | 72.5166 | 72.5166 | 151.3296 | 0.8 | 80.88 | 25.88 | 978264 | 81.522 | 81.522 | 87.4925 | 39.6719 | 944190.6408 | 78.6826 | 78.6826 | 160.2046 | 0.9 | 81.74 | 26.74 | 1010772 | 84.231 | 84.231 | 90.6014 | 42.7807 | 1018181.4959 | 84.8485 | 84.8485 | 169.0795 | 1 | 82.6 | 27.6 | 1043280 | 86.94 | 86.94 | 93.7102 | 45.8896 | 1092172.351 | 91.0144 | 91.0144 | 177.9544 | 85 | 55 | 34.5335 | 34 | 55.9
8/11/20XX 3:00:00 PM | 0.625 | 4 | 82.1 | 56.7 | 82.2439 | 99.088 | 16.8441 | 50 | 82.1 |  | 82.1 | 93.5294 | 0.1 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 65.7124 | 17.8918 | 425824.3032 | 35.4854 | 35.4854 | 97.8869 | 0.2 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 68.8032 | 20.9826 | 499384.8064 | 41.6154 | 41.6154 | 106.5684 | 0.3 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 71.894 | 24.0733 | 572945.3096 | 47.7454 | 47.7454 | 115.2499 | 0.4 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 74.9847 | 27.1641 | 646505.8128 | 53.8755 | 53.8755 | 123.9315 | 0.5 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 78.0755 | 30.2549 | 720066.316 | 60.0055 | 60.0055 | 132.613 | 0.6 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 81.1663 | 33.3457 | 793626.8192 | 66.1356 | 66.1356 | 141.2946 | 0.7 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 84.2571 | 36.4364 | 867187.3224 | 72.2656 | 72.2656 | 149.9761 | 0.8 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 87.3479 | 39.5272 | 940747.8256 | 78.3957 | 78.3957 | 158.6577 | 0.9 | 81.29 | 26.29 | 993762 | 82.8135 | 82.8135 | 90.4386 | 42.618 | 1014308.3288 | 84.5257 | 84.5257 | 167.3392 | 1 | 82.1 | 27.1 | 1024380 | 85.365 | 85.365 | 93.5294 | 45.7088 | 1087868.832 | 90.6557 | 90.6557 | 176.0207 | 80 | 55 | 34.3821 | 34 | 56.7
8/11/20XX 4:00:00 PM | 0.66667 | 4 | 81.3 | 58.1 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 93.3868 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 65.6981 | 17.8775 | 425484.9014 | 35.4571 | 35.4571 | 97.6066 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 68.7747 | 20.954 | 498706.0028 | 41.5588 | 41.5588 | 106.0078 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 71.8512 | 24.0306 | 571927.1042 | 47.6606 | 47.6606 | 114.4091 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 74.9277 | 27.1071 | 645148.2056 | 53.7624 | 53.7624 | 122.8104 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 78.0042 | 30.1836 | 718369.307 | 59.8641 | 59.8641 | 131.2116 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 81.0807 | 33.2601 | 791590.4084 | 65.9659 | 65.9659 | 139.6129 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 84.1573 | 36.3366 | 864811.5099 | 72.0676 | 72.0676 | 148.0141 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 87.2338 | 39.4131 | 938032.6113 | 78.1694 | 78.1694 | 156.4154 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 90.3103 | 42.4897 | 1011253.7127 | 84.2711 | 84.2711 | 164.8166 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 93.3868 | 45.5662 | 1084474.8141 | 90.3729 | 90.3729 | 173.2179 | 80 | 60 | 34.163 | 34 | 58.1
8/11/20XX 5:00:00 PM | 0.70833 | 4 | 80 | 60.3 | 92.42 | 108.2066 | 15.7866 | 60 | 80 |  | 80 | 92.8936 | 0.1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 65.6488 | 17.8282 | 424311.0415 | 35.3593 | 35.3593 | 97.0993 | 0.2 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 68.676 | 20.8554 | 496358.2829 | 41.3632 | 41.3632 | 104.9932 | 0.3 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 71.7032 | 23.8826 | 568405.5244 | 47.3671 | 47.3671 | 112.8871 | 0.4 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 74.7304 | 26.9098 | 640452.7659 | 53.3711 | 53.3711 | 120.7811 | 0.5 | 77 | 22 | 831600 | 69.3 | 69.3 | 77.7576 | 29.937 | 712500.0073 | 59.375 | 59.375 | 128.675 | 0.6 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 80.7848 | 32.9642 | 784547.2488 | 65.3789 | 65.3789 | 136.5689 | 0.7 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 83.812 | 35.9914 | 856594.4902 | 71.3829 | 71.3829 | 144.4629 | 0.8 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 86.8392 | 39.0186 | 928641.7317 | 77.3868 | 77.3868 | 152.3568 | 0.9 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 89.8664 | 42.0458 | 1000688.9732 | 83.3907 | 83.3907 | 160.2507 | 1 | 80 | 25 | 945000 | 78.75 | 78.75 | 92.8936 | 45.073 | 1072736.2146 | 89.3947 | 89.3947 | 168.1447 | 80 | 60 | 33.7659 | 34 | 60.3
8/11/20XX 6:00:00 PM | 0.75 | 4 | 78.6 | 63.3 | 88.1844 | 103.2334 | 15.049 | 60 | 78.6 |  | 78.6 | 93.1506 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 65.6745 | 17.8539 | 424922.6845 | 35.4102 | 35.4102 | 96.7092 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 68.7274 | 20.9068 | 497581.5691 | 41.4651 | 41.4651 | 104.2131 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 71.7803 | 23.9597 | 570240.4536 | 47.52 | 47.52 | 111.717 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 74.8332 | 27.0126 | 642899.3382 | 53.5749 | 53.5749 | 119.2209 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 77.8861 | 30.0655 | 715558.2227 | 59.6299 | 59.6299 | 126.7249 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 80.939 | 33.1184 | 788217.1073 | 65.6848 | 65.6848 | 134.2288 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 83.9919 | 36.1713 | 860875.9918 | 71.7397 | 71.7397 | 141.7327 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 87.0448 | 39.2242 | 933534.8764 | 77.7946 | 77.7946 | 149.2366 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 90.0977 | 42.277 | 1006193.7609 | 83.8495 | 83.8495 | 156.7405 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 93.1506 | 45.3299 | 1078852.6454 | 89.9044 | 89.9044 | 164.2444 | 80 | 65 | 33.462 | 34 | 63.3
8/11/20XX 7:00:00 PM | 0.79167 | 4 | 77.7 | 65 | 85.548 | 100.1379 | 14.59 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/11/20XX 8:00:00 PM | 0.83333 | 4 | 76.9 | 66.3 | 83.2602 | 97.452 | 14.1918 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/11/20XX 9:00:00 PM | 0.875 | 4 | 76.5 | 68.1 | 82.1358 | 96.1318 | 13.9961 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/11/20XX 10:00:00 PM | 0.91667 | 4 | 76 | 69.8 | 80.7483 | 94.5029 | 13.7546 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/11/20XX 11:00:00 PM | 0.95833 | 4 | 75.8 | 71.3 | 93.8579 | 107.6171 | 13.7592 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/11/20XX 12:00:00 AM | 0 | 5 | 74.1 | 75.2 | 88.5243 | 101.4817 | 12.9575 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/12/20XX 1:00:00 AM | 0.041667 | 5 | 73.2 | 77.4 | 85.8067 | 98.3566 | 12.5498 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/12/20XX 2:00:00 AM | 0.083333 | 5 | 72.3 | 78.8 | 83.1611 | 95.3147 | 12.1536 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/12/20XX 3:00:00 AM | 0.125 | 5 | 72.1 | 79.8 | 82.5828 | 94.6498 | 12.0671 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/12/20XX 4:00:00 AM | 0.16667 | 5 | 71.6 | 81.3 | 93.0054 | 104.8714 | 11.866 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/12/20XX 5:00:00 AM | 0.20833 | 5 | 71.7 | 80.2 | 93.3322 | 105.2414 | 11.9091 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/12/20XX 6:00:00 AM | 0.25 | 5 | 71.7 | 78.8 | 81.4366 | 93.3322 | 11.8956 | 70 | 71.7 |  | 71.7 | 91.9048 | 0.1 | 73.77 | 18.77 | 709506 | 59.1255 | 59.1255 | 65.5499 | 17.7293 | 421957.6717 | 35.1631 | 35.1631 | 94.2886 | 0.2 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 68.4783 | 20.6576 | 491651.5433 | 40.971 | 40.971 | 99.372 | 0.3 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 71.4066 | 23.5859 | 561345.415 | 46.7788 | 46.7788 | 104.4553 | 0.4 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 74.3349 | 26.5143 | 631039.2867 | 52.5866 | 52.5866 | 109.5386 | 0.5 | 72.85 | 17.85 | 674730 | 56.2275 | 56.2275 | 77.2632 | 29.4426 | 700733.1583 | 58.3944 | 58.3944 | 114.6219 | 0.6 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 80.1915 | 32.3709 | 770427.03 | 64.2023 | 64.2023 | 119.7053 | 0.7 | 72.39 | 17.39 | 657342 | 54.7785 | 54.7785 | 83.1198 | 35.2992 | 840120.9016 | 70.0101 | 70.0101 | 124.7886 | 0.8 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 86.0481 | 38.2275 | 909814.7733 | 75.8179 | 75.8179 | 129.8719 | 0.9 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 88.9765 | 41.1558 | 979508.645 | 81.6257 | 81.6257 | 134.9552 | 1 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 91.9048 | 44.0841 | 1049202.5166 | 87.4335 | 87.4335 | 140.0385 | 70 | 80 | 31.5705 | 32 | 78.8
8/12/20XX 7:00:00 AM | 0.29167 | 5 | 72.2 | 77.7 | 82.8715 | 94.9817 | 12.1103 | 70 | 72.2 |  | 72.2 | 92.1964 | 0.1 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 65.5791 | 17.7585 | 422651.7 | 35.221 | 35.221 | 94.504 | 0.2 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 68.5366 | 20.7159 | 493039.5999 | 41.0866 | 41.0866 | 99.8026 | 0.3 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 71.4941 | 23.6734 | 563427.4999 | 46.9523 | 46.9523 | 105.1013 | 0.4 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 74.4515 | 26.6309 | 633815.3999 | 52.8179 | 52.8179 | 110.3999 | 0.5 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 77.409 | 29.5884 | 704203.2999 | 58.6836 | 58.6836 | 115.6986 | 0.6 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 80.3665 | 32.5458 | 774591.1998 | 64.5493 | 64.5493 | 120.9973 | 0.7 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 83.324 | 35.5033 | 844979.0998 | 70.4149 | 70.4149 | 126.2959 | 0.8 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 86.2814 | 38.4608 | 915366.9998 | 76.2806 | 76.2806 | 131.5946 | 0.9 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 89.2389 | 41.4183 | 985754.8997 | 82.1462 | 82.1462 | 136.8932 | 1 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 92.1964 | 44.3757 | 1056142.7997 | 88.0119 | 88.0119 | 142.1919 | 70 | 80 | 31.739 | 32 | 77.7
8/12/20XX 8:00:00 AM | 0.33333 | 5 | 73.5 | 75.1 | 86.7045 | 99.389 | 12.6844 | 70 | 73.5 |  | 73.5 | 93.1736 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 65.6768 | 17.8562 | 424977.4646 | 35.4148 | 35.4148 | 95.1073 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 68.732 | 20.9114 | 497691.1292 | 41.4743 | 41.4743 | 101.0093 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 71.7872 | 23.9666 | 570404.7938 | 47.5337 | 47.5337 | 106.9112 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 74.8424 | 27.0218 | 643118.4584 | 53.5932 | 53.5932 | 112.8132 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 77.8976 | 30.077 | 715832.123 | 59.6527 | 59.6527 | 118.7152 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 80.9528 | 33.1322 | 788545.7876 | 65.7121 | 65.7121 | 124.6171 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 84.008 | 36.1874 | 861259.4522 | 71.7716 | 71.7716 | 130.5191 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 87.0632 | 39.2426 | 933973.1167 | 77.8311 | 77.8311 | 136.4211 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 90.1184 | 42.2978 | 1006686.7813 | 83.8906 | 83.8906 | 142.3231 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 93.1736 | 45.353 | 1079400.4459 | 89.95 | 89.95 | 148.225 | 75 | 75 | 32.2114 | 32 | 75.1
8/12/20XX 9:00:00 AM | 0.375 | 5 | 75.2 | 72.7 | 91.9451 | 105.4166 | 13.4714 | 70 | 75.2 |  | 75.2 | 95.5824 | 0.1 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.9177 | 18.0971 | 430710.4468 | 35.8925 | 35.8925 | 96.1205 | 0.2 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 69.2138 | 21.3932 | 509157.0937 | 42.4298 | 42.4298 | 103.0358 | 0.3 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 72.5099 | 24.6892 | 587603.7405 | 48.967 | 48.967 | 109.951 | 0.4 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 75.8059 | 27.9853 | 666050.3874 | 55.5042 | 55.5042 | 116.8662 | 0.5 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 79.102 | 31.2814 | 744497.0342 | 62.0414 | 62.0414 | 123.7814 | 0.6 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 82.3981 | 34.5775 | 822943.6811 | 68.5786 | 68.5786 | 130.6966 | 0.7 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 85.6942 | 37.8735 | 901390.3279 | 75.1159 | 75.1159 | 137.6119 | 0.8 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 88.9903 | 41.1696 | 979836.9748 | 81.6531 | 81.6531 | 144.5271 | 0.9 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 92.2863 | 44.4657 | 1058283.6216 | 88.1903 | 88.1903 | 151.4423 | 1 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 95.5824 | 47.7618 | 1136730.2685 | 94.7275 | 94.7275 | 158.3575 | 75 | 75 | 33.0064 | 34 | 72.7
8/12/20XX 10:00:00 AM | 0.41667 | 5 | 76.3 | 69 | 81.5784 | 95.4774 | 13.8991 | 60 | 76.3 |  | 76.3 | 94.0875 | 0.1 | 74.23 | 19.23 | 726894 | 60.5745 | 60.5745 | 65.7682 | 17.9476 | 427152.6614 | 35.5961 | 35.5961 | 96.1706 | 0.2 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 68.9148 | 21.0942 | 502041.5228 | 41.8368 | 41.8368 | 103.1358 | 0.3 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 72.0614 | 24.2408 | 576930.3842 | 48.0775 | 48.0775 | 110.101 | 0.4 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 75.208 | 27.3874 | 651819.2456 | 54.3183 | 54.3183 | 117.0663 | 0.5 | 75.15 | 20.15 | 761670 | 63.4725 | 63.4725 | 78.3546 | 30.534 | 726708.107 | 60.559 | 60.559 | 124.0315 | 0.6 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 81.5012 | 33.6805 | 801596.9684 | 66.7997 | 66.7997 | 130.9967 | 0.7 | 75.61 | 20.61 | 779058 | 64.9215 | 64.9215 | 84.6478 | 36.8271 | 876485.8298 | 73.0405 | 73.0405 | 137.962 | 0.8 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 87.7944 | 39.9737 | 951374.6912 | 79.2812 | 79.2812 | 144.9272 | 0.9 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 90.9409 | 43.1203 | 1026263.5527 | 85.522 | 85.522 | 151.8925 | 1 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 94.0875 | 46.2669 | 1101152.4141 | 91.7627 | 91.7627 | 158.8577 | 75 | 70 | 33.043 | 34 | 69
8/12/20XX 11:00:00 AM | 0.45833 | 5 | 78.8 | 64 | 88.7794 | 103.932 | 15.1526 | 60 | 78.8 |  | 78.8 | 94.8404 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 65.8435 | 18.0229 | 428944.5771 | 35.7454 | 35.7454 | 97.1074 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 69.0654 | 21.2448 | 505625.3542 | 42.1354 | 42.1354 | 105.0094 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 72.2873 | 24.4666 | 582306.1314 | 48.5255 | 48.5255 | 112.9115 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 75.5092 | 27.6885 | 658986.9085 | 54.9156 | 54.9156 | 120.8136 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 78.731 | 30.9104 | 735667.6856 | 61.3056 | 61.3056 | 128.7156 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 81.9529 | 34.1323 | 812348.4627 | 67.6957 | 67.6957 | 136.6177 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 85.1748 | 37.3542 | 889029.2399 | 74.0858 | 74.0858 | 144.5198 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 88.3967 | 40.5761 | 965710.017 | 80.4758 | 80.4758 | 152.4218 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 91.6186 | 43.7979 | 1042390.7941 | 86.8659 | 86.8659 | 160.3239 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 94.8404 | 47.0198 | 1119071.5712 | 93.256 | 93.256 | 168.226 | 80 | 65 | 33.776 | 34 | 64
8/12/20XX 12:00:00 PM | 0.5 | 5 | 79.5 | 63.7 | 90.8883 | 106.4082 | 15.5199 | 60 | 79.5 |  | 79.5 | 96.6306 | 0.1 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 66.0225 | 18.2019 | 433205.2508 | 36.1004 | 36.1004 | 97.6829 | 0.2 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 69.4234 | 21.6028 | 514146.7016 | 42.8456 | 42.8456 | 106.1606 | 0.3 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 72.8243 | 25.0037 | 595088.1525 | 49.5907 | 49.5907 | 114.6382 | 0.4 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 76.2252 | 28.4046 | 676029.6033 | 56.3358 | 56.3358 | 123.1158 | 0.5 | 76.75 | 21.75 | 822150 | 68.5125 | 68.5125 | 79.6261 | 31.8055 | 756971.0541 | 63.0809 | 63.0809 | 131.5934 | 0.6 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 83.027 | 35.2064 | 837912.5049 | 69.826 | 69.826 | 140.071 | 0.7 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 86.4279 | 38.6073 | 918853.9558 | 76.5712 | 76.5712 | 148.5487 | 0.8 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 89.8288 | 42.0082 | 999795.4066 | 83.3163 | 83.3163 | 157.0263 | 0.9 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 93.2297 | 45.4091 | 1080736.8574 | 90.0614 | 90.0614 | 165.5039 | 1 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 96.6306 | 48.81 | 1161678.3082 | 96.8065 | 96.8065 | 173.9815 | 80 | 65 | 34.2288 | 34 | 63.7
8/12/20XX 1:00:00 PM | 0.54167 | 5 | 80.5 | 60.9 | 93.973 | 110.0302 | 16.0572 | 60 | 80.5 |  | 80.5 | 95.4181 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 65.9013 | 18.0807 | 430319.4723 | 35.86 | 35.86 | 97.7575 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 69.1809 | 21.3603 | 508375.1446 | 42.3646 | 42.3646 | 106.3096 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 72.4606 | 24.64 | 586430.8169 | 48.8692 | 48.8692 | 114.8617 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 75.7402 | 27.9196 | 664486.4892 | 55.3739 | 55.3739 | 123.4139 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 79.0199 | 31.1993 | 742542.1616 | 61.8785 | 61.8785 | 131.966 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 82.2995 | 34.4789 | 820597.8339 | 68.3832 | 68.3832 | 140.5182 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 85.5792 | 37.7586 | 898653.5062 | 74.8878 | 74.8878 | 149.0703 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 88.8588 | 41.0382 | 976709.1785 | 81.3924 | 81.3924 | 157.6224 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 92.1385 | 44.3179 | 1054764.8508 | 87.8971 | 87.8971 | 166.1746 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 95.4181 | 47.5975 | 1132820.5231 | 94.4017 | 94.4017 | 174.7267 | 80 | 60 | 34.2848 | 34 | 60.9
8/12/20XX 2:00:00 PM | 0.58333 | 5 | 80.6 | 59 | 78.2688 | 94.2862 | 16.0174 | 50 | 80.6 |  | 80.6 | 92.6844 | 0.1 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 65.6279 | 17.8073 | 423813.2494 | 35.3178 | 35.3178 | 97.2468 | 0.2 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 68.6342 | 20.8136 | 495362.6989 | 41.2802 | 41.2802 | 105.2882 | 0.3 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 71.6405 | 23.8198 | 566912.1483 | 47.2427 | 47.2427 | 113.3297 | 0.4 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 74.6467 | 26.8261 | 638461.5977 | 53.2051 | 53.2051 | 121.3711 | 0.5 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 77.653 | 29.8324 | 710011.0471 | 59.1676 | 59.1676 | 129.4126 | 0.6 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 80.6593 | 32.8387 | 781560.4966 | 65.13 | 65.13 | 137.454 | 0.7 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 83.6656 | 35.845 | 853109.946 | 71.0925 | 71.0925 | 145.4955 | 0.8 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 86.6719 | 38.8512 | 924659.3954 | 77.0549 | 77.0549 | 153.5369 | 0.9 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 89.6781 | 41.8575 | 996208.8448 | 83.0174 | 83.0174 | 161.5784 | 1 | 80.6 | 25.6 | 967680 | 80.64 | 80.64 | 92.6844 | 44.8638 | 1067758.2943 | 88.9799 | 88.9799 | 169.6199 | 80 | 60 | 33.8807 | 34 | 59
8/12/20XX 3:00:00 PM | 0.625 | 5 | 79.8 | 60.9 | 91.8048 | 107.4842 | 15.6795 | 60 | 79.8 |  | 79.8 | 93.2159 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 65.6811 | 17.8604 | 425078.1914 | 35.4232 | 35.4232 | 97.1002 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 68.7405 | 20.9199 | 497892.5828 | 41.491 | 41.491 | 104.995 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 71.7999 | 23.9793 | 570706.9742 | 47.5589 | 47.5589 | 112.8899 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 74.8593 | 27.0387 | 643521.3655 | 53.6268 | 53.6268 | 120.7848 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 77.9188 | 30.0981 | 716335.7569 | 59.6946 | 59.6946 | 128.6796 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 80.9782 | 33.1576 | 789150.1483 | 65.7625 | 65.7625 | 136.5745 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 84.0376 | 36.217 | 861964.5397 | 71.8304 | 71.8304 | 144.4694 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 87.0971 | 39.2764 | 934778.9311 | 77.8982 | 77.8982 | 152.3642 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 90.1565 | 42.3359 | 1007593.3225 | 83.9661 | 83.9661 | 160.2591 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 93.2159 | 45.3953 | 1080407.7138 | 90.034 | 90.034 | 168.154 | 80 | 60 | 33.7673 | 34 | 60.9
8/12/20XX 4:00:00 PM | 0.66667 | 5 | 79.5 | 64.4 | 90.8883 | 106.4082 | 15.5199 | 60 | 79.5 |  | 79.5 | 97.717 | 0.1 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 66.1312 | 18.3105 | 435790.8591 | 36.3159 | 36.3159 | 97.8984 | 0.2 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 69.6407 | 21.8201 | 519317.9182 | 43.2765 | 43.2765 | 106.5915 | 0.3 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 73.1503 | 25.3296 | 602844.9773 | 50.2371 | 50.2371 | 115.2846 | 0.4 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 76.6598 | 28.8392 | 686372.0364 | 57.1977 | 57.1977 | 123.9777 | 0.5 | 76.75 | 21.75 | 822150 | 68.5125 | 68.5125 | 80.1693 | 32.3487 | 769899.0955 | 64.1583 | 64.1583 | 132.6708 | 0.6 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 83.6789 | 35.8582 | 853426.1545 | 71.1188 | 71.1188 | 141.3638 | 0.7 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 87.1884 | 39.3678 | 936953.2136 | 78.0794 | 78.0794 | 150.0569 | 0.8 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 90.698 | 42.8773 | 1020480.2727 | 85.04 | 85.04 | 158.75 | 0.9 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 94.2075 | 46.3869 | 1104007.3318 | 92.0006 | 92.0006 | 167.4431 | 1 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 97.717 | 49.8964 | 1187534.3909 | 98.9612 | 98.9612 | 176.1362 | 80 | 65 | 34.3992 | 34 | 64.4
8/12/20XX 5:00:00 PM | 0.70833 | 5 | 79.5 | 63.4 | 90.8883 | 106.4082 | 15.5199 | 60 | 79.5 |  | 79.5 | 96.165 | 0.1 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 65.976 | 18.1553 | 432097.133 | 36.0081 | 36.0081 | 97.5906 | 0.2 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 69.3303 | 21.5097 | 511930.466 | 42.6609 | 42.6609 | 105.9759 | 0.3 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 72.6847 | 24.864 | 591763.799 | 49.3136 | 49.3136 | 114.3611 | 0.4 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 76.039 | 28.2184 | 671597.132 | 55.9664 | 55.9664 | 122.7464 | 0.5 | 76.75 | 21.75 | 822150 | 68.5125 | 68.5125 | 79.3933 | 31.5727 | 751430.465 | 62.6192 | 62.6192 | 131.1317 | 0.6 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 82.7477 | 34.9271 | 831263.798 | 69.272 | 69.272 | 139.517 | 0.7 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 86.102 | 38.2814 | 911097.131 | 75.9248 | 75.9248 | 147.9023 | 0.8 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 89.4564 | 41.6357 | 990930.464 | 82.5775 | 82.5775 | 156.2875 | 0.9 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 92.8107 | 44.9901 | 1070763.797 | 89.2303 | 89.2303 | 164.6728 | 1 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 96.165 | 48.3444 | 1150597.13 | 95.8831 | 95.8831 | 173.0581 | 80 | 65 | 34.1559 | 34 | 63.4
8/12/20XX 6:00:00 PM | 0.75 | 5 | 78.6 | 65.1 | 88.1844 | 103.2334 | 15.049 | 60 | 78.6 |  | 78.6 | 95.8594 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 65.9454 | 18.1248 | 431369.6687 | 35.9475 | 35.9475 | 97.2465 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 69.2692 | 21.4486 | 510475.5375 | 42.5396 | 42.5396 | 105.2876 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 72.593 | 24.7723 | 589581.4062 | 49.1318 | 49.1318 | 113.3288 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 75.9167 | 28.0961 | 668687.2749 | 55.7239 | 55.7239 | 121.3699 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 79.2405 | 31.4199 | 747793.1436 | 62.3161 | 62.3161 | 129.4111 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 82.5643 | 34.7437 | 826899.0124 | 68.9083 | 68.9083 | 137.4523 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 85.8881 | 38.0674 | 906004.8811 | 75.5004 | 75.5004 | 145.4934 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 89.2118 | 41.3912 | 985110.7498 | 82.0926 | 82.0926 | 153.5346 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 92.5356 | 44.715 | 1064216.6185 | 88.6847 | 88.6847 | 161.5757 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 95.8594 | 48.0388 | 1143322.4873 | 95.2769 | 95.2769 | 169.6169 | 80 | 65 | 33.8865 | 34 | 65.1
8/12/20XX 7:00:00 PM | 0.79167 | 5 | 76.1 | 70.1 | 94.8268 | 108.7319 | 13.9051 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/12/20XX 8:00:00 PM | 0.83333 | 5 | 75.6 | 70.7 | 93.2166 | 106.8793 | 13.6627 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/12/20XX 9:00:00 PM | 0.875 | 5 | 75.4 | 71.2 | 92.579 | 106.1458 | 13.5668 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/12/20XX 10:00:00 PM | 0.91667 | 5 | 74.8 | 72.7 | 90.6884 | 103.9709 | 13.2825 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/12/20XX 11:00:00 PM | 0.95833 | 5 | 73.9 | 75.7 | 87.9141 | 100.78 | 12.8659 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/12/20XX 12:00:00 AM | 0 | 6 | 73.7 | 75.6 | 87.3075 | 100.0824 | 12.7749 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/13/20XX 1:00:00 AM | 0.041667 | 6 | 73.3 | 77 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/13/20XX 2:00:00 AM | 0.083333 | 6 | 72.8 | 78.2 | 84.6221 | 96.9944 | 12.3723 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/13/20XX 3:00:00 AM | 0.125 | 6 | 72.4 | 78.2 | 83.4515 | 95.6486 | 12.1971 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/13/20XX 4:00:00 AM | 0.16667 | 6 | 72.1 | 78.9 | 82.5828 | 94.6498 | 12.0671 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/13/20XX 5:00:00 AM | 0.20833 | 6 | 71.5 | 80 | 92.6795 | 104.5026 | 11.8231 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/13/20XX 6:00:00 AM | 0.25 | 6 | 71.6 | 80.5 | 93.0054 | 104.8714 | 11.866 | 80 | 71.6 |  | 71.6 | 93.5987 | 0.1 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 65.7193 | 17.8987 | 425989.1151 | 35.4991 | 35.4991 | 94.5931 | 0.2 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 68.817 | 20.9964 | 499714.4302 | 41.6429 | 41.6429 | 99.9809 | 0.3 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 71.9147 | 24.0941 | 573439.7453 | 47.7866 | 47.7866 | 105.3686 | 0.4 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 75.0124 | 27.1918 | 647165.0604 | 53.9304 | 53.9304 | 110.7564 | 0.5 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 78.1101 | 30.2895 | 720890.3755 | 60.0742 | 60.0742 | 116.1442 | 0.6 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 81.2078 | 33.3872 | 794615.6906 | 66.218 | 66.218 | 121.532 | 0.7 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 84.3055 | 36.4849 | 868341.0057 | 72.3618 | 72.3618 | 126.9198 | 0.8 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 87.4033 | 39.5826 | 942066.3208 | 78.5055 | 78.5055 | 132.3075 | 0.9 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 90.501 | 42.6803 | 1015791.6359 | 84.6493 | 84.6493 | 137.6953 | 1 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 93.5987 | 45.778 | 1089516.951 | 90.7931 | 90.7931 | 143.0831 | 70 | 80 | 31.8106 | 32 | 80.5
8/13/20XX 7:00:00 AM | 0.29167 | 6 | 72.1 | 79.6 | 82.5828 | 94.6498 | 12.0671 | 70 | 72.1 |  | 72.1 | 94.1672 | 0.1 | 73.81 | 18.81 | 711018 | 59.2515 | 59.2515 | 65.7762 | 17.9556 | 427342.1361 | 35.6118 | 35.6118 | 94.8633 | 0.2 | 73.62 | 18.62 | 703836 | 58.653 | 58.653 | 68.9307 | 21.1101 | 502420.4722 | 41.8684 | 41.8684 | 100.5214 | 0.3 | 73.43 | 18.43 | 696654 | 58.0545 | 58.0545 | 72.0853 | 24.2647 | 577498.8084 | 48.1249 | 48.1249 | 106.1794 | 0.4 | 73.24 | 18.24 | 689472 | 57.456 | 57.456 | 75.2398 | 27.4192 | 652577.1445 | 54.3814 | 54.3814 | 111.8374 | 0.5 | 73.05 | 18.05 | 682290 | 56.8575 | 56.8575 | 78.3944 | 30.5738 | 727655.4806 | 60.638 | 60.638 | 117.4955 | 0.6 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 81.5489 | 33.7283 | 802733.8167 | 66.8945 | 66.8945 | 123.1535 | 0.7 | 72.67 | 17.67 | 667926 | 55.6605 | 55.6605 | 84.7035 | 36.8829 | 877812.1528 | 73.151 | 73.151 | 128.8115 | 0.8 | 72.48 | 17.48 | 660744 | 55.062 | 55.062 | 87.858 | 40.0374 | 952890.489 | 79.4075 | 79.4075 | 134.4695 | 0.9 | 72.29 | 17.29 | 653562 | 54.4635 | 54.4635 | 91.0126 | 43.192 | 1027968.8251 | 85.6641 | 85.6641 | 140.1276 | 1 | 72.1 | 17.1 | 646380 | 53.865 | 53.865 | 94.1672 | 46.3465 | 1103047.1612 | 91.9206 | 91.9206 | 145.7856 | 70 | 80 | 32.0224 | 32 | 79.6
8/13/20XX 8:00:00 AM | 0.33333 | 6 | 73.1 | 77.4 | 85.5092 | 98.0145 | 12.5053 | 70 | 73.1 |  | 73.1 | 94.7631 | 0.1 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 65.8358 | 18.0151 | 428760.5581 | 35.73 | 35.73 | 95.2965 | 0.2 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 69.0499 | 21.2293 | 505257.3162 | 42.1048 | 42.1048 | 101.3878 | 0.3 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 72.2641 | 24.4434 | 581754.0743 | 48.4795 | 48.4795 | 107.479 | 0.4 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 75.4782 | 27.6576 | 658250.8324 | 54.8542 | 54.8542 | 113.5702 | 0.5 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 78.6924 | 30.8717 | 734747.5905 | 61.229 | 61.229 | 119.6615 | 0.6 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 81.9065 | 34.0859 | 811244.3486 | 67.6037 | 67.6037 | 125.7527 | 0.7 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 85.1207 | 37.3 | 887741.1067 | 73.9784 | 73.9784 | 131.8439 | 0.8 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 88.3348 | 40.5142 | 964237.8648 | 80.3532 | 80.3532 | 137.9352 | 0.9 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 91.549 | 43.7283 | 1040734.6229 | 86.7279 | 86.7279 | 144.0264 | 1 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 94.7631 | 46.9425 | 1117231.381 | 93.1026 | 93.1026 | 150.1176 | 75 | 75 | 32.3616 | 32 | 77.4
8/13/20XX 9:00:00 AM | 0.375 | 6 | 74.5 | 72.8 | 89.7555 | 102.8978 | 13.1423 | 70 | 74.5 |  | 74.5 | 93.4353 | 0.1 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 65.703 | 17.8824 | 425600.3636 | 35.4667 | 35.4667 | 95.4742 | 0.2 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 68.7844 | 20.9637 | 498936.9272 | 41.5781 | 41.5781 | 101.7431 | 0.3 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 71.8657 | 24.0451 | 572273.4908 | 47.6895 | 47.6895 | 108.012 | 0.4 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 74.9471 | 27.1265 | 645610.0544 | 53.8008 | 53.8008 | 114.2808 | 0.5 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 78.0285 | 30.2078 | 718946.618 | 59.9122 | 59.9122 | 120.5497 | 0.6 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 81.1098 | 33.2892 | 792283.1816 | 66.0236 | 66.0236 | 126.8186 | 0.7 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 84.1912 | 36.3706 | 865619.7452 | 72.135 | 72.135 | 133.0875 | 0.8 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 87.2726 | 39.4519 | 938956.3088 | 78.2464 | 78.2464 | 139.3564 | 0.9 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 90.3539 | 42.5333 | 1012292.8725 | 84.3577 | 84.3577 | 145.6252 | 1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 93.4353 | 45.6147 | 1085629.4361 | 90.4691 | 90.4691 | 151.8941 | 75 | 75 | 32.4982 | 32 | 72.8
8/13/20XX 10:00:00 AM | 0.41667 | 6 | 75.8 | 69 | 80.1988 | 93.8579 | 13.6591 | 60 | 75.8 |  | 75.8 | 92.492 | 0.1 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 65.6087 | 17.788 | 423355.2174 | 35.2796 | 35.2796 | 95.6966 | 0.2 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 68.5957 | 20.7751 | 494446.6349 | 41.2039 | 41.2039 | 102.1879 | 0.3 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 71.5827 | 23.7621 | 565538.0523 | 47.1282 | 47.1282 | 108.6792 | 0.4 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 74.5698 | 26.7491 | 636629.4697 | 53.0525 | 53.0525 | 115.1705 | 0.5 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 77.5568 | 29.7362 | 707720.8871 | 58.9767 | 58.9767 | 121.6617 | 0.6 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 80.5438 | 32.7232 | 778812.3046 | 64.901 | 64.901 | 128.153 | 0.7 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 83.5309 | 35.7102 | 849903.722 | 70.8253 | 70.8253 | 134.6443 | 0.8 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 86.5179 | 38.6973 | 920995.1394 | 76.7496 | 76.7496 | 141.1356 | 0.9 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 89.5049 | 41.6843 | 992086.5569 | 82.6739 | 82.6739 | 147.6269 | 1 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 92.492 | 44.6713 | 1063177.9743 | 88.5982 | 88.5982 | 154.1182 | 75 | 70 | 32.6703 | 32 | 69
8/13/20XX 11:00:00 AM | 0.45833 | 6 | 77.6 | 66.1 | 85.2591 | 99.7988 | 14.5397 | 60 | 77.6 |  | 77.6 | 94.1283 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 65.7723 | 17.9517 | 427249.7803 | 35.6041 | 35.6041 | 96.5881 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 68.923 | 21.1023 | 502235.7605 | 41.853 | 41.853 | 103.971 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 72.0736 | 24.253 | 577221.7408 | 48.1018 | 48.1018 | 111.3538 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 75.2243 | 27.4037 | 652207.7211 | 54.3506 | 54.3506 | 118.7366 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 78.375 | 30.5544 | 727193.7013 | 60.5995 | 60.5995 | 126.1195 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 81.5257 | 33.705 | 802179.6816 | 66.8483 | 66.8483 | 133.5023 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 84.6763 | 36.8557 | 877165.6619 | 73.0971 | 73.0971 | 140.8851 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 87.827 | 40.0064 | 952151.6421 | 79.346 | 79.346 | 148.268 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 90.9777 | 43.157 | 1027137.6224 | 85.5948 | 85.5948 | 155.6508 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 94.1283 | 46.3077 | 1102123.6027 | 91.8436 | 91.8436 | 163.0336 | 80 | 65 | 33.3692 | 34 | 66.1
8/13/20XX 12:00:00 PM | 0.5 | 6 | 78.8 | 62.9 | 88.7794 | 103.932 | 15.1526 | 60 | 78.8 |  | 78.8 | 93.1737 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 65.6768 | 17.8562 | 424977.629 | 35.4148 | 35.4148 | 96.7768 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 68.732 | 20.9114 | 497691.458 | 41.4743 | 41.4743 | 104.3483 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 71.7872 | 23.9666 | 570405.287 | 47.5338 | 47.5338 | 111.9198 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 74.8424 | 27.0218 | 643119.116 | 53.5933 | 53.5933 | 119.4913 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 77.8976 | 30.077 | 715832.945 | 59.6527 | 59.6527 | 127.0627 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 80.9528 | 33.1322 | 788546.774 | 65.7122 | 65.7122 | 134.6342 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 84.0081 | 36.1874 | 861260.603 | 71.7717 | 71.7717 | 142.2057 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 87.0633 | 39.2426 | 933974.432 | 77.8312 | 77.8312 | 149.7772 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 90.1185 | 42.2978 | 1006688.261 | 83.8907 | 83.8907 | 157.3487 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 93.1737 | 45.353 | 1079402.09 | 89.9502 | 89.9502 | 164.9202 | 80 | 65 | 33.5148 | 34 | 62.9
8/13/20XX 1:00:00 PM | 0.54167 | 6 | 79.6 | 61.3 | 91.1929 | 106.7659 | 15.5729 | 60 | 79.6 |  | 79.6 | 93.2174 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.6812 | 17.8606 | 425081.7685 | 35.4235 | 35.4235 | 97.0375 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 68.7408 | 20.9202 | 497899.737 | 41.4916 | 41.4916 | 104.8696 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 71.8004 | 23.9797 | 570717.7055 | 47.5598 | 47.5598 | 112.7018 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 74.8599 | 27.0393 | 643535.674 | 53.628 | 53.628 | 120.534 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 77.9195 | 30.0989 | 716353.6425 | 59.6961 | 59.6961 | 128.3661 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 80.9791 | 33.1585 | 789171.611 | 65.7643 | 65.7643 | 136.1983 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 84.0387 | 36.218 | 861989.5795 | 71.8325 | 71.8325 | 144.0305 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 87.0983 | 39.2776 | 934807.548 | 77.9006 | 77.9006 | 151.8626 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 90.1578 | 42.3372 | 1007625.5165 | 83.9688 | 83.9688 | 159.6948 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 93.2174 | 45.3968 | 1080443.485 | 90.037 | 90.037 | 167.527 | 80 | 60 | 33.7183 | 34 | 61.3
8/13/20XX 2:00:00 PM | 0.58333 | 6 | 79.6 | 60.5 | 91.1929 | 106.7659 | 15.5729 | 60 | 79.6 |  | 79.6 | 91.9716 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.5566 | 17.736 | 422116.6851 | 35.1764 | 35.1764 | 96.7904 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 68.4916 | 20.671 | 491969.5702 | 40.9975 | 40.9975 | 104.3755 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 71.4266 | 23.606 | 561822.4553 | 46.8185 | 46.8185 | 111.9605 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 74.3616 | 26.541 | 631675.3404 | 52.6396 | 52.6396 | 119.5456 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 77.2966 | 29.476 | 701528.2255 | 58.4607 | 58.4607 | 127.1307 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 80.2316 | 32.411 | 771381.1106 | 64.2818 | 64.2818 | 134.7158 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 83.1666 | 35.346 | 841233.9957 | 70.1028 | 70.1028 | 142.3008 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 86.1016 | 38.281 | 911086.8808 | 75.9239 | 75.9239 | 149.8859 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 89.0366 | 41.216 | 980939.7659 | 81.745 | 81.745 | 157.471 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 91.9716 | 44.151 | 1050792.651 | 87.5661 | 87.5661 | 165.0561 | 80 | 60 | 33.523 | 34 | 60.5
8/13/20XX 3:00:00 PM | 0.625 | 6 | 79.5 | 60.1 | 90.8883 | 106.4082 | 15.5199 | 60 | 79.5 |  | 79.5 | 91.0435 | 0.1 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 65.4638 | 17.6432 | 419907.8369 | 34.9923 | 34.9923 | 96.5748 | 0.2 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 68.306 | 20.4854 | 487551.8738 | 40.6293 | 40.6293 | 103.9443 | 0.3 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 71.1482 | 23.3276 | 555195.9107 | 46.2663 | 46.2663 | 111.3138 | 0.4 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 73.9904 | 26.1697 | 622839.9475 | 51.9033 | 51.9033 | 118.6833 | 0.5 | 76.75 | 21.75 | 822150 | 68.5125 | 68.5125 | 76.8326 | 29.0119 | 690483.9844 | 57.5403 | 57.5403 | 126.0528 | 0.6 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 79.6748 | 31.8541 | 758128.0213 | 63.1773 | 63.1773 | 133.4223 | 0.7 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 82.5169 | 34.6963 | 825772.0582 | 68.8143 | 68.8143 | 140.7918 | 0.8 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 85.3591 | 37.5385 | 893416.0951 | 74.4513 | 74.4513 | 148.1613 | 0.9 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 88.2013 | 40.3807 | 961060.132 | 80.0883 | 80.0883 | 155.5308 | 1 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 91.0435 | 43.2229 | 1028704.1689 | 85.7253 | 85.7253 | 162.9003 | 80 | 60 | 33.3529 | 34 | 60.1
8/13/20XX 4:00:00 PM | 0.66667 | 6 | 79.8 | 58.1 | 76.2143 | 91.8048 | 15.5904 | 50 | 79.8 |  | 79.8 | 88.8426 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 65.2437 | 17.4231 | 414669.648 | 34.5558 | 34.5558 | 96.2328 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 67.8658 | 20.0452 | 477075.4959 | 39.7563 | 39.7563 | 103.2603 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 70.4879 | 22.6673 | 539481.3439 | 44.9568 | 44.9568 | 110.2878 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 73.11 | 25.2894 | 601887.1918 | 50.1573 | 50.1573 | 117.3153 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 75.7321 | 27.9115 | 664293.0398 | 55.3578 | 55.3578 | 124.3428 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 78.3542 | 30.5336 | 726698.8878 | 60.5582 | 60.5582 | 131.3702 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 80.9763 | 33.1557 | 789104.7357 | 65.7587 | 65.7587 | 138.3977 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 83.5984 | 35.7778 | 851510.5837 | 70.9592 | 70.9592 | 145.4252 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 86.2205 | 38.3999 | 913916.4316 | 76.1597 | 76.1597 | 152.4527 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 88.8426 | 41.0219 | 976322.2796 | 81.3602 | 81.3602 | 159.4802 | 80 | 60 | 33.0816 | 34 | 58.1
8/13/20XX 5:00:00 PM | 0.70833 | 6 | 79.1 | 57.7 | 74.4534 | 89.6782 | 15.2248 | 50 | 79.1 |  | 79.1 | 86.1765 | 0.1 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 64.9771 | 17.1565 | 408324.3449 | 34.027 | 34.027 | 95.4835 | 0.2 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 67.3326 | 19.512 | 464384.8898 | 38.6987 | 38.6987 | 101.7617 | 0.3 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 69.6881 | 21.8675 | 520445.4347 | 43.3705 | 43.3705 | 108.04 | 0.4 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 72.0436 | 24.2229 | 576505.9796 | 48.0422 | 48.0422 | 114.3182 | 0.5 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 74.3991 | 26.5784 | 632566.5246 | 52.7139 | 52.7139 | 120.5964 | 0.6 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 76.7545 | 28.9339 | 688627.0695 | 57.3856 | 57.3856 | 126.8746 | 0.7 | 77.57 | 22.57 | 853146 | 71.0955 | 71.0955 | 79.11 | 31.2894 | 744687.6144 | 62.0573 | 62.0573 | 133.1528 | 0.8 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 81.4655 | 33.6449 | 800748.1593 | 66.729 | 66.729 | 139.431 | 0.9 | 78.59 | 23.59 | 891702 | 74.3085 | 74.3085 | 83.821 | 36.0004 | 856808.7042 | 71.4007 | 71.4007 | 145.7092 | 1 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 86.1765 | 38.3559 | 912869.2491 | 76.0724 | 76.0724 | 151.9874 | 80 | 60 | 32.4918 | 32 | 57.7
8/13/20XX 6:00:00 PM | 0.75 | 6 | 78 | 60.9 | 86.4193 | 101.161 | 14.7417 | 60 | 78 |  | 78 | 87.7461 | 0.1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 65.1341 | 17.3134 | 412060.0289 | 34.3383 | 34.3383 | 95.4483 | 0.2 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 67.6465 | 19.8259 | 471856.2578 | 39.3214 | 39.3214 | 101.6914 | 0.3 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 70.159 | 22.3383 | 531652.4867 | 44.3044 | 44.3044 | 107.9344 | 0.4 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 72.6714 | 24.8508 | 591448.7157 | 49.2874 | 49.2874 | 114.1774 | 0.5 | 76 | 21 | 793800 | 66.15 | 66.15 | 75.1839 | 27.3632 | 651244.9446 | 54.2704 | 54.2704 | 120.4204 | 0.6 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 77.6963 | 29.8757 | 711041.1735 | 59.2534 | 59.2534 | 126.6634 | 0.7 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 80.2088 | 32.3881 | 770837.4024 | 64.2365 | 64.2365 | 132.9065 | 0.8 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 82.7212 | 34.9006 | 830633.6313 | 69.2195 | 69.2195 | 139.1495 | 0.9 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 85.2337 | 37.413 | 890429.8602 | 74.2025 | 74.2025 | 145.3925 | 1 | 78 | 23 | 869400 | 72.45 | 72.45 | 87.7461 | 39.9255 | 950226.0892 | 79.1855 | 79.1855 | 151.6355 | 80 | 60 | 32.4677 | 32 | 60.9
8/13/20XX 7:00:00 PM | 0.79167 | 6 | 76.8 | 62.8 | 82.9779 | 97.1205 | 14.1426 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/13/20XX 8:00:00 PM | 0.83333 | 6 | 76.2 | 64.3 | 81.3009 | 95.1517 | 13.8508 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/13/20XX 9:00:00 PM | 0.875 | 6 | 75.8 | 65.2 | 80.1988 | 93.8579 | 13.6591 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/13/20XX 10:00:00 PM | 0.91667 | 6 | 74.9 | 67 | 77.7654 | 91.0012 | 13.2358 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/13/20XX 11:00:00 PM | 0.95833 | 6 | 73.4 | 69.6 | 73.8495 | 86.4044 | 12.5549 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/13/20XX 12:00:00 AM | 0 | 7 | 72.7 | 70.3 | 84.3281 | 96.6564 | 12.3283 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/14/20XX 1:00:00 AM | 0.041667 | 7 | 71.7 | 71.7 | 81.4366 | 93.3322 | 11.8956 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/14/20XX 2:00:00 AM | 0.083333 | 7 | 70.9 | 73 | 79.1855 | 90.7449 | 11.5593 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/14/20XX 3:00:00 AM | 0.125 | 7 | 70.7 | 71.6 | 78.6313 | 90.1079 | 11.4766 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/14/20XX 4:00:00 AM | 0.16667 | 7 | 69.8 | 74.5 | 76.1788 | 87.2896 | 11.1108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/14/20XX 5:00:00 AM | 0.20833 | 7 | 69.2 | 75.5 | 74.5812 | 85.4541 | 10.8729 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/14/20XX 6:00:00 AM | 0.25 | 7 | 69.3 | 75.1 | 74.8454 | 85.7577 | 10.9122 | 70 | 69.3 |  | 69.3 | 80.4107 | 0.1 | 73.53 | 18.53 | 700434 | 58.3695 | 58.3695 | 64.4005 | 16.5799 | 394601.6829 | 32.8835 | 32.8835 | 91.253 | 0.2 | 73.06 | 18.06 | 682668 | 56.889 | 56.889 | 66.1794 | 18.3588 | 436939.5657 | 36.4116 | 36.4116 | 93.3006 | 0.3 | 72.59 | 17.59 | 664902 | 55.4085 | 55.4085 | 67.9583 | 20.1377 | 479277.4486 | 39.9398 | 39.9398 | 95.3483 | 0.4 | 72.12 | 17.12 | 647136 | 53.928 | 53.928 | 69.7372 | 21.9166 | 521615.3314 | 43.4679 | 43.4679 | 97.3959 | 0.5 | 71.65 | 16.65 | 629370 | 52.4475 | 52.4475 | 71.5161 | 23.6955 | 563953.2143 | 46.9961 | 46.9961 | 99.4436 | 0.6 | 71.18 | 16.18 | 611604 | 50.967 | 50.967 | 73.295 | 25.4744 | 606291.0972 | 50.5243 | 50.5243 | 101.4913 | 0.7 | 70.71 | 15.71 | 593838 | 49.4865 | 49.4865 | 75.074 | 27.2533 | 648628.98 | 54.0524 | 54.0524 | 103.5389 | 0.8 | 70.24 | 15.24 | 576072 | 48.006 | 48.006 | 76.8529 | 29.0322 | 690966.8629 | 57.5806 | 57.5806 | 105.5866 | 0.9 | 69.77 | 14.77 | 558306 | 46.5255 | 46.5255 | 78.6318 | 30.8111 | 733304.7458 | 61.1087 | 61.1087 | 107.6342 | 1 | 69.3 | 14.3 | 540540 | 45.045 | 45.045 | 80.4107 | 32.59 | 775642.6286 | 64.6369 | 64.6369 | 109.6819 | 70 | 75 | 29.186 | 30 | 75.1
8/14/20XX 7:00:00 AM | 0.29167 | 7 | 70.8 | 72.4 | 78.908 | 90.4259 | 11.5179 | 70 | 70.8 |  | 70.8 | 81.6723 | 0.1 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 64.5267 | 16.7061 | 397604.3388 | 33.1337 | 33.1337 | 91.9757 | 0.2 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 66.4318 | 18.6111 | 442944.8776 | 36.9121 | 36.9121 | 94.7461 | 0.3 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 68.3368 | 20.5162 | 488285.4164 | 40.6905 | 40.6905 | 97.5165 | 0.4 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 70.2419 | 22.4213 | 533625.9553 | 44.4688 | 44.4688 | 100.2868 | 0.5 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 72.147 | 24.3263 | 578966.4941 | 48.2472 | 48.2472 | 103.0572 | 0.6 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 74.052 | 26.2314 | 624307.0329 | 52.0256 | 52.0256 | 105.8276 | 0.7 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 75.9571 | 28.1365 | 669647.5717 | 55.804 | 55.804 | 108.598 | 0.8 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 77.8621 | 30.0415 | 714988.1105 | 59.5823 | 59.5823 | 111.3683 | 0.9 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 79.7672 | 31.9466 | 760328.6493 | 63.3607 | 63.3607 | 114.1387 | 1 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 81.6723 | 33.8516 | 805669.1881 | 67.1391 | 67.1391 | 116.9091 | 70 | 70 | 29.7507 | 30 | 72.4
8/14/20XX 8:00:00 AM | 0.33333 | 7 | 72.7 | 66.4 | 72.0807 | 84.3281 | 12.2474 | 60 | 72.7 |  | 72.7 | 79.919 | 0.1 | 73.87 | 18.87 | 713286 | 59.4405 | 59.4405 | 64.3514 | 16.5307 | 393431.6285 | 32.786 | 32.786 | 92.2265 | 0.2 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 66.0811 | 18.2605 | 434599.4569 | 36.2166 | 36.2166 | 95.2476 | 0.3 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 67.8109 | 19.9902 | 475767.2854 | 39.6473 | 39.6473 | 98.2688 | 0.4 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 69.5406 | 21.72 | 516935.1139 | 43.0779 | 43.0779 | 101.2899 | 0.5 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 71.2703 | 23.4497 | 558102.9423 | 46.5086 | 46.5086 | 104.3111 | 0.6 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 73.0001 | 25.1794 | 599270.7708 | 49.9392 | 49.9392 | 107.3322 | 0.7 | 73.09 | 18.09 | 683802 | 56.9835 | 56.9835 | 74.7298 | 26.9092 | 640438.5993 | 53.3699 | 53.3699 | 110.3534 | 0.8 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 76.4596 | 28.6389 | 681606.4277 | 56.8005 | 56.8005 | 113.3745 | 0.9 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 78.1893 | 30.3687 | 722774.2562 | 60.2312 | 60.2312 | 116.3957 | 1 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 79.919 | 32.0984 | 763942.0847 | 63.6618 | 63.6618 | 119.4168 | 75 | 65 | 29.9425 | 30 | 66.4
8/14/20XX 9:00:00 AM | 0.375 | 7 | 74.2 | 63.4 | 75.9165 | 88.8307 | 12.9142 | 60 | 74.2 |  | 74.2 | 80.3073 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 64.3902 | 16.5696 | 394355.7322 | 32.863 | 32.863 | 92.776 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 66.1588 | 18.3381 | 436447.6644 | 36.3706 | 36.3706 | 96.3466 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 67.9273 | 20.1067 | 478539.5966 | 39.8783 | 39.8783 | 99.9173 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 69.6959 | 21.8753 | 520631.5288 | 43.386 | 43.386 | 103.488 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 71.4645 | 23.6438 | 562723.4609 | 46.8936 | 46.8936 | 107.0586 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 73.233 | 25.4124 | 604815.3931 | 50.4013 | 50.4013 | 110.6293 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 75.0016 | 27.181 | 646907.3253 | 53.9089 | 53.9089 | 114.1999 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 76.7702 | 28.9495 | 688999.2575 | 57.4166 | 57.4166 | 117.7706 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 78.5387 | 30.7181 | 731091.1897 | 60.9243 | 60.9243 | 121.3413 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 80.3073 | 32.4867 | 773183.1219 | 64.4319 | 64.4319 | 124.9119 | 75 | 65 | 30.3708 | 30 | 63.4
8/14/20XX 10:00:00 AM | 0.41667 | 7 | 76 | 60.5 | 80.7483 | 94.5029 | 13.7546 | 60 | 76 |  | 76 | 81.436 | 0.1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 64.5031 | 16.6824 | 397041.9671 | 33.0868 | 33.0868 | 93.5668 | 0.2 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 66.3845 | 18.5639 | 441820.1341 | 36.8183 | 36.8183 | 97.9283 | 0.3 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 68.2659 | 20.4453 | 486598.3012 | 40.5499 | 40.5499 | 102.2899 | 0.4 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 70.1474 | 22.3267 | 531376.4682 | 44.2814 | 44.2814 | 106.6514 | 0.5 | 75 | 20 | 756000 | 63 | 63 | 72.0288 | 24.2082 | 576154.6353 | 48.0129 | 48.0129 | 111.0129 | 0.6 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 73.9102 | 26.0896 | 620932.8023 | 51.7444 | 51.7444 | 115.3744 | 0.7 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 75.7917 | 27.971 | 665710.9694 | 55.4759 | 55.4759 | 119.7359 | 0.8 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 77.6731 | 29.8525 | 710489.1364 | 59.2074 | 59.2074 | 124.0974 | 0.9 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 79.5546 | 31.7339 | 755267.3035 | 62.9389 | 62.9389 | 128.4589 | 1 | 76 | 21 | 793800 | 66.15 | 66.15 | 81.436 | 33.6154 | 800045.4705 | 66.6705 | 66.6705 | 132.8205 | 75 | 60 | 30.9887 | 30 | 60.5
8/14/20XX 11:00:00 AM | 0.45833 | 7 | 78 | 57.9 | 71.7546 | 86.4193 | 14.6647 | 50 | 78 |  | 78 | 83.3398 | 0.1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 64.6934 | 16.8728 | 401572.9368 | 33.4644 | 33.4644 | 94.5744 | 0.2 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 66.7653 | 18.9446 | 450882.0736 | 37.5735 | 37.5735 | 99.9435 | 0.3 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 68.8371 | 21.0164 | 500191.2105 | 41.6826 | 41.6826 | 105.3126 | 0.4 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 70.9089 | 23.0882 | 549500.3473 | 45.7917 | 45.7917 | 110.6817 | 0.5 | 76 | 21 | 793800 | 66.15 | 66.15 | 72.9807 | 25.1601 | 598809.4841 | 49.9008 | 49.9008 | 116.0508 | 0.6 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 75.0525 | 27.2319 | 648118.6209 | 54.0099 | 54.0099 | 121.4199 | 0.7 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 77.1243 | 29.3037 | 697427.7578 | 58.119 | 58.119 | 126.789 | 0.8 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 79.1961 | 31.3755 | 746736.8946 | 62.2281 | 62.2281 | 132.1581 | 0.9 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 81.2679 | 33.4473 | 796046.0314 | 66.3372 | 66.3372 | 137.5272 | 1 | 78 | 23 | 869400 | 72.45 | 72.45 | 83.3398 | 35.5191 | 845355.1682 | 70.4463 | 70.4463 | 142.8963 | 80 | 60 | 31.7773 | 32 | 57.9
8/14/20XX 12:00:00 PM | 0.5 | 7 | 79.1 | 56.6 | 74.4534 | 89.6782 | 15.2248 | 50 | 79.1 |  | 79.1 | 84.5018 | 0.1 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 64.8096 | 16.989 | 404338.5028 | 33.6949 | 33.6949 | 95.1514 | 0.2 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 66.9977 | 19.177 | 456413.2056 | 38.0344 | 38.0344 | 101.0974 | 0.3 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 69.1857 | 21.365 | 508487.9084 | 42.374 | 42.374 | 107.0435 | 0.4 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 71.3737 | 23.5531 | 560562.6112 | 46.7136 | 46.7136 | 112.9896 | 0.5 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 73.5617 | 25.7411 | 612637.314 | 51.0531 | 51.0531 | 118.9356 | 0.6 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 75.7497 | 27.9291 | 664712.0168 | 55.3927 | 55.3927 | 124.8817 | 0.7 | 77.57 | 22.57 | 853146 | 71.0955 | 71.0955 | 77.9377 | 30.1171 | 716786.7196 | 59.7322 | 59.7322 | 130.8277 | 0.8 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 80.1257 | 32.3051 | 768861.4223 | 64.0718 | 64.0718 | 136.7738 | 0.9 | 78.59 | 23.59 | 891702 | 74.3085 | 74.3085 | 82.3137 | 34.4931 | 820936.1251 | 68.4113 | 68.4113 | 142.7198 | 1 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 84.5018 | 36.6811 | 873010.8279 | 72.7509 | 72.7509 | 148.6659 | 80 | 55 | 32.2292 | 32 | 56.6
8/14/20XX 1:00:00 PM | 0.54167 | 7 | 79.7 | 55.9 | 75.9607 | 91.4984 | 15.5378 | 50 | 79.7 |  | 79.7 | 85.1279 | 0.1 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 64.8723 | 17.0516 | 405828.8259 | 33.8191 | 33.8191 | 95.4646 | 0.2 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 67.1229 | 19.3023 | 459393.8518 | 38.2828 | 38.2828 | 101.7238 | 0.3 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 69.3735 | 21.5529 | 512958.8777 | 42.7466 | 42.7466 | 107.9831 | 0.4 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 71.6242 | 23.8035 | 566523.9035 | 47.2103 | 47.2103 | 114.2423 | 0.5 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 73.8748 | 26.0542 | 620088.9294 | 51.6741 | 51.6741 | 120.5016 | 0.6 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 76.1254 | 28.3048 | 673653.9553 | 56.1378 | 56.1378 | 126.7608 | 0.7 | 77.99 | 22.99 | 869022 | 72.4185 | 72.4185 | 78.3761 | 30.5554 | 727218.9812 | 60.6016 | 60.6016 | 133.0201 | 0.8 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 80.6267 | 32.8061 | 780784.0071 | 65.0653 | 65.0653 | 139.2793 | 0.9 | 79.13 | 24.13 | 912114 | 76.0095 | 76.0095 | 82.8773 | 35.0567 | 834349.033 | 69.5291 | 69.5291 | 145.5386 | 1 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 85.1279 | 37.3073 | 887914.0589 | 73.9928 | 73.9928 | 151.7978 | 80 | 55 | 32.4746 | 32 | 55.9
8/14/20XX 2:00:00 PM | 0.58333 | 7 | 80 | 55.4 | 76.7237 | 92.42 | 15.6963 | 50 | 80 |  | 80 | 85.1997 | 0.1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 64.8794 | 17.0588 | 405999.6018 | 33.8333 | 33.8333 | 95.5733 | 0.2 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 67.1372 | 19.3166 | 459735.4036 | 38.3113 | 38.3113 | 101.9413 | 0.3 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 69.3951 | 21.5744 | 513471.2054 | 42.7893 | 42.7893 | 108.3093 | 0.4 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 71.6529 | 23.8322 | 567207.0072 | 47.2673 | 47.2673 | 114.6773 | 0.5 | 77 | 22 | 831600 | 69.3 | 69.3 | 73.9107 | 26.09 | 620942.809 | 51.7452 | 51.7452 | 121.0452 | 0.6 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 76.1685 | 28.3478 | 674678.6108 | 56.2232 | 56.2232 | 127.4132 | 0.7 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 78.4263 | 30.6056 | 728414.4125 | 60.7012 | 60.7012 | 133.7812 | 0.8 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 80.6841 | 32.8635 | 782150.2143 | 65.1792 | 65.1792 | 140.1492 | 0.9 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 82.9419 | 35.1213 | 835886.0161 | 69.6572 | 69.6572 | 146.5172 | 1 | 80 | 25 | 945000 | 78.75 | 78.75 | 85.1997 | 37.3791 | 889621.8179 | 74.1352 | 74.1352 | 152.8852 | 80 | 55 | 32.5595 | 32 | 55.4
8/14/20XX 3:00:00 PM | 0.625 | 7 | 79.1 | 57.3 | 74.4534 | 89.6782 | 15.2248 | 50 | 79.1 |  | 79.1 | 85.5675 | 0.1 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 64.9162 | 17.0956 | 406874.9478 | 33.9062 | 33.9062 | 95.3627 | 0.2 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 67.2108 | 19.3902 | 461486.0956 | 38.4572 | 38.4572 | 101.5202 | 0.3 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 69.5054 | 21.6848 | 516097.2433 | 43.0081 | 43.0081 | 107.6776 | 0.4 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 71.8 | 23.9793 | 570708.3911 | 47.559 | 47.559 | 113.835 | 0.5 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 74.0946 | 26.2739 | 625319.5389 | 52.11 | 52.11 | 119.9925 | 0.6 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 76.3891 | 28.5685 | 679930.6867 | 56.6609 | 56.6609 | 126.1499 | 0.7 | 77.57 | 22.57 | 853146 | 71.0955 | 71.0955 | 78.6837 | 30.8631 | 734541.8344 | 61.2118 | 61.2118 | 132.3073 | 0.8 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 80.9783 | 33.1577 | 789152.9822 | 65.7627 | 65.7627 | 138.4647 | 0.9 | 78.59 | 23.59 | 891702 | 74.3085 | 74.3085 | 83.2729 | 35.4523 | 843764.13 | 70.3137 | 70.3137 | 144.6222 | 1 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 85.5675 | 37.7469 | 898375.2778 | 74.8646 | 74.8646 | 150.7796 | 80 | 55 | 32.3963 | 32 | 57.3
8/14/20XX 4:00:00 PM | 0.66667 | 7 | 78.2 | 61.2 | 87.0044 | 101.8479 | 14.8435 | 60 | 78.2 |  | 78.2 | 88.7856 | 0.1 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 65.238 | 17.4174 | 414534.0775 | 34.5445 | 34.5445 | 95.7175 | 0.2 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 67.8544 | 20.0338 | 476804.355 | 39.7337 | 39.7337 | 102.2297 | 0.3 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 70.4708 | 22.6502 | 539074.6325 | 44.9229 | 44.9229 | 108.7419 | 0.4 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 73.0872 | 25.2666 | 601344.91 | 50.1121 | 50.1121 | 115.2541 | 0.5 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 75.7036 | 27.883 | 663615.1875 | 55.3013 | 55.3013 | 121.7663 | 0.6 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 78.32 | 30.4994 | 725885.465 | 60.4905 | 60.4905 | 128.2785 | 0.7 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 80.9364 | 33.1158 | 788155.7425 | 65.6796 | 65.6796 | 134.7906 | 0.8 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 83.5528 | 35.7322 | 850426.02 | 70.8688 | 70.8688 | 141.3028 | 0.9 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 86.1692 | 38.3486 | 912696.2975 | 76.058 | 76.058 | 147.815 | 1 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 88.7856 | 40.965 | 974966.575 | 81.2472 | 81.2472 | 154.3272 | 80 | 60 | 32.6796 | 32 | 61.2
8/14/20XX 5:00:00 PM | 0.70833 | 7 | 77.6 | 61.5 | 85.2591 | 99.7988 | 14.5397 | 60 | 77.6 |  | 77.6 | 87.4401 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 65.1035 | 17.2828 | 411331.7283 | 34.2776 | 34.2776 | 95.2616 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 67.5853 | 19.7647 | 470399.6565 | 39.2 | 39.2 | 101.318 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 70.0672 | 22.2465 | 529467.5848 | 44.1223 | 44.1223 | 107.3743 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 72.549 | 24.7284 | 588535.5131 | 49.0446 | 49.0446 | 113.4306 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 75.0309 | 27.2102 | 647603.4414 | 53.967 | 53.967 | 119.487 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 77.5127 | 29.6921 | 706671.3696 | 58.8893 | 58.8893 | 125.5433 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 79.9946 | 32.1739 | 765739.2979 | 63.8116 | 63.8116 | 131.5996 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 82.4764 | 34.6558 | 824807.2262 | 68.7339 | 68.7339 | 137.6559 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 84.9582 | 37.1376 | 883875.1545 | 73.6563 | 73.6563 | 143.7123 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 87.4401 | 39.6195 | 942943.0827 | 78.5786 | 78.5786 | 149.7686 | 80 | 60 | 32.3215 | 32 | 61.5
8/14/20XX 6:00:00 PM | 0.75 | 7 | 76.3 | 63.1 | 81.5784 | 95.4774 | 13.8991 | 60 | 76.3 |  | 76.3 | 85.8871 | 0.1 | 74.23 | 19.23 | 726894 | 60.5745 | 60.5745 | 64.9482 | 17.1275 | 407635.5689 | 33.9696 | 33.9696 | 94.5441 | 0.2 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 67.2747 | 19.4541 | 463007.3377 | 38.5839 | 38.5839 | 99.8829 | 0.3 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 69.6013 | 21.7806 | 518379.1066 | 43.1983 | 43.1983 | 105.2218 | 0.4 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 71.9278 | 24.1072 | 573750.8755 | 47.8126 | 47.8126 | 110.5606 | 0.5 | 75.15 | 20.15 | 761670 | 63.4725 | 63.4725 | 74.2544 | 26.4337 | 629122.6443 | 52.4269 | 52.4269 | 115.8994 | 0.6 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 76.5809 | 28.7603 | 684494.4132 | 57.0412 | 57.0412 | 121.2382 | 0.7 | 75.61 | 20.61 | 779058 | 64.9215 | 64.9215 | 78.9074 | 31.0868 | 739866.1821 | 61.6555 | 61.6555 | 126.577 | 0.8 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 81.234 | 33.4134 | 795237.951 | 66.2698 | 66.2698 | 131.9158 | 0.9 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 83.5605 | 35.7399 | 850609.7198 | 70.8841 | 70.8841 | 137.2546 | 1 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 85.8871 | 38.0664 | 905981.4887 | 75.4985 | 75.4985 | 142.5935 | 75 | 65 | 31.7591 | 32 | 63.1
8/14/20XX 7:00:00 PM | 0.79167 | 7 | 74.5 | 69.7 | 76.7042 | 89.7555 | 13.0512 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/14/20XX 8:00:00 PM | 0.83333 | 7 | 74.1 | 70.7 | 88.5243 | 101.4817 | 12.9575 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/14/20XX 9:00:00 PM | 0.875 | 7 | 73.4 | 73.1 | 86.4044 | 99.0438 | 12.6394 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/14/20XX 10:00:00 PM | 0.91667 | 7 | 73.1 | 72.7 | 85.5092 | 98.0145 | 12.5053 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/14/20XX 11:00:00 PM | 0.95833 | 7 | 72.8 | 74.7 | 84.6221 | 96.9944 | 12.3723 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/14/20XX 12:00:00 AM | 0 | 1 | 72.2 | 74.9 | 82.8715 | 94.9817 | 12.1103 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/15/20XX 1:00:00 AM | 0.041667 | 1 | 71.9 | 73.8 | 82.008 | 93.989 | 11.9811 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/15/20XX 2:00:00 AM | 0.083333 | 1 | 71 | 77.1 | 79.4639 | 91.0648 | 11.6009 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/15/20XX 3:00:00 AM | 0.125 | 1 | 70.5 | 78.4 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/15/20XX 4:00:00 AM | 0.16667 | 1 | 70.1 | 78.8 | 76.9888 | 88.2203 | 11.2316 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/15/20XX 5:00:00 AM | 0.20833 | 1 | 69.8 | 79.2 | 76.1788 | 87.2896 | 11.1108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/15/20XX 6:00:00 AM | 0.25 | 1 | 70 | 78.7 | 76.7179 | 87.9091 | 11.1912 | 70 | 70 |  | 70 | 86.4543 | 0.1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 65.0049 | 17.1843 | 408985.51 | 34.0821 | 34.0821 | 92.6721 | 0.2 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 67.3882 | 19.5675 | 465707.22 | 38.8089 | 38.8089 | 96.1389 | 0.3 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 69.7714 | 21.9508 | 522428.93 | 43.5357 | 43.5357 | 99.6057 | 0.4 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 72.1547 | 24.3341 | 579150.64 | 48.2626 | 48.2626 | 103.0726 | 0.5 | 72 | 17 | 642600 | 53.55 | 53.55 | 74.538 | 26.7173 | 635872.35 | 52.9894 | 52.9894 | 106.5394 | 0.6 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 76.9212 | 29.1006 | 692594.06 | 57.7162 | 57.7162 | 110.0062 | 0.7 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 79.3045 | 31.4839 | 749315.77 | 62.443 | 62.443 | 113.473 | 0.8 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 81.6878 | 33.8671 | 806037.48 | 67.1698 | 67.1698 | 116.9398 | 0.9 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 84.071 | 36.2504 | 862759.1899 | 71.8966 | 71.8966 | 120.4066 | 1 | 70 | 15 | 567000 | 47.25 | 47.25 | 86.4543 | 38.6337 | 919480.8999 | 76.6234 | 76.6234 | 123.8734 | 70 | 80 | 30.3013 | 30 | 78.7
8/15/20XX 7:00:00 AM | 0.29167 | 1 | 71 | 77.9 | 79.4639 | 91.0648 | 11.6009 | 70 | 71 |  | 71 | 88.6286 | 0.1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 65.2223 | 17.4017 | 414160.4727 | 34.5134 | 34.5134 | 93.4184 | 0.2 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 67.823 | 20.0024 | 476057.1454 | 39.6714 | 39.6714 | 97.6314 | 0.3 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 70.4237 | 22.6031 | 537953.8181 | 44.8295 | 44.8295 | 101.8445 | 0.4 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 73.0244 | 25.2038 | 599850.4907 | 49.9875 | 49.9875 | 106.0575 | 0.5 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 75.6251 | 27.8045 | 661747.1634 | 55.1456 | 55.1456 | 110.2706 | 0.6 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 78.2258 | 30.4052 | 723643.8361 | 60.3037 | 60.3037 | 114.4837 | 0.7 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 80.8265 | 33.0059 | 785540.5088 | 65.4617 | 65.4617 | 118.6967 | 0.8 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 83.4272 | 35.6066 | 847437.1815 | 70.6198 | 70.6198 | 122.9098 | 0.9 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 86.0279 | 38.2073 | 909333.8542 | 75.7778 | 75.7778 | 127.1228 | 1 | 71 | 16 | 604800 | 50.4 | 50.4 | 88.6286 | 40.808 | 971230.5269 | 80.9359 | 80.9359 | 131.3359 | 70 | 80 | 30.8865 | 30 | 77.9
8/15/20XX 8:00:00 AM | 0.33333 | 1 | 72.8 | 72.9 | 84.6221 | 96.9944 | 12.3723 | 70 | 72.8 |  | 72.8 | 88.2101 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.1805 | 17.3598 | 413164.2373 | 34.4304 | 34.4304 | 93.9024 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 67.7393 | 19.9187 | 474064.6746 | 39.5054 | 39.5054 | 98.5994 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 70.2982 | 22.4775 | 534965.1119 | 44.5804 | 44.5804 | 103.2964 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 72.857 | 25.0364 | 595865.5492 | 49.6555 | 49.6555 | 107.9935 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 75.4158 | 27.5952 | 656765.9865 | 54.7305 | 54.7305 | 112.6905 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 77.9747 | 30.1541 | 717666.4238 | 59.8055 | 59.8055 | 117.3875 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 80.5335 | 32.7129 | 778566.8611 | 64.8806 | 64.8806 | 122.0846 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 83.0924 | 35.2717 | 839467.2984 | 69.9556 | 69.9556 | 126.7816 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 85.6512 | 37.8306 | 900367.7357 | 75.0306 | 75.0306 | 131.4786 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 88.2101 | 40.3894 | 961268.173 | 80.1057 | 80.1057 | 136.1757 | 75 | 75 | 31.2632 | 32 | 72.9
8/15/20XX 9:00:00 AM | 0.375 | 1 | 74.7 | 68.8 | 77.2333 | 90.3765 | 13.1432 | 60 | 74.7 |  | 74.7 | 88.7993 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 65.2394 | 17.4188 | 414566.689 | 34.5472 | 34.5472 | 94.6177 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 67.8572 | 20.0365 | 476869.5779 | 39.7391 | 39.7391 | 100.0301 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 70.4749 | 22.6543 | 539172.4669 | 44.931 | 44.931 | 105.4425 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 73.0927 | 25.2721 | 601475.3559 | 50.1229 | 50.1229 | 110.8549 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 75.7105 | 27.8898 | 663778.2449 | 55.3149 | 55.3149 | 116.2674 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 78.3282 | 30.5076 | 726081.1338 | 60.5068 | 60.5068 | 121.6798 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 80.946 | 33.1254 | 788384.0228 | 65.6987 | 65.6987 | 127.0922 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 83.5638 | 35.7431 | 850686.9118 | 70.8906 | 70.8906 | 132.5046 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 86.1815 | 38.3609 | 912989.8007 | 76.0825 | 76.0825 | 137.917 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 88.7993 | 40.9787 | 975292.6897 | 81.2744 | 81.2744 | 143.3294 | 75 | 70 | 31.8221 | 32 | 68.8
8/15/20XX 10:00:00 AM | 0.41667 | 1 | 77.1 | 63.1 | 83.8273 | 98.1177 | 14.2905 | 60 | 77.1 |  | 77.1 | 88.2573 | 0.1 | 74.31 | 19.31 | 729918 | 60.8265 | 60.8265 | 65.1852 | 17.3646 | 413276.7078 | 34.4397 | 34.4397 | 95.2662 | 0.2 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 67.7488 | 19.9281 | 474289.6155 | 39.5241 | 39.5241 | 101.3271 | 0.3 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 70.3123 | 22.4917 | 535302.5233 | 44.6085 | 44.6085 | 107.388 | 0.4 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 72.8759 | 25.0553 | 596315.4311 | 49.693 | 49.693 | 113.449 | 0.5 | 75.55 | 20.55 | 776790 | 64.7325 | 64.7325 | 75.4395 | 27.6188 | 657328.3389 | 54.7774 | 54.7774 | 119.5099 | 0.6 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 78.003 | 30.1824 | 718341.2466 | 59.8618 | 59.8618 | 125.5708 | 0.7 | 76.17 | 21.17 | 800226 | 66.6855 | 66.6855 | 80.5666 | 32.746 | 779354.1544 | 64.9462 | 64.9462 | 131.6317 | 0.8 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 83.1302 | 35.3095 | 840367.0622 | 70.0306 | 70.0306 | 137.6926 | 0.9 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 85.6937 | 37.8731 | 901379.97 | 75.115 | 75.115 | 143.7535 | 1 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 88.2573 | 40.4367 | 962392.8777 | 80.1994 | 80.1994 | 149.8144 | 75 | 65 | 32.3267 | 32 | 63.1
8/15/20XX 11:00:00 AM | 0.45833 | 1 | 79 | 59.3 | 74.2046 | 89.3778 | 15.1731 | 50 | 79 |  | 79 | 88.3156 | 0.1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 65.191 | 17.3704 | 413415.5214 | 34.4513 | 34.4513 | 95.8763 | 0.2 | 75 | 20 | 756000 | 63 | 63 | 67.7604 | 19.9398 | 474567.2428 | 39.5473 | 39.5473 | 102.5473 | 0.3 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 70.3298 | 22.5092 | 535718.9642 | 44.6432 | 44.6432 | 109.2182 | 0.4 | 76 | 21 | 793800 | 66.15 | 66.15 | 72.8992 | 25.0786 | 596870.6856 | 49.7392 | 49.7392 | 115.8892 | 0.5 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 75.4686 | 27.648 | 658022.407 | 54.8352 | 54.8352 | 122.5602 | 0.6 | 77 | 22 | 831600 | 69.3 | 69.3 | 78.038 | 30.2174 | 719174.1284 | 59.9312 | 59.9312 | 129.2312 | 0.7 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 80.6074 | 32.7868 | 780325.8498 | 65.0272 | 65.0272 | 135.9022 | 0.8 | 78 | 23 | 869400 | 72.45 | 72.45 | 83.1768 | 35.3562 | 841477.5712 | 70.1231 | 70.1231 | 142.5731 | 0.9 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 85.7462 | 37.9256 | 902629.2926 | 75.2191 | 75.2191 | 149.2441 | 1 | 79 | 24 | 907200 | 75.6 | 75.6 | 88.3156 | 40.495 | 963781.014 | 80.3151 | 80.3151 | 155.9151 | 80 | 60 | 32.8025 | 32 | 59.3
8/15/20XX 12:00:00 PM | 0.5 | 1 | 79.5 | 58.5 | 75.4555 | 90.8883 | 15.4328 | 50 | 79.5 |  | 79.5 | 88.5734 | 0.1 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 65.2168 | 17.3962 | 414028.9445 | 34.5024 | 34.5024 | 96.0849 | 0.2 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 67.812 | 19.9913 | 475794.089 | 39.6495 | 39.6495 | 102.9645 | 0.3 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 70.4072 | 22.5865 | 537559.2336 | 44.7966 | 44.7966 | 109.8441 | 0.4 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 73.0023 | 25.1817 | 599324.3781 | 49.9437 | 49.9437 | 116.7237 | 0.5 | 76.75 | 21.75 | 822150 | 68.5125 | 68.5125 | 75.5975 | 27.7769 | 661089.5226 | 55.0908 | 55.0908 | 123.6033 | 0.6 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 78.1927 | 30.372 | 722854.6671 | 60.2379 | 60.2379 | 130.4829 | 0.7 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 80.7879 | 32.9672 | 784619.8117 | 65.385 | 65.385 | 137.3625 | 0.8 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 83.383 | 35.5624 | 846384.9562 | 70.5321 | 70.5321 | 144.2421 | 0.9 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 85.9782 | 38.1576 | 908150.1007 | 75.6792 | 75.6792 | 151.1217 | 1 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 88.5734 | 40.7527 | 969915.2452 | 80.8263 | 80.8263 | 158.0013 | 80 | 60 | 32.9657 | 32 | 58.5
8/15/20XX 1:00:00 PM | 0.54167 | 1 | 79.2 | 60 | 89.9794 | 105.341 | 15.3616 | 60 | 79.2 |  | 79.2 | 89.9794 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 65.3574 | 17.5368 | 417375.3934 | 34.7813 | 34.7813 | 96.2693 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 68.0932 | 20.2726 | 482486.9868 | 40.2072 | 40.2072 | 103.3332 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 70.829 | 23.0083 | 547598.5803 | 45.6332 | 45.6332 | 110.3972 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 73.5648 | 25.7441 | 612710.1737 | 51.0592 | 51.0592 | 117.4612 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 76.3005 | 28.4799 | 677821.7671 | 56.4851 | 56.4851 | 124.5251 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 79.0363 | 31.2157 | 742933.3605 | 61.9111 | 61.9111 | 131.5891 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 81.7721 | 33.9515 | 808044.9539 | 67.3371 | 67.3371 | 138.6531 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 84.5079 | 36.6872 | 873156.5474 | 72.763 | 72.763 | 145.717 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 87.2437 | 39.423 | 938268.1408 | 78.189 | 78.189 | 152.781 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 89.9794 | 42.1588 | 1003379.7342 | 83.615 | 83.615 | 159.845 | 80 | 60 | 33.1124 | 34 | 60
8/15/20XX 2:00:00 PM | 0.58333 | 1 | 79 | 60.3 | 89.3778 | 104.6345 | 15.2568 | 60 | 79 |  | 79 | 89.8355 | 0.1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 65.343 | 17.5224 | 417032.6965 | 34.7527 | 34.7527 | 96.1777 | 0.2 | 75 | 20 | 756000 | 63 | 63 | 68.0644 | 20.2438 | 481801.593 | 40.1501 | 40.1501 | 103.1501 | 0.3 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 70.7858 | 22.9651 | 546570.4895 | 45.5475 | 45.5475 | 110.1225 | 0.4 | 76 | 21 | 793800 | 66.15 | 66.15 | 73.5072 | 25.6865 | 611339.386 | 50.9449 | 50.9449 | 117.0949 | 0.5 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 76.2285 | 28.4079 | 676108.2825 | 56.3424 | 56.3424 | 124.0674 | 0.6 | 77 | 22 | 831600 | 69.3 | 69.3 | 78.9499 | 31.1293 | 740877.179 | 61.7398 | 61.7398 | 131.0398 | 0.7 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 81.6713 | 33.8507 | 805646.0756 | 67.1372 | 67.1372 | 138.0122 | 0.8 | 78 | 23 | 869400 | 72.45 | 72.45 | 84.3927 | 36.5721 | 870414.9721 | 72.5346 | 72.5346 | 144.9846 | 0.9 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 87.1141 | 39.2934 | 935183.8686 | 77.932 | 77.932 | 151.957 | 1 | 79 | 24 | 907200 | 75.6 | 75.6 | 89.8355 | 42.0148 | 999952.7651 | 83.3294 | 83.3294 | 158.9294 | 80 | 60 | 33.0407 | 34 | 60.3
8/15/20XX 3:00:00 PM | 0.625 | 1 | 78.4 | 63.6 | 87.5927 | 102.5387 | 14.946 | 60 | 78.4 |  | 78.4 | 92.9733 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 65.6568 | 17.8362 | 424500.7407 | 35.3751 | 35.3751 | 96.6111 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 68.692 | 20.8713 | 496737.6813 | 41.3948 | 41.3948 | 104.0168 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 71.7271 | 23.9065 | 568974.622 | 47.4146 | 47.4146 | 111.4226 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 74.7623 | 26.9417 | 641211.5626 | 53.4343 | 53.4343 | 118.8283 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 77.7975 | 29.9768 | 713448.5033 | 59.454 | 59.454 | 126.234 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 80.8326 | 33.012 | 785685.444 | 65.4738 | 65.4738 | 133.6398 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 83.8678 | 36.0472 | 857922.3846 | 71.4935 | 71.4935 | 141.0455 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 86.903 | 39.0823 | 930159.3253 | 77.5133 | 77.5133 | 148.4513 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 89.9381 | 42.1175 | 1002396.2659 | 83.533 | 83.533 | 155.857 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 92.9733 | 45.1527 | 1074633.2066 | 89.5528 | 89.5528 | 163.2628 | 80 | 65 | 33.385 | 34 | 63.6
8/15/20XX 4:00:00 PM | 0.66667 | 1 | 77.5 | 64.9 | 84.9711 | 99.4607 | 14.4896 | 60 | 77.5 |  | 77.5 | 92.071 | 0.1 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 65.5666 | 17.7459 | 422353.3289 | 35.1961 | 35.1961 | 96.1486 | 0.2 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 68.5115 | 20.6909 | 492442.8578 | 41.0369 | 41.0369 | 103.0919 | 0.3 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 71.4564 | 23.6358 | 562532.3868 | 46.8777 | 46.8777 | 110.0352 | 0.4 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 74.4014 | 26.5808 | 632621.9157 | 52.7185 | 52.7185 | 116.9785 | 0.5 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 77.3463 | 29.5257 | 702711.4446 | 58.5593 | 58.5593 | 123.9218 | 0.6 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 80.2913 | 32.4706 | 772800.9735 | 64.4001 | 64.4001 | 130.8651 | 0.7 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 83.2362 | 35.4156 | 842890.5024 | 70.2409 | 70.2409 | 137.8084 | 0.8 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 86.1811 | 38.3605 | 912980.0314 | 76.0817 | 76.0817 | 144.7517 | 0.9 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 89.1261 | 41.3054 | 983069.5603 | 81.9225 | 81.9225 | 151.695 | 1 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 92.071 | 44.2504 | 1053159.0892 | 87.7633 | 87.7633 | 158.6383 | 75 | 65 | 33.0223 | 34 | 64.9
8/15/20XX 5:00:00 PM | 0.70833 | 1 | 76.9 | 65.3 | 83.2602 | 97.452 | 14.1918 | 60 | 76.9 |  | 76.9 | 90.7818 | 0.1 | 74.29 | 19.29 | 729162 | 60.7635 | 60.7635 | 65.4377 | 17.617 | 419285.091 | 34.9404 | 34.9404 | 95.7039 | 0.2 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 68.2537 | 20.433 | 486306.3821 | 40.5255 | 40.5255 | 102.2025 | 0.3 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 71.0697 | 23.2491 | 553327.6731 | 46.1106 | 46.1106 | 108.7011 | 0.4 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 73.8857 | 26.0651 | 620348.9642 | 51.6957 | 51.6957 | 115.1997 | 0.5 | 75.45 | 20.45 | 773010 | 64.4175 | 64.4175 | 76.7017 | 28.8811 | 687370.2552 | 57.2809 | 57.2809 | 121.6984 | 0.6 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 79.5178 | 31.6971 | 754391.5463 | 62.866 | 62.866 | 128.197 | 0.7 | 76.03 | 21.03 | 794934 | 66.2445 | 66.2445 | 82.3338 | 34.5131 | 821412.8373 | 68.4511 | 68.4511 | 134.6956 | 0.8 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 85.1498 | 37.3292 | 888434.1284 | 74.0362 | 74.0362 | 141.1942 | 0.9 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 87.9658 | 40.1452 | 955455.4194 | 79.6213 | 79.6213 | 147.6928 | 1 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 90.7818 | 42.9612 | 1022476.7104 | 85.2064 | 85.2064 | 154.1914 | 75 | 65 | 32.6729 | 32 | 65.3
8/15/20XX 6:00:00 PM | 0.75 | 1 | 76.2 | 66.8 | 81.3009 | 95.1517 | 13.8508 | 60 | 76.2 |  | 76.2 | 90.7194 | 0.1 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 65.4314 | 17.6108 | 419136.504 | 34.928 | 34.928 | 95.471 | 0.2 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 68.2412 | 20.4206 | 486009.208 | 40.5008 | 40.5008 | 101.7368 | 0.3 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 71.051 | 23.2303 | 552881.9119 | 46.0735 | 46.0735 | 108.0025 | 0.4 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 73.8607 | 26.0401 | 619754.6159 | 51.6462 | 51.6462 | 114.2682 | 0.5 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 76.6705 | 28.8499 | 686627.3199 | 57.2189 | 57.2189 | 120.5339 | 0.6 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 79.4803 | 31.6597 | 753500.0239 | 62.7917 | 62.7917 | 126.7997 | 0.7 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 82.2901 | 34.4694 | 820372.7278 | 68.3644 | 68.3644 | 133.0654 | 0.8 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 85.0999 | 37.2792 | 887245.4318 | 73.9371 | 73.9371 | 139.3311 | 0.9 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 87.9096 | 40.089 | 954118.1358 | 79.5098 | 79.5098 | 145.5968 | 1 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 90.7194 | 42.8988 | 1020990.8398 | 85.0826 | 85.0826 | 151.8626 | 75 | 65 | 32.4911 | 32 | 66.8
8/15/20XX 7:00:00 PM | 0.79167 | 1 | 74.8 | 69 | 77.499 | 90.6884 | 13.1894 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/15/20XX 8:00:00 PM | 0.83333 | 1 | 74 | 72.9 | 88.2187 | 101.1303 | 12.9116 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/15/20XX 9:00:00 PM | 0.875 | 1 | 74 | 72.5 | 88.2187 | 101.1303 | 12.9116 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/15/20XX 10:00:00 PM | 0.91667 | 1 | 73.6 | 74.5 | 87.0056 | 99.7352 | 12.7296 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/15/20XX 11:00:00 PM | 0.95833 | 1 | 73.3 | 75.2 | 86.1051 | 98.6997 | 12.5946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/15/20XX 12:00:00 AM | 0 | 2 | 72.9 | 75.1 | 84.9169 | 97.3334 | 12.4165 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/16/20XX 1:00:00 AM | 0.041667 | 2 | 72.5 | 75.9 | 83.7428 | 95.9835 | 12.2407 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/16/20XX 2:00:00 AM | 0.083333 | 2 | 71.9 | 77.5 | 82.008 | 93.989 | 11.9811 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/16/20XX 3:00:00 AM | 0.125 | 2 | 71.4 | 80 | 92.3545 | 104.1348 | 11.7803 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/16/20XX 4:00:00 AM | 0.16667 | 2 | 71.3 | 80.1 | 92.0306 | 103.7683 | 11.7376 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/16/20XX 5:00:00 AM | 0.20833 | 2 | 70.7 | 81.4 | 90.1079 | 101.5924 | 11.4845 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/16/20XX 6:00:00 AM | 0.25 | 2 | 70.6 | 81.8 | 89.7909 | 101.2336 | 11.4428 | 80 | 70.6 |  | 70.6 | 91.8506 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 65.5445 | 17.7239 | 421828.6321 | 35.1524 | 35.1524 | 93.9314 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 68.4674 | 20.6468 | 491393.4642 | 40.9495 | 40.9495 | 98.6575 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 71.3903 | 23.5697 | 560958.2964 | 46.7465 | 46.7465 | 103.3835 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 74.3132 | 26.4926 | 630523.1285 | 52.5436 | 52.5436 | 108.1096 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 77.2361 | 29.4155 | 700087.9606 | 58.3407 | 58.3407 | 112.8357 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 80.159 | 32.3384 | 769652.7927 | 64.1377 | 64.1377 | 117.5617 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 83.0819 | 35.2612 | 839217.6249 | 69.9348 | 69.9348 | 122.2878 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 86.0048 | 38.1841 | 908782.457 | 75.7319 | 75.7319 | 127.0139 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 88.9277 | 41.107 | 978347.2891 | 81.5289 | 81.5289 | 131.7399 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 91.8506 | 44.0299 | 1047912.1212 | 87.326 | 87.326 | 136.466 | 70 | 80 | 31.2916 | 32 | 81.8
8/16/20XX 7:00:00 AM | 0.29167 | 2 | 71.8 | 77.4 | 81.7218 | 93.6601 | 11.9383 | 70 | 71.8 |  | 71.8 | 90.5562 | 0.1 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 65.4151 | 17.5945 | 418748.0384 | 34.8957 | 34.8957 | 94.0527 | 0.2 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 68.2085 | 20.3879 | 485232.2767 | 40.436 | 40.436 | 98.9 | 0.3 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 71.002 | 23.1814 | 551716.5151 | 45.9764 | 45.9764 | 103.7474 | 0.4 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 73.7955 | 25.9748 | 618200.7534 | 51.5167 | 51.5167 | 108.5947 | 0.5 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 76.5889 | 28.7683 | 684684.9918 | 57.0571 | 57.0571 | 113.4421 | 0.6 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 79.3824 | 31.5617 | 751169.2302 | 62.5974 | 62.5974 | 118.2894 | 0.7 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 82.1758 | 34.3552 | 817653.4685 | 68.1378 | 68.1378 | 123.1368 | 0.8 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 84.9693 | 37.1486 | 884137.7069 | 73.6781 | 73.6781 | 127.9841 | 0.9 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 87.7627 | 39.9421 | 950621.9453 | 79.2185 | 79.2185 | 132.8315 | 1 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 90.5562 | 42.7356 | 1017106.1836 | 84.7588 | 84.7588 | 137.6788 | 70 | 75 | 31.3843 | 32 | 77.4
8/16/20XX 8:00:00 AM | 0.33333 | 2 | 73.4 | 73 | 86.4044 | 99.0438 | 12.6394 | 70 | 73.4 |  | 73.4 | 90.1962 | 0.1 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 65.3791 | 17.5585 | 417891.2676 | 34.8243 | 34.8243 | 94.4853 | 0.2 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 68.1365 | 20.3159 | 483518.7353 | 40.2932 | 40.2932 | 99.7652 | 0.3 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 70.894 | 23.0734 | 549146.2029 | 45.7622 | 45.7622 | 105.0452 | 0.4 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 73.6515 | 25.8308 | 614773.6705 | 51.2311 | 51.2311 | 110.3251 | 0.5 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 76.4089 | 28.5883 | 680401.1381 | 56.7001 | 56.7001 | 115.6051 | 0.6 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 79.1664 | 31.3457 | 746028.6058 | 62.1691 | 62.1691 | 120.8851 | 0.7 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 81.9238 | 34.1032 | 811656.0734 | 67.638 | 67.638 | 126.165 | 0.8 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 84.6813 | 36.8607 | 877283.541 | 73.107 | 73.107 | 131.445 | 0.9 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 87.4387 | 39.6181 | 942911.0086 | 78.5759 | 78.5759 | 136.7249 | 1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 90.1962 | 42.3756 | 1008538.4763 | 84.0449 | 84.0449 | 142.0049 | 75 | 75 | 31.7212 | 32 | 73
8/16/20XX 9:00:00 AM | 0.375 | 2 | 74.9 | 69.9 | 77.7654 | 91.0012 | 13.2358 | 60 | 74.9 |  | 74.9 | 90.8688 | 0.1 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 65.4464 | 17.6257 | 419492.1572 | 34.9577 | 34.9577 | 95.0912 | 0.2 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 68.2711 | 20.4504 | 486720.5144 | 40.56 | 40.56 | 100.977 | 0.3 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 71.0958 | 23.2752 | 553948.8716 | 46.1624 | 46.1624 | 106.8629 | 0.4 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 73.9205 | 26.0999 | 621177.2288 | 51.7648 | 51.7648 | 112.7488 | 0.5 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 76.7452 | 28.9246 | 688405.586 | 57.3671 | 57.3671 | 118.6346 | 0.6 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 79.57 | 31.7493 | 755633.9432 | 62.9695 | 62.9695 | 124.5205 | 0.7 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 82.3947 | 34.574 | 822862.3004 | 68.5719 | 68.5719 | 130.4064 | 0.8 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 85.2194 | 37.3988 | 890090.6576 | 74.1742 | 74.1742 | 136.2922 | 0.9 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 88.0441 | 40.2235 | 957319.0148 | 79.7766 | 79.7766 | 142.1781 | 1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 90.8688 | 43.0482 | 1024547.372 | 85.3789 | 85.3789 | 148.0639 | 75 | 70 | 32.195 | 32 | 69.9
8/16/20XX 10:00:00 AM | 0.41667 | 2 | 78 | 63.3 | 86.4193 | 101.161 | 14.7417 | 60 | 78 |  | 78 | 91.2841 | 0.1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 65.4879 | 17.6672 | 420480.4685 | 35.04 | 35.04 | 96.15 | 0.2 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 68.3541 | 20.5335 | 488697.137 | 40.7248 | 40.7248 | 103.0948 | 0.3 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 71.2204 | 23.3997 | 556913.8054 | 46.4095 | 46.4095 | 110.0395 | 0.4 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 74.0866 | 26.266 | 625130.4739 | 52.0942 | 52.0942 | 116.9842 | 0.5 | 76 | 21 | 793800 | 66.15 | 66.15 | 76.9529 | 29.1322 | 693347.1424 | 57.7789 | 57.7789 | 123.9289 | 0.6 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 79.8191 | 31.9985 | 761563.8109 | 63.4637 | 63.4637 | 130.8737 | 0.7 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 82.6854 | 34.8647 | 829780.4793 | 69.1484 | 69.1484 | 137.8184 | 0.8 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 85.5516 | 37.731 | 897997.1478 | 74.8331 | 74.8331 | 144.7631 | 0.9 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 88.4179 | 40.5972 | 966213.8163 | 80.5178 | 80.5178 | 151.7078 | 1 | 78 | 23 | 869400 | 72.45 | 72.45 | 91.2841 | 43.4635 | 1034430.4848 | 86.2025 | 86.2025 | 158.6525 | 80 | 65 | 33.022 | 34 | 63.3
8/16/20XX 11:00:00 AM | 0.45833 | 2 | 80.9 | 54.6 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 86.4937 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 65.0088 | 17.1882 | 409079.2995 | 34.0899 | 34.0899 | 96.1134 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 67.396 | 19.5754 | 465894.7989 | 38.8246 | 38.8246 | 103.0216 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 69.7832 | 21.9626 | 522710.2984 | 43.5592 | 43.5592 | 109.9297 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 72.1705 | 24.3498 | 579525.7978 | 48.2938 | 48.2938 | 116.8378 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 74.5577 | 26.737 | 636341.2973 | 53.0284 | 53.0284 | 123.7459 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 76.9449 | 29.1242 | 693156.7967 | 57.7631 | 57.7631 | 130.6541 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 79.3321 | 31.5114 | 749972.2962 | 62.4977 | 62.4977 | 137.5622 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 81.7193 | 33.8986 | 806787.7957 | 67.2323 | 67.2323 | 144.4703 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 84.1065 | 36.2859 | 863603.2951 | 71.9669 | 71.9669 | 151.3784 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 86.4937 | 38.6731 | 920418.7946 | 76.7016 | 76.7016 | 158.2866 | 80 | 55 | 32.9834 | 32 | 54.6
8/16/20XX 12:00:00 PM | 0.5 | 2 | 82.8 | 50.2 | 84.1546 | 101.3965 | 17.2419 | 50 | 82.8 |  | 82.8 | 84.4995 | 0.1 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 64.8094 | 16.9888 | 404333.0719 | 33.6944 | 33.6944 | 96.3164 | 0.2 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 66.9972 | 19.1766 | 456402.3438 | 38.0335 | 38.0335 | 103.4275 | 0.3 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 69.185 | 21.3644 | 508471.6156 | 42.3726 | 42.3726 | 110.5386 | 0.4 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 71.3728 | 23.5521 | 560540.8875 | 46.7117 | 46.7117 | 117.6497 | 0.5 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 73.5606 | 25.7399 | 612610.1594 | 51.0508 | 51.0508 | 124.7608 | 0.6 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 75.7483 | 27.9277 | 664679.4313 | 55.39 | 55.39 | 131.872 | 0.7 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 77.9361 | 30.1155 | 716748.7031 | 59.7291 | 59.7291 | 138.9831 | 0.8 | 81.04 | 26.04 | 984312 | 82.026 | 82.026 | 80.1239 | 32.3033 | 768817.975 | 64.0682 | 64.0682 | 146.0942 | 0.9 | 81.92 | 26.92 | 1017576 | 84.798 | 84.798 | 82.3117 | 34.4911 | 820887.2469 | 68.4073 | 68.4073 | 153.2053 | 1 | 82.8 | 27.8 | 1050840 | 87.57 | 87.57 | 84.4995 | 36.6788 | 872956.5188 | 72.7464 | 72.7464 | 160.3164 | 85 | 50 | 33.1367 | 34 | 50.2
8/16/20XX 1:00:00 PM | 0.54167 | 2 | 83.1 | 51.8 | 84.9846 | 102.3992 | 17.4147 | 50 | 83.1 |  | 83.1 | 88.1192 | 0.1 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 65.1714 | 17.3508 | 412948.0151 | 34.4123 | 34.4123 | 97.1288 | 0.2 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 67.7211 | 19.9005 | 473632.2303 | 39.4694 | 39.4694 | 105.0524 | 0.3 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 70.2709 | 22.4503 | 534316.4454 | 44.5264 | 44.5264 | 112.9759 | 0.4 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 72.8207 | 25 | 595000.6606 | 49.5834 | 49.5834 | 120.8994 | 0.5 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 75.3704 | 27.5498 | 655684.8757 | 54.6404 | 54.6404 | 128.8229 | 0.6 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 77.9202 | 30.0995 | 716369.0909 | 59.6974 | 59.6974 | 136.7464 | 0.7 | 80.37 | 25.37 | 958986 | 79.9155 | 79.9155 | 80.4699 | 32.6493 | 777053.306 | 64.7544 | 64.7544 | 144.6699 | 0.8 | 81.28 | 26.28 | 993384 | 82.782 | 82.782 | 83.0197 | 35.1991 | 837737.5212 | 69.8115 | 69.8115 | 152.5935 | 0.9 | 82.19 | 27.19 | 1027782 | 85.6485 | 85.6485 | 85.5694 | 37.7488 | 898421.7363 | 74.8685 | 74.8685 | 160.517 | 1 | 83.1 | 28.1 | 1062180 | 88.515 | 88.515 | 88.1192 | 40.2986 | 959105.9514 | 79.9255 | 79.9255 | 168.4405 | 85 | 50 | 33.7786 | 34 | 51.8
8/16/20XX 2:00:00 PM | 0.58333 | 2 | 83.3 | 51.6 | 85.5415 | 103.0722 | 17.5307 | 50 | 83.3 |  | 83.3 | 88.3464 | 0.1 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 65.1941 | 17.3735 | 413488.8461 | 34.4574 | 34.4574 | 97.2369 | 0.2 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 67.7666 | 19.946 | 474713.8922 | 39.5595 | 39.5595 | 105.2685 | 0.3 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 70.3391 | 22.5184 | 535938.9383 | 44.6616 | 44.6616 | 113.3001 | 0.4 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 72.9116 | 25.0909 | 597163.9844 | 49.7637 | 49.7637 | 121.3317 | 0.5 | 78.65 | 23.65 | 893970 | 74.4975 | 74.4975 | 75.484 | 27.6634 | 658389.0305 | 54.8658 | 54.8658 | 129.3633 | 0.6 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 78.0565 | 30.2359 | 719614.0766 | 59.9678 | 59.9678 | 137.3948 | 0.7 | 80.51 | 25.51 | 964278 | 80.3565 | 80.3565 | 80.629 | 32.8084 | 780839.1227 | 65.0699 | 65.0699 | 145.4264 | 0.8 | 81.44 | 26.44 | 999432 | 83.286 | 83.286 | 83.2015 | 35.3808 | 842064.1688 | 70.172 | 70.172 | 153.458 | 0.9 | 82.37 | 27.37 | 1034586 | 86.2155 | 86.2155 | 85.774 | 37.9533 | 903289.2149 | 75.2741 | 75.2741 | 161.4896 | 1 | 83.3 | 28.3 | 1069740 | 89.145 | 89.145 | 88.3464 | 40.5258 | 964514.261 | 80.3762 | 80.3762 | 169.5212 | 85 | 50 | 33.8634 | 34 | 51.6
8/16/20XX 3:00:00 PM | 0.625 | 2 | 82.7 | 51.9 | 83.8795 | 101.064 | 17.1846 | 50 | 82.7 |  | 82.7 | 87.1445 | 0.1 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 65.0739 | 17.2533 | 410628.3246 | 34.219 | 34.219 | 96.8095 | 0.2 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 67.5262 | 19.7056 | 468992.8492 | 39.0827 | 39.0827 | 104.4137 | 0.3 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 69.9785 | 22.1579 | 527357.3738 | 43.9464 | 43.9464 | 112.0179 | 0.4 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 72.4308 | 24.6102 | 585721.8984 | 48.8102 | 48.8102 | 119.6222 | 0.5 | 78.35 | 23.35 | 882630 | 73.5525 | 73.5525 | 74.8831 | 27.0625 | 644086.423 | 53.6739 | 53.6739 | 127.2264 | 0.6 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 77.3354 | 29.5147 | 702450.9476 | 58.5376 | 58.5376 | 134.8306 | 0.7 | 80.09 | 25.09 | 948402 | 79.0335 | 79.0335 | 79.7877 | 31.967 | 760815.4722 | 63.4013 | 63.4013 | 142.4348 | 0.8 | 80.96 | 25.96 | 981288 | 81.774 | 81.774 | 82.24 | 34.4193 | 819179.9969 | 68.265 | 68.265 | 150.039 | 0.9 | 81.83 | 26.83 | 1014174 | 84.5145 | 84.5145 | 84.6923 | 36.8716 | 877544.5215 | 73.1287 | 73.1287 | 157.6432 | 1 | 82.7 | 27.7 | 1047060 | 87.255 | 87.255 | 87.1445 | 39.3239 | 935909.0461 | 77.9924 | 77.9924 | 165.2474 | 85 | 50 | 33.5274 | 34 | 51.9
8/16/20XX 4:00:00 PM | 0.66667 | 2 | 82.2 | 55.7 | 82.5146 | 99.4151 | 16.9005 | 50 | 82.2 |  | 82.2 | 92.1479 | 0.1 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 65.5743 | 17.7536 | 422536.3055 | 35.2114 | 35.2114 | 97.6444 | 0.2 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 68.5269 | 20.7063 | 492808.811 | 41.0674 | 41.0674 | 106.0834 | 0.3 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 71.4795 | 23.6589 | 563081.3165 | 46.9234 | 46.9234 | 114.5224 | 0.4 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 74.4321 | 26.6115 | 633353.822 | 52.7795 | 52.7795 | 122.9615 | 0.5 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 77.3848 | 29.5641 | 703626.3275 | 58.6355 | 58.6355 | 131.4005 | 0.6 | 78.92 | 23.92 | 904176 | 75.348 | 75.348 | 80.3374 | 32.5168 | 773898.833 | 64.4916 | 64.4916 | 139.8396 | 0.7 | 79.74 | 24.74 | 935172 | 77.931 | 77.931 | 83.29 | 35.4694 | 844171.3385 | 70.3476 | 70.3476 | 148.2786 | 0.8 | 80.56 | 25.56 | 966168 | 80.514 | 80.514 | 86.2426 | 38.422 | 914443.8439 | 76.2037 | 76.2037 | 156.7177 | 0.9 | 81.38 | 26.38 | 997164 | 83.097 | 83.097 | 89.1953 | 41.3746 | 984716.3494 | 82.0597 | 82.0597 | 165.1567 | 1 | 82.2 | 27.2 | 1028160 | 85.68 | 85.68 | 92.1479 | 44.3273 | 1054988.8549 | 87.9157 | 87.9157 | 173.5957 | 80 | 55 | 34.1899 | 34 | 55.7
8/16/20XX 5:00:00 PM | 0.70833 | 2 | 81.8 | 55.9 | 81.4359 | 98.1119 | 16.676 | 50 | 81.8 |  | 81.8 | 91.2747 | 0.1 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 65.4869 | 17.6663 | 420458.1261 | 35.0382 | 35.0382 | 97.3452 | 0.2 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 68.3522 | 20.5316 | 488652.4521 | 40.721 | 40.721 | 105.485 | 0.3 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 71.2176 | 23.3969 | 556846.7782 | 46.4039 | 46.4039 | 113.6249 | 0.4 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 74.0829 | 26.2622 | 625041.1042 | 52.0868 | 52.0868 | 121.7648 | 0.5 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 76.9482 | 29.1275 | 693235.4303 | 57.7696 | 57.7696 | 129.9046 | 0.6 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 79.8135 | 31.9928 | 761429.7563 | 63.4525 | 63.4525 | 138.0445 | 0.7 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 82.6788 | 34.8582 | 829624.0824 | 69.1353 | 69.1353 | 146.1843 | 0.8 | 80.24 | 25.24 | 954072 | 79.506 | 79.506 | 85.5441 | 37.7235 | 897818.4085 | 74.8182 | 74.8182 | 154.3242 | 0.9 | 81.02 | 26.02 | 983556 | 81.963 | 81.963 | 88.4094 | 40.5888 | 966012.7345 | 80.5011 | 80.5011 | 162.4641 | 1 | 81.8 | 26.8 | 1013040 | 84.42 | 84.42 | 91.2747 | 43.4541 | 1034207.0606 | 86.1839 | 86.1839 | 170.6039 | 80 | 55 | 33.9545 | 34 | 55.9
8/16/20XX 6:00:00 PM | 0.75 | 2 | 80.2 | 58.9 | 77.2359 | 93.0386 | 15.8027 | 50 | 80.2 |  | 80.2 | 91.3003 | 0.1 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 65.4895 | 17.6689 | 420519.0769 | 35.0433 | 35.0433 | 96.8463 | 0.2 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 68.3574 | 20.5367 | 488774.3538 | 40.7312 | 40.7312 | 104.4872 | 0.3 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 71.2252 | 23.4046 | 557029.6307 | 46.4191 | 46.4191 | 112.1281 | 0.4 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 74.0931 | 26.2725 | 625284.9077 | 52.1071 | 52.1071 | 119.7691 | 0.5 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 76.961 | 29.1403 | 693540.1846 | 57.795 | 57.795 | 127.41 | 0.6 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 79.8288 | 32.0082 | 761795.4615 | 63.483 | 63.483 | 135.051 | 0.7 | 78.34 | 23.34 | 882252 | 73.521 | 73.521 | 82.6967 | 34.8761 | 830050.7384 | 69.1709 | 69.1709 | 142.6919 | 0.8 | 78.96 | 23.96 | 905688 | 75.474 | 75.474 | 85.5646 | 37.744 | 898306.0153 | 74.8588 | 74.8588 | 150.3328 | 0.9 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 88.4325 | 40.6118 | 966561.2922 | 80.5468 | 80.5468 | 157.9738 | 1 | 80.2 | 25.2 | 952560 | 79.38 | 79.38 | 91.3003 | 43.4797 | 1034816.5691 | 86.2347 | 86.2347 | 165.6147 | 80 | 60 | 33.5653 | 34 | 58.9
8/16/20XX 7:00:00 PM | 0.79167 | 2 | 79 | 60.9 | 89.3778 | 104.6345 | 15.2568 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/16/20XX 8:00:00 PM | 0.83333 | 2 | 77.8 | 63.9 | 85.8376 | 100.478 | 14.6404 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/16/20XX 9:00:00 PM | 0.875 | 2 | 77.3 | 64.9 | 84.3976 | 98.7873 | 14.3897 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/16/20XX 10:00:00 PM | 0.91667 | 2 | 77 | 65.6 | 83.5433 | 97.7844 | 14.241 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/16/20XX 11:00:00 PM | 0.95833 | 2 | 76.2 | 67.6 | 81.3009 | 95.1517 | 13.8508 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/16/20XX 12:00:00 AM | 0 | 3 | 76.2 | 67.7 | 81.3009 | 95.1517 | 13.8508 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/17/20XX 1:00:00 AM | 0.041667 | 3 | 75.2 | 68.6 | 78.5695 | 91.9451 | 13.3756 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/17/20XX 2:00:00 AM | 0.083333 | 3 | 74.7 | 68.1 | 77.2333 | 90.3765 | 13.1432 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/17/20XX 3:00:00 AM | 0.125 | 3 | 73.9 | 68.6 | 75.1356 | 87.9141 | 12.7785 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/17/20XX 4:00:00 AM | 0.16667 | 3 | 72.9 | 70.8 | 84.9169 | 97.3334 | 12.4165 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/17/20XX 5:00:00 AM | 0.20833 | 3 | 72.7 | 70.7 | 84.3281 | 96.6564 | 12.3283 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/17/20XX 6:00:00 AM | 0.25 | 3 | 73 | 70.8 | 85.2126 | 97.6734 | 12.4608 | 70 | 73 |  | 73 | 86.2095 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.9804 | 17.1598 | 408402.9121 | 34.0336 | 34.0336 | 93.5686 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 67.3392 | 19.5186 | 464542.0242 | 38.7118 | 38.7118 | 97.9318 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 69.698 | 21.8774 | 520681.1363 | 43.3901 | 43.3901 | 102.2951 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 72.0568 | 24.2361 | 576820.2484 | 48.0684 | 48.0684 | 106.6584 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 74.4156 | 26.5949 | 632959.3605 | 52.7466 | 52.7466 | 111.0216 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 76.7743 | 28.9537 | 689098.4726 | 57.4249 | 57.4249 | 115.3849 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 79.1331 | 31.3125 | 745237.5847 | 62.1031 | 62.1031 | 119.7481 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 81.4919 | 33.6713 | 801376.6968 | 66.7814 | 66.7814 | 124.1114 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 83.8507 | 36.0301 | 857515.8089 | 71.4597 | 71.4597 | 128.4747 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 86.2095 | 38.3889 | 913654.921 | 76.1379 | 76.1379 | 132.8379 | 75 | 70 | 30.9995 | 30 | 70.8
8/17/20XX 7:00:00 AM | 0.29167 | 3 | 73.8 | 70.8 | 87.6104 | 100.4307 | 12.8203 | 70 | 73.8 |  | 73.8 | 88.636 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 65.2231 | 17.4024 | 414177.9499 | 34.5148 | 34.5148 | 94.3018 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 67.8245 | 20.0039 | 476092.0998 | 39.6743 | 39.6743 | 99.3983 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 70.4259 | 22.6053 | 538006.2497 | 44.8339 | 44.8339 | 104.4949 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 73.0274 | 25.2067 | 599920.3995 | 49.9934 | 49.9934 | 109.5914 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 75.6288 | 27.8082 | 661834.5494 | 55.1529 | 55.1529 | 114.6879 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 78.2302 | 30.4096 | 723748.6993 | 60.3124 | 60.3124 | 119.7844 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 80.8317 | 33.011 | 785662.8492 | 65.4719 | 65.4719 | 124.8809 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 83.4331 | 35.6125 | 847576.9991 | 70.6314 | 70.6314 | 129.9774 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 86.0345 | 38.2139 | 909491.149 | 75.7909 | 75.7909 | 135.0739 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 88.636 | 40.8153 | 971405.2989 | 80.9504 | 80.9504 | 140.1704 | 75 | 70 | 31.5754 | 32 | 70.8
8/17/20XX 8:00:00 AM | 0.33333 | 3 | 75.8 | 66.2 | 80.1988 | 93.8579 | 13.6591 | 60 | 75.8 |  | 75.8 | 88.6674 | 0.1 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 65.2262 | 17.4056 | 414252.8235 | 34.5211 | 34.5211 | 94.9381 | 0.2 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 67.8308 | 20.0102 | 476241.847 | 39.6868 | 39.6868 | 100.6708 | 0.3 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 70.4354 | 22.6147 | 538230.8705 | 44.8526 | 44.8526 | 106.4036 | 0.4 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 73.04 | 25.2193 | 600219.894 | 50.0183 | 50.0183 | 112.1363 | 0.5 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 75.6445 | 27.8239 | 662208.9174 | 55.1841 | 55.1841 | 117.8691 | 0.6 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 78.2491 | 30.4285 | 724197.9409 | 60.3498 | 60.3498 | 123.6018 | 0.7 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 80.8537 | 33.0331 | 786186.9644 | 65.5156 | 65.5156 | 129.3346 | 0.8 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 83.4583 | 35.6376 | 848175.9879 | 70.6813 | 70.6813 | 135.0673 | 0.9 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 86.0629 | 38.2422 | 910165.0114 | 75.8471 | 75.8471 | 140.8001 | 1 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 88.6674 | 40.8468 | 972154.0349 | 81.0128 | 81.0128 | 146.5328 | 75 | 65 | 32.0716 | 32 | 66.2
8/17/20XX 9:00:00 AM | 0.375 | 3 | 77.7 | 63.5 | 85.548 | 100.1379 | 14.59 | 60 | 77.7 |  | 77.7 | 90.6544 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 65.4249 | 17.6043 | 418981.8988 | 34.9152 | 34.9152 | 95.9307 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 68.2282 | 20.4076 | 485699.9976 | 40.475 | 40.475 | 102.656 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 71.0315 | 23.2108 | 552418.0965 | 46.0348 | 46.0348 | 109.3813 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 73.8348 | 26.0141 | 619136.1953 | 51.5947 | 51.5947 | 116.1067 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 76.638 | 28.8174 | 685854.2941 | 57.1545 | 57.1545 | 122.832 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 79.4413 | 31.6207 | 752572.3929 | 62.7144 | 62.7144 | 129.5574 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 82.2446 | 34.424 | 819290.4917 | 68.2742 | 68.2742 | 136.2827 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 85.0479 | 37.2273 | 886008.5906 | 73.834 | 73.834 | 143.008 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 87.8512 | 40.0305 | 952726.6894 | 79.3939 | 79.3939 | 149.7334 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 90.6544 | 42.8338 | 1019444.7882 | 84.9537 | 84.9537 | 156.4587 | 80 | 65 | 32.8496 | 32 | 63.5
8/17/20XX 10:00:00 AM | 0.41667 | 3 | 80.4 | 58.1 | 77.751 | 93.6607 | 15.9097 | 50 | 80.4 |  | 80.4 | 90.6378 | 0.1 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 65.4233 | 17.6026 | 418942.3385 | 34.9119 | 34.9119 | 96.7779 | 0.2 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 68.2249 | 20.4042 | 485620.8771 | 40.4684 | 40.4684 | 104.3504 | 0.3 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 71.0265 | 23.2059 | 552299.4156 | 46.025 | 46.025 | 111.923 | 0.4 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 73.8281 | 26.0075 | 618977.9542 | 51.5815 | 51.5815 | 119.4955 | 0.5 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 76.6297 | 28.8091 | 685656.4927 | 57.138 | 57.138 | 127.068 | 0.6 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 79.4313 | 31.6107 | 752335.0313 | 62.6946 | 62.6946 | 134.6406 | 0.7 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 82.233 | 34.4123 | 819013.5698 | 68.2511 | 68.2511 | 142.2131 | 0.8 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 85.0346 | 37.214 | 885692.1083 | 73.8077 | 73.8077 | 149.7857 | 0.9 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 87.8362 | 40.0156 | 952370.6469 | 79.3642 | 79.3642 | 157.3582 | 1 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 90.6378 | 42.8172 | 1019049.1854 | 84.9208 | 84.9208 | 164.9308 | 80 | 60 | 33.5105 | 34 | 58.1
8/17/20XX 11:00:00 AM | 0.45833 | 3 | 83.4 | 51.1 | 85.8211 | 103.4101 | 17.5889 | 50 | 83.4 |  | 83.4 | 87.7559 | 0.1 | 74.94 | 19.94 | 753732 | 62.811 | 62.811 | 65.1351 | 17.3144 | 412083.3842 | 34.3403 | 34.3403 | 97.1513 | 0.2 | 75.88 | 20.88 | 789264 | 65.772 | 65.772 | 67.6485 | 19.8279 | 471902.9684 | 39.3252 | 39.3252 | 105.0972 | 0.3 | 76.82 | 21.82 | 824796 | 68.733 | 68.733 | 70.1619 | 22.3413 | 531722.5526 | 44.3102 | 44.3102 | 113.0432 | 0.4 | 77.76 | 22.76 | 860328 | 71.694 | 71.694 | 72.6753 | 24.8547 | 591542.1368 | 49.2952 | 49.2952 | 120.9892 | 0.5 | 78.7 | 23.7 | 895860 | 74.655 | 74.655 | 75.1888 | 27.3681 | 651361.721 | 54.2801 | 54.2801 | 128.9351 | 0.6 | 79.64 | 24.64 | 931392 | 77.616 | 77.616 | 77.7022 | 29.8816 | 711181.3052 | 59.2651 | 59.2651 | 136.8811 | 0.7 | 80.58 | 25.58 | 966924 | 80.577 | 80.577 | 80.2156 | 32.395 | 771000.8894 | 64.2501 | 64.2501 | 144.8271 | 0.8 | 81.52 | 26.52 | 1002456 | 83.538 | 83.538 | 82.7291 | 34.9084 | 830820.4736 | 69.235 | 69.235 | 152.773 | 0.9 | 82.46 | 27.46 | 1037988 | 86.499 | 86.499 | 85.2425 | 37.4219 | 890640.0578 | 74.22 | 74.22 | 160.719 | 1 | 83.4 | 28.4 | 1073520 | 89.46 | 89.46 | 87.7559 | 39.9353 | 950459.642 | 79.205 | 79.205 | 168.665 | 85 | 50 | 33.7953 | 34 | 51.1
8/17/20XX 12:00:00 PM | 0.5 | 3 | 84.7 | 49.2 | 71.283 | 89.5239 | 18.241 | 40 | 84.7 |  | 84.7 | 88.0646 | 0.1 | 75.07 | 20.07 | 758646 | 63.2205 | 63.2205 | 65.1659 | 17.3453 | 412818.1541 | 34.4015 | 34.4015 | 97.622 | 0.2 | 76.14 | 21.14 | 799092 | 66.591 | 66.591 | 67.7102 | 19.8896 | 473372.5082 | 39.4477 | 39.4477 | 106.0387 | 0.3 | 77.21 | 22.21 | 839538 | 69.9615 | 69.9615 | 70.2545 | 22.4339 | 533926.8623 | 44.4939 | 44.4939 | 114.4554 | 0.4 | 78.28 | 23.28 | 879984 | 73.332 | 73.332 | 72.7988 | 24.9782 | 594481.2164 | 49.5401 | 49.5401 | 122.8721 | 0.5 | 79.35 | 24.35 | 920430 | 76.7025 | 76.7025 | 75.3431 | 27.5225 | 655035.5705 | 54.5863 | 54.5863 | 131.2888 | 0.6 | 80.42 | 25.42 | 960876 | 80.073 | 80.073 | 77.8874 | 30.0668 | 715589.9246 | 59.6325 | 59.6325 | 139.7055 | 0.7 | 81.49 | 26.49 | 1001322 | 83.4435 | 83.4435 | 80.4317 | 32.6111 | 776144.2787 | 64.6787 | 64.6787 | 148.1222 | 0.8 | 82.56 | 27.56 | 1041768 | 86.814 | 86.814 | 82.976 | 35.1554 | 836698.6328 | 69.7249 | 69.7249 | 156.5389 | 0.9 | 83.63 | 28.63 | 1082214 | 90.1845 | 90.1845 | 85.5203 | 37.6997 | 897252.9869 | 74.7711 | 74.7711 | 164.9556 | 1 | 84.7 | 29.7 | 1122660 | 93.555 | 93.555 | 88.0646 | 40.244 | 957807.341 | 79.8173 | 79.8173 | 173.3723 | 85 | 50 | 34.163 | 34 | 49.2
8/17/20XX 1:00:00 PM | 0.54167 | 3 | 85.4 | 46.7 | 72.9026 | 91.5706 | 18.6681 | 40 | 85.4 |  | 85.4 | 85.4102 | 0.1 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 64.9005 | 17.0799 | 406500.503 | 33.875 | 33.875 | 97.316 | 0.2 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 67.1793 | 19.3587 | 460737.2061 | 38.3948 | 38.3948 | 105.4268 | 0.3 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 69.4582 | 21.6376 | 514973.9091 | 42.9145 | 42.9145 | 113.5375 | 0.4 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 71.737 | 23.9164 | 569210.6121 | 47.4342 | 47.4342 | 121.6482 | 0.5 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 74.0159 | 26.1953 | 623447.3151 | 51.9539 | 51.9539 | 129.7589 | 0.6 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 76.2948 | 28.4741 | 677684.0182 | 56.4737 | 56.4737 | 137.8697 | 0.7 | 81.98 | 26.98 | 1019844 | 84.987 | 84.987 | 78.5736 | 30.753 | 731920.7212 | 60.9934 | 60.9934 | 145.9804 | 0.8 | 83.12 | 28.12 | 1062936 | 88.578 | 88.578 | 80.8525 | 33.0318 | 786157.4242 | 65.5131 | 65.5131 | 154.0911 | 0.9 | 84.26 | 29.26 | 1106028 | 92.169 | 92.169 | 83.1313 | 35.3107 | 840394.1273 | 70.0328 | 70.0328 | 162.2018 | 1 | 85.4 | 30.4 | 1149120 | 95.76 | 95.76 | 85.4102 | 37.5895 | 894630.8303 | 74.5526 | 74.5526 | 170.3126 | 85 | 45 | 33.9178 | 34 | 46.7
8/17/20XX 2:00:00 PM | 0.58333 | 3 | 85 | 47.6 | 71.9735 | 90.3965 | 18.423 | 40 | 85 |  | 85 | 85.975 | 0.1 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 64.957 | 17.1363 | 407844.7655 | 33.9871 | 33.9871 | 97.3021 | 0.2 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 67.2923 | 19.4717 | 463425.7311 | 38.6188 | 38.6188 | 105.3988 | 0.3 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 69.6276 | 21.807 | 519006.6966 | 43.2506 | 43.2506 | 113.4956 | 0.4 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 71.963 | 24.1423 | 574587.6621 | 47.8823 | 47.8823 | 121.5923 | 0.5 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 74.2983 | 26.4777 | 630168.6276 | 52.5141 | 52.5141 | 129.6891 | 0.6 | 80.6 | 25.6 | 967680 | 80.64 | 80.64 | 76.6336 | 28.813 | 685749.5932 | 57.1458 | 57.1458 | 137.7858 | 0.7 | 81.7 | 26.7 | 1009260 | 84.105 | 84.105 | 78.969 | 31.1483 | 741330.5587 | 61.7775 | 61.7775 | 145.8825 | 0.8 | 82.8 | 27.8 | 1050840 | 87.57 | 87.57 | 81.3043 | 33.4837 | 796911.5242 | 66.4093 | 66.4093 | 153.9793 | 0.9 | 83.9 | 28.9 | 1092420 | 91.035 | 91.035 | 83.6396 | 35.819 | 852492.4897 | 71.041 | 71.041 | 162.076 | 1 | 85 | 30 | 1134000 | 94.5 | 94.5 | 85.975 | 38.1543 | 908073.4553 | 75.6728 | 75.6728 | 170.1728 | 85 | 50 | 33.9084 | 34 | 47.6
8/17/20XX 3:00:00 PM | 0.625 | 3 | 84 | 50.1 | 87.5144 | 105.4561 | 17.9417 | 50 | 84 |  | 84 | 87.6938 | 0.1 | 75 | 20 | 756000 | 63 | 63 | 65.1288 | 17.3082 | 411935.4894 | 34.328 | 34.328 | 97.328 | 0.2 | 76 | 21 | 793800 | 66.15 | 66.15 | 67.6361 | 19.8154 | 471607.1788 | 39.3006 | 39.3006 | 105.4506 | 0.3 | 77 | 22 | 831600 | 69.3 | 69.3 | 70.1433 | 22.3226 | 531278.8682 | 44.2732 | 44.2732 | 113.5732 | 0.4 | 78 | 23 | 869400 | 72.45 | 72.45 | 72.6505 | 24.8299 | 590950.5577 | 49.2459 | 49.2459 | 121.6959 | 0.5 | 79 | 24 | 907200 | 75.6 | 75.6 | 75.1577 | 27.3371 | 650622.2471 | 54.2185 | 54.2185 | 129.8185 | 0.6 | 80 | 25 | 945000 | 78.75 | 78.75 | 77.6649 | 29.8443 | 710293.9365 | 59.1912 | 59.1912 | 137.9412 | 0.7 | 81 | 26 | 982800 | 81.9 | 81.9 | 80.1721 | 32.3515 | 769965.6259 | 64.1638 | 64.1638 | 146.0638 | 0.8 | 82 | 27 | 1020600 | 85.05 | 85.05 | 82.6793 | 34.8587 | 829637.3153 | 69.1364 | 69.1364 | 154.1864 | 0.9 | 83 | 28 | 1058400 | 88.2 | 88.2 | 85.1866 | 37.3659 | 889309.0047 | 74.1091 | 74.1091 | 162.3091 | 1 | 84 | 29 | 1096200 | 91.35 | 91.35 | 87.6938 | 39.8731 | 948980.6942 | 79.0817 | 79.0817 | 170.4317 | 85 | 50 | 33.9329 | 34 | 50.1
8/17/20XX 4:00:00 PM | 0.66667 | 3 | 83.6 | 49.8 | 68.7966 | 86.3826 | 17.586 | 40 | 83.6 |  | 83.6 | 86.0308 | 0.1 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 64.9626 | 17.1419 | 407977.6994 | 33.9981 | 33.9981 | 96.8721 | 0.2 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 67.3035 | 19.4828 | 463691.5987 | 38.641 | 38.641 | 104.539 | 0.3 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 69.6444 | 21.8238 | 519405.4981 | 43.2838 | 43.2838 | 112.2058 | 0.4 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 71.9853 | 24.1647 | 575119.3975 | 47.9266 | 47.9266 | 119.8726 | 0.5 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 74.3262 | 26.5056 | 630833.2968 | 52.5694 | 52.5694 | 127.5394 | 0.6 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 76.6672 | 28.8465 | 686547.1962 | 57.2123 | 57.2123 | 135.2063 | 0.7 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 79.0081 | 31.1874 | 742261.0956 | 61.8551 | 61.8551 | 142.8731 | 0.8 | 81.68 | 26.68 | 1008504 | 84.042 | 84.042 | 81.349 | 33.5284 | 797974.995 | 66.4979 | 66.4979 | 150.5399 | 0.9 | 82.64 | 27.64 | 1044792 | 87.066 | 87.066 | 83.6899 | 35.8693 | 853688.8943 | 71.1407 | 71.1407 | 158.2067 | 1 | 83.6 | 28.6 | 1081080 | 90.09 | 90.09 | 86.0308 | 38.2102 | 909402.7937 | 75.7836 | 75.7836 | 165.8736 | 85 | 50 | 33.5735 | 34 | 49.8
8/17/20XX 5:00:00 PM | 0.70833 | 3 | 82.9 | 50.2 | 84.4305 | 101.7299 | 17.2993 | 50 | 82.9 |  | 82.9 | 84.7765 | 0.1 | 74.89 | 19.89 | 751842 | 62.6535 | 62.6535 | 64.8371 | 17.0165 | 404992.4535 | 33.7494 | 33.7494 | 96.4029 | 0.2 | 75.78 | 20.78 | 785484 | 65.457 | 65.457 | 67.0526 | 19.232 | 457721.107 | 38.1434 | 38.1434 | 103.6004 | 0.3 | 76.67 | 21.67 | 819126 | 68.2605 | 68.2605 | 69.2681 | 21.4475 | 510449.7606 | 42.5375 | 42.5375 | 110.798 | 0.4 | 77.56 | 22.56 | 852768 | 71.064 | 71.064 | 71.4836 | 23.663 | 563178.4141 | 46.9315 | 46.9315 | 117.9955 | 0.5 | 78.45 | 23.45 | 886410 | 73.8675 | 73.8675 | 73.6991 | 25.8784 | 615907.0676 | 51.3256 | 51.3256 | 125.1931 | 0.6 | 79.34 | 24.34 | 920052 | 76.671 | 76.671 | 75.9146 | 28.0939 | 668635.7211 | 55.7196 | 55.7196 | 132.3906 | 0.7 | 80.23 | 25.23 | 953694 | 79.4745 | 79.4745 | 78.1301 | 30.3094 | 721364.3746 | 60.1137 | 60.1137 | 139.5882 | 0.8 | 81.12 | 26.12 | 987336 | 82.278 | 82.278 | 80.3455 | 32.5249 | 774093.0282 | 64.5078 | 64.5078 | 146.7858 | 0.9 | 82.01 | 27.01 | 1020978 | 85.0815 | 85.0815 | 82.561 | 34.7404 | 826821.6817 | 68.9018 | 68.9018 | 153.9833 | 1 | 82.9 | 27.9 | 1054620 | 87.885 | 87.885 | 84.7765 | 36.9559 | 879550.3352 | 73.2959 | 73.2959 | 161.1809 | 85 | 50 | 33.2048 | 34 | 50.2
8/17/20XX 6:00:00 PM | 0.75 | 3 | 81.7 | 52.4 | 81.168 | 97.7883 | 16.6202 | 50 | 81.7 |  | 81.7 | 85.1569 | 0.1 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 64.8752 | 17.0545 | 405897.6573 | 33.8248 | 33.8248 | 96.1003 | 0.2 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 67.1287 | 19.308 | 459531.5145 | 38.2943 | 38.2943 | 102.9953 | 0.3 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 69.3822 | 21.5616 | 513165.3718 | 42.7638 | 42.7638 | 109.8903 | 0.4 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 71.6357 | 23.8151 | 566799.2291 | 47.2333 | 47.2333 | 116.7853 | 0.5 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 73.8892 | 26.0686 | 620433.0864 | 51.7028 | 51.7028 | 123.6803 | 0.6 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 76.1428 | 28.3221 | 674066.9436 | 56.1722 | 56.1722 | 130.5752 | 0.7 | 79.39 | 24.39 | 921942 | 76.8285 | 76.8285 | 78.3963 | 30.5757 | 727700.8009 | 60.6417 | 60.6417 | 137.4702 | 0.8 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 80.6498 | 32.8292 | 781334.6582 | 65.1112 | 65.1112 | 144.3652 | 0.9 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 82.9033 | 35.0827 | 834968.5154 | 69.5807 | 69.5807 | 151.2602 | 1 | 81.7 | 26.7 | 1009260 | 84.105 | 84.105 | 85.1569 | 37.3362 | 888602.3727 | 74.0502 | 74.0502 | 158.1552 | 80 | 50 | 32.97 | 32 | 52.4
8/17/20XX 7:00:00 PM | 0.79167 | 3 | 79.3 | 59.5 | 74.9531 | 90.2816 | 15.3285 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/17/20XX 8:00:00 PM | 0.83333 | 3 | 78.9 | 58.3 | 73.9565 | 89.0782 | 15.1216 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/17/20XX 9:00:00 PM | 0.875 | 3 | 77.7 | 60.2 | 85.548 | 100.1379 | 14.59 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/17/20XX 10:00:00 PM | 0.91667 | 3 | 76.7 | 62.9 | 82.6964 | 96.79 | 14.0936 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/17/20XX 11:00:00 PM | 0.95833 | 3 | 76 | 65.4 | 80.7483 | 94.5029 | 13.7546 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/17/20XX 12:00:00 AM | 0 | 4 | 74.6 | 68 | 76.9684 | 90.0655 | 13.0971 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/18/20XX 1:00:00 AM | 0.041667 | 4 | 73.9 | 69.8 | 75.1356 | 87.9141 | 12.7785 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/18/20XX 2:00:00 AM | 0.083333 | 4 | 73.2 | 71.3 | 85.8067 | 98.3566 | 12.5498 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/18/20XX 3:00:00 AM | 0.125 | 4 | 73 | 71.7 | 85.2126 | 97.6734 | 12.4608 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/18/20XX 4:00:00 AM | 0.16667 | 4 | 71.9 | 75.1 | 82.008 | 93.989 | 11.9811 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/18/20XX 5:00:00 AM | 0.20833 | 4 | 71.3 | 77.7 | 80.3042 | 92.0306 | 11.7264 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/18/20XX 6:00:00 AM | 0.25 | 4 | 71 | 78.1 | 79.4639 | 91.0648 | 11.6009 | 70 | 71 |  | 71 | 88.8607 | 0.1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 65.2455 | 17.4249 | 414712.6754 | 34.5594 | 34.5594 | 93.4644 | 0.2 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 67.8694 | 20.0488 | 477161.5508 | 39.7635 | 39.7635 | 97.7235 | 0.3 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 70.4933 | 22.6727 | 539610.4261 | 44.9675 | 44.9675 | 101.9825 | 0.4 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 73.1172 | 25.2966 | 602059.3015 | 50.1716 | 50.1716 | 106.2416 | 0.5 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 75.7411 | 27.9205 | 664508.1769 | 55.3757 | 55.3757 | 110.5007 | 0.6 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 78.365 | 30.5444 | 726957.0523 | 60.5798 | 60.5798 | 114.7598 | 0.7 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 80.9889 | 33.1683 | 789405.9277 | 65.7838 | 65.7838 | 119.0188 | 0.8 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 83.6129 | 35.7922 | 851854.8031 | 70.9879 | 70.9879 | 123.2779 | 0.9 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 86.2368 | 38.4161 | 914303.6784 | 76.192 | 76.192 | 127.537 | 1 | 71 | 16 | 604800 | 50.4 | 50.4 | 88.8607 | 41.04 | 976752.5538 | 81.396 | 81.396 | 131.796 | 70 | 80 | 30.9228 | 30 | 78.1
8/18/20XX 7:00:00 AM | 0.29167 | 4 | 71.3 | 80.9 | 92.0306 | 103.7683 | 11.7376 | 80 | 71.3 |  | 71.3 | 93.087 | 0.1 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 65.6682 | 17.8475 | 424771.4235 | 35.3976 | 35.3976 | 94.3971 | 0.2 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 68.7147 | 20.8941 | 497279.0471 | 41.4399 | 41.4399 | 99.5889 | 0.3 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 71.7612 | 23.9406 | 569786.6706 | 47.4822 | 47.4822 | 104.7807 | 0.4 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 74.8078 | 26.9872 | 642294.2941 | 53.5245 | 53.5245 | 109.9725 | 0.5 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 77.8543 | 30.0337 | 714801.9177 | 59.5668 | 59.5668 | 115.1643 | 0.6 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 80.9009 | 33.0802 | 787309.5412 | 65.6091 | 65.6091 | 120.3561 | 0.7 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 83.9474 | 36.1268 | 859817.1647 | 71.6514 | 71.6514 | 125.5479 | 0.8 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 86.9939 | 39.1733 | 932324.7882 | 77.6937 | 77.6937 | 130.7397 | 0.9 | 71.57 | 16.57 | 626346 | 52.1955 | 52.1955 | 90.0405 | 42.2198 | 1004832.4118 | 83.736 | 83.736 | 135.9315 | 1 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 93.087 | 45.2664 | 1077340.0353 | 89.7783 | 89.7783 | 141.1233 | 70 | 80 | 31.6568 | 32 | 80.9
8/18/20XX 8:00:00 AM | 0.33333 | 4 | 72.8 | 77 | 84.6221 | 96.9944 | 12.3723 | 70 | 72.8 |  | 72.8 | 93.2827 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.6877 | 17.8671 | 425237.1712 | 35.4364 | 35.4364 | 94.9084 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 68.7538 | 20.9332 | 498210.5423 | 41.5175 | 41.5175 | 100.6115 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 71.82 | 23.9993 | 571183.9135 | 47.5987 | 47.5987 | 106.3147 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 74.8861 | 27.0654 | 644157.2847 | 53.6798 | 53.6798 | 112.0178 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 77.9522 | 30.1315 | 717130.6559 | 59.7609 | 59.7609 | 117.7209 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 81.0183 | 33.1976 | 790104.027 | 65.842 | 65.842 | 123.424 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 84.0844 | 36.2638 | 863077.3982 | 71.9231 | 71.9231 | 129.1271 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 87.1505 | 39.3299 | 936050.7694 | 78.0042 | 78.0042 | 134.8302 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 90.2166 | 42.396 | 1009024.1406 | 84.0853 | 84.0853 | 140.5333 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 93.2827 | 45.4621 | 1081997.5117 | 90.1665 | 90.1665 | 146.2365 | 75 | 75 | 32.0563 | 32 | 77
8/18/20XX 9:00:00 AM | 0.375 | 4 | 74 | 76.9 | 88.2187 | 101.1303 | 12.9116 | 70 | 74 |  | 74 | 97.1277 | 0.1 | 74 | 19 | 718200 | 59.85 | 59.85 | 66.0722 | 18.2516 | 434388.3424 | 36.199 | 36.199 | 96.049 | 0.2 | 74 | 19 | 718200 | 59.85 | 59.85 | 69.5229 | 21.7022 | 516512.8848 | 43.0427 | 43.0427 | 102.8927 | 0.3 | 74 | 19 | 718200 | 59.85 | 59.85 | 72.9735 | 25.1528 | 598637.4272 | 49.8865 | 49.8865 | 109.7365 | 0.4 | 74 | 19 | 718200 | 59.85 | 59.85 | 76.4241 | 28.6034 | 680761.9696 | 56.7302 | 56.7302 | 116.5802 | 0.5 | 74 | 19 | 718200 | 59.85 | 59.85 | 79.8747 | 32.0541 | 762886.512 | 63.5739 | 63.5739 | 123.4239 | 0.6 | 74 | 19 | 718200 | 59.85 | 59.85 | 83.3253 | 35.5047 | 845011.0544 | 70.4176 | 70.4176 | 130.2676 | 0.7 | 74 | 19 | 718200 | 59.85 | 59.85 | 86.7759 | 38.9553 | 927135.5968 | 77.2613 | 77.2613 | 137.1113 | 0.8 | 74 | 19 | 718200 | 59.85 | 59.85 | 90.2265 | 42.4059 | 1009260.1392 | 84.105 | 84.105 | 143.955 | 0.9 | 74 | 19 | 718200 | 59.85 | 59.85 | 93.6771 | 45.8565 | 1091384.6816 | 90.9487 | 90.9487 | 150.7987 | 1 | 74 | 19 | 718200 | 59.85 | 59.85 | 97.1277 | 49.3071 | 1173509.224 | 97.7924 | 97.7924 | 157.6424 | 75 | 75 | 32.9529 | 32 | 76.9
8/18/20XX 10:00:00 AM | 0.41667 | 4 | 76.7 | 69.5 | 82.6964 | 96.79 | 14.0936 | 60 | 76.7 |  | 76.7 | 96.0853 | 0.1 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 65.968 | 18.1474 | 431907.3997 | 35.9923 | 35.9923 | 96.6928 | 0.2 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 69.3144 | 21.4937 | 511550.9993 | 42.6292 | 42.6292 | 104.1802 | 0.3 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 72.6607 | 24.8401 | 591194.599 | 49.2662 | 49.2662 | 111.6677 | 0.4 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 76.0071 | 28.1865 | 670838.1987 | 55.9032 | 55.9032 | 119.1552 | 0.5 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 79.3535 | 31.5328 | 750481.7983 | 62.5401 | 62.5401 | 126.6426 | 0.6 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 82.6999 | 34.8792 | 830125.398 | 69.1771 | 69.1771 | 134.1301 | 0.7 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 86.0462 | 38.2256 | 909768.9977 | 75.8141 | 75.8141 | 141.6176 | 0.8 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 89.3926 | 41.572 | 989412.5973 | 82.451 | 82.451 | 149.105 | 0.9 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 92.739 | 44.9183 | 1069056.197 | 89.088 | 89.088 | 156.5925 | 1 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 96.0853 | 48.2647 | 1148699.7966 | 95.725 | 95.725 | 164.08 | 75 | 70 | 33.4543 | 34 | 69.5
8/18/20XX 11:00:00 AM | 0.45833 | 4 | 77.7 | 67.4 | 85.548 | 100.1379 | 14.59 | 60 | 77.7 |  | 77.7 | 96.3445 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 65.9939 | 18.1733 | 432524.3063 | 36.0437 | 36.0437 | 97.0592 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 69.3662 | 21.5456 | 512784.8125 | 42.7321 | 42.7321 | 104.9131 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 72.7385 | 24.9179 | 593045.3188 | 49.4204 | 49.4204 | 112.7669 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 76.1108 | 28.2902 | 673305.825 | 56.1088 | 56.1088 | 120.6208 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 79.4831 | 31.6625 | 753566.3313 | 62.7972 | 62.7972 | 128.4747 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 82.8554 | 35.0347 | 833826.8376 | 69.4856 | 69.4856 | 136.3286 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 86.2277 | 38.407 | 914087.3438 | 76.1739 | 76.1739 | 144.1824 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 89.6 | 41.7793 | 994347.8501 | 82.8623 | 82.8623 | 152.0363 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 92.9722 | 45.1516 | 1074608.3564 | 89.5507 | 89.5507 | 159.8902 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 96.3445 | 48.5239 | 1154868.8626 | 96.2391 | 96.2391 | 167.7441 | 80 | 65 | 33.741 | 34 | 67.4
8/18/20XX 12:00:00 PM | 0.5 | 4 | 80.5 | 59.4 | 78.0095 | 93.973 | 15.9635 | 50 | 80.5 |  | 80.5 | 93.0152 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 65.661 | 17.8404 | 424600.4413 | 35.3834 | 35.3834 | 97.2809 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 68.7003 | 20.8797 | 496937.0825 | 41.4114 | 41.4114 | 105.3564 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 71.7397 | 23.9191 | 569273.7238 | 47.4395 | 47.4395 | 113.432 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 74.7791 | 26.9584 | 641610.3651 | 53.4675 | 53.4675 | 121.5075 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 77.8184 | 29.9978 | 713947.0063 | 59.4956 | 59.4956 | 129.5831 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 80.8578 | 33.0371 | 786283.6476 | 65.5236 | 65.5236 | 137.6586 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 83.8971 | 36.0765 | 858620.2889 | 71.5517 | 71.5517 | 145.7342 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 86.9365 | 39.1158 | 930956.9301 | 77.5797 | 77.5797 | 153.8097 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 89.9758 | 42.1552 | 1003293.5714 | 83.6078 | 83.6078 | 161.8853 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 93.0152 | 45.1945 | 1075630.2126 | 89.6359 | 89.6359 | 169.9609 | 80 | 60 | 33.908 | 34 | 59.4
8/18/20XX 1:00:00 PM | 0.54167 | 4 | 81.5 | 57.6 | 80.6344 | 97.1437 | 16.5092 | 50 | 81.5 |  | 81.5 | 93.1815 | 0.1 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 65.6776 | 17.857 | 424996.1704 | 35.4163 | 35.4163 | 97.6288 | 0.2 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 68.7336 | 20.913 | 497728.5409 | 41.4774 | 41.4774 | 106.0524 | 0.3 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 71.7896 | 23.9689 | 570460.9113 | 47.5384 | 47.5384 | 114.4759 | 0.4 | 77 | 22 | 831600 | 69.3 | 69.3 | 74.8456 | 27.0249 | 643193.2817 | 53.5994 | 53.5994 | 122.8994 | 0.5 | 77.75 | 22.75 | 859950 | 71.6625 | 71.6625 | 77.9015 | 30.0809 | 715925.6521 | 59.6605 | 59.6605 | 131.323 | 0.6 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 80.9575 | 33.1369 | 788658.0226 | 65.7215 | 65.7215 | 139.7465 | 0.7 | 79.25 | 24.25 | 916650 | 76.3875 | 76.3875 | 84.0135 | 36.1929 | 861390.393 | 71.7825 | 71.7825 | 148.17 | 0.8 | 80 | 25 | 945000 | 78.75 | 78.75 | 87.0695 | 39.2489 | 934122.7634 | 77.8436 | 77.8436 | 156.5936 | 0.9 | 80.75 | 25.75 | 973350 | 81.1125 | 81.1125 | 90.1255 | 42.3048 | 1006855.1339 | 83.9046 | 83.9046 | 165.0171 | 1 | 81.5 | 26.5 | 1001700 | 83.475 | 83.475 | 93.1815 | 45.3608 | 1079587.5043 | 89.9656 | 89.9656 | 173.4406 | 80 | 60 | 34.1799 | 34 | 57.6
8/18/20XX 2:00:00 PM | 0.58333 | 4 | 81.4 | 58 | 80.3687 | 96.8227 | 16.454 | 50 | 81.4 |  | 81.4 | 93.5319 | 0.1 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 65.7127 | 17.892 | 425830.2275 | 35.4859 | 35.4859 | 97.6669 | 0.2 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 68.8037 | 20.9831 | 499396.6549 | 41.6164 | 41.6164 | 106.1284 | 0.3 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 71.8947 | 24.0741 | 572963.0824 | 47.7469 | 47.7469 | 114.5899 | 0.4 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 74.9857 | 27.1651 | 646529.5099 | 53.8775 | 53.8775 | 123.0515 | 0.5 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 78.0768 | 30.2561 | 720095.9374 | 60.008 | 60.008 | 131.513 | 0.6 | 78.44 | 23.44 | 886032 | 73.836 | 73.836 | 81.1678 | 33.3472 | 793662.3648 | 66.1385 | 66.1385 | 139.9745 | 0.7 | 79.18 | 24.18 | 914004 | 76.167 | 76.167 | 84.2588 | 36.4382 | 867228.7923 | 72.2691 | 72.2691 | 148.4361 | 0.8 | 79.92 | 24.92 | 941976 | 78.498 | 78.498 | 87.3498 | 39.5292 | 940795.2198 | 78.3996 | 78.3996 | 156.8976 | 0.9 | 80.66 | 25.66 | 969948 | 80.829 | 80.829 | 90.4409 | 42.6202 | 1014361.6473 | 84.5301 | 84.5301 | 165.3591 | 1 | 81.4 | 26.4 | 997920 | 83.16 | 83.16 | 93.5319 | 45.7113 | 1087928.0747 | 90.6607 | 90.6607 | 173.8207 | 80 | 60 | 34.2103 | 34 | 58
8/18/20XX 3:00:00 PM | 0.625 | 4 | 81.3 | 57 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 91.5829 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 65.5178 | 17.6971 | 421191.6781 | 35.0993 | 35.0993 | 97.2488 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 68.4139 | 20.5933 | 490119.5562 | 40.8433 | 40.8433 | 105.2923 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 71.31 | 23.4894 | 559047.4343 | 46.5873 | 46.5873 | 113.3358 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 74.2061 | 26.3855 | 627975.3124 | 52.3313 | 52.3313 | 121.3793 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 77.1023 | 29.2816 | 696903.1906 | 58.0753 | 58.0753 | 129.4228 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 79.9984 | 32.1778 | 765831.0687 | 63.8193 | 63.8193 | 137.4663 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 82.8945 | 35.0739 | 834758.9468 | 69.5632 | 69.5632 | 145.5097 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 85.7907 | 37.97 | 903686.8249 | 75.3072 | 75.3072 | 153.5532 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 88.6868 | 40.8662 | 972614.703 | 81.0512 | 81.0512 | 161.5967 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 91.5829 | 43.7623 | 1041542.5811 | 86.7952 | 86.7952 | 169.6402 | 80 | 55 | 33.88 | 34 | 57
8/18/20XX 4:00:00 PM | 0.66667 | 4 | 80.7 | 58.4 | 78.5288 | 94.6002 | 16.0714 | 50 | 80.7 |  | 80.7 | 92.0288 | 0.1 | 74.67 | 19.67 | 743526 | 61.9605 | 61.9605 | 65.5623 | 17.7417 | 422252.7975 | 35.1877 | 35.1877 | 97.1482 | 0.2 | 75.34 | 20.34 | 768852 | 64.071 | 64.071 | 68.5031 | 20.6824 | 492241.7949 | 41.0201 | 41.0201 | 105.0911 | 0.3 | 76.01 | 21.01 | 794178 | 66.1815 | 66.1815 | 71.4438 | 23.6231 | 562230.7924 | 46.8526 | 46.8526 | 113.0341 | 0.4 | 76.68 | 21.68 | 819504 | 68.292 | 68.292 | 74.3845 | 26.5639 | 632219.7899 | 52.685 | 52.685 | 120.977 | 0.5 | 77.35 | 22.35 | 844830 | 70.4025 | 70.4025 | 77.3252 | 29.5046 | 702208.7873 | 58.5174 | 58.5174 | 128.9199 | 0.6 | 78.02 | 23.02 | 870156 | 72.513 | 72.513 | 80.2659 | 32.4453 | 772197.7848 | 64.3498 | 64.3498 | 136.8628 | 0.7 | 78.69 | 23.69 | 895482 | 74.6235 | 74.6235 | 83.2066 | 35.386 | 842186.7822 | 70.1822 | 70.1822 | 144.8057 | 0.8 | 79.36 | 24.36 | 920808 | 76.734 | 76.734 | 86.1473 | 38.3267 | 912175.7797 | 76.0146 | 76.0146 | 152.7486 | 0.9 | 80.03 | 25.03 | 946134 | 78.8445 | 78.8445 | 89.0881 | 41.2674 | 982164.7772 | 81.8471 | 81.8471 | 160.6916 | 1 | 80.7 | 25.7 | 971460 | 80.955 | 80.955 | 92.0288 | 44.2081 | 1052153.7746 | 87.6795 | 87.6795 | 168.6345 | 80 | 60 | 33.8024 | 34 | 58.4
8/18/20XX 5:00:00 PM | 0.70833 | 4 | 79.6 | 60.6 | 91.1929 | 106.7659 | 15.5729 | 60 | 79.6 |  | 79.6 | 92.1273 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.5722 | 17.7516 | 422487.3205 | 35.2073 | 35.2073 | 96.8213 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 68.5228 | 20.7021 | 492710.8411 | 41.0592 | 41.0592 | 104.4372 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 71.4733 | 23.6527 | 562934.3616 | 46.9112 | 46.9112 | 112.0532 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 74.4239 | 26.6033 | 633157.8821 | 52.7632 | 52.7632 | 119.6692 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 77.3745 | 29.5538 | 703381.4026 | 58.6151 | 58.6151 | 127.2851 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 80.325 | 32.5044 | 773604.9232 | 64.4671 | 64.4671 | 134.9011 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 83.2756 | 35.455 | 843828.4437 | 70.319 | 70.319 | 142.517 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 86.2262 | 38.4055 | 914051.9642 | 76.171 | 76.171 | 150.133 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 89.1767 | 41.3561 | 984275.4847 | 82.023 | 82.023 | 157.749 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 92.1273 | 44.3067 | 1054499.0053 | 87.8749 | 87.8749 | 165.3649 | 80 | 60 | 33.5474 | 34 | 60.6
8/18/20XX 6:00:00 PM | 0.75 | 4 | 78.5 | 63.9 | 87.8882 | 102.8856 | 14.9974 | 60 | 78.5 |  | 78.5 | 93.7371 | 0.1 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 65.7332 | 17.9126 | 426318.724 | 35.5266 | 35.5266 | 96.7941 | 0.2 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 68.8447 | 21.0241 | 500373.6479 | 41.6978 | 41.6978 | 104.3828 | 0.3 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 71.9563 | 24.1357 | 574428.5719 | 47.869 | 47.869 | 111.9715 | 0.4 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 75.0678 | 27.2472 | 648483.4958 | 54.0403 | 54.0403 | 119.5603 | 0.5 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 78.1794 | 30.3588 | 722538.4198 | 60.2115 | 60.2115 | 127.149 | 0.6 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 81.2909 | 33.4703 | 796593.3437 | 66.3828 | 66.3828 | 134.7378 | 0.7 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 84.4025 | 36.5819 | 870648.2677 | 72.554 | 72.554 | 142.3265 | 0.8 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 87.514 | 39.6934 | 944703.1916 | 78.7253 | 78.7253 | 149.9153 | 0.9 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 90.6256 | 42.805 | 1018758.1156 | 84.8965 | 84.8965 | 157.504 | 1 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 93.7371 | 45.9165 | 1092813.0395 | 91.0678 | 91.0678 | 165.0928 | 80 | 65 | 33.5293 | 34 | 63.9
8/18/20XX 7:00:00 PM | 0.79167 | 4 | 77 | 63 | 83.5433 | 97.7844 | 14.241 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/18/20XX 8:00:00 PM | 0.83333 | 4 | 75.8 | 65.3 | 80.1988 | 93.8579 | 13.6591 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/18/20XX 9:00:00 PM | 0.875 | 4 | 75.2 | 68.4 | 78.5695 | 91.9451 | 13.3756 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/18/20XX 10:00:00 PM | 0.91667 | 4 | 73.6 | 70.6 | 87.0056 | 99.7352 | 12.7296 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/18/20XX 11:00:00 PM | 0.95833 | 4 | 72.7 | 73.3 | 84.3281 | 96.6564 | 12.3283 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/18/20XX 12:00:00 AM | 0 | 5 | 71.9 | 75.5 | 82.008 | 93.989 | 11.9811 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/19/20XX 1:00:00 AM | 0.041667 | 5 | 71.8 | 76.3 | 81.7218 | 93.6601 | 11.9383 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/19/20XX 2:00:00 AM | 0.083333 | 5 | 71.3 | 76.8 | 80.3042 | 92.0306 | 11.7264 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/19/20XX 3:00:00 AM | 0.125 | 5 | 71.3 | 77.9 | 80.3042 | 92.0306 | 11.7264 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/19/20XX 4:00:00 AM | 0.16667 | 5 | 70.7 | 79.9 | 78.6313 | 90.1079 | 11.4766 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/19/20XX 5:00:00 AM | 0.20833 | 5 | 70.4 | 80.5 | 89.1597 | 100.5195 | 11.3598 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/19/20XX 6:00:00 AM | 0.25 | 5 | 70.5 | 81.4 | 89.4748 | 100.876 | 11.4012 | 80 | 70.5 |  | 70.5 | 91.071 | 0.1 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 65.4666 | 17.6459 | 419973.2318 | 34.9978 | 34.9978 | 93.7453 | 0.2 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 68.3115 | 20.4909 | 487682.6637 | 40.6402 | 40.6402 | 98.2852 | 0.3 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 71.1564 | 23.3358 | 555392.0955 | 46.2827 | 46.2827 | 102.8252 | 0.4 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 74.0014 | 26.1807 | 623101.5274 | 51.9251 | 51.9251 | 107.3651 | 0.5 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 76.8463 | 29.0257 | 690810.9592 | 57.5676 | 57.5676 | 111.9051 | 0.6 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 79.6912 | 31.8706 | 758520.3911 | 63.21 | 63.21 | 116.445 | 0.7 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 82.5362 | 34.7155 | 826229.8229 | 68.8525 | 68.8525 | 120.985 | 0.8 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 85.3811 | 37.5605 | 893939.2548 | 74.4949 | 74.4949 | 125.5249 | 0.9 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 88.226 | 40.4054 | 961648.6866 | 80.1374 | 80.1374 | 130.0649 | 1 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 91.071 | 43.2503 | 1029358.1184 | 85.7798 | 85.7798 | 134.6048 | 70 | 80 | 31.1452 | 32 | 81.4
8/19/20XX 7:00:00 AM | 0.29167 | 5 | 71.9 | 77.3 | 82.008 | 93.989 | 11.9811 | 70 | 71.9 |  | 71.9 | 90.7541 | 0.1 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 65.4349 | 17.6143 | 419219.1808 | 34.9349 | 34.9349 | 94.1234 | 0.2 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 68.2481 | 20.4275 | 486174.5616 | 40.5145 | 40.5145 | 99.0415 | 0.3 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 71.0614 | 23.2408 | 553129.9425 | 46.0942 | 46.0942 | 103.9597 | 0.4 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 73.8746 | 26.054 | 620085.3233 | 51.6738 | 51.6738 | 108.8778 | 0.5 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 76.6879 | 28.8673 | 687040.7041 | 57.2534 | 57.2534 | 113.7959 | 0.6 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 79.5011 | 31.6805 | 753996.0849 | 62.833 | 62.833 | 118.714 | 0.7 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 82.3144 | 34.4938 | 820951.4658 | 68.4126 | 68.4126 | 123.6321 | 0.8 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 85.1276 | 37.307 | 887906.8466 | 73.9922 | 73.9922 | 128.5502 | 0.9 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 87.9409 | 40.1203 | 954862.2274 | 79.5719 | 79.5719 | 133.4684 | 1 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 90.7541 | 42.9335 | 1021817.6082 | 85.1515 | 85.1515 | 138.3865 | 70 | 75 | 31.4398 | 32 | 77.3
8/19/20XX 8:00:00 AM | 0.33333 | 5 | 73.2 | 72.7 | 85.8067 | 98.3566 | 12.5498 | 70 | 73.2 |  | 73.2 | 89.1952 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 65.279 | 17.4584 | 415508.8481 | 34.6257 | 34.6257 | 94.2237 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 67.9363 | 20.1157 | 478753.8961 | 39.8962 | 39.8962 | 99.2422 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 70.5937 | 22.7731 | 541998.9442 | 45.1666 | 45.1666 | 104.2606 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 73.2511 | 25.4304 | 605243.9922 | 50.437 | 50.437 | 109.279 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 75.9084 | 28.0878 | 668489.0403 | 55.7074 | 55.7074 | 114.2974 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 78.5658 | 30.7451 | 731734.0883 | 60.9778 | 60.9778 | 119.3158 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 81.2231 | 33.4025 | 794979.1364 | 66.2483 | 66.2483 | 124.3343 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 83.8805 | 36.0598 | 858224.1844 | 71.5187 | 71.5187 | 129.3527 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 86.5378 | 38.7172 | 921469.2325 | 76.7891 | 76.7891 | 134.3711 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 89.1952 | 41.3745 | 984714.2806 | 82.0595 | 82.0595 | 139.3895 | 75 | 75 | 31.5155 | 32 | 72.7
8/19/20XX 9:00:00 AM | 0.375 | 5 | 75.2 | 66.9 | 78.5695 | 91.9451 | 13.3756 | 60 | 75.2 |  | 75.2 | 87.7987 | 0.1 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.1393 | 17.3187 | 412185.1695 | 34.3488 | 34.3488 | 94.5768 | 0.2 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 67.657 | 19.8364 | 472106.5391 | 39.3422 | 39.3422 | 99.9482 | 0.3 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 70.1747 | 22.3541 | 532027.9086 | 44.3357 | 44.3357 | 105.3197 | 0.4 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 72.6925 | 24.8718 | 591949.2782 | 49.3291 | 49.3291 | 110.6911 | 0.5 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 75.2102 | 27.3895 | 651870.6477 | 54.3226 | 54.3226 | 116.0626 | 0.6 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 77.7279 | 29.9072 | 711792.0172 | 59.316 | 59.316 | 121.434 | 0.7 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 80.2456 | 32.4249 | 771713.3868 | 64.3094 | 64.3094 | 126.8054 | 0.8 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 82.7633 | 34.9426 | 831634.7563 | 69.3029 | 69.3029 | 132.1769 | 0.9 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 85.281 | 37.4603 | 891556.1259 | 74.2963 | 74.2963 | 137.5483 | 1 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 87.7987 | 39.978 | 951477.4954 | 79.2898 | 79.2898 | 142.9198 | 75 | 65 | 31.7883 | 32 | 66.9
8/19/20XX 10:00:00 AM | 0.41667 | 5 | 77.2 | 62.6 | 84.112 | 98.452 | 14.34 | 60 | 77.2 |  | 77.2 | 87.8404 | 0.1 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 65.1435 | 17.3229 | 412284.5081 | 34.357 | 34.357 | 95.215 | 0.2 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 67.6654 | 19.8448 | 472305.2163 | 39.3588 | 39.3588 | 101.2248 | 0.3 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 70.1873 | 22.3666 | 532325.9244 | 44.3605 | 44.3605 | 107.2345 | 0.4 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 72.7091 | 24.8885 | 592346.6326 | 49.3622 | 49.3622 | 113.2442 | 0.5 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 75.231 | 27.4104 | 652367.3407 | 54.3639 | 54.3639 | 119.2539 | 0.6 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 77.7529 | 29.9323 | 712388.0489 | 59.3657 | 59.3657 | 125.2637 | 0.7 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 80.2748 | 32.4541 | 772408.757 | 64.3674 | 64.3674 | 131.2734 | 0.8 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 82.7967 | 34.976 | 832429.4652 | 69.3691 | 69.3691 | 137.2831 | 0.9 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 85.3185 | 37.4979 | 892450.1733 | 74.3708 | 74.3708 | 143.2928 | 1 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 87.8404 | 40.0198 | 952470.8814 | 79.3726 | 79.3726 | 149.3026 | 75 | 65 | 32.286 | 32 | 62.6
8/19/20XX 11:00:00 AM | 0.45833 | 5 | 79.7 | 58.3 | 75.9607 | 91.4984 | 15.5378 | 50 | 79.7 |  | 79.7 | 88.857 | 0.1 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 65.2452 | 17.4245 | 414703.9917 | 34.5587 | 34.5587 | 96.2042 | 0.2 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 67.8687 | 20.0481 | 477144.1834 | 39.762 | 39.762 | 103.203 | 0.3 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 70.4922 | 22.6716 | 539584.3751 | 44.9654 | 44.9654 | 110.2019 | 0.4 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 73.1158 | 25.2951 | 602024.5667 | 50.1687 | 50.1687 | 117.2007 | 0.5 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 75.7393 | 27.9187 | 664464.7584 | 55.3721 | 55.3721 | 124.1996 | 0.6 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 78.3629 | 30.5422 | 726904.9501 | 60.5754 | 60.5754 | 131.1984 | 0.7 | 77.99 | 22.99 | 869022 | 72.4185 | 72.4185 | 80.9864 | 33.1658 | 789345.1418 | 65.7788 | 65.7788 | 138.1973 | 0.8 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 83.6099 | 35.7893 | 851785.3335 | 70.9821 | 70.9821 | 145.1961 | 0.9 | 79.13 | 24.13 | 912114 | 76.0095 | 76.0095 | 86.2335 | 38.4128 | 914225.5252 | 76.1855 | 76.1855 | 152.195 | 1 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 88.857 | 41.0364 | 976665.7169 | 81.3888 | 81.3888 | 159.1938 | 80 | 60 | 33.0593 | 34 | 58.3
8/19/20XX 12:00:00 PM | 0.5 | 5 | 80.6 | 56.2 | 78.2688 | 94.2862 | 16.0174 | 50 | 80.6 |  | 80.6 | 88.1996 | 0.1 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 65.1794 | 17.3588 | 413139.2848 | 34.4283 | 34.4283 | 96.3573 | 0.2 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 67.7372 | 19.9166 | 474014.7695 | 39.5012 | 39.5012 | 103.5092 | 0.3 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 70.295 | 22.4744 | 534890.2543 | 44.5742 | 44.5742 | 110.6612 | 0.4 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 72.8528 | 25.0322 | 595765.739 | 49.6471 | 49.6471 | 117.8131 | 0.5 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 75.4106 | 27.59 | 656641.2238 | 54.7201 | 54.7201 | 124.9651 | 0.6 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 77.9684 | 30.1478 | 717516.7085 | 59.7931 | 59.7931 | 132.1171 | 0.7 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 80.5262 | 32.7056 | 778392.1933 | 64.866 | 64.866 | 139.269 | 0.8 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 83.084 | 35.2633 | 839267.678 | 69.939 | 69.939 | 146.421 | 0.9 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 85.6418 | 37.8211 | 900143.1628 | 75.0119 | 75.0119 | 153.5729 | 1 | 80.6 | 25.6 | 967680 | 80.64 | 80.64 | 88.1996 | 40.3789 | 961018.6476 | 80.0849 | 80.0849 | 160.7249 | 80 | 55 | 33.1773 | 34 | 56.2
8/19/20XX 1:00:00 PM | 0.54167 | 5 | 81.5 | 53.7 | 80.6344 | 97.1437 | 16.5092 | 50 | 81.5 |  | 81.5 | 86.7428 | 0.1 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 65.0338 | 17.2131 | 409672.2853 | 34.1394 | 34.1394 | 96.3519 | 0.2 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 67.4459 | 19.6252 | 467080.7707 | 38.9234 | 38.9234 | 103.4984 | 0.3 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 69.858 | 22.0374 | 524489.256 | 43.7074 | 43.7074 | 110.6449 | 0.4 | 77 | 22 | 831600 | 69.3 | 69.3 | 72.2701 | 24.4495 | 581897.7413 | 48.4915 | 48.4915 | 117.7915 | 0.5 | 77.75 | 22.75 | 859950 | 71.6625 | 71.6625 | 74.6822 | 26.8616 | 639306.2267 | 53.2755 | 53.2755 | 124.938 | 0.6 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 77.0944 | 29.2737 | 696714.712 | 58.0596 | 58.0596 | 132.0846 | 0.7 | 79.25 | 24.25 | 916650 | 76.3875 | 76.3875 | 79.5065 | 31.6858 | 754123.1973 | 62.8436 | 62.8436 | 139.2311 | 0.8 | 80 | 25 | 945000 | 78.75 | 78.75 | 81.9186 | 34.098 | 811531.6827 | 67.6276 | 67.6276 | 146.3776 | 0.9 | 80.75 | 25.75 | 973350 | 81.1125 | 81.1125 | 84.3307 | 36.5101 | 868940.168 | 72.4117 | 72.4117 | 153.5242 | 1 | 81.5 | 26.5 | 1001700 | 83.475 | 83.475 | 86.7428 | 38.9222 | 926348.6533 | 77.1957 | 77.1957 | 160.6707 | 80 | 55 | 33.1697 | 34 | 53.7
8/19/20XX 2:00:00 PM | 0.58333 | 5 | 81.1 | 54.9 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 87.5575 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 65.1152 | 17.2946 | 411611.273 | 34.3009 | 34.3009 | 96.3874 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 67.6088 | 19.7882 | 470958.7461 | 39.2466 | 39.2466 | 103.5696 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 70.1024 | 22.2818 | 530306.2191 | 44.1922 | 44.1922 | 110.7517 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 72.596 | 24.7754 | 589653.6921 | 49.1378 | 49.1378 | 117.9338 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 75.0896 | 27.269 | 649001.1652 | 54.0834 | 54.0834 | 125.1159 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 77.5832 | 29.7625 | 708348.6382 | 59.0291 | 59.0291 | 132.2981 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 80.0768 | 32.2561 | 767696.1112 | 63.9747 | 63.9747 | 139.4802 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 82.5704 | 34.7497 | 827043.5842 | 68.9203 | 68.9203 | 146.6623 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 85.064 | 37.2433 | 886391.0573 | 73.8659 | 73.8659 | 153.8444 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 87.5575 | 39.7369 | 945738.5303 | 78.8115 | 78.8115 | 161.0265 | 80 | 55 | 33.1993 | 34 | 54.9
8/19/20XX 3:00:00 PM | 0.625 | 5 | 80.9 | 55.7 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 88.2735 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 65.1868 | 17.3662 | 413315.2086 | 34.4429 | 34.4429 | 96.4664 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 67.752 | 19.9314 | 474366.6172 | 39.5306 | 39.5306 | 103.7276 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 70.3172 | 22.4966 | 535418.0258 | 44.6182 | 44.6182 | 110.9887 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 72.8824 | 25.0617 | 596469.4345 | 49.7058 | 49.7058 | 118.2498 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 75.4476 | 27.6269 | 657520.8431 | 54.7934 | 54.7934 | 125.5109 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 78.0127 | 30.1921 | 718572.2517 | 59.881 | 59.881 | 132.772 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 80.5779 | 32.7573 | 779623.6603 | 64.9686 | 64.9686 | 140.0331 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 83.1431 | 35.3225 | 840675.0689 | 70.0563 | 70.0563 | 147.2943 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 85.7083 | 37.8877 | 901726.4775 | 75.1439 | 75.1439 | 154.5554 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 88.2735 | 40.4529 | 962777.8861 | 80.2315 | 80.2315 | 161.8165 | 80 | 55 | 33.2625 | 34 | 55.7
8/19/20XX 4:00:00 PM | 0.66667 | 5 | 80.2 | 58.3 | 77.2359 | 93.0386 | 15.8027 | 50 | 80.2 |  | 80.2 | 90.3522 | 0.1 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 65.3947 | 17.5741 | 418262.4525 | 34.8552 | 34.8552 | 96.6582 | 0.2 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 68.1677 | 20.3471 | 484261.1049 | 40.3551 | 40.3551 | 104.1111 | 0.3 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 70.9408 | 23.1202 | 550259.7574 | 45.855 | 45.855 | 111.564 | 0.4 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 73.7138 | 25.8932 | 616258.4098 | 51.3549 | 51.3549 | 119.0169 | 0.5 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 76.4869 | 28.6663 | 682257.0623 | 56.8548 | 56.8548 | 126.4698 | 0.6 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 79.2599 | 31.4393 | 748255.7148 | 62.3546 | 62.3546 | 133.9226 | 0.7 | 78.34 | 23.34 | 882252 | 73.521 | 73.521 | 82.033 | 34.2124 | 814254.3672 | 67.8545 | 67.8545 | 141.3755 | 0.8 | 78.96 | 23.96 | 905688 | 75.474 | 75.474 | 84.8061 | 36.9854 | 880253.0197 | 73.3544 | 73.3544 | 148.8284 | 0.9 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 87.5791 | 39.7585 | 946251.6722 | 78.8543 | 78.8543 | 156.2813 | 1 | 80.2 | 25.2 | 952560 | 79.38 | 79.38 | 90.3522 | 42.5315 | 1012250.3246 | 84.3542 | 84.3542 | 163.7342 | 80 | 60 | 33.4166 | 34 | 58.3
8/19/20XX 5:00:00 PM | 0.70833 | 5 | 79.1 | 60.2 | 89.6782 | 104.9873 | 15.3091 | 60 | 79.1 |  | 79.1 | 89.9844 | 0.1 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 65.3579 | 17.5373 | 417387.0918 | 34.7823 | 34.7823 | 96.2388 | 0.2 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 68.0942 | 20.2735 | 482510.3836 | 40.2092 | 40.2092 | 103.2722 | 0.3 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 70.8305 | 23.0098 | 547633.6753 | 45.6361 | 45.6361 | 110.3056 | 0.4 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 73.5667 | 25.7461 | 612756.9671 | 51.0631 | 51.0631 | 117.3391 | 0.5 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 76.303 | 28.4824 | 677880.2589 | 56.49 | 56.49 | 124.3725 | 0.6 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 79.0393 | 31.2186 | 743003.5507 | 61.917 | 61.917 | 131.406 | 0.7 | 77.57 | 22.57 | 853146 | 71.0955 | 71.0955 | 81.7755 | 33.9549 | 808126.8425 | 67.3439 | 67.3439 | 138.4394 | 0.8 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 84.5118 | 36.6912 | 873250.1343 | 72.7708 | 72.7708 | 145.4728 | 0.9 | 78.59 | 23.59 | 891702 | 74.3085 | 74.3085 | 87.2481 | 39.4275 | 938373.426 | 78.1978 | 78.1978 | 152.5063 | 1 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 89.9844 | 42.1637 | 1003496.7178 | 83.6247 | 83.6247 | 159.5397 | 80 | 60 | 33.0886 | 34 | 60.2
8/19/20XX 6:00:00 PM | 0.75 | 5 | 77.6 | 62.2 | 85.2591 | 99.7988 | 14.5397 | 60 | 77.6 |  | 77.6 | 88.4579 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 65.2053 | 17.3846 | 413754.0405 | 34.4795 | 34.4795 | 95.4635 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 67.7889 | 19.9682 | 475244.2811 | 39.6037 | 39.6037 | 101.7217 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 70.3725 | 22.5519 | 536734.5216 | 44.7279 | 44.7279 | 107.9799 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 72.9561 | 25.1355 | 598224.7621 | 49.8521 | 49.8521 | 114.2381 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 75.5398 | 27.7191 | 659715.0027 | 54.9763 | 54.9763 | 120.4963 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 78.1234 | 30.3027 | 721205.2432 | 60.1004 | 60.1004 | 126.7544 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 80.707 | 32.8864 | 782695.4837 | 65.2246 | 65.2246 | 133.0126 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 83.2906 | 35.47 | 844185.7243 | 70.3488 | 70.3488 | 139.2708 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 85.8742 | 38.0536 | 905675.9648 | 75.473 | 75.473 | 145.529 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 88.4579 | 40.6372 | 967166.2053 | 80.5972 | 80.5972 | 151.7872 | 80 | 60 | 32.4809 | 32 | 62.2
8/19/20XX 7:00:00 PM | 0.79167 | 5 | 76.1 | 66 | 81.0242 | 94.8268 | 13.8027 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/19/20XX 8:00:00 PM | 0.83333 | 5 | 75.5 | 67.9 | 79.3806 | 92.8973 | 13.5167 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/19/20XX 9:00:00 PM | 0.875 | 5 | 74.9 | 71.8 | 91.0012 | 104.3307 | 13.3295 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/19/20XX 10:00:00 PM | 0.91667 | 5 | 74.6 | 72 | 90.0655 | 103.2545 | 13.1889 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/19/20XX 11:00:00 PM | 0.95833 | 5 | 73.9 | 72.8 | 87.9141 | 100.78 | 12.8659 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/19/20XX 12:00:00 AM | 0 | 6 | 73.9 | 72.7 | 87.9141 | 100.78 | 12.8659 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/20/20XX 1:00:00 AM | 0.041667 | 6 | 72.9 | 75.4 | 84.9169 | 97.3334 | 12.4165 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/20/20XX 2:00:00 AM | 0.083333 | 6 | 72.1 | 75.9 | 82.5828 | 94.6498 | 12.0671 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/20/20XX 3:00:00 AM | 0.125 | 6 | 71.5 | 77.7 | 80.8687 | 92.6795 | 11.8108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/20/20XX 4:00:00 AM | 0.16667 | 6 | 71.1 | 77.8 | 79.7432 | 91.3858 | 11.6426 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/20/20XX 5:00:00 AM | 0.20833 | 6 | 70.9 | 79.3 | 79.1855 | 90.7449 | 11.5593 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/20/20XX 6:00:00 AM | 0.25 | 6 | 71.1 | 79.7 | 79.7432 | 91.3858 | 11.6426 | 70 | 71.1 |  | 71.1 | 91.0365 | 0.1 | 73.71 | 18.71 | 707238 | 58.9365 | 58.9365 | 65.4631 | 17.6425 | 419891.1783 | 34.9909 | 34.9909 | 93.9274 | 0.2 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 68.3046 | 20.484 | 487518.5566 | 40.6265 | 40.6265 | 98.6495 | 0.3 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 71.1461 | 23.3255 | 555145.9349 | 46.2622 | 46.2622 | 103.3717 | 0.4 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 73.9876 | 26.1669 | 622773.3131 | 51.8978 | 51.8978 | 108.0938 | 0.5 | 72.55 | 17.55 | 663390 | 55.2825 | 55.2825 | 76.8291 | 29.0084 | 690400.6914 | 57.5334 | 57.5334 | 112.8159 | 0.6 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 79.6706 | 31.8499 | 758028.0697 | 63.169 | 63.169 | 117.538 | 0.7 | 71.97 | 16.97 | 641466 | 53.4555 | 53.4555 | 82.512 | 34.6914 | 825655.448 | 68.8046 | 68.8046 | 122.2601 | 0.8 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 85.3535 | 37.5329 | 893282.8263 | 74.4402 | 74.4402 | 126.9822 | 0.9 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 88.195 | 40.3744 | 960910.2046 | 80.0759 | 80.0759 | 131.7044 | 1 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 91.0365 | 43.2159 | 1028537.5829 | 85.7115 | 85.7115 | 136.4265 | 70 | 80 | 31.2873 | 32 | 79.7
8/20/20XX 7:00:00 AM | 0.29167 | 6 | 72.2 | 77.7 | 82.8715 | 94.9817 | 12.1103 | 70 | 72.2 |  | 72.2 | 92.1964 | 0.1 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 65.5791 | 17.7585 | 422651.7 | 35.221 | 35.221 | 94.504 | 0.2 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 68.5366 | 20.7159 | 493039.5999 | 41.0866 | 41.0866 | 99.8026 | 0.3 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 71.4941 | 23.6734 | 563427.4999 | 46.9523 | 46.9523 | 105.1013 | 0.4 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 74.4515 | 26.6309 | 633815.3999 | 52.8179 | 52.8179 | 110.3999 | 0.5 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 77.409 | 29.5884 | 704203.2999 | 58.6836 | 58.6836 | 115.6986 | 0.6 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 80.3665 | 32.5458 | 774591.1998 | 64.5493 | 64.5493 | 120.9973 | 0.7 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 83.324 | 35.5033 | 844979.0998 | 70.4149 | 70.4149 | 126.2959 | 0.8 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 86.2814 | 38.4608 | 915366.9998 | 76.2806 | 76.2806 | 131.5946 | 0.9 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 89.2389 | 41.4183 | 985754.8997 | 82.1462 | 82.1462 | 136.8932 | 1 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 92.1964 | 44.3757 | 1056142.7997 | 88.0119 | 88.0119 | 142.1919 | 70 | 80 | 31.739 | 32 | 77.7
8/20/20XX 8:00:00 AM | 0.33333 | 6 | 74.2 | 72.3 | 88.8307 | 101.8342 | 13.0035 | 70 | 74.2 |  | 74.2 | 91.8215 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 65.5416 | 17.721 | 421759.497 | 35.1466 | 35.1466 | 95.0596 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 68.4616 | 20.641 | 491255.194 | 40.9379 | 40.9379 | 100.9139 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 71.3816 | 23.561 | 560750.8909 | 46.7292 | 46.7292 | 106.7682 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 74.3016 | 26.4809 | 630246.5879 | 52.5205 | 52.5205 | 112.6225 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 77.2216 | 29.4009 | 699742.2849 | 58.3119 | 58.3119 | 118.4769 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 80.1416 | 32.3209 | 769237.9819 | 64.1032 | 64.1032 | 124.3312 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 83.0615 | 35.2409 | 838733.6789 | 69.8945 | 69.8945 | 130.1855 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 85.9815 | 38.1609 | 908229.3758 | 75.6858 | 75.6858 | 136.0398 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 88.9015 | 41.0809 | 977725.0728 | 81.4771 | 81.4771 | 141.8941 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 91.8215 | 44.0009 | 1047220.7698 | 87.2684 | 87.2684 | 147.7484 | 75 | 70 | 32.172 | 32 | 72.3
8/20/20XX 9:00:00 AM | 0.375 | 6 | 76.1 | 65.8 | 81.0242 | 94.8268 | 13.8027 | 60 | 76.1 |  | 76.1 | 89.0297 | 0.1 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 65.2624 | 17.4418 | 415115.0015 | 34.5929 | 34.5929 | 95.1044 | 0.2 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 67.9032 | 20.0826 | 477966.203 | 39.8305 | 39.8305 | 101.0035 | 0.3 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 70.5441 | 22.7234 | 540817.4045 | 45.0681 | 45.0681 | 106.9026 | 0.4 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 73.1849 | 25.3642 | 603668.606 | 50.3057 | 50.3057 | 112.8017 | 0.5 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 75.8257 | 28.005 | 666519.8075 | 55.5433 | 55.5433 | 118.7008 | 0.6 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 78.4665 | 30.6458 | 729371.009 | 60.7809 | 60.7809 | 124.5999 | 0.7 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 81.1073 | 33.2866 | 792222.2105 | 66.0185 | 66.0185 | 130.499 | 0.8 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 83.7481 | 35.9275 | 855073.412 | 71.2561 | 71.2561 | 136.3981 | 0.9 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 86.3889 | 38.5683 | 917924.6135 | 76.4937 | 76.4937 | 142.2972 | 1 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 89.0297 | 41.2091 | 980775.815 | 81.7313 | 81.7313 | 148.1963 | 75 | 65 | 32.202 | 32 | 65.8
8/20/20XX 10:00:00 AM | 0.41667 | 6 | 78.1 | 62.7 | 86.7115 | 101.504 | 14.7925 | 60 | 78.1 |  | 78.1 | 90.7054 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 65.43 | 17.6094 | 419103.2581 | 34.9253 | 34.9253 | 96.0668 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 68.2384 | 20.4178 | 485942.7161 | 40.4952 | 40.4952 | 102.9282 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 71.0468 | 23.2261 | 552782.1742 | 46.0652 | 46.0652 | 109.7897 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 73.8552 | 26.0345 | 619621.6323 | 51.6351 | 51.6351 | 116.6511 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 76.6635 | 28.8429 | 686461.0904 | 57.2051 | 57.2051 | 123.5126 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 79.4719 | 31.6513 | 753300.5484 | 62.775 | 62.775 | 130.374 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 82.2803 | 34.4597 | 820140.0065 | 68.345 | 68.345 | 137.2355 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 85.0887 | 37.268 | 886979.4646 | 73.915 | 73.915 | 144.097 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 87.8971 | 40.0764 | 953818.9226 | 79.4849 | 79.4849 | 150.9584 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 90.7054 | 42.8848 | 1020658.3807 | 85.0549 | 85.0549 | 157.8199 | 80 | 65 | 32.9559 | 32 | 62.7
8/20/20XX 11:00:00 AM | 0.45833 | 6 | 80.8 | 57.7 | 78.7895 | 94.9151 | 16.1256 | 50 | 80.8 |  | 80.8 | 91.2062 | 0.1 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 65.4801 | 17.6595 | 420295.0953 | 35.0246 | 35.0246 | 97.0166 | 0.2 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 68.3385 | 20.5179 | 488326.3905 | 40.6939 | 40.6939 | 104.8279 | 0.3 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 71.197 | 23.3764 | 556357.6858 | 46.3631 | 46.3631 | 112.6391 | 0.4 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 74.0555 | 26.2348 | 624388.981 | 52.0324 | 52.0324 | 120.4504 | 0.5 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 76.9139 | 29.0933 | 692420.2763 | 57.7017 | 57.7017 | 128.2617 | 0.6 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 79.7724 | 31.9517 | 760451.5715 | 63.371 | 63.371 | 136.073 | 0.7 | 78.76 | 23.76 | 898128 | 74.844 | 74.844 | 82.6308 | 34.8102 | 828482.8668 | 69.0402 | 69.0402 | 143.8842 | 0.8 | 79.44 | 24.44 | 923832 | 76.986 | 76.986 | 85.4893 | 37.6687 | 896514.1621 | 74.7095 | 74.7095 | 151.6955 | 0.9 | 80.12 | 25.12 | 949536 | 79.128 | 79.128 | 88.3478 | 40.5271 | 964545.4573 | 80.3788 | 80.3788 | 159.5068 | 1 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 91.2062 | 43.3856 | 1032576.7526 | 86.0481 | 86.0481 | 167.3181 | 80 | 60 | 33.698 | 34 | 57.7
8/20/20XX 12:00:00 PM | 0.5 | 6 | 81.1 | 56.7 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 90.4896 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 65.4084 | 17.5878 | 418589.5229 | 34.8825 | 34.8825 | 96.969 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 68.1952 | 20.3746 | 484915.2459 | 40.4096 | 40.4096 | 104.7326 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 70.982 | 23.1614 | 551240.9688 | 45.9367 | 45.9367 | 112.4962 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 73.7688 | 25.9482 | 617566.6917 | 51.4639 | 51.4639 | 120.2599 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 76.5556 | 28.735 | 683892.4147 | 56.991 | 56.991 | 128.0235 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 79.3424 | 31.5218 | 750218.1376 | 62.5182 | 62.5182 | 135.7872 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 82.1292 | 34.3086 | 816543.8605 | 68.0453 | 68.0453 | 143.5508 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 84.916 | 37.0954 | 882869.5835 | 73.5725 | 73.5725 | 151.3145 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 87.7028 | 39.8822 | 949195.3064 | 79.0996 | 79.0996 | 159.0781 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 90.4896 | 42.669 | 1015521.0294 | 84.6268 | 84.6268 | 166.8418 | 80 | 55 | 33.6593 | 34 | 56.7
8/20/20XX 1:00:00 PM | 0.54167 | 6 | 81.6 | 54.9 | 80.9009 | 97.4655 | 16.5647 | 50 | 81.6 |  | 81.6 | 89.0175 | 0.1 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 65.2612 | 17.4406 | 415086.0674 | 34.5905 | 34.5905 | 96.8345 | 0.2 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 67.9008 | 20.0802 | 477908.3349 | 39.8257 | 39.8257 | 104.4637 | 0.3 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 70.5404 | 22.7198 | 540730.6023 | 45.0609 | 45.0609 | 112.0929 | 0.4 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 73.18 | 25.3594 | 603552.8698 | 50.2961 | 50.2961 | 119.7221 | 0.5 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 75.8196 | 27.999 | 666375.1372 | 55.5313 | 55.5313 | 127.3513 | 0.6 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 78.4592 | 30.6385 | 729197.4047 | 60.7665 | 60.7665 | 134.9805 | 0.7 | 79.32 | 24.32 | 919296 | 76.608 | 76.608 | 81.0988 | 33.2781 | 792019.6721 | 66.0016 | 66.0016 | 142.6096 | 0.8 | 80.08 | 25.08 | 948024 | 79.002 | 79.002 | 83.7384 | 35.9177 | 854841.9395 | 71.2368 | 71.2368 | 150.2388 | 0.9 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 86.378 | 38.5573 | 917664.207 | 76.472 | 76.472 | 157.868 | 1 | 81.6 | 26.6 | 1005480 | 83.79 | 83.79 | 89.0175 | 41.1969 | 980486.4744 | 81.7072 | 81.7072 | 165.4972 | 80 | 55 | 33.5512 | 34 | 54.9
8/20/20XX 2:00:00 PM | 0.58333 | 6 | 81.3 | 56.8 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 91.2549 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 65.485 | 17.6643 | 420411.0921 | 35.0343 | 35.0343 | 97.1838 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 68.3483 | 20.5277 | 488558.3841 | 40.7132 | 40.7132 | 105.1622 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 71.2116 | 23.391 | 556705.6762 | 46.3921 | 46.3921 | 113.1406 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 74.075 | 26.2543 | 624852.9682 | 52.0711 | 52.0711 | 121.1191 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 76.9383 | 29.1177 | 693000.2603 | 57.75 | 57.75 | 129.0975 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 79.8016 | 31.981 | 761147.5523 | 63.429 | 63.429 | 137.076 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 82.665 | 34.8443 | 829294.8444 | 69.1079 | 69.1079 | 145.0544 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 85.5283 | 37.7077 | 897442.1364 | 74.7868 | 74.7868 | 153.0328 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 88.3916 | 40.571 | 965589.4285 | 80.4658 | 80.4658 | 161.0113 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 91.2549 | 43.4343 | 1033736.7206 | 86.1447 | 86.1447 | 168.9897 | 80 | 55 | 33.8285 | 34 | 56.8
8/20/20XX 3:00:00 PM | 0.625 | 6 | 81.6 | 54.5 | 80.9009 | 97.4655 | 16.5647 | 50 | 81.6 |  | 81.6 | 88.355 | 0.1 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 65.195 | 17.3743 | 413509.1107 | 34.4591 | 34.4591 | 96.7031 | 0.2 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 67.7683 | 19.9477 | 474754.4214 | 39.5629 | 39.5629 | 104.2009 | 0.3 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 70.3416 | 22.521 | 535999.7321 | 44.6666 | 44.6666 | 111.6986 | 0.4 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 72.915 | 25.0943 | 597245.0428 | 49.7704 | 49.7704 | 119.1964 | 0.5 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 75.4883 | 27.6677 | 658490.3535 | 54.8742 | 54.8742 | 126.6942 | 0.6 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 78.0616 | 30.241 | 719735.6643 | 59.978 | 59.978 | 134.192 | 0.7 | 79.32 | 24.32 | 919296 | 76.608 | 76.608 | 80.635 | 32.8143 | 780980.975 | 65.0817 | 65.0817 | 141.6897 | 0.8 | 80.08 | 25.08 | 948024 | 79.002 | 79.002 | 83.2083 | 35.3877 | 842226.2857 | 70.1855 | 70.1855 | 149.1875 | 0.9 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 85.7816 | 37.961 | 903471.5964 | 75.2893 | 75.2893 | 156.6853 | 1 | 81.6 | 26.6 | 1005480 | 83.79 | 83.79 | 88.355 | 40.5343 | 964716.9071 | 80.3931 | 80.3931 | 164.1831 | 80 | 55 | 33.4472 | 34 | 54.5
8/20/20XX 4:00:00 PM | 0.66667 | 6 | 81.5 | 52.5 | 80.6344 | 97.1437 | 16.5092 | 50 | 81.5 |  | 81.5 | 84.7617 | 0.1 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 64.8356 | 17.015 | 404957.2438 | 33.7464 | 33.7464 | 95.9589 | 0.2 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 67.0497 | 19.229 | 457650.6875 | 38.1376 | 38.1376 | 102.7126 | 0.3 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 69.2637 | 21.443 | 510344.1313 | 42.5287 | 42.5287 | 109.4662 | 0.4 | 77 | 22 | 831600 | 69.3 | 69.3 | 71.4777 | 23.657 | 563037.5751 | 46.9198 | 46.9198 | 116.2198 | 0.5 | 77.75 | 22.75 | 859950 | 71.6625 | 71.6625 | 73.6917 | 25.8711 | 615731.0188 | 51.3109 | 51.3109 | 122.9734 | 0.6 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 75.9057 | 28.0851 | 668424.4626 | 55.702 | 55.702 | 129.727 | 0.7 | 79.25 | 24.25 | 916650 | 76.3875 | 76.3875 | 78.1197 | 30.2991 | 721117.9063 | 60.0932 | 60.0932 | 136.4807 | 0.8 | 80 | 25 | 945000 | 78.75 | 78.75 | 80.3337 | 32.5131 | 773811.3501 | 64.4843 | 64.4843 | 143.2343 | 0.9 | 80.75 | 25.75 | 973350 | 81.1125 | 81.1125 | 82.5477 | 34.7271 | 826504.7939 | 68.8754 | 68.8754 | 149.9879 | 1 | 81.5 | 26.5 | 1001700 | 83.475 | 83.475 | 84.7617 | 36.9411 | 879198.2376 | 73.2665 | 73.2665 | 156.7415 | 80 | 50 | 32.8589 | 32 | 52.5
8/20/20XX 5:00:00 PM | 0.70833 | 6 | 80.5 | 55.5 | 78.0095 | 93.973 | 15.9635 | 50 | 80.5 |  | 80.5 | 86.7894 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 65.0384 | 17.2178 | 409783.1563 | 34.1486 | 34.1486 | 96.0461 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 67.4552 | 19.6346 | 467302.5127 | 38.9419 | 38.9419 | 102.8869 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 69.872 | 22.0513 | 524821.869 | 43.7352 | 43.7352 | 109.7277 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 72.2888 | 24.4681 | 582341.2253 | 48.5284 | 48.5284 | 116.5684 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 74.7055 | 26.8849 | 639860.5817 | 53.3217 | 53.3217 | 123.4092 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 77.1223 | 29.3017 | 697379.938 | 58.115 | 58.115 | 130.25 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 79.5391 | 31.7185 | 754899.2943 | 62.9083 | 62.9083 | 137.0908 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 81.9559 | 34.1352 | 812418.6507 | 67.7016 | 67.7016 | 143.9316 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 84.3726 | 36.552 | 869938.007 | 72.4948 | 72.4948 | 150.7723 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 86.7894 | 38.9688 | 927457.3633 | 77.2881 | 77.2881 | 157.6131 | 80 | 55 | 32.9315 | 32 | 55.5
8/20/20XX 6:00:00 PM | 0.75 | 6 | 78.7 | 58.8 | 73.4624 | 88.4815 | 15.0191 | 50 | 78.7 |  | 78.7 | 86.6792 | 0.1 | 74.47 | 19.47 | 735966 | 61.3305 | 61.3305 | 65.0274 | 17.2068 | 409520.8272 | 34.1267 | 34.1267 | 95.4572 | 0.2 | 74.94 | 19.94 | 753732 | 62.811 | 62.811 | 67.4331 | 19.6125 | 466777.8545 | 38.8982 | 38.8982 | 101.7092 | 0.3 | 75.41 | 20.41 | 771498 | 64.2915 | 64.2915 | 69.8389 | 22.0183 | 524034.8817 | 43.6696 | 43.6696 | 107.9611 | 0.4 | 75.88 | 20.88 | 789264 | 65.772 | 65.772 | 72.2447 | 24.424 | 581291.9089 | 48.441 | 48.441 | 114.213 | 0.5 | 76.35 | 21.35 | 807030 | 67.2525 | 67.2525 | 74.6504 | 26.8298 | 638548.9362 | 53.2124 | 53.2124 | 120.4649 | 0.6 | 76.82 | 21.82 | 824796 | 68.733 | 68.733 | 77.0562 | 29.2355 | 695805.9634 | 57.9838 | 57.9838 | 126.7168 | 0.7 | 77.29 | 22.29 | 842562 | 70.2135 | 70.2135 | 79.4619 | 31.6413 | 753062.9906 | 62.7552 | 62.7552 | 132.9687 | 0.8 | 77.76 | 22.76 | 860328 | 71.694 | 71.694 | 81.8677 | 34.0471 | 810320.0179 | 67.5267 | 67.5267 | 139.2207 | 0.9 | 78.23 | 23.23 | 878094 | 73.1745 | 73.1745 | 84.2734 | 36.4528 | 867577.0451 | 72.2981 | 72.2981 | 145.4726 | 1 | 78.7 | 23.7 | 895860 | 74.655 | 74.655 | 86.6792 | 38.8586 | 924834.0723 | 77.0695 | 77.0695 | 151.7245 | 80 | 60 | 32.4723 | 32 | 58.8
8/20/20XX 7:00:00 PM | 0.79167 | 6 | 77.5 | 62.1 | 84.9711 | 99.4607 | 14.4896 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/20/20XX 8:00:00 PM | 0.83333 | 6 | 76.8 | 64.1 | 82.9779 | 97.1205 | 14.1426 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/20/20XX 9:00:00 PM | 0.875 | 6 | 76.3 | 66 | 81.5784 | 95.4774 | 13.8991 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/20/20XX 10:00:00 PM | 0.91667 | 6 | 75.8 | 67.8 | 80.1988 | 93.8579 | 13.6591 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/20/20XX 11:00:00 PM | 0.95833 | 6 | 75.4 | 67.6 | 79.1095 | 92.579 | 13.4695 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/20/20XX 12:00:00 AM | 0 | 7 | 74.9 | 70.2 | 91.0012 | 104.3307 | 13.3295 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/21/20XX 1:00:00 AM | 0.041667 | 7 | 74.3 | 70.7 | 89.138 | 102.1877 | 13.0496 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/21/20XX 2:00:00 AM | 0.083333 | 7 | 73.7 | 72.8 | 87.3075 | 100.0824 | 12.7749 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/21/20XX 3:00:00 AM | 0.125 | 7 | 73 | 74.6 | 85.2126 | 97.6734 | 12.4608 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/21/20XX 4:00:00 AM | 0.16667 | 7 | 72.2 | 76.7 | 82.8715 | 94.9817 | 12.1103 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/21/20XX 5:00:00 AM | 0.20833 | 7 | 71.3 | 79 | 80.3042 | 92.0306 | 11.7264 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/21/20XX 6:00:00 AM | 0.25 | 7 | 71.5 | 77.6 | 80.8687 | 92.6795 | 11.8108 | 70 | 71.5 |  | 71.5 | 89.8449 | 0.1 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 65.344 | 17.5233 | 417055.11 | 34.7546 | 34.7546 | 93.8171 | 0.2 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 68.0663 | 20.2456 | 481846.4199 | 40.1539 | 40.1539 | 98.4289 | 0.3 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 70.7886 | 22.968 | 546637.7299 | 45.5531 | 45.5531 | 103.0406 | 0.4 | 73 | 18 | 680400 | 56.7 | 56.7 | 73.5109 | 25.6903 | 611429.0399 | 50.9524 | 50.9524 | 107.6524 | 0.5 | 72.75 | 17.75 | 670950 | 55.9125 | 55.9125 | 76.2333 | 28.4126 | 676220.3498 | 56.3517 | 56.3517 | 112.2642 | 0.6 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 78.9556 | 31.1349 | 741011.6598 | 61.751 | 61.751 | 116.876 | 0.7 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 81.6779 | 33.8573 | 805802.9698 | 67.1502 | 67.1502 | 121.4877 | 0.8 | 72 | 17 | 642600 | 53.55 | 53.55 | 84.4002 | 36.5796 | 870594.2797 | 72.5495 | 72.5495 | 126.0995 | 0.9 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 87.1225 | 39.3019 | 935385.5897 | 77.9488 | 77.9488 | 130.7113 | 1 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 89.8449 | 42.0242 | 1000176.8997 | 83.3481 | 83.3481 | 135.3231 | 70 | 80 | 31.1994 | 32 | 77.6
8/21/20XX 7:00:00 AM | 0.29167 | 7 | 72.8 | 76.2 | 84.6221 | 96.9944 | 12.3723 | 70 | 72.8 |  | 72.8 | 92.2929 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.5888 | 17.7681 | 422881.4768 | 35.2401 | 35.2401 | 94.7121 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 68.5559 | 20.7353 | 493499.1535 | 41.1249 | 41.1249 | 100.2189 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 71.523 | 23.7024 | 564116.8303 | 47.0097 | 47.0097 | 105.7257 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 74.4901 | 26.6695 | 634734.507 | 52.8945 | 52.8945 | 111.2325 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 77.4573 | 29.6366 | 705352.1838 | 58.7793 | 58.7793 | 116.7393 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 80.4244 | 32.6038 | 775969.8606 | 64.6642 | 64.6642 | 122.2462 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 83.3915 | 35.5709 | 846587.5373 | 70.549 | 70.549 | 127.753 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 86.3587 | 38.538 | 917205.2141 | 76.4338 | 76.4338 | 133.2598 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 89.3258 | 41.5052 | 987822.8908 | 82.3186 | 82.3186 | 138.7666 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 92.2929 | 44.4723 | 1058440.5676 | 88.2034 | 88.2034 | 144.2734 | 75 | 75 | 31.9016 | 32 | 76.2
8/21/20XX 8:00:00 AM | 0.33333 | 7 | 73.8 | 74.8 | 87.6104 | 100.4307 | 12.8203 | 70 | 73.8 |  | 73.8 | 93.7641 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 65.7359 | 17.9152 | 426382.897 | 35.5319 | 35.5319 | 95.3189 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 68.8501 | 21.0295 | 500501.9939 | 41.7085 | 41.7085 | 101.4325 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 71.9644 | 24.1437 | 574621.0909 | 47.8851 | 47.8851 | 107.5461 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 75.0786 | 27.258 | 648740.1878 | 54.0617 | 54.0617 | 113.6597 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 78.1929 | 30.3722 | 722859.2848 | 60.2383 | 60.2383 | 119.7733 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 81.3071 | 33.4865 | 796978.3818 | 66.4149 | 66.4149 | 125.8869 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 84.4214 | 36.6007 | 871097.4787 | 72.5915 | 72.5915 | 132.0005 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 87.5356 | 39.715 | 945216.5757 | 78.768 | 78.768 | 138.114 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 90.6499 | 42.8292 | 1019335.6727 | 84.9446 | 84.9446 | 144.2276 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 93.7641 | 45.9435 | 1093454.7696 | 91.1212 | 91.1212 | 150.3412 | 75 | 75 | 32.3775 | 32 | 74.8
8/21/20XX 9:00:00 AM | 0.375 | 7 | 75.9 | 69.8 | 80.4731 | 94.1799 | 13.7068 | 60 | 75.9 |  | 75.9 | 93.9058 | 0.1 | 74.19 | 19.19 | 725382 | 60.4485 | 60.4485 | 65.75 | 17.9294 | 426720.0939 | 35.56 | 35.56 | 96.0085 | 0.2 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 68.8785 | 21.0578 | 501176.3879 | 41.7647 | 41.7647 | 102.8117 | 0.3 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 72.0069 | 24.1862 | 575632.6818 | 47.9694 | 47.9694 | 109.6149 | 0.4 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 75.1353 | 27.3147 | 650088.9758 | 54.1741 | 54.1741 | 116.4181 | 0.5 | 74.95 | 19.95 | 754110 | 62.8425 | 62.8425 | 78.2637 | 30.4431 | 724545.2697 | 60.3788 | 60.3788 | 123.2213 | 0.6 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 81.3921 | 33.5715 | 799001.5637 | 66.5835 | 66.5835 | 130.0245 | 0.7 | 75.33 | 20.33 | 768474 | 64.0395 | 64.0395 | 84.5205 | 36.6999 | 873457.8576 | 72.7882 | 72.7882 | 136.8277 | 0.8 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 87.649 | 39.8283 | 947914.1516 | 78.9928 | 78.9928 | 143.6308 | 0.9 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 90.7774 | 42.9567 | 1022370.4455 | 85.1975 | 85.1975 | 150.434 | 1 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 93.9058 | 46.0852 | 1096826.7395 | 91.4022 | 91.4022 | 157.2372 | 75 | 70 | 32.9162 | 32 | 69.8
8/21/20XX 10:00:00 AM | 0.41667 | 7 | 77.8 | 65.1 | 85.8376 | 100.478 | 14.6404 | 60 | 77.8 |  | 77.8 | 93.3042 | 0.1 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 65.6899 | 17.8693 | 425288.3078 | 35.4407 | 35.4407 | 96.4877 | 0.2 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 68.7581 | 20.9375 | 498312.8156 | 41.5261 | 41.5261 | 103.7701 | 0.3 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 71.8264 | 24.0058 | 571337.3234 | 47.6114 | 47.6114 | 111.0524 | 0.4 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 74.8947 | 27.074 | 644361.8313 | 53.6968 | 53.6968 | 118.3348 | 0.5 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 77.9629 | 30.1423 | 717386.3391 | 59.7822 | 59.7822 | 125.6172 | 0.6 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 81.0312 | 33.2105 | 790410.8469 | 65.8676 | 65.8676 | 132.8996 | 0.7 | 76.66 | 21.66 | 818748 | 68.229 | 68.229 | 84.0994 | 36.2788 | 863435.3547 | 71.9529 | 71.9529 | 140.1819 | 0.8 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 87.1677 | 39.3471 | 936459.8625 | 78.0383 | 78.0383 | 147.4643 | 0.9 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 90.2359 | 42.4153 | 1009484.3703 | 84.1237 | 84.1237 | 154.7467 | 1 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 93.3042 | 45.4836 | 1082508.8782 | 90.2091 | 90.2091 | 162.0291 | 80 | 65 | 33.2893 | 34 | 65.1
8/21/20XX 11:00:00 AM | 0.45833 | 7 | 81.1 | 56.4 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 90.0009 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 65.3596 | 17.5389 | 417426.4813 | 34.7855 | 34.7855 | 96.872 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 68.0975 | 20.2769 | 482589.1626 | 40.2158 | 40.2158 | 104.5388 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 70.8354 | 23.0148 | 547751.8439 | 45.646 | 45.646 | 112.2055 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 73.5733 | 25.7527 | 612914.5251 | 51.0762 | 51.0762 | 119.8722 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 76.3113 | 28.4906 | 678077.2064 | 56.5064 | 56.5064 | 127.5389 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 79.0492 | 31.2286 | 743239.8877 | 61.9367 | 61.9367 | 135.2057 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 81.7871 | 33.9665 | 808402.569 | 67.3669 | 67.3669 | 142.8724 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 84.5251 | 36.7044 | 873565.2503 | 72.7971 | 72.7971 | 150.5391 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 87.263 | 39.4424 | 938727.9316 | 78.2273 | 78.2273 | 158.2058 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 90.0009 | 42.1803 | 1003890.6128 | 83.6576 | 83.6576 | 165.8726 | 80 | 55 | 33.5826 | 34 | 56.4
8/21/20XX 12:00:00 PM | 0.5 | 7 | 82 | 54.2 | 81.9738 | 98.7617 | 16.7879 | 50 | 82 |  | 82 | 89.0247 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 65.2619 | 17.4413 | 415103.166 | 34.5919 | 34.5919 | 96.9619 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 67.9023 | 20.0816 | 477942.532 | 39.8285 | 39.8285 | 104.7185 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 70.5426 | 22.7219 | 540781.898 | 45.0652 | 45.0652 | 112.4752 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 73.1829 | 25.3622 | 603621.264 | 50.3018 | 50.3018 | 120.2318 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 75.8232 | 28.0025 | 666460.63 | 55.5384 | 55.5384 | 127.9884 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 78.4635 | 30.6429 | 729299.996 | 60.775 | 60.775 | 135.745 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 81.1038 | 33.2832 | 792139.362 | 66.0116 | 66.0116 | 143.5016 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 83.7441 | 35.9235 | 854978.728 | 71.2482 | 71.2482 | 151.2582 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 86.3844 | 38.5638 | 917818.094 | 76.4848 | 76.4848 | 159.0148 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 89.0247 | 41.2041 | 980657.46 | 81.7215 | 81.7215 | 166.7715 | 80 | 55 | 33.6506 | 34 | 54.2
8/21/20XX 1:00:00 PM | 0.54167 | 7 | 83.3 | 53 | 85.5415 | 103.0722 | 17.5307 | 50 | 83.3 |  | 83.3 | 90.8007 | 0.1 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 65.4395 | 17.6189 | 419330.0733 | 34.9442 | 34.9442 | 97.7237 | 0.2 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 68.2575 | 20.4368 | 486396.3466 | 40.533 | 40.533 | 106.242 | 0.3 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 71.0754 | 23.2547 | 553462.6199 | 46.1219 | 46.1219 | 114.7604 | 0.4 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 73.8933 | 26.0726 | 620528.8932 | 51.7107 | 51.7107 | 123.2787 | 0.5 | 78.65 | 23.65 | 893970 | 74.4975 | 74.4975 | 76.7112 | 28.8906 | 687595.1665 | 57.2996 | 57.2996 | 131.7971 | 0.6 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 79.5291 | 31.7085 | 754661.4398 | 62.8885 | 62.8885 | 140.3155 | 0.7 | 80.51 | 25.51 | 964278 | 80.3565 | 80.3565 | 82.347 | 34.5264 | 821727.7131 | 68.4773 | 68.4773 | 148.8338 | 0.8 | 81.44 | 26.44 | 999432 | 83.286 | 83.286 | 85.1649 | 37.3443 | 888793.9864 | 74.0662 | 74.0662 | 157.3522 | 0.9 | 82.37 | 27.37 | 1034586 | 86.2155 | 86.2155 | 87.9828 | 40.1622 | 955860.2597 | 79.655 | 79.655 | 165.8705 | 1 | 83.3 | 28.3 | 1069740 | 89.145 | 89.145 | 90.8007 | 42.9801 | 1022926.533 | 85.2439 | 85.2439 | 174.3889 | 85 | 55 | 34.2488 | 34 | 53
8/21/20XX 2:00:00 PM | 0.58333 | 7 | 82.9 | 53.1 | 84.4305 | 101.7299 | 17.2993 | 50 | 82.9 |  | 82.9 | 89.7933 | 0.1 | 74.89 | 19.89 | 751842 | 62.6535 | 62.6535 | 65.3388 | 17.5182 | 416932.4381 | 34.7444 | 34.7444 | 97.3979 | 0.2 | 75.78 | 20.78 | 785484 | 65.457 | 65.457 | 68.056 | 20.2353 | 481601.0761 | 40.1334 | 40.1334 | 105.5904 | 0.3 | 76.67 | 21.67 | 819126 | 68.2605 | 68.2605 | 70.7731 | 22.9525 | 546269.7142 | 45.5225 | 45.5225 | 113.783 | 0.4 | 77.56 | 22.56 | 852768 | 71.064 | 71.064 | 73.4903 | 25.6697 | 610938.3522 | 50.9115 | 50.9115 | 121.9755 | 0.5 | 78.45 | 23.45 | 886410 | 73.8675 | 73.8675 | 76.2075 | 28.3868 | 675606.9903 | 56.3006 | 56.3006 | 130.1681 | 0.6 | 79.34 | 24.34 | 920052 | 76.671 | 76.671 | 78.9247 | 31.104 | 740275.6284 | 61.6896 | 61.6896 | 138.3606 | 0.7 | 80.23 | 25.23 | 953694 | 79.4745 | 79.4745 | 81.6418 | 33.8212 | 804944.2664 | 67.0787 | 67.0787 | 146.5532 | 0.8 | 81.12 | 26.12 | 987336 | 82.278 | 82.278 | 84.359 | 36.5384 | 869612.9045 | 72.4677 | 72.4677 | 154.7457 | 0.9 | 82.01 | 27.01 | 1020978 | 85.0815 | 85.0815 | 87.0762 | 39.2555 | 934281.5426 | 77.8568 | 77.8568 | 162.9383 | 1 | 82.9 | 27.9 | 1054620 | 87.885 | 87.885 | 89.7933 | 41.9727 | 998950.1806 | 83.2458 | 83.2458 | 171.1308 | 85 | 55 | 33.9923 | 34 | 53.1
8/21/20XX 3:00:00 PM | 0.625 | 7 | 81.7 | 55.8 | 81.168 | 97.7883 | 16.6202 | 50 | 81.7 |  | 81.7 | 90.8078 | 0.1 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 65.4402 | 17.6196 | 419346.7623 | 34.9456 | 34.9456 | 97.2211 | 0.2 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 68.2589 | 20.4382 | 486429.7245 | 40.5358 | 40.5358 | 105.2368 | 0.3 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 71.0775 | 23.2568 | 553512.6868 | 46.1261 | 46.1261 | 113.2526 | 0.4 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 73.8961 | 26.0754 | 620595.649 | 51.7163 | 51.7163 | 121.2683 | 0.5 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 76.7147 | 28.8941 | 687678.6113 | 57.3066 | 57.3066 | 129.2841 | 0.6 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 79.5333 | 31.7127 | 754761.5735 | 62.8968 | 62.8968 | 137.2998 | 0.7 | 79.39 | 24.39 | 921942 | 76.8285 | 76.8285 | 82.3519 | 34.5313 | 821844.5358 | 68.487 | 68.487 | 145.3155 | 0.8 | 80.16 | 25.16 | 951048 | 79.254 | 79.254 | 85.1705 | 37.3499 | 888927.498 | 74.0773 | 74.0773 | 153.3313 | 0.9 | 80.93 | 25.93 | 980154 | 81.6795 | 81.6795 | 87.9891 | 40.1685 | 956010.4603 | 79.6675 | 79.6675 | 161.347 | 1 | 81.7 | 26.7 | 1009260 | 84.105 | 84.105 | 90.8078 | 42.9871 | 1023093.4225 | 85.2578 | 85.2578 | 169.3628 | 80 | 55 | 33.8567 | 34 | 55.8
8/21/20XX 4:00:00 PM | 0.66667 | 7 | 79.9 | 58.1 | 76.4687 | 92.1119 | 15.6433 | 50 | 79.9 |  | 79.9 | 89.1397 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 65.2734 | 17.4528 | 415376.8563 | 34.6147 | 34.6147 | 96.3232 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 67.9253 | 20.1046 | 478489.9127 | 39.8742 | 39.8742 | 103.4412 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 70.5771 | 22.7564 | 541602.969 | 45.1336 | 45.1336 | 110.5591 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 73.2289 | 25.4082 | 604716.0253 | 50.393 | 50.393 | 117.677 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 75.8807 | 28.06 | 667829.0817 | 55.6524 | 55.6524 | 124.7949 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 78.5325 | 30.7119 | 730942.138 | 60.9118 | 60.9118 | 131.9128 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 81.1843 | 33.3637 | 794055.1943 | 66.1713 | 66.1713 | 139.0308 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 83.8361 | 36.0155 | 857168.2506 | 71.4307 | 71.4307 | 146.1487 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 86.4879 | 38.6673 | 920281.307 | 76.6901 | 76.6901 | 153.2666 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 89.1397 | 41.3191 | 983394.3633 | 81.9495 | 81.9495 | 160.3845 | 80 | 60 | 33.1528 | 34 | 58.1
8/21/20XX 5:00:00 PM | 0.70833 | 7 | 78.4 | 64.2 | 87.5927 | 102.5387 | 14.946 | 60 | 78.4 |  | 78.4 | 93.87 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 65.7465 | 17.9258 | 426635.0239 | 35.5529 | 35.5529 | 96.7889 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 68.8713 | 21.0507 | 501006.2477 | 41.7505 | 41.7505 | 104.3725 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 71.9962 | 24.1755 | 575377.4716 | 47.9481 | 47.9481 | 111.9561 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 75.121 | 27.3004 | 649748.6955 | 54.1457 | 54.1457 | 119.5397 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 78.2458 | 30.4252 | 724119.9193 | 60.3433 | 60.3433 | 127.1233 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 81.3707 | 33.55 | 798491.1432 | 66.5409 | 66.5409 | 134.7069 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 84.4955 | 36.6749 | 872862.367 | 72.7385 | 72.7385 | 142.2905 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 87.6204 | 39.7997 | 947233.5909 | 78.9361 | 78.9361 | 149.8741 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 90.7452 | 42.9246 | 1021604.8148 | 85.1337 | 85.1337 | 157.4577 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 93.87 | 46.0494 | 1095976.0386 | 91.3313 | 91.3313 | 165.0413 | 80 | 65 | 33.5255 | 34 | 64.2
8/21/20XX 6:00:00 PM | 0.75 | 7 | 76.8 | 69.2 | 82.9779 | 97.1205 | 14.1426 | 60 | 76.8 |  | 76.8 | 95.9891 | 0.1 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 65.9584 | 18.1377 | 431678.3837 | 35.9732 | 35.9732 | 96.7052 | 0.2 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 69.2951 | 21.4745 | 511092.9674 | 42.5911 | 42.5911 | 104.2051 | 0.3 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 72.6319 | 24.8112 | 590507.5511 | 49.209 | 49.209 | 111.705 | 0.4 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 75.9686 | 28.148 | 669922.1348 | 55.8268 | 55.8268 | 119.2048 | 0.5 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 79.3054 | 31.4847 | 749336.7186 | 62.4447 | 62.4447 | 126.7047 | 0.6 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 82.6421 | 34.8215 | 828751.3023 | 69.0626 | 69.0626 | 134.2046 | 0.7 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 85.9789 | 38.1582 | 908165.886 | 75.6805 | 75.6805 | 141.7045 | 0.8 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 89.3156 | 41.495 | 987580.4697 | 82.2984 | 82.2984 | 149.2044 | 0.9 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 92.6524 | 44.8317 | 1066995.0534 | 88.9163 | 88.9163 | 156.7043 | 1 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 95.9891 | 48.1685 | 1146409.6371 | 95.5341 | 95.5341 | 164.2041 | 75 | 70 | 33.4638 | 34 | 69.2
8/21/20XX 7:00:00 PM | 0.79167 | 7 | 76.1 | 71.1 | 94.8268 | 108.7319 | 13.9051 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/21/20XX 8:00:00 PM | 0.83333 | 7 | 75.4 | 74.6 | 92.579 | 106.1458 | 13.5668 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/21/20XX 9:00:00 PM | 0.875 | 7 | 75.3 | 76 | 92.2616 | 105.7806 | 13.519 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/21/20XX 10:00:00 PM | 0.91667 | 7 | 74.6 | 78.2 | 90.0655 | 103.2545 | 13.1889 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/21/20XX 11:00:00 PM | 0.95833 | 7 | 74 | 79 | 88.2187 | 101.1303 | 12.9116 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/21/20XX 12:00:00 AM | 0 | 1 | 73.1 | 81.3 | 98.0145 | 110.5414 | 12.5269 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/22/20XX 1:00:00 AM | 0.041667 | 1 | 73.3 | 81.9 | 98.6997 | 111.3171 | 12.6175 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/22/20XX 2:00:00 AM | 0.083333 | 1 | 72.7 | 82.3 | 96.6564 | 109.004 | 12.3476 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/22/20XX 3:00:00 AM | 0.125 | 1 | 71.7 | 83.7 | 93.3322 | 105.2414 | 11.9091 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/22/20XX 4:00:00 AM | 0.16667 | 1 | 71.6 | 83.8 | 93.0054 | 104.8714 | 11.866 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/22/20XX 5:00:00 AM | 0.20833 | 1 | 71.2 | 84.2 | 91.7077 | 103.4028 | 11.6951 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/22/20XX 6:00:00 AM | 0.25 | 1 | 71.1 | 83.5 | 91.3858 | 103.0385 | 11.6527 | 80 | 71.1 |  | 71.1 | 95.4642 | 0.1 | 73.71 | 18.71 | 707238 | 58.9365 | 58.9365 | 65.9059 | 18.0853 | 430429.1623 | 35.8691 | 35.8691 | 94.8056 | 0.2 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 69.1902 | 21.3695 | 508594.5245 | 42.3829 | 42.3829 | 100.4059 | 0.3 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 72.4744 | 24.6538 | 586759.8868 | 48.8967 | 48.8967 | 106.0062 | 0.4 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 75.7587 | 27.938 | 664925.249 | 55.4104 | 55.4104 | 111.6064 | 0.5 | 72.55 | 17.55 | 663390 | 55.2825 | 55.2825 | 79.0429 | 31.2223 | 743090.6113 | 61.9242 | 61.9242 | 117.2067 | 0.6 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 82.3272 | 34.5066 | 821255.9735 | 68.438 | 68.438 | 122.807 | 0.7 | 71.97 | 16.97 | 641466 | 53.4555 | 53.4555 | 85.6114 | 37.7908 | 899421.3358 | 74.9518 | 74.9518 | 128.4073 | 0.8 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 88.8957 | 41.0751 | 977586.698 | 81.4656 | 81.4656 | 134.0076 | 0.9 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 92.18 | 44.3593 | 1055752.0603 | 87.9793 | 87.9793 | 139.6078 | 1 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 95.4642 | 47.6436 | 1133917.4225 | 94.4931 | 94.4931 | 145.2081 | 70 | 85 | 31.9791 | 32 | 83.5
8/22/20XX 7:00:00 AM | 0.29167 | 1 | 71.6 | 81.6 | 93.0054 | 104.8714 | 11.866 | 80 | 71.6 |  | 71.6 | 94.9039 | 0.1 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 65.8499 | 18.0292 | 429095.645 | 35.758 | 35.758 | 94.852 | 0.2 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 69.0781 | 21.2575 | 505927.49 | 42.1606 | 42.1606 | 100.4986 | 0.3 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 72.3063 | 24.4857 | 582759.3351 | 48.5633 | 48.5633 | 106.1453 | 0.4 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 75.5345 | 27.7139 | 659591.1801 | 54.9659 | 54.9659 | 111.7919 | 0.5 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 78.7628 | 30.9421 | 736423.0251 | 61.3686 | 61.3686 | 117.4386 | 0.6 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 81.991 | 34.1704 | 813254.8701 | 67.7712 | 67.7712 | 123.0852 | 0.7 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 85.2192 | 37.3986 | 890086.7152 | 74.1739 | 74.1739 | 128.7319 | 0.8 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 88.4475 | 40.6268 | 966918.5602 | 80.5765 | 80.5765 | 134.3785 | 0.9 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 91.6757 | 43.8551 | 1043750.4052 | 86.9792 | 86.9792 | 140.0252 | 1 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 94.9039 | 47.0833 | 1120582.2502 | 93.3819 | 93.3819 | 145.6719 | 70 | 80 | 32.0145 | 32 | 81.6
8/22/20XX 8:00:00 AM | 0.33333 | 1 | 72.8 | 77.4 | 84.6221 | 96.9944 | 12.3723 | 70 | 72.8 |  | 72.8 | 93.7776 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.7372 | 17.9166 | 426415.0184 | 35.5346 | 35.5346 | 95.0066 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 68.8528 | 21.0322 | 500566.2368 | 41.7139 | 41.7139 | 100.8079 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 71.9684 | 24.1478 | 574717.4551 | 47.8931 | 47.8931 | 106.6091 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 75.084 | 27.2634 | 648868.6735 | 54.0724 | 54.0724 | 112.4104 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 78.1996 | 30.379 | 723019.8919 | 60.2517 | 60.2517 | 118.2117 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 81.3152 | 33.4946 | 797171.1103 | 66.4309 | 66.4309 | 124.0129 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 84.4308 | 36.6102 | 871322.3287 | 72.6102 | 72.6102 | 129.8142 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 87.5464 | 39.7258 | 945473.5471 | 78.7895 | 78.7895 | 135.6155 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 90.662 | 42.8414 | 1019624.7654 | 84.9687 | 84.9687 | 141.4167 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 93.7776 | 45.957 | 1093775.9838 | 91.148 | 91.148 | 147.218 | 75 | 75 | 32.1337 | 32 | 77.4
8/22/20XX 9:00:00 AM | 0.375 | 1 | 74.1 | 73.8 | 88.5243 | 101.4817 | 12.9575 | 70 | 74.1 |  | 74.1 | 93.4481 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 65.7043 | 17.8836 | 425630.807 | 35.4692 | 35.4692 | 95.3507 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 68.7869 | 20.9663 | 498997.814 | 41.5832 | 41.5832 | 101.4962 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 71.8696 | 24.0489 | 572364.821 | 47.6971 | 47.6971 | 107.6416 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 74.9522 | 27.1316 | 645731.828 | 53.811 | 53.811 | 113.787 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 78.0349 | 30.2142 | 719098.835 | 59.9249 | 59.9249 | 119.9324 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 81.1175 | 33.2969 | 792465.842 | 66.0388 | 66.0388 | 126.0778 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 84.2002 | 36.3795 | 865832.849 | 72.1527 | 72.1527 | 132.2232 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 87.2828 | 39.4622 | 939199.856 | 78.2667 | 78.2667 | 138.3687 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 90.3655 | 42.5448 | 1012566.863 | 84.3806 | 84.3806 | 144.5141 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 93.4481 | 45.6275 | 1085933.87 | 90.4945 | 90.4945 | 150.6595 | 75 | 75 | 32.4019 | 32 | 73.8
8/22/20XX 10:00:00 AM | 0.41667 | 1 | 75.7 | 70 | 93.5368 | 107.2477 | 13.7109 | 70 | 75.7 |  | 75.7 | 93.5368 | 0.1 | 74.17 | 19.17 | 724626 | 60.3855 | 60.3855 | 65.7131 | 17.8925 | 425841.825 | 35.4868 | 35.4868 | 95.8723 | 0.2 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 68.8047 | 20.984 | 499419.85 | 41.6183 | 41.6183 | 102.5393 | 0.3 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 71.8962 | 24.0755 | 572997.8749 | 47.7498 | 47.7498 | 109.2063 | 0.4 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 74.9877 | 27.1671 | 646575.8999 | 53.8813 | 53.8813 | 115.8733 | 0.5 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 78.0792 | 30.2586 | 720153.9249 | 60.0128 | 60.0128 | 122.5403 | 0.6 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 81.1707 | 33.3501 | 793731.9499 | 66.1443 | 66.1443 | 129.2073 | 0.7 | 75.19 | 20.19 | 763182 | 63.5985 | 63.5985 | 84.2622 | 36.4416 | 867309.9749 | 72.2758 | 72.2758 | 135.8743 | 0.8 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 87.3537 | 39.5331 | 940887.9999 | 78.4073 | 78.4073 | 142.5413 | 0.9 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 90.4453 | 42.6246 | 1014466.0248 | 84.5388 | 84.5388 | 149.2083 | 1 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 93.5368 | 45.7161 | 1088044.0498 | 90.6703 | 90.6703 | 155.8753 | 75 | 70 | 32.8092 | 32 | 70
8/22/20XX 11:00:00 AM | 0.45833 | 1 | 77.7 | 65.8 | 85.548 | 100.1379 | 14.59 | 60 | 77.7 |  | 77.7 | 94.0101 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 65.7605 | 17.9399 | 426968.4468 | 35.5807 | 35.5807 | 96.5962 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 68.8993 | 21.0787 | 501673.0936 | 41.8061 | 41.8061 | 103.9871 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 72.0382 | 24.2176 | 576377.7404 | 48.0315 | 48.0315 | 111.378 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 75.177 | 27.3564 | 651082.3872 | 54.2569 | 54.2569 | 118.7689 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 78.3159 | 30.4953 | 725787.034 | 60.4823 | 60.4823 | 126.1598 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 81.4547 | 33.6341 | 800491.6808 | 66.7076 | 66.7076 | 133.5506 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 84.5936 | 36.773 | 875196.3276 | 72.933 | 72.933 | 140.9415 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 87.7324 | 39.9118 | 949900.9744 | 79.1584 | 79.1584 | 148.3324 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 90.8713 | 43.0507 | 1024605.6212 | 85.3838 | 85.3838 | 155.7233 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 94.0101 | 46.1895 | 1099310.268 | 91.6092 | 91.6092 | 163.1142 | 80 | 65 | 33.3753 | 34 | 65.8
8/22/20XX 12:00:00 PM | 0.5 | 1 | 78.6 | 63.4 | 88.1844 | 103.2334 | 15.049 | 60 | 78.6 |  | 78.6 | 93.3011 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 65.6896 | 17.8689 | 425280.8503 | 35.4401 | 35.4401 | 96.7391 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 68.7575 | 20.9369 | 498297.9007 | 41.5248 | 41.5248 | 104.2728 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 71.8255 | 24.0048 | 571314.951 | 47.6096 | 47.6096 | 111.8066 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 74.8934 | 27.0728 | 644332.0013 | 53.6943 | 53.6943 | 119.3403 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 77.9613 | 30.1407 | 717349.0517 | 59.7791 | 59.7791 | 126.8741 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 81.0293 | 33.2087 | 790366.102 | 65.8638 | 65.8638 | 134.4078 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 84.0972 | 36.2766 | 863383.1523 | 71.9486 | 71.9486 | 141.9416 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 87.1652 | 39.3445 | 936400.2027 | 78.0334 | 78.0334 | 149.4754 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 90.2331 | 42.4125 | 1009417.253 | 84.1181 | 84.1181 | 157.0091 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 93.3011 | 45.4804 | 1082434.3033 | 90.2029 | 90.2029 | 164.5429 | 80 | 65 | 33.4855 | 34 | 63.4
8/22/20XX 1:00:00 PM | 0.54167 | 1 | 78.8 | 63.4 | 88.7794 | 103.932 | 15.1526 | 60 | 78.8 |  | 78.8 | 93.9313 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 65.7526 | 17.932 | 426780.7872 | 35.5651 | 35.5651 | 96.9271 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 68.8836 | 21.0629 | 501297.7745 | 41.7748 | 41.7748 | 104.6488 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 72.0145 | 24.1939 | 575814.7617 | 47.9846 | 47.9846 | 112.3706 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 75.1455 | 27.3249 | 650331.749 | 54.1943 | 54.1943 | 120.0923 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 78.2765 | 30.4558 | 724848.7362 | 60.4041 | 60.4041 | 127.8141 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 81.4074 | 33.5868 | 799365.7234 | 66.6138 | 66.6138 | 135.5358 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 84.5384 | 36.7178 | 873882.7107 | 72.8236 | 72.8236 | 143.2576 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 87.6694 | 39.8487 | 948399.6979 | 79.0333 | 79.0333 | 150.9793 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 90.8003 | 42.9797 | 1022916.6852 | 85.2431 | 85.2431 | 158.7011 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 93.9313 | 46.1107 | 1097433.6724 | 91.4528 | 91.4528 | 166.4228 | 80 | 65 | 33.6335 | 34 | 63.4
8/22/20XX 2:00:00 PM | 0.58333 | 1 | 78.4 | 64.5 | 87.5927 | 102.5387 | 14.946 | 60 | 78.4 |  | 78.4 | 94.3184 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 65.7913 | 17.9707 | 427702.1655 | 35.6418 | 35.6418 | 96.8778 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 68.961 | 21.1404 | 503140.5309 | 41.9284 | 41.9284 | 104.5504 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 72.1307 | 24.31 | 578578.8964 | 48.2149 | 48.2149 | 112.2229 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 75.3003 | 27.4797 | 654017.2619 | 54.5014 | 54.5014 | 119.8954 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 78.47 | 30.6494 | 729455.6273 | 60.788 | 60.788 | 127.568 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 81.6397 | 33.8191 | 804893.9928 | 67.0745 | 67.0745 | 135.2405 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 84.8094 | 36.9888 | 880332.3582 | 73.361 | 73.361 | 142.913 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 87.9791 | 40.1584 | 955770.7237 | 79.6476 | 79.6476 | 150.5856 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 91.1487 | 43.3281 | 1031209.0892 | 85.9341 | 85.9341 | 158.2581 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 94.3184 | 46.4978 | 1106647.4546 | 92.2206 | 92.2206 | 165.9306 | 80 | 65 | 33.5958 | 34 | 64.5
8/22/20XX 3:00:00 PM | 0.625 | 1 | 78.4 | 63.4 | 87.5927 | 102.5387 | 14.946 | 60 | 78.4 |  | 78.4 | 92.6744 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 65.6269 | 17.8063 | 423789.3129 | 35.3158 | 35.3158 | 96.5518 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 68.6322 | 20.8115 | 495314.8259 | 41.2762 | 41.2762 | 103.8982 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 71.6375 | 23.8168 | 566840.3388 | 47.2367 | 47.2367 | 111.2447 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 74.6427 | 26.8221 | 638365.8517 | 53.1972 | 53.1972 | 118.5912 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 77.648 | 29.8274 | 709891.3646 | 59.1576 | 59.1576 | 125.9376 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 80.6533 | 32.8326 | 781416.8776 | 65.1181 | 65.1181 | 133.2841 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 83.6585 | 35.8379 | 852942.3905 | 71.0785 | 71.0785 | 140.6305 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 86.6638 | 38.8432 | 924467.9034 | 77.039 | 77.039 | 147.977 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 89.6691 | 41.8485 | 995993.4163 | 82.9995 | 82.9995 | 155.3235 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 92.6744 | 44.8537 | 1067518.9293 | 88.9599 | 88.9599 | 162.6699 | 80 | 65 | 33.3381 | 34 | 63.4
8/22/20XX 4:00:00 PM | 0.66667 | 1 | 78.1 | 62.1 | 86.7115 | 101.504 | 14.7925 | 60 | 78.1 |  | 78.1 | 89.8179 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 65.3413 | 17.5206 | 416990.886 | 34.7492 | 34.7492 | 95.8907 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 68.0609 | 20.2403 | 481717.972 | 40.1432 | 40.1432 | 102.5762 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 70.7805 | 22.9599 | 546445.0579 | 45.5371 | 45.5371 | 109.2616 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 73.5001 | 25.6795 | 611172.1439 | 50.931 | 50.931 | 115.947 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 76.2198 | 28.3991 | 675899.2299 | 56.3249 | 56.3249 | 122.6324 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 78.9394 | 31.1188 | 740626.3159 | 61.7189 | 61.7189 | 129.3179 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 81.659 | 33.8384 | 805353.4019 | 67.1128 | 67.1128 | 136.0033 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 84.3786 | 36.558 | 870080.4878 | 72.5067 | 72.5067 | 142.6887 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 87.0983 | 39.2776 | 934807.5738 | 77.9006 | 77.9006 | 149.3741 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 89.8179 | 41.9973 | 999534.6598 | 83.2946 | 83.2946 | 156.0596 | 80 | 60 | 32.8168 | 32 | 62.1
8/22/20XX 5:00:00 PM | 0.70833 | 1 | 77.4 | 61.1 | 84.6839 | 99.1235 | 14.4396 | 60 | 77.4 |  | 77.4 | 86.2723 | 0.1 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 64.9867 | 17.1661 | 408552.3809 | 34.046 | 34.046 | 94.967 | 0.2 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 67.3518 | 19.5311 | 464840.9617 | 38.7367 | 38.7367 | 100.7287 | 0.3 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 69.7168 | 21.8962 | 521129.5426 | 43.4275 | 43.4275 | 106.4905 | 0.4 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 72.0819 | 24.2613 | 577418.1235 | 48.1182 | 48.1182 | 112.2522 | 0.5 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 74.447 | 26.6263 | 633706.7044 | 52.8089 | 52.8089 | 118.0139 | 0.6 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 76.812 | 28.9914 | 689995.2852 | 57.4996 | 57.4996 | 123.7756 | 0.7 | 76.38 | 21.38 | 808164 | 67.347 | 67.347 | 79.1771 | 31.3565 | 746283.8661 | 62.1903 | 62.1903 | 129.5373 | 0.8 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 81.5422 | 33.7215 | 802572.447 | 66.881 | 66.881 | 135.299 | 0.9 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 83.9072 | 36.0866 | 858861.0278 | 71.5718 | 71.5718 | 141.0608 | 1 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 86.2723 | 38.4517 | 915149.6087 | 76.2625 | 76.2625 | 146.8225 | 75 | 60 | 32.0895 | 32 | 61.1
8/22/20XX 6:00:00 PM | 0.75 | 1 | 76.7 | 61.8 | 82.6964 | 96.79 | 14.0936 | 60 | 76.7 |  | 76.7 | 85.2332 | 0.1 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 64.8828 | 17.0622 | 406079.4027 | 33.84 | 33.84 | 94.5405 | 0.2 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 67.144 | 19.3233 | 459895.0053 | 38.3246 | 38.3246 | 99.8756 | 0.3 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 69.4051 | 21.5845 | 513710.608 | 42.8092 | 42.8092 | 105.2107 | 0.4 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 71.6663 | 23.8456 | 567526.2107 | 47.2939 | 47.2939 | 110.5459 | 0.5 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 73.9274 | 26.1068 | 621341.8134 | 51.7785 | 51.7785 | 115.881 | 0.6 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 76.1886 | 28.368 | 675157.416 | 56.2631 | 56.2631 | 121.2161 | 0.7 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 78.4498 | 30.6291 | 728973.0187 | 60.7478 | 60.7478 | 126.5513 | 0.8 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 80.7109 | 32.8903 | 782788.6214 | 65.2324 | 65.2324 | 131.8864 | 0.9 | 76.43 | 21.43 | 810054 | 67.5045 | 67.5045 | 82.9721 | 35.1514 | 836604.224 | 69.717 | 69.717 | 137.2215 | 1 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 85.2332 | 37.4126 | 890419.8267 | 74.2017 | 74.2017 | 142.5567 | 75 | 60 | 31.7549 | 32 | 61.8
8/22/20XX 7:00:00 PM | 0.79167 | 1 | 75.7 | 64.5 | 79.9253 | 93.5368 | 13.6115 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/22/20XX 8:00:00 PM | 0.83333 | 1 | 74.1 | 67.8 | 75.6554 | 88.5243 | 12.8688 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/22/20XX 9:00:00 PM | 0.875 | 1 | 74 | 66.6 | 75.3952 | 88.2187 | 12.8236 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/22/20XX 10:00:00 PM | 0.91667 | 1 | 73.5 | 68.6 | 74.1052 | 86.7045 | 12.5993 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/22/20XX 11:00:00 PM | 0.95833 | 1 | 71.7 | 71.7 | 81.4366 | 93.3322 | 11.8956 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/22/20XX 12:00:00 AM | 0 | 2 | 70.5 | 73.6 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/23/20XX 1:00:00 AM | 0.041667 | 2 | 69.9 | 74.8 | 76.4479 | 87.5989 | 11.151 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/23/20XX 2:00:00 AM | 0.083333 | 2 | 69.7 | 74.7 | 75.9105 | 86.9813 | 11.0709 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/23/20XX 3:00:00 AM | 0.125 | 2 | 69.5 | 77.2 | 75.3763 | 86.3676 | 10.9913 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/23/20XX 4:00:00 AM | 0.16667 | 2 | 68.9 | 80.4 | 84.5492 | 95.3034 | 10.7542 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/23/20XX 5:00:00 AM | 0.20833 | 2 | 68.6 | 80.7 | 83.6528 | 94.2893 | 10.6366 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/23/20XX 6:00:00 AM | 0.25 | 2 | 69 | 79.2 | 74.0553 | 84.8499 | 10.7946 | 70 | 69 |  | 69 | 83.9863 | 0.1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 64.7581 | 16.9375 | 403111.7641 | 33.5926 | 33.5926 | 91.8676 | 0.2 | 73 | 18 | 680400 | 56.7 | 56.7 | 66.8946 | 19.0739 | 453959.7281 | 37.83 | 37.83 | 94.53 | 0.3 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 69.031 | 21.2104 | 504807.6922 | 42.0673 | 42.0673 | 97.1923 | 0.4 | 72 | 17 | 642600 | 53.55 | 53.55 | 71.1675 | 23.3469 | 555655.6562 | 46.3046 | 46.3046 | 99.8546 | 0.5 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 73.304 | 25.4833 | 606503.6203 | 50.542 | 50.542 | 102.517 | 0.6 | 71 | 16 | 604800 | 50.4 | 50.4 | 75.4404 | 27.6198 | 657351.5843 | 54.7793 | 54.7793 | 105.1793 | 0.7 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 77.5769 | 29.7563 | 708199.5484 | 59.0166 | 59.0166 | 107.8416 | 0.8 | 70 | 15 | 567000 | 47.25 | 47.25 | 79.7134 | 31.8928 | 759047.5125 | 63.254 | 63.254 | 110.504 | 0.9 | 69.5 | 14.5 | 548100 | 45.675 | 45.675 | 81.8499 | 34.0292 | 809895.4765 | 67.4913 | 67.4913 | 113.1663 | 1 | 69 | 14 | 529200 | 44.1 | 44.1 | 83.9863 | 36.1657 | 860743.4406 | 71.7286 | 71.7286 | 115.8286 | 70 | 80 | 29.6706 | 30 | 79.2
8/23/20XX 7:00:00 AM | 0.29167 | 2 | 69.7 | 76.1 | 75.9105 | 86.9813 | 11.0709 | 70 | 69.7 |  | 69.7 | 82.6637 | 0.1 | 73.57 | 18.57 | 701946 | 58.4955 | 58.4955 | 64.6258 | 16.8052 | 399963.9009 | 33.3303 | 33.3303 | 91.8258 | 0.2 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 66.63 | 18.8094 | 447664.0017 | 37.3053 | 37.3053 | 94.4463 | 0.3 | 72.71 | 17.71 | 669438 | 55.7865 | 55.7865 | 68.6343 | 20.8136 | 495364.1026 | 41.2803 | 41.2803 | 97.0668 | 0.4 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 70.6385 | 22.8178 | 543064.2034 | 45.2554 | 45.2554 | 99.6874 | 0.5 | 71.85 | 16.85 | 636930 | 53.0775 | 53.0775 | 72.6427 | 24.822 | 590764.3043 | 49.2304 | 49.2304 | 102.3079 | 0.6 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 74.6469 | 26.8262 | 638464.4051 | 53.2054 | 53.2054 | 104.9284 | 0.7 | 70.99 | 15.99 | 604422 | 50.3685 | 50.3685 | 76.6511 | 28.8304 | 686164.506 | 57.1804 | 57.1804 | 107.5489 | 0.8 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 78.6553 | 30.8346 | 733864.6068 | 61.1554 | 61.1554 | 110.1694 | 0.9 | 70.13 | 15.13 | 571914 | 47.6595 | 47.6595 | 80.6595 | 32.8389 | 781564.7077 | 65.1304 | 65.1304 | 112.7899 | 1 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 82.6637 | 34.8431 | 829264.8085 | 69.1054 | 69.1054 | 115.4104 | 70 | 75 | 29.6358 | 30 | 76.1
8/23/20XX 8:00:00 AM | 0.33333 | 2 | 70.2 | 72.2 | 77.2604 | 88.5325 | 11.2721 | 70 | 70.2 |  | 70.2 | 79.7403 | 0.1 | 73.62 | 18.62 | 703836 | 58.653 | 58.653 | 64.3335 | 16.5129 | 393006.1675 | 32.7505 | 32.7505 | 91.4035 | 0.2 | 73.24 | 18.24 | 689472 | 57.456 | 57.456 | 66.0454 | 18.2247 | 433748.5351 | 36.1457 | 36.1457 | 93.6017 | 0.3 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 67.7572 | 19.9366 | 474490.9026 | 39.5409 | 39.5409 | 95.7999 | 0.4 | 72.48 | 17.48 | 660744 | 55.062 | 55.062 | 69.4691 | 21.6485 | 515233.2701 | 42.9361 | 42.9361 | 97.9981 | 0.5 | 72.1 | 17.1 | 646380 | 53.865 | 53.865 | 71.181 | 23.3603 | 555975.6376 | 46.3313 | 46.3313 | 100.1963 | 0.6 | 71.72 | 16.72 | 632016 | 52.668 | 52.668 | 72.8928 | 25.0722 | 596718.0052 | 49.7265 | 49.7265 | 102.3945 | 0.7 | 71.34 | 16.34 | 617652 | 51.471 | 51.471 | 74.6047 | 26.784 | 637460.3727 | 53.1217 | 53.1217 | 104.5927 | 0.8 | 70.96 | 15.96 | 603288 | 50.274 | 50.274 | 76.3165 | 28.4959 | 678202.7402 | 56.5169 | 56.5169 | 106.7909 | 0.9 | 70.58 | 15.58 | 588924 | 49.077 | 49.077 | 78.0284 | 30.2078 | 718945.1078 | 59.9121 | 59.9121 | 108.9891 | 1 | 70.2 | 15.2 | 574560 | 47.88 | 47.88 | 79.7403 | 31.9196 | 759687.4753 | 63.3073 | 63.3073 | 111.1873 | 70 | 70 | 29.3018 | 30 | 72.2
8/23/20XX 9:00:00 AM | 0.375 | 2 | 71.5 | 67.6 | 69.1333 | 80.8687 | 11.7354 | 60 | 71.5 |  | 71.5 | 78.0522 | 0.1 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 64.1647 | 16.3441 | 388988.5794 | 32.4157 | 32.4157 | 91.4782 | 0.2 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 65.7077 | 17.8871 | 425713.3589 | 35.4761 | 35.4761 | 93.7511 | 0.3 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 67.2508 | 19.4302 | 462438.1383 | 38.5365 | 38.5365 | 96.024 | 0.4 | 73 | 18 | 680400 | 56.7 | 56.7 | 68.7939 | 20.9732 | 499162.9178 | 41.5969 | 41.5969 | 98.2969 | 0.5 | 72.75 | 17.75 | 670950 | 55.9125 | 55.9125 | 70.3369 | 22.5163 | 535887.6972 | 44.6573 | 44.6573 | 100.5698 | 0.6 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 71.88 | 24.0593 | 572612.4767 | 47.7177 | 47.7177 | 102.8427 | 0.7 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 73.423 | 25.6024 | 609337.2561 | 50.7781 | 50.7781 | 105.1156 | 0.8 | 72 | 17 | 642600 | 53.55 | 53.55 | 74.9661 | 27.1455 | 646062.0356 | 53.8385 | 53.8385 | 107.3885 | 0.9 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 76.5092 | 28.6885 | 682786.815 | 56.8989 | 56.8989 | 109.6614 | 1 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 78.0522 | 30.2316 | 719511.5945 | 59.9593 | 59.9593 | 111.9343 | 70 | 70 | 29.3566 | 30 | 67.6
8/23/20XX 10:00:00 AM | 0.41667 | 2 | 74.1 | 60.6 | 75.6554 | 88.5243 | 12.8688 | 60 | 74.1 |  | 74.1 | 76.4276 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 64.0022 | 16.1816 | 385121.9163 | 32.0935 | 32.0935 | 91.975 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 65.3828 | 17.5622 | 417980.0325 | 34.8317 | 34.8317 | 94.7447 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 66.7634 | 18.9428 | 450838.1488 | 37.5698 | 37.5698 | 97.5143 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 68.144 | 20.3234 | 483696.2651 | 40.308 | 40.308 | 100.284 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 69.5246 | 21.704 | 516554.3813 | 43.0462 | 43.0462 | 103.0537 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 70.9052 | 23.0846 | 549412.4976 | 45.7844 | 45.7844 | 105.8234 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 72.2858 | 24.4652 | 582270.6139 | 48.5226 | 48.5226 | 108.5931 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 73.6664 | 25.8457 | 615128.7301 | 51.2607 | 51.2607 | 111.3627 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 75.047 | 27.2263 | 647986.8464 | 53.9989 | 53.9989 | 114.1324 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 76.4276 | 28.6069 | 680844.9627 | 56.7371 | 56.7371 | 116.9021 | 75 | 60 | 29.7394 | 30 | 60.6
8/23/20XX 11:00:00 AM | 0.45833 | 2 | 76.1 | 54.9 | 67.2857 | 81.0242 | 13.7385 | 50 | 76.1 |  | 76.1 | 74.0175 | 0.1 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 63.7612 | 15.9406 | 379386.0263 | 31.6155 | 31.6155 | 92.127 | 0.2 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 64.9008 | 17.0802 | 406508.2525 | 33.8757 | 33.8757 | 95.0487 | 0.3 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 66.0404 | 18.2198 | 433630.4788 | 36.1359 | 36.1359 | 97.9704 | 0.4 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 67.18 | 19.3594 | 460752.7051 | 38.3961 | 38.3961 | 100.8921 | 0.5 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 68.3196 | 20.4989 | 487874.9314 | 40.6562 | 40.6562 | 103.8137 | 0.6 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 69.4592 | 21.6385 | 514997.1576 | 42.9164 | 42.9164 | 106.7354 | 0.7 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 70.5988 | 22.7781 | 542119.3839 | 45.1766 | 45.1766 | 109.6571 | 0.8 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 71.7383 | 23.9177 | 569241.6102 | 47.4368 | 47.4368 | 112.5788 | 0.9 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 72.8779 | 25.0573 | 596363.8365 | 49.697 | 49.697 | 115.5005 | 1 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 74.0175 | 26.1969 | 623486.0627 | 51.9572 | 51.9572 | 118.4222 | 75 | 55 | 29.8518 | 30 | 54.9
8/23/20XX 12:00:00 PM | 0.5 | 2 | 77.6 | 52.3 | 70.7937 | 85.2591 | 14.4654 | 50 | 77.6 |  | 77.6 | 74.1207 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 63.7715 | 15.9509 | 379631.6978 | 31.636 | 31.636 | 92.62 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 64.9215 | 17.1008 | 406999.5956 | 33.9166 | 33.9166 | 96.0346 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 66.0714 | 18.2507 | 434367.4934 | 36.1973 | 36.1973 | 99.4493 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 67.2213 | 19.4006 | 461735.3912 | 38.4779 | 38.4779 | 102.8639 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 68.3712 | 20.5506 | 489103.289 | 40.7586 | 40.7586 | 106.2786 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 69.5211 | 21.7005 | 516471.1868 | 43.0393 | 43.0393 | 109.6933 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 70.671 | 22.8504 | 543839.0846 | 45.3199 | 45.3199 | 113.1079 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 71.8209 | 24.0003 | 571206.9824 | 47.6006 | 47.6006 | 116.5226 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 72.9708 | 25.1502 | 598574.8802 | 49.8812 | 49.8812 | 119.9372 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 74.1207 | 26.3001 | 625942.778 | 52.1619 | 52.1619 | 123.3519 | 80 | 50 | 30.235 | 30 | 52.3
8/23/20XX 1:00:00 PM | 0.54167 | 2 | 78.2 | 49.5 | 57.5932 | 72.2392 | 14.646 | 40 | 78.2 |  | 78.2 | 71.5069 | 0.1 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 63.5102 | 15.6895 | 373410.6453 | 31.1176 | 31.1176 | 92.2906 | 0.2 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 64.3987 | 16.578 | 394557.4905 | 32.8798 | 32.8798 | 95.3758 | 0.3 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 65.2872 | 17.4666 | 415704.3358 | 34.642 | 34.642 | 98.461 | 0.4 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 66.1757 | 18.3551 | 436851.1811 | 36.4043 | 36.4043 | 101.5463 | 0.5 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 67.0642 | 19.2436 | 457998.0263 | 38.1665 | 38.1665 | 104.6315 | 0.6 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 67.9528 | 20.1321 | 479144.8716 | 39.9287 | 39.9287 | 107.7167 | 0.7 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 68.8413 | 21.0207 | 500291.7169 | 41.691 | 41.691 | 110.802 | 0.8 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 69.7298 | 21.9092 | 521438.5621 | 43.4532 | 43.4532 | 113.8872 | 0.9 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 70.6183 | 22.7977 | 542585.4074 | 45.2155 | 45.2155 | 116.9725 | 1 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 71.5069 | 23.6862 | 563732.2527 | 46.9777 | 46.9777 | 120.0577 | 80 | 50 | 29.9723 | 30 | 49.5
8/23/20XX 2:00:00 PM | 0.58333 | 2 | 78.8 | 48.7 | 58.7583 | 73.7091 | 14.9508 | 40 | 78.8 |  | 78.8 | 71.7655 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 63.536 | 15.7154 | 374026.3068 | 31.1689 | 31.1689 | 92.5309 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 64.4504 | 16.6298 | 395788.8137 | 32.9824 | 32.9824 | 95.8564 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 65.3648 | 17.5442 | 417551.3205 | 34.7959 | 34.7959 | 99.1819 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 66.2792 | 18.4586 | 439313.8273 | 36.6095 | 36.6095 | 102.5075 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 67.1936 | 19.373 | 461076.3342 | 38.423 | 38.423 | 105.833 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 68.108 | 20.2873 | 482838.841 | 40.2366 | 40.2366 | 109.1586 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 69.0224 | 21.2017 | 504601.3479 | 42.0501 | 42.0501 | 112.4841 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 69.9368 | 22.1161 | 526363.8547 | 43.8637 | 43.8637 | 115.8097 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 70.8512 | 23.0305 | 548126.3615 | 45.6772 | 45.6772 | 119.1352 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 71.7655 | 23.9449 | 569888.8684 | 47.4907 | 47.4907 | 122.4607 | 80 | 50 | 30.1595 | 30 | 48.7
8/23/20XX 3:00:00 PM | 0.625 | 2 | 78 | 51.5 | 71.7546 | 86.4193 | 14.6647 | 50 | 78 |  | 78 | 73.9543 | 0.1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 63.7549 | 15.9343 | 379235.6347 | 31.603 | 31.603 | 92.713 | 0.2 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 64.8882 | 17.0675 | 406207.4694 | 33.8506 | 33.8506 | 96.2206 | 0.3 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 66.0214 | 18.2008 | 433179.3041 | 36.0983 | 36.0983 | 99.7283 | 0.4 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 67.1547 | 19.3341 | 460151.1388 | 38.3459 | 38.3459 | 103.2359 | 0.5 | 76 | 21 | 793800 | 66.15 | 66.15 | 68.288 | 20.4674 | 487122.9736 | 40.5936 | 40.5936 | 106.7436 | 0.6 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 69.4213 | 21.6006 | 514094.8083 | 42.8412 | 42.8412 | 110.2512 | 0.7 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 70.5545 | 22.7339 | 541066.643 | 45.0889 | 45.0889 | 113.7589 | 0.8 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 71.6878 | 23.8672 | 568038.4777 | 47.3365 | 47.3365 | 117.2665 | 0.9 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 72.8211 | 25.0004 | 595010.3124 | 49.5842 | 49.5842 | 120.7742 | 1 | 78 | 23 | 869400 | 72.45 | 72.45 | 73.9543 | 26.1337 | 621982.1471 | 51.8318 | 51.8318 | 124.2818 | 80 | 50 | 30.3068 | 30 | 51.5
8/23/20XX 4:00:00 PM | 0.66667 | 2 | 77.7 | 53.4 | 71.0329 | 85.548 | 14.515 | 50 | 77.7 |  | 77.7 | 75.968 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 63.9563 | 16.1356 | 384028.2284 | 32.0024 | 32.0024 | 93.0179 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 65.2909 | 17.4703 | 415792.6569 | 34.6494 | 34.6494 | 96.8304 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 66.6256 | 18.8049 | 447557.0853 | 37.2964 | 37.2964 | 100.6429 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 67.9602 | 20.1396 | 479321.5137 | 39.9435 | 39.9435 | 104.4555 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 69.2948 | 21.4742 | 511085.9422 | 42.5905 | 42.5905 | 108.268 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 70.6295 | 22.8088 | 542850.3706 | 45.2375 | 45.2375 | 112.0805 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 71.9641 | 24.1435 | 574614.7991 | 47.8846 | 47.8846 | 115.8931 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 73.2988 | 25.4781 | 606379.2275 | 50.5316 | 50.5316 | 119.7056 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 74.6334 | 26.8128 | 638143.6559 | 53.1786 | 53.1786 | 123.5181 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 75.968 | 28.1474 | 669908.0844 | 55.8257 | 55.8257 | 127.3307 | 80 | 55 | 30.5489 | 30 | 53.4
8/23/20XX 5:00:00 PM | 0.70833 | 2 | 76.5 | 55.8 | 68.2065 | 82.1358 | 13.9292 | 50 | 76.5 |  | 76.5 | 76.2855 | 0.1 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 63.988 | 16.1674 | 384783.7749 | 32.0653 | 32.0653 | 92.7028 | 0.2 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 65.3544 | 17.5338 | 417303.7498 | 34.7753 | 34.7753 | 96.2003 | 0.3 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 66.7208 | 18.9002 | 449823.7247 | 37.4853 | 37.4853 | 99.6978 | 0.4 | 75 | 20 | 756000 | 63 | 63 | 68.0872 | 20.2665 | 482343.6996 | 40.1953 | 40.1953 | 103.1953 | 0.5 | 75.25 | 20.25 | 765450 | 63.7875 | 63.7875 | 69.4536 | 21.6329 | 514863.6745 | 42.9053 | 42.9053 | 106.6928 | 0.6 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 70.8199 | 22.9993 | 547383.6494 | 45.6153 | 45.6153 | 110.1903 | 0.7 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 72.1863 | 24.3657 | 579903.6243 | 48.3253 | 48.3253 | 113.6878 | 0.8 | 76 | 21 | 793800 | 66.15 | 66.15 | 73.5527 | 25.7321 | 612423.5992 | 51.0353 | 51.0353 | 117.1853 | 0.9 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 74.9191 | 27.0985 | 644943.5741 | 53.7453 | 53.7453 | 120.6828 | 1 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 76.2855 | 28.4649 | 677463.549 | 56.4553 | 56.4553 | 124.1803 | 75 | 55 | 30.3048 | 30 | 55.8
8/23/20XX 6:00:00 PM | 0.75 | 2 | 75.5 | 57.1 | 65.924 | 79.3806 | 13.4566 | 50 | 75.5 |  | 75.5 | 75.4782 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 63.9073 | 16.0867 | 382862.4455 | 31.9052 | 31.9052 | 92.2277 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 65.1929 | 17.3723 | 413461.0911 | 34.4551 | 34.4551 | 95.2501 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 66.4786 | 18.658 | 444059.7366 | 37.005 | 37.005 | 98.2725 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 67.7643 | 19.9436 | 474658.3821 | 39.5549 | 39.5549 | 101.2949 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 69.0499 | 21.2293 | 505257.0277 | 42.1048 | 42.1048 | 104.3173 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 70.3356 | 22.5149 | 535855.6732 | 44.6546 | 44.6546 | 107.3396 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 71.6212 | 23.8006 | 566454.3188 | 47.2045 | 47.2045 | 110.362 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 72.9069 | 25.0863 | 597052.9643 | 49.7544 | 49.7544 | 113.3844 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 74.1925 | 26.3719 | 627651.6098 | 52.3043 | 52.3043 | 116.4068 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 75.4782 | 27.6576 | 658250.2554 | 54.8542 | 54.8542 | 119.4292 | 75 | 55 | 29.9336 | 30 | 57.1
8/23/20XX 7:00:00 PM | 0.79167 | 2 | 74 | 58.7 | 62.6216 | 75.3952 | 12.7735 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/23/20XX 8:00:00 PM | 0.83333 | 2 | 73.1 | 61.9 | 73.0869 | 85.5092 | 12.4223 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/23/20XX 9:00:00 PM | 0.875 | 2 | 73.1 | 61.6 | 73.0869 | 85.5092 | 12.4223 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/23/20XX 10:00:00 PM | 0.91667 | 2 | 72.5 | 62.3 | 71.5821 | 83.7428 | 12.1608 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/23/20XX 11:00:00 PM | 0.95833 | 2 | 71.7 | 64.3 | 69.6172 | 81.4366 | 11.8194 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/23/20XX 12:00:00 AM | 0 | 3 | 71 | 64.6 | 67.9365 | 79.4639 | 11.5275 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/24/20XX 1:00:00 AM | 0.041667 | 3 | 70.2 | 67 | 66.0589 | 77.2604 | 11.2015 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/24/20XX 2:00:00 AM | 0.083333 | 3 | 69.7 | 66.8 | 64.9086 | 75.9105 | 11.0018 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/24/20XX 3:00:00 AM | 0.125 | 3 | 69.1 | 69.5 | 63.5515 | 74.3178 | 10.7663 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/24/20XX 4:00:00 AM | 0.16667 | 3 | 68 | 72.1 | 71.4742 | 81.8851 | 10.4109 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/24/20XX 5:00:00 AM | 0.20833 | 3 | 67.6 | 73.8 | 70.4642 | 80.7252 | 10.261 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/24/20XX 6:00:00 AM | 0.25 | 3 | 67.3 | 74.3 | 69.7151 | 79.8649 | 10.1498 | 70 | 67.3 |  | 67.3 | 74.0795 | 0.1 | 73.33 | 18.33 | 692874 | 57.7395 | 57.7395 | 63.7674 | 15.9468 | 379533.5503 | 31.6278 | 31.6278 | 89.3673 | 0.2 | 72.66 | 17.66 | 667548 | 55.629 | 55.629 | 64.9132 | 17.0926 | 406803.3006 | 33.9003 | 33.9003 | 89.5293 | 0.3 | 71.99 | 16.99 | 642222 | 53.5185 | 53.5185 | 66.059 | 18.2384 | 434073.0509 | 36.1728 | 36.1728 | 89.6913 | 0.4 | 71.32 | 16.32 | 616896 | 51.408 | 51.408 | 67.2048 | 19.3842 | 461342.8012 | 38.4452 | 38.4452 | 89.8532 | 0.5 | 70.65 | 15.65 | 591570 | 49.2975 | 49.2975 | 68.3506 | 20.5299 | 488612.5515 | 40.7177 | 40.7177 | 90.0152 | 0.6 | 69.98 | 14.98 | 566244 | 47.187 | 47.187 | 69.4964 | 21.6757 | 515882.3018 | 42.9902 | 42.9902 | 90.1772 | 0.7 | 69.31 | 14.31 | 540918 | 45.0765 | 45.0765 | 70.6421 | 22.8215 | 543152.0521 | 45.2627 | 45.2627 | 90.3392 | 0.8 | 68.64 | 13.64 | 515592 | 42.966 | 42.966 | 71.7879 | 23.9673 | 570421.8024 | 47.5352 | 47.5352 | 90.5012 | 0.9 | 67.97 | 12.97 | 490266 | 40.8555 | 40.8555 | 72.9337 | 25.1131 | 597691.5527 | 49.8076 | 49.8076 | 90.6631 | 1 | 67.3 | 12.3 | 464940 | 38.745 | 38.745 | 74.0795 | 26.2589 | 624961.303 | 52.0801 | 52.0801 | 90.8251 | 65 | 75 | 27.7081 | 28 | 74.3
8/24/20XX 7:00:00 AM | 0.29167 | 3 | 68.6 | 71.6 | 73.0131 | 83.6528 | 10.6396 | 70 | 68.6 |  | 68.6 | 74.7155 | 0.1 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 63.831 | 16.0104 | 381047.1336 | 31.7539 | 31.7539 | 89.9029 | 0.2 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 65.0404 | 17.2198 | 409830.4672 | 34.1525 | 34.1525 | 90.6005 | 0.3 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 66.2498 | 18.4292 | 438613.8009 | 36.5512 | 36.5512 | 91.2982 | 0.4 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 67.4592 | 19.6385 | 467397.1345 | 38.9498 | 38.9498 | 91.9958 | 0.5 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 68.6686 | 20.8479 | 496180.4681 | 41.3484 | 41.3484 | 92.6934 | 0.6 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 69.8779 | 22.0573 | 524963.8017 | 43.747 | 43.747 | 93.391 | 0.7 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 71.0873 | 23.2667 | 553747.1353 | 46.1456 | 46.1456 | 94.0886 | 0.8 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 72.2967 | 24.4761 | 582530.4689 | 48.5442 | 48.5442 | 94.7862 | 0.9 | 69.14 | 14.14 | 534492 | 44.541 | 44.541 | 73.5061 | 25.6855 | 611313.8026 | 50.9428 | 50.9428 | 95.4838 | 1 | 68.6 | 13.6 | 514080 | 42.84 | 42.84 | 74.7155 | 26.8948 | 640097.1362 | 53.3414 | 53.3414 | 96.1814 | 70 | 70 | 28.1255 | 28 | 71.6
8/24/20XX 8:00:00 AM | 0.33333 | 3 | 70.6 | 67 | 66.992 | 78.3554 | 11.3635 | 60 | 70.6 |  | 70.6 | 74.9464 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 63.8541 | 16.0335 | 381596.7132 | 31.7997 | 31.7997 | 90.5787 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 65.0866 | 17.266 | 410929.6264 | 34.2441 | 34.2441 | 91.9521 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 66.3191 | 18.4984 | 440262.5396 | 36.6885 | 36.6885 | 93.3255 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 67.5515 | 19.7309 | 469595.4528 | 39.133 | 39.133 | 94.699 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 68.784 | 20.9634 | 498928.366 | 41.5774 | 41.5774 | 96.0724 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 70.0165 | 22.1959 | 528261.2792 | 44.0218 | 44.0218 | 97.4458 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 71.249 | 23.4283 | 557594.1924 | 46.4662 | 46.4662 | 98.8192 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 72.4814 | 24.6608 | 586927.1056 | 48.9106 | 48.9106 | 100.1926 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 73.7139 | 25.8933 | 616260.0188 | 51.355 | 51.355 | 101.566 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 74.9464 | 27.1258 | 645592.932 | 53.7994 | 53.7994 | 102.9394 | 70 | 65 | 28.651 | 28 | 67
8/24/20XX 9:00:00 AM | 0.375 | 3 | 72.8 | 62.8 | 72.3311 | 84.6221 | 12.291 | 60 | 72.8 |  | 72.8 | 75.7726 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 63.9367 | 16.1161 | 383563.0681 | 31.9636 | 31.9636 | 91.4356 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 65.2518 | 17.4312 | 414862.3362 | 34.5719 | 34.5719 | 93.6659 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 66.5669 | 18.7463 | 446161.6043 | 37.1801 | 37.1801 | 95.8961 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 67.882 | 20.0614 | 477460.8724 | 39.7884 | 39.7884 | 98.1264 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 69.1971 | 21.3765 | 508760.1405 | 42.3967 | 42.3967 | 100.3567 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 70.5122 | 22.6916 | 540059.4086 | 45.005 | 45.005 | 102.587 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 71.8273 | 24.0067 | 571358.6768 | 47.6132 | 47.6132 | 104.8172 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 73.1424 | 25.3218 | 602657.9449 | 50.2215 | 50.2215 | 107.0475 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 74.4575 | 26.6369 | 633957.213 | 52.8298 | 52.8298 | 109.2778 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 75.7726 | 27.952 | 665256.4811 | 55.438 | 55.438 | 111.508 | 75 | 65 | 29.3187 | 30 | 62.8
8/24/20XX 10:00:00 AM | 0.41667 | 3 | 75.4 | 55.3 | 65.6994 | 79.1095 | 13.4101 | 50 | 75.4 |  | 75.4 | 72.8067 | 0.1 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 63.6401 | 15.8195 | 376504.2945 | 31.3754 | 31.3754 | 91.6664 | 0.2 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 64.6586 | 16.838 | 400744.7889 | 33.3954 | 33.3954 | 94.1274 | 0.3 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 65.6772 | 17.8565 | 424985.2834 | 35.4154 | 35.4154 | 96.5884 | 0.4 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 66.6957 | 18.875 | 449225.7778 | 37.4355 | 37.4355 | 99.0495 | 0.5 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 67.7142 | 19.8935 | 473466.2723 | 39.4555 | 39.4555 | 101.5105 | 0.6 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 68.7327 | 20.912 | 497706.7668 | 41.4756 | 41.4756 | 103.9716 | 0.7 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 69.7512 | 21.9306 | 521947.2612 | 43.4956 | 43.4956 | 106.4326 | 0.8 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 70.7697 | 22.9491 | 546187.7557 | 45.5156 | 45.5156 | 108.8936 | 0.9 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 71.7882 | 23.9676 | 570428.2501 | 47.5357 | 47.5357 | 111.3547 | 1 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 72.8067 | 24.9861 | 594668.7446 | 49.5557 | 49.5557 | 113.8157 | 75 | 55 | 29.491 | 30 | 55.3
8/24/20XX 11:00:00 AM | 0.45833 | 3 | 77.7 | 52.3 | 71.0329 | 85.548 | 14.515 | 50 | 77.7 |  | 77.7 | 74.3714 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 63.7966 | 15.976 | 380228.1905 | 31.6857 | 31.6857 | 92.7012 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 64.9716 | 17.1509 | 408192.5809 | 34.016 | 34.016 | 96.197 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 66.1466 | 18.3259 | 436156.9714 | 36.3464 | 36.3464 | 99.6929 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 67.3215 | 19.5009 | 464121.3619 | 38.6768 | 38.6768 | 103.1888 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 68.4965 | 20.6759 | 492085.7523 | 41.0071 | 41.0071 | 106.6846 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 69.6715 | 21.8508 | 520050.1428 | 43.3375 | 43.3375 | 110.1805 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 70.8465 | 23.0258 | 548014.5333 | 45.6679 | 45.6679 | 113.6764 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 72.0214 | 24.2008 | 575978.9238 | 47.9982 | 47.9982 | 117.1722 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 73.1964 | 25.3758 | 603943.3142 | 50.3286 | 50.3286 | 120.6681 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 74.3714 | 26.5507 | 631907.7047 | 52.659 | 52.659 | 124.164 | 80 | 50 | 30.2987 | 30 | 52.3
8/24/20XX 12:00:00 PM | 0.5 | 3 | 78.9 | 51 | 73.9565 | 89.0782 | 15.1216 | 50 | 78.9 |  | 78.9 | 75.4687 | 0.1 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 63.9063 | 16.0857 | 382839.844 | 31.9033 | 31.9033 | 93.2968 | 0.2 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 65.191 | 17.3704 | 413415.888 | 34.4513 | 34.4513 | 97.3883 | 0.3 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 66.4758 | 18.6551 | 443991.932 | 36.9993 | 36.9993 | 101.4798 | 0.4 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 67.7605 | 19.9398 | 474567.976 | 39.5473 | 39.5473 | 105.5713 | 0.5 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 69.0452 | 21.2245 | 505144.0201 | 42.0953 | 42.0953 | 109.6628 | 0.6 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 70.3299 | 22.5092 | 535720.0641 | 44.6433 | 44.6433 | 113.7543 | 0.7 | 77.43 | 22.43 | 847854 | 70.6545 | 70.6545 | 71.6146 | 23.794 | 566296.1081 | 47.1913 | 47.1913 | 117.8458 | 0.8 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 72.8993 | 25.0787 | 596872.1521 | 49.7393 | 49.7393 | 121.9373 | 0.9 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 74.184 | 26.3634 | 627448.1961 | 52.2873 | 52.2873 | 126.0288 | 1 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 75.4687 | 27.6481 | 658024.2401 | 54.8354 | 54.8354 | 130.1204 | 80 | 50 | 30.7644 | 30 | 51
8/24/20XX 1:00:00 PM | 0.54167 | 3 | 80.3 | 48 | 61.7568 | 77.4931 | 15.7363 | 40 | 80.3 |  | 80.3 | 74.3458 | 0.1 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 63.7941 | 15.9734 | 380167.3818 | 31.6806 | 31.6806 | 93.5151 | 0.2 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 64.9665 | 17.1458 | 408070.9637 | 34.0059 | 34.0059 | 97.8249 | 0.3 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 66.1389 | 18.3183 | 435974.5455 | 36.3312 | 36.3312 | 102.1347 | 0.4 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 67.3113 | 19.4907 | 463878.1274 | 38.6565 | 38.6565 | 106.4445 | 0.5 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 68.4837 | 20.6631 | 491781.7092 | 40.9818 | 40.9818 | 110.7543 | 0.6 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 69.6561 | 21.8355 | 519685.2911 | 43.3071 | 43.3071 | 115.0641 | 0.7 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 70.8286 | 23.0079 | 547588.8729 | 45.6324 | 45.6324 | 119.3739 | 0.8 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 72.001 | 24.1804 | 575492.4548 | 47.9577 | 47.9577 | 123.6837 | 0.9 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 73.1734 | 25.3528 | 603396.0366 | 50.283 | 50.283 | 127.9935 | 1 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 74.3458 | 26.5252 | 631299.6185 | 52.6083 | 52.6083 | 132.3033 | 80 | 50 | 30.931 | 30 | 48
8/24/20XX 2:00:00 PM | 0.58333 | 3 | 80.4 | 46.5 | 61.9611 | 77.751 | 15.7899 | 40 | 80.4 |  | 80.4 | 72.2245 | 0.1 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 63.5819 | 15.7613 | 375118.6236 | 31.2599 | 31.2599 | 93.1259 | 0.2 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 64.5422 | 16.7216 | 397973.4471 | 33.1645 | 33.1645 | 97.0465 | 0.3 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 65.5025 | 17.6819 | 420828.2707 | 35.069 | 35.069 | 100.967 | 0.4 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 66.4628 | 18.6421 | 443683.0942 | 36.9736 | 36.9736 | 104.8876 | 0.5 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 67.4231 | 19.6024 | 466537.9178 | 38.8782 | 38.8782 | 108.8082 | 0.6 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 68.3834 | 20.5627 | 489392.7413 | 40.7827 | 40.7827 | 112.7287 | 0.7 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 69.3436 | 21.523 | 512247.5649 | 42.6873 | 42.6873 | 116.6493 | 0.8 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 70.3039 | 22.4833 | 535102.3884 | 44.5919 | 44.5919 | 120.5699 | 0.9 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 71.2642 | 23.4436 | 557957.212 | 46.4964 | 46.4964 | 124.4904 | 1 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 72.2245 | 24.4039 | 580812.0356 | 48.401 | 48.401 | 128.411 | 80 | 45 | 30.6228 | 30 | 46.5
8/24/20XX 3:00:00 PM | 0.625 | 3 | 79.6 | 47.5 | 60.3422 | 75.7077 | 15.3655 | 40 | 79.6 |  | 79.6 | 71.8663 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 63.5461 | 15.7255 | 374266.1992 | 31.1888 | 31.1888 | 92.8028 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 64.4706 | 16.6499 | 396268.5984 | 33.0224 | 33.0224 | 96.4004 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 65.395 | 17.5744 | 418270.9975 | 34.8559 | 34.8559 | 99.9979 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 66.3195 | 18.4989 | 440273.3967 | 36.6894 | 36.6894 | 103.5954 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 67.244 | 19.4234 | 462275.7959 | 38.523 | 38.523 | 107.193 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 68.1685 | 20.3478 | 484278.1951 | 40.3565 | 40.3565 | 110.7905 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 69.0929 | 21.2723 | 506280.5943 | 42.19 | 42.19 | 114.388 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 70.0174 | 22.1968 | 528282.9934 | 44.0236 | 44.0236 | 117.9856 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 70.9419 | 23.1212 | 550285.3926 | 45.8571 | 45.8571 | 121.5831 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 71.8663 | 24.0457 | 572287.7918 | 47.6906 | 47.6906 | 125.1806 | 80 | 45 | 30.371 | 30 | 47.5
8/24/20XX 4:00:00 PM | 0.66667 | 3 | 79 | 48.7 | 59.151 | 74.2046 | 15.0536 | 40 | 79 |  | 79 | 72.2477 | 0.1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 63.5842 | 15.7636 | 375173.7699 | 31.2645 | 31.2645 | 92.6895 | 0.2 | 75 | 20 | 756000 | 63 | 63 | 64.5468 | 16.7262 | 398083.7398 | 33.1736 | 33.1736 | 96.1736 | 0.3 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 65.5094 | 17.6888 | 420993.7097 | 35.0828 | 35.0828 | 99.6578 | 0.4 | 76 | 21 | 793800 | 66.15 | 66.15 | 66.472 | 18.6514 | 443903.6796 | 36.992 | 36.992 | 103.142 | 0.5 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 67.4347 | 19.614 | 466813.6495 | 38.9011 | 38.9011 | 106.6261 | 0.6 | 77 | 22 | 831600 | 69.3 | 69.3 | 68.3973 | 20.5766 | 489723.6194 | 40.8103 | 40.8103 | 110.1103 | 0.7 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 69.3599 | 21.5392 | 512633.5893 | 42.7195 | 42.7195 | 113.5945 | 0.8 | 78 | 23 | 869400 | 72.45 | 72.45 | 70.3225 | 22.5018 | 535543.5592 | 44.6286 | 44.6286 | 117.0786 | 0.9 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 71.2851 | 23.4644 | 558453.5291 | 46.5378 | 46.5378 | 120.5628 | 1 | 79 | 24 | 907200 | 75.6 | 75.6 | 72.2477 | 24.427 | 581363.499 | 48.447 | 48.447 | 124.047 | 80 | 50 | 30.284 | 30 | 48.7
8/24/20XX 5:00:00 PM | 0.70833 | 3 | 77.6 | 53.1 | 70.7937 | 85.2591 | 14.4654 | 50 | 77.6 |  | 77.6 | 75.278 | 0.1 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 63.8873 | 16.0666 | 382385.9172 | 31.8655 | 31.8655 | 92.8495 | 0.2 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 65.1529 | 17.3323 | 412508.0343 | 34.3757 | 34.3757 | 96.4937 | 0.3 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 66.4185 | 18.5979 | 442630.1515 | 36.8858 | 36.8858 | 100.1378 | 0.4 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 67.6842 | 19.8635 | 472752.2686 | 39.396 | 39.396 | 103.782 | 0.5 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 68.9498 | 21.1292 | 502874.3858 | 41.9062 | 41.9062 | 107.4262 | 0.6 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 70.2154 | 22.3948 | 532996.503 | 44.4164 | 44.4164 | 111.0704 | 0.7 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 71.4811 | 23.6604 | 563118.6201 | 46.9266 | 46.9266 | 114.7146 | 0.8 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 72.7467 | 24.9261 | 593240.7373 | 49.4367 | 49.4367 | 118.3587 | 0.9 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 74.0123 | 26.1917 | 623362.8544 | 51.9469 | 51.9469 | 122.0029 | 1 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 75.278 | 27.4574 | 653484.9716 | 54.4571 | 54.4571 | 125.6471 | 80 | 55 | 30.4163 | 30 | 53.1
8/24/20XX 6:00:00 PM | 0.75 | 3 | 75.9 | 55.9 | 66.8292 | 80.4731 | 13.644 | 50 | 75.9 |  | 75.9 | 74.8791 | 0.1 | 74.19 | 19.19 | 725382 | 60.4485 | 60.4485 | 63.8474 | 16.0267 | 381436.6055 | 31.7864 | 31.7864 | 92.2349 | 0.2 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 65.0731 | 17.2525 | 410609.4109 | 34.2175 | 34.2175 | 95.2645 | 0.3 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 66.2989 | 18.4782 | 439782.2164 | 36.6485 | 36.6485 | 98.294 | 0.4 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 67.5246 | 19.704 | 468955.0218 | 39.0796 | 39.0796 | 101.3236 | 0.5 | 74.95 | 19.95 | 754110 | 62.8425 | 62.8425 | 68.7504 | 20.9297 | 498127.8273 | 41.5107 | 41.5107 | 104.3532 | 0.6 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 69.9761 | 22.1555 | 527300.6328 | 43.9417 | 43.9417 | 107.3827 | 0.7 | 75.33 | 20.33 | 768474 | 64.0395 | 64.0395 | 71.2019 | 23.3812 | 556473.4382 | 46.3728 | 46.3728 | 110.4123 | 0.8 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 72.4276 | 24.607 | 585646.2437 | 48.8039 | 48.8039 | 113.4419 | 0.9 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 73.6534 | 25.8327 | 614819.0491 | 51.2349 | 51.2349 | 116.4714 | 1 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 74.8791 | 27.0585 | 643991.8546 | 53.666 | 53.666 | 119.501 | 75 | 55 | 29.9377 | 30 | 55.9
8/24/20XX 7:00:00 PM | 0.79167 | 3 | 74.5 | 58.3 | 63.7064 | 76.7042 | 12.9978 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/24/20XX 8:00:00 PM | 0.83333 | 3 | 73.6 | 60.3 | 74.3617 | 87.0056 | 12.6439 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/24/20XX 9:00:00 PM | 0.875 | 3 | 73.2 | 61.4 | 73.3404 | 85.8067 | 12.4664 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/24/20XX 10:00:00 PM | 0.91667 | 3 | 72.5 | 63.7 | 71.5821 | 83.7428 | 12.1608 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/24/20XX 11:00:00 PM | 0.95833 | 3 | 71.5 | 66.3 | 69.1333 | 80.8687 | 11.7354 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/24/20XX 12:00:00 AM | 0 | 4 | 71.2 | 69.4 | 68.413 | 80.0233 | 11.6102 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/25/20XX 1:00:00 AM | 0.041667 | 4 | 70.5 | 71.1 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/25/20XX 2:00:00 AM | 0.083333 | 4 | 70.1 | 73.7 | 76.9888 | 88.2203 | 11.2316 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/25/20XX 3:00:00 AM | 0.125 | 4 | 69.8 | 75.1 | 76.1788 | 87.2896 | 11.1108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/25/20XX 4:00:00 AM | 0.16667 | 4 | 69.1 | 77 | 74.3178 | 85.1515 | 10.8337 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/25/20XX 5:00:00 AM | 0.20833 | 4 | 68.7 | 78.9 | 73.2724 | 83.9506 | 10.6782 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/25/20XX 6:00:00 AM | 0.25 | 4 | 69.1 | 78.4 | 74.3178 | 85.1515 | 10.8337 | 70 | 69.1 |  | 69.1 | 83.4181 | 0.1 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 64.7013 | 16.8807 | 401759.4917 | 33.48 | 33.48 | 91.7865 | 0.2 | 73.02 | 18.02 | 681156 | 56.763 | 56.763 | 66.7809 | 18.9603 | 451255.1833 | 37.6046 | 37.6046 | 94.3676 | 0.3 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 68.8606 | 21.04 | 500750.875 | 41.7292 | 41.7292 | 96.9487 | 0.4 | 72.04 | 17.04 | 644112 | 53.676 | 53.676 | 70.9402 | 23.1196 | 550246.5667 | 45.8539 | 45.8539 | 99.5299 | 0.5 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 73.0199 | 25.1993 | 599742.2584 | 49.9785 | 49.9785 | 102.111 | 0.6 | 71.06 | 16.06 | 607068 | 50.589 | 50.589 | 75.0995 | 27.2789 | 649237.95 | 54.1032 | 54.1032 | 104.6922 | 0.7 | 70.57 | 15.57 | 588546 | 49.0455 | 49.0455 | 77.1792 | 29.3586 | 698733.6417 | 58.2278 | 58.2278 | 107.2733 | 0.8 | 70.08 | 15.08 | 570024 | 47.502 | 47.502 | 79.2588 | 31.4382 | 748229.3334 | 62.3524 | 62.3524 | 109.8544 | 0.9 | 69.59 | 14.59 | 551502 | 45.9585 | 45.9585 | 81.3385 | 33.5179 | 797725.0251 | 66.4771 | 66.4771 | 112.4356 | 1 | 69.1 | 14.1 | 532980 | 44.415 | 44.415 | 83.4181 | 35.5975 | 847220.7167 | 70.6017 | 70.6017 | 115.0167 | 70 | 80 | 29.6064 | 30 | 78.4
8/25/20XX 7:00:00 AM | 0.29167 | 4 | 70.1 | 77.1 | 76.9888 | 88.2203 | 11.2316 | 70 | 70.1 |  | 70.1 | 84.9632 | 0.1 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 64.8558 | 17.0352 | 405436.6804 | 33.7864 | 33.7864 | 92.4079 | 0.2 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 67.0899 | 19.2693 | 458609.5608 | 38.2175 | 38.2175 | 95.6105 | 0.3 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 69.3241 | 21.5035 | 511782.4413 | 42.6485 | 42.6485 | 98.813 | 0.4 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 71.5583 | 23.7376 | 564955.3217 | 47.0796 | 47.0796 | 102.0156 | 0.5 | 72.05 | 17.05 | 644490 | 53.7075 | 53.7075 | 73.7924 | 25.9718 | 618128.2021 | 51.5107 | 51.5107 | 105.2182 | 0.6 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 76.0266 | 28.2059 | 671301.0825 | 55.9418 | 55.9418 | 108.4208 | 0.7 | 71.27 | 16.27 | 615006 | 51.2505 | 51.2505 | 78.2607 | 30.4401 | 724473.963 | 60.3728 | 60.3728 | 111.6233 | 0.8 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 80.4949 | 32.6742 | 777646.8434 | 64.8039 | 64.8039 | 114.8259 | 0.9 | 70.49 | 15.49 | 585522 | 48.7935 | 48.7935 | 82.729 | 34.9084 | 830819.7238 | 69.235 | 69.235 | 118.0285 | 1 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 84.9632 | 37.1425 | 883992.6042 | 73.6661 | 73.6661 | 121.2311 | 70 | 75 | 30.093 | 30 | 77.1
8/25/20XX 8:00:00 AM | 0.33333 | 4 | 72.2 | 72.9 | 82.8715 | 94.9817 | 12.1103 | 70 | 72.2 |  | 72.2 | 86.3835 | 0.1 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 64.9978 | 17.1772 | 408816.9357 | 34.0681 | 34.0681 | 93.3511 | 0.2 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 67.374 | 19.5534 | 465370.0714 | 38.7808 | 38.7808 | 97.4968 | 0.3 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 69.7502 | 21.9295 | 521923.2071 | 43.4936 | 43.4936 | 101.6426 | 0.4 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 72.1264 | 24.3057 | 578476.3428 | 48.2064 | 48.2064 | 105.7884 | 0.5 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 74.5025 | 26.6819 | 635029.4785 | 52.9191 | 52.9191 | 109.9341 | 0.6 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 76.8787 | 29.0581 | 691582.6143 | 57.6319 | 57.6319 | 114.0799 | 0.7 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 79.2549 | 31.4343 | 748135.75 | 62.3446 | 62.3446 | 118.2256 | 0.8 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 81.6311 | 33.8105 | 804688.8857 | 67.0574 | 67.0574 | 122.3714 | 0.9 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 84.0073 | 36.1866 | 861242.0214 | 71.7702 | 71.7702 | 126.5172 | 1 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 86.3835 | 38.5628 | 917795.1571 | 76.4829 | 76.4829 | 130.6629 | 70 | 75 | 30.8303 | 30 | 72.9
8/25/20XX 9:00:00 AM | 0.375 | 4 | 74.1 | 69.4 | 75.6554 | 88.5243 | 12.8688 | 60 | 74.1 |  | 74.1 | 87.7521 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 65.1347 | 17.3141 | 412074.3973 | 34.3395 | 34.3395 | 94.221 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 67.6477 | 19.8271 | 471884.9946 | 39.3237 | 39.3237 | 99.2367 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 70.1608 | 22.3402 | 531695.5919 | 44.308 | 44.308 | 104.2525 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 72.6738 | 24.8532 | 591506.1891 | 49.2922 | 49.2922 | 109.2682 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 75.1869 | 27.3663 | 651316.7864 | 54.2764 | 54.2764 | 114.2839 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 77.6999 | 29.8793 | 711127.3837 | 59.2606 | 59.2606 | 119.2996 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 80.213 | 32.3924 | 770937.981 | 64.2448 | 64.2448 | 124.3153 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 82.726 | 34.9054 | 830748.5783 | 69.229 | 69.229 | 129.331 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 85.2391 | 37.4185 | 890559.1756 | 74.2133 | 74.2133 | 134.3468 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 87.7521 | 39.9315 | 950369.7728 | 79.1975 | 79.1975 | 139.3625 | 75 | 70 | 31.5109 | 32 | 69.4
8/25/20XX 10:00:00 AM | 0.41667 | 4 | 76.4 | 62.4 | 81.8567 | 95.8042 | 13.9475 | 60 | 76.4 |  | 76.4 | 85.2041 | 0.1 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 64.8799 | 17.0592 | 406009.9967 | 33.8342 | 33.8342 | 94.4402 | 0.2 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 67.1381 | 19.3175 | 459756.1934 | 38.313 | 38.313 | 99.675 | 0.3 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 69.3964 | 21.5757 | 513502.3902 | 42.7919 | 42.7919 | 104.9099 | 0.4 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 71.6546 | 23.834 | 567248.5869 | 47.2707 | 47.2707 | 110.1447 | 0.5 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 73.9129 | 26.0922 | 620994.7836 | 51.7496 | 51.7496 | 115.3796 | 0.6 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 76.1711 | 28.3505 | 674740.9803 | 56.2284 | 56.2284 | 120.6144 | 0.7 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 78.4293 | 30.6087 | 728487.177 | 60.7073 | 60.7073 | 125.8493 | 0.8 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 80.6876 | 32.8669 | 782233.3738 | 65.1861 | 65.1861 | 131.0841 | 0.9 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 82.9458 | 35.1252 | 835979.5705 | 69.665 | 69.665 | 136.319 | 1 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 85.2041 | 37.3834 | 889725.7672 | 74.1438 | 74.1438 | 141.5538 | 75 | 60 | 31.6767 | 32 | 62.4
8/25/20XX 11:00:00 AM | 0.45833 | 4 | 78.4 | 59.5 | 72.7264 | 87.5927 | 14.8663 | 50 | 78.4 |  | 78.4 | 86.8494 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 65.0444 | 17.2238 | 409925.949 | 34.1605 | 34.1605 | 95.3965 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 67.4672 | 19.6466 | 467588.0981 | 38.9657 | 38.9657 | 101.5877 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 69.89 | 22.0693 | 525250.2471 | 43.7709 | 43.7709 | 107.7789 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 72.3127 | 24.4921 | 582912.3961 | 48.576 | 48.576 | 113.97 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 74.7355 | 26.9149 | 640574.5452 | 53.3812 | 53.3812 | 120.1612 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 77.1583 | 29.3377 | 698236.6942 | 58.1864 | 58.1864 | 126.3524 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 79.5811 | 31.7605 | 755898.8432 | 62.9916 | 62.9916 | 132.5436 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 82.0039 | 34.1832 | 813560.9922 | 67.7967 | 67.7967 | 138.7347 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 84.4266 | 36.606 | 871223.1413 | 72.6019 | 72.6019 | 144.9259 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 86.8494 | 39.0288 | 928885.2903 | 77.4071 | 77.4071 | 151.1171 | 80 | 60 | 32.4254 | 32 | 59.5
8/25/20XX 12:00:00 PM | 0.5 | 4 | 79.4 | 56.7 | 75.2039 | 90.5845 | 15.3806 | 50 | 79.4 |  | 79.4 | 85.5089 | 0.1 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 64.9104 | 17.0897 | 406735.5187 | 33.8946 | 33.8946 | 95.4456 | 0.2 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 67.1991 | 19.3785 | 461207.2373 | 38.4339 | 38.4339 | 101.6859 | 0.3 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 69.4878 | 21.6672 | 515678.956 | 42.9732 | 42.9732 | 107.9262 | 0.4 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 71.7765 | 23.9559 | 570150.6746 | 47.5126 | 47.5126 | 114.1666 | 0.5 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 74.0653 | 26.2446 | 624622.3933 | 52.0519 | 52.0519 | 120.4069 | 0.6 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 76.354 | 28.5334 | 679094.112 | 56.5912 | 56.5912 | 126.6472 | 0.7 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 78.6427 | 30.8221 | 733565.8306 | 61.1305 | 61.1305 | 132.8875 | 0.8 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 80.9315 | 33.1108 | 788037.5493 | 65.6698 | 65.6698 | 139.1278 | 0.9 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 83.2202 | 35.3995 | 842509.2679 | 70.2091 | 70.2091 | 145.3681 | 1 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 85.5089 | 37.6883 | 896980.9866 | 74.7484 | 74.7484 | 151.6084 | 80 | 55 | 32.4607 | 32 | 56.7
8/25/20XX 1:00:00 PM | 0.54167 | 4 | 80.3 | 56.3 | 77.4931 | 93.3492 | 15.8561 | 50 | 80.3 |  | 80.3 | 87.4824 | 0.1 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 65.1077 | 17.2871 | 411432.5392 | 34.286 | 34.286 | 96.1205 | 0.2 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 67.5938 | 19.7732 | 470601.2784 | 39.2168 | 39.2168 | 103.0358 | 0.3 | 75.89 | 20.89 | 789642 | 65.8035 | 65.8035 | 70.0799 | 22.2592 | 529770.0176 | 44.1475 | 44.1475 | 109.951 | 0.4 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 72.566 | 24.7453 | 588938.7568 | 49.0782 | 49.0782 | 116.8662 | 0.5 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 75.052 | 27.2314 | 648107.496 | 54.009 | 54.009 | 123.7815 | 0.6 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 77.5381 | 29.7175 | 707276.2351 | 58.9397 | 58.9397 | 130.6967 | 0.7 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 80.0242 | 32.2036 | 766444.9743 | 63.8704 | 63.8704 | 137.6119 | 0.8 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 82.5103 | 34.6897 | 825613.7135 | 68.8011 | 68.8011 | 144.5271 | 0.9 | 79.67 | 24.67 | 932526 | 77.7105 | 77.7105 | 84.9964 | 37.1757 | 884782.4527 | 73.7319 | 73.7319 | 151.4424 | 1 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 87.4824 | 39.6618 | 943951.1919 | 78.6626 | 78.6626 | 158.3576 | 80 | 55 | 32.9911 | 32 | 56.3
8/25/20XX 2:00:00 PM | 0.58333 | 4 | 80 | 56.7 | 76.7237 | 92.42 | 15.6963 | 50 | 80 |  | 80 | 87.2402 | 0.1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 65.0835 | 17.2629 | 410856.0268 | 34.238 | 34.238 | 95.978 | 0.2 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 67.5453 | 19.7247 | 469448.2536 | 39.1207 | 39.1207 | 102.7507 | 0.3 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 70.0072 | 22.1866 | 528040.4804 | 44.0034 | 44.0034 | 109.5234 | 0.4 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 72.4691 | 24.6484 | 586632.7072 | 48.8861 | 48.8861 | 116.2961 | 0.5 | 77 | 22 | 831600 | 69.3 | 69.3 | 74.9309 | 27.1103 | 645224.934 | 53.7687 | 53.7687 | 123.0687 | 0.6 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 77.3928 | 29.5721 | 703817.1608 | 58.6514 | 58.6514 | 129.8414 | 0.7 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 79.8546 | 32.034 | 762409.3876 | 63.5341 | 63.5341 | 136.6141 | 0.8 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 82.3165 | 34.4959 | 821001.6144 | 68.4168 | 68.4168 | 143.3868 | 0.9 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 84.7784 | 36.9577 | 879593.8412 | 73.2995 | 73.2995 | 150.1595 | 1 | 80 | 25 | 945000 | 78.75 | 78.75 | 87.2402 | 39.4196 | 938186.068 | 78.1822 | 78.1822 | 156.9322 | 80 | 55 | 32.8795 | 32 | 56.7
8/25/20XX 3:00:00 PM | 0.625 | 4 | 79.4 | 59 | 75.2039 | 90.5845 | 15.3806 | 50 | 79.4 |  | 79.4 | 89.0464 | 0.1 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 65.2641 | 17.4435 | 415154.8528 | 34.5962 | 34.5962 | 96.1472 | 0.2 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 67.9066 | 20.086 | 478045.9057 | 39.8372 | 39.8372 | 103.0892 | 0.3 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 70.5491 | 22.7284 | 540936.9585 | 45.0781 | 45.0781 | 110.0311 | 0.4 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 73.1916 | 25.3709 | 603828.0113 | 50.319 | 50.319 | 116.973 | 0.5 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 75.834 | 28.0134 | 666719.0642 | 55.5599 | 55.5599 | 123.9149 | 0.6 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 78.4765 | 30.6559 | 729610.117 | 60.8008 | 60.8008 | 130.8568 | 0.7 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 81.119 | 33.2984 | 792501.1698 | 66.0418 | 66.0418 | 137.7988 | 0.8 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 83.7615 | 35.9408 | 855392.2226 | 71.2827 | 71.2827 | 144.7407 | 0.9 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 86.404 | 38.5833 | 918283.2755 | 76.5236 | 76.5236 | 151.6826 | 1 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 89.0464 | 41.2258 | 981174.3283 | 81.7645 | 81.7645 | 158.6245 | 80 | 60 | 33.0153 | 34 | 59
8/25/20XX 4:00:00 PM | 0.66667 | 4 | 78.8 | 58 | 73.7091 | 88.7794 | 15.0703 | 50 | 78.8 |  | 78.8 | 85.7654 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 64.936 | 17.1154 | 407345.8665 | 33.9455 | 33.9455 | 95.3075 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 67.2504 | 19.4297 | 462427.9331 | 38.5357 | 38.5357 | 101.4097 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 69.5648 | 21.7441 | 517509.9996 | 43.1258 | 43.1258 | 107.5118 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 71.8791 | 24.0585 | 572592.0662 | 47.716 | 47.716 | 113.614 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 74.1935 | 26.3729 | 627674.1327 | 52.3062 | 52.3062 | 119.7162 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 76.5079 | 28.6872 | 682756.1993 | 56.8963 | 56.8963 | 125.8183 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 78.8222 | 31.0016 | 737838.2658 | 61.4865 | 61.4865 | 131.9205 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 81.1366 | 33.316 | 792920.3324 | 66.0767 | 66.0767 | 138.0227 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 83.451 | 35.6304 | 848002.3989 | 70.6669 | 70.6669 | 144.1249 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 85.7654 | 37.9447 | 903084.4654 | 75.257 | 75.257 | 150.227 | 80 | 60 | 32.3537 | 32 | 58
8/25/20XX 5:00:00 PM | 0.70833 | 4 | 78.4 | 57.8 | 72.7264 | 87.5927 | 14.8663 | 50 | 78.4 |  | 78.4 | 84.3222 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 64.7917 | 16.9711 | 403911.0348 | 33.6593 | 33.6593 | 94.8953 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 66.9617 | 19.1411 | 455558.2696 | 37.9632 | 37.9632 | 100.5852 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 69.1318 | 21.3112 | 507205.5044 | 42.2671 | 42.2671 | 106.2751 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 71.3018 | 23.4812 | 558852.7392 | 46.5711 | 46.5711 | 111.9651 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 73.4719 | 25.6513 | 610499.974 | 50.875 | 50.875 | 117.655 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 75.6419 | 27.8213 | 662147.2088 | 55.1789 | 55.1789 | 123.3449 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 77.812 | 29.9914 | 713794.4436 | 59.4829 | 59.4829 | 129.0349 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 79.982 | 32.1614 | 765441.6784 | 63.7868 | 63.7868 | 134.7248 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 82.1521 | 34.3315 | 817088.9132 | 68.0907 | 68.0907 | 140.4147 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 84.3222 | 36.5015 | 868736.148 | 72.3947 | 72.3947 | 146.1047 | 80 | 60 | 32.0293 | 32 | 57.8
8/25/20XX 6:00:00 PM | 0.75 | 4 | 77.3 | 58.4 | 70.0801 | 84.3976 | 14.3175 | 50 | 77.3 |  | 77.3 | 82.1068 | 0.1 | 74.33 | 19.33 | 730674 | 60.8895 | 60.8895 | 64.5701 | 16.7495 | 398638.4368 | 33.2199 | 33.2199 | 94.1094 | 0.2 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 66.5187 | 18.698 | 445013.0735 | 37.0844 | 37.0844 | 99.0134 | 0.3 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 68.4672 | 20.6465 | 491387.7103 | 40.949 | 40.949 | 103.9175 | 0.4 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 70.4157 | 22.5951 | 537762.3471 | 44.8135 | 44.8135 | 108.8215 | 0.5 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 72.3642 | 24.5436 | 584136.9838 | 48.6781 | 48.6781 | 113.7256 | 0.6 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 74.3127 | 26.4921 | 630511.6206 | 52.5426 | 52.5426 | 118.6296 | 0.7 | 76.31 | 21.31 | 805518 | 67.1265 | 67.1265 | 76.2612 | 28.4406 | 676886.2574 | 56.4072 | 56.4072 | 123.5337 | 0.8 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 78.2097 | 30.3891 | 723260.8941 | 60.2717 | 60.2717 | 128.4377 | 0.9 | 76.97 | 21.97 | 830466 | 69.2055 | 69.2055 | 80.1583 | 32.3376 | 769635.5309 | 64.1363 | 64.1363 | 133.3418 | 1 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 82.1068 | 34.2861 | 816010.1677 | 68.0008 | 68.0008 | 138.2458 | 75 | 60 | 31.4125 | 32 | 58.4
8/25/20XX 7:00:00 PM | 0.79167 | 4 | 76.1 | 59.6 | 67.2857 | 81.0242 | 13.7385 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/25/20XX 8:00:00 PM | 0.83333 | 4 | 75.2 | 61.9 | 78.5695 | 91.9451 | 13.3756 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/25/20XX 9:00:00 PM | 0.875 | 4 | 74.5 | 62.4 | 76.7042 | 89.7555 | 13.0512 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/25/20XX 10:00:00 PM | 0.91667 | 4 | 74 | 62.4 | 75.3952 | 88.2187 | 12.8236 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/25/20XX 11:00:00 PM | 0.95833 | 4 | 73.4 | 65.1 | 73.8495 | 86.4044 | 12.5549 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/25/20XX 12:00:00 AM | 0 | 5 | 72.4 | 67.2 | 71.3339 | 83.4515 | 12.1177 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/26/20XX 1:00:00 AM | 0.041667 | 5 | 71.8 | 68.4 | 69.8602 | 81.7218 | 11.8616 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/26/20XX 2:00:00 AM | 0.083333 | 5 | 70.8 | 70.7 | 78.908 | 90.4259 | 11.5179 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/26/20XX 3:00:00 AM | 0.125 | 5 | 70.5 | 72.3 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/26/20XX 4:00:00 AM | 0.16667 | 5 | 69.9 | 75.6 | 76.4479 | 87.5989 | 11.151 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/26/20XX 5:00:00 AM | 0.20833 | 5 | 69.2 | 77.2 | 74.5812 | 85.4541 | 10.8729 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/26/20XX 6:00:00 AM | 0.25 | 5 | 69.3 | 77.4 | 74.8454 | 85.7577 | 10.9122 | 70 | 69.3 |  | 69.3 | 82.9205 | 0.1 | 73.53 | 18.53 | 700434 | 58.3695 | 58.3695 | 64.6515 | 16.8309 | 400575.0468 | 33.3813 | 33.3813 | 91.7508 | 0.2 | 73.06 | 18.06 | 682668 | 56.889 | 56.889 | 66.6814 | 18.8608 | 448886.2935 | 37.4072 | 37.4072 | 94.2962 | 0.3 | 72.59 | 17.59 | 664902 | 55.4085 | 55.4085 | 68.7113 | 20.8907 | 497197.5403 | 41.4331 | 41.4331 | 96.8416 | 0.4 | 72.12 | 17.12 | 647136 | 53.928 | 53.928 | 70.7412 | 22.9205 | 545508.787 | 45.4591 | 45.4591 | 99.3871 | 0.5 | 71.65 | 16.65 | 629370 | 52.4475 | 52.4475 | 72.7711 | 24.9504 | 593820.0338 | 49.485 | 49.485 | 101.9325 | 0.6 | 71.18 | 16.18 | 611604 | 50.967 | 50.967 | 74.8009 | 26.9803 | 642131.2805 | 53.5109 | 53.5109 | 104.4779 | 0.7 | 70.71 | 15.71 | 593838 | 49.4865 | 49.4865 | 76.8308 | 29.0102 | 690442.5273 | 57.5369 | 57.5369 | 107.0234 | 0.8 | 70.24 | 15.24 | 576072 | 48.006 | 48.006 | 78.8607 | 31.0401 | 738753.774 | 61.5628 | 61.5628 | 109.5688 | 0.9 | 69.77 | 14.77 | 558306 | 46.5255 | 46.5255 | 80.8906 | 33.07 | 787065.0208 | 65.5888 | 65.5888 | 112.1143 | 1 | 69.3 | 14.3 | 540540 | 45.045 | 45.045 | 82.9205 | 35.0998 | 835376.2675 | 69.6147 | 69.6147 | 114.6597 | 70 | 75 | 29.5778 | 30 | 77.4
8/26/20XX 7:00:00 AM | 0.29167 | 5 | 70.5 | 76 | 78.0804 | 89.4748 | 11.3944 | 70 | 70.5 |  | 70.5 | 84.917 | 0.1 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 64.8512 | 17.0305 | 405326.8885 | 33.7772 | 33.7772 | 92.5247 | 0.2 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 67.0807 | 19.2601 | 458389.9771 | 38.1992 | 38.1992 | 95.8442 | 0.3 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 69.3103 | 21.4896 | 511453.0656 | 42.6211 | 42.6211 | 99.1636 | 0.4 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 71.5398 | 23.7192 | 564516.1541 | 47.043 | 47.043 | 102.483 | 0.5 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 73.7693 | 25.9487 | 617579.2426 | 51.4649 | 51.4649 | 105.8024 | 0.6 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 75.9989 | 28.1782 | 670642.3312 | 55.8869 | 55.8869 | 109.1219 | 0.7 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 78.2284 | 30.4078 | 723705.4197 | 60.3088 | 60.3088 | 112.4413 | 0.8 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 80.458 | 32.6373 | 776768.5082 | 64.7307 | 64.7307 | 115.7607 | 0.9 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 82.6875 | 34.8669 | 829831.5967 | 69.1526 | 69.1526 | 119.0801 | 1 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 84.917 | 37.0964 | 882894.6853 | 73.5746 | 73.5746 | 122.3996 | 70 | 75 | 30.184 | 30 | 76
8/26/20XX 8:00:00 AM | 0.33333 | 5 | 72.4 | 72.5 | 83.4515 | 95.6486 | 12.1971 | 70 | 72.4 |  | 72.4 | 86.5008 | 0.1 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 65.0095 | 17.1889 | 409096.1638 | 34.0913 | 34.0913 | 93.4373 | 0.2 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 67.3975 | 19.5768 | 465928.5277 | 38.8274 | 38.8274 | 97.6694 | 0.3 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 69.7854 | 21.9647 | 522760.8915 | 43.5634 | 43.5634 | 101.9014 | 0.4 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 72.1733 | 24.3527 | 579593.2553 | 48.2994 | 48.2994 | 106.1334 | 0.5 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 74.5612 | 26.7406 | 636425.6192 | 53.0355 | 53.0355 | 110.3655 | 0.6 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 76.9491 | 29.1285 | 693257.983 | 57.7715 | 57.7715 | 114.5975 | 0.7 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 79.337 | 31.5164 | 750090.3468 | 62.5075 | 62.5075 | 118.8295 | 0.8 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 81.7249 | 33.9043 | 806922.7107 | 67.2436 | 67.2436 | 123.0616 | 0.9 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 84.1129 | 36.2922 | 863755.0745 | 71.9796 | 71.9796 | 127.2936 | 1 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 86.5008 | 38.6801 | 920587.4383 | 76.7156 | 76.7156 | 131.5256 | 70 | 70 | 30.8978 | 30 | 72.5
8/26/20XX 9:00:00 AM | 0.375 | 5 | 74.4 | 66.9 | 76.4409 | 89.4463 | 13.0054 | 60 | 74.4 |  | 74.4 | 85.4146 | 0.1 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 64.9009 | 17.0803 | 406511.1149 | 33.8759 | 33.8759 | 93.8519 | 0.2 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 67.1802 | 19.3596 | 460758.4297 | 38.3965 | 38.3965 | 98.4985 | 0.3 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 69.4595 | 21.6389 | 515005.7446 | 42.9171 | 42.9171 | 103.1451 | 0.4 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 71.7388 | 23.9182 | 569253.0595 | 47.4378 | 47.4378 | 107.7918 | 0.5 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 74.0181 | 26.1975 | 623500.3743 | 51.9584 | 51.9584 | 112.4384 | 0.6 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 76.2974 | 28.4768 | 677747.6892 | 56.479 | 56.479 | 117.085 | 0.7 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 78.5767 | 30.7561 | 731995.0041 | 60.9996 | 60.9996 | 121.7316 | 0.8 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 80.856 | 33.0354 | 786242.3189 | 65.5202 | 65.5202 | 126.3782 | 0.9 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 83.1353 | 35.3147 | 840489.6338 | 70.0408 | 70.0408 | 131.0248 | 1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 85.4146 | 37.594 | 894736.9487 | 74.5614 | 74.5614 | 135.6714 | 75 | 65 | 31.2188 | 32 | 66.9
8/26/20XX 10:00:00 AM | 0.41667 | 5 | 77.1 | 60 | 83.8273 | 98.1177 | 14.2905 | 60 | 77.1 |  | 77.1 | 83.8273 | 0.1 | 74.31 | 19.31 | 729918 | 60.8265 | 60.8265 | 64.7422 | 16.9216 | 402733.2103 | 33.5611 | 33.5611 | 94.3876 | 0.2 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 66.8628 | 19.0421 | 453202.6207 | 37.7669 | 37.7669 | 99.5699 | 0.3 | 74.93 | 19.93 | 753354 | 62.7795 | 62.7795 | 68.9833 | 21.1627 | 503672.031 | 41.9727 | 41.9727 | 104.7522 | 0.4 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 71.1039 | 23.2833 | 554141.4414 | 46.1785 | 46.1785 | 109.9345 | 0.5 | 75.55 | 20.55 | 776790 | 64.7325 | 64.7325 | 73.2244 | 25.4038 | 604610.8517 | 50.3842 | 50.3842 | 115.1167 | 0.6 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 75.345 | 27.5244 | 655080.2621 | 54.59 | 54.59 | 120.299 | 0.7 | 76.17 | 21.17 | 800226 | 66.6855 | 66.6855 | 77.4656 | 29.6449 | 705549.6724 | 58.7958 | 58.7958 | 125.4813 | 0.8 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 79.5861 | 31.7655 | 756019.0827 | 63.0016 | 63.0016 | 130.6636 | 0.9 | 76.79 | 21.79 | 823662 | 68.6385 | 68.6385 | 81.7067 | 33.8861 | 806488.4931 | 67.2074 | 67.2074 | 135.8459 | 1 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 83.8273 | 36.0066 | 856957.9034 | 71.4132 | 71.4132 | 141.0282 | 75 | 60 | 31.6329 | 32 | 60
8/26/20XX 11:00:00 AM | 0.45833 | 5 | 80.5 | 51.7 | 78.0095 | 93.973 | 15.9635 | 50 | 80.5 |  | 80.5 | 80.7233 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 64.4318 | 16.6112 | 395345.8018 | 32.9455 | 32.9455 | 94.843 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 66.242 | 18.4213 | 438427.8036 | 36.5357 | 36.5357 | 100.4807 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 68.0521 | 20.2315 | 481509.8054 | 40.1258 | 40.1258 | 106.1183 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 69.8623 | 22.0417 | 524591.8072 | 43.716 | 43.716 | 111.756 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 71.6725 | 23.8518 | 567673.8089 | 47.3062 | 47.3062 | 117.3937 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 73.4826 | 25.662 | 610755.8107 | 50.8963 | 50.8963 | 123.0313 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 75.2928 | 27.4722 | 653837.8125 | 54.4865 | 54.4865 | 128.669 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 77.103 | 29.2823 | 696919.8143 | 58.0767 | 58.0767 | 134.3067 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 78.9131 | 31.0925 | 740001.8161 | 61.6668 | 61.6668 | 139.9443 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 80.7233 | 32.9027 | 783083.8179 | 65.257 | 65.257 | 145.582 | 80 | 50 | 31.9802 | 32 | 51.7
8/26/20XX 12:00:00 PM | 0.5 | 5 | 82.2 | 48.5 | 65.7342 | 82.5146 | 16.7804 | 40 | 82.2 |  | 82.2 | 79.9976 | 0.1 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 64.3592 | 16.5386 | 393618.5269 | 32.8015 | 32.8015 | 95.2345 | 0.2 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 66.0968 | 18.2762 | 434973.2538 | 36.2478 | 36.2478 | 101.2638 | 0.3 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 67.8344 | 20.0138 | 476327.9807 | 39.694 | 39.694 | 107.293 | 0.4 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 69.572 | 21.7514 | 517682.7076 | 43.1402 | 43.1402 | 113.3222 | 0.5 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 71.3096 | 23.489 | 559037.4345 | 46.5865 | 46.5865 | 119.3515 | 0.6 | 78.92 | 23.92 | 904176 | 75.348 | 75.348 | 73.0472 | 25.2266 | 600392.1614 | 50.0327 | 50.0327 | 125.3807 | 0.7 | 79.74 | 24.74 | 935172 | 77.931 | 77.931 | 74.7848 | 26.9642 | 641746.8883 | 53.4789 | 53.4789 | 131.4099 | 0.8 | 80.56 | 25.56 | 966168 | 80.514 | 80.514 | 76.5224 | 28.7017 | 683101.6152 | 56.9251 | 56.9251 | 137.4391 | 0.9 | 81.38 | 26.38 | 997164 | 83.097 | 83.097 | 78.26 | 30.4393 | 724456.3421 | 60.3714 | 60.3714 | 143.4684 | 1 | 82.2 | 27.2 | 1028160 | 85.68 | 85.68 | 79.9976 | 32.1769 | 765811.069 | 63.8176 | 63.8176 | 149.4976 | 80 | 50 | 32.283 | 32 | 48.5
8/26/20XX 1:00:00 PM | 0.54167 | 5 | 81.5 | 49.6 | 64.2452 | 80.6344 | 16.3893 | 40 | 81.5 |  | 81.5 | 79.9789 | 0.1 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 64.3574 | 16.5367 | 393573.9834 | 32.7978 | 32.7978 | 95.0103 | 0.2 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 66.0931 | 18.2724 | 434884.1667 | 36.2403 | 36.2403 | 100.8153 | 0.3 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 67.8288 | 20.0082 | 476194.3501 | 39.6829 | 39.6829 | 106.6204 | 0.4 | 77 | 22 | 831600 | 69.3 | 69.3 | 69.5645 | 21.7439 | 517504.5334 | 43.1254 | 43.1254 | 112.4254 | 0.5 | 77.75 | 22.75 | 859950 | 71.6625 | 71.6625 | 71.3002 | 23.4796 | 558814.7168 | 46.5679 | 46.5679 | 118.2304 | 0.6 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 73.036 | 25.2153 | 600124.9002 | 50.0104 | 50.0104 | 124.0354 | 0.7 | 79.25 | 24.25 | 916650 | 76.3875 | 76.3875 | 74.7717 | 26.9511 | 641435.0835 | 53.4529 | 53.4529 | 129.8404 | 0.8 | 80 | 25 | 945000 | 78.75 | 78.75 | 76.5074 | 28.6868 | 682745.2669 | 56.8954 | 56.8954 | 135.6454 | 0.9 | 80.75 | 25.75 | 973350 | 81.1125 | 81.1125 | 78.2431 | 30.4225 | 724055.4502 | 60.338 | 60.338 | 141.4505 | 1 | 81.5 | 26.5 | 1001700 | 83.475 | 83.475 | 79.9789 | 32.1582 | 765365.6336 | 63.7805 | 63.7805 | 147.2555 | 80 | 50 | 32.1085 | 32 | 49.6
8/26/20XX 2:00:00 PM | 0.58333 | 5 | 82.4 | 48.6 | 66.1648 | 83.0584 | 16.8936 | 40 | 82.4 |  | 82.4 | 80.6933 | 0.1 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 64.4288 | 16.6082 | 395274.2974 | 32.9395 | 32.9395 | 95.4355 | 0.2 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 66.236 | 18.4153 | 438284.7948 | 36.5237 | 36.5237 | 101.6657 | 0.3 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 68.0431 | 20.2225 | 481295.2923 | 40.1079 | 40.1079 | 107.8959 | 0.4 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 69.8503 | 22.0297 | 524305.7897 | 43.6921 | 43.6921 | 114.1261 | 0.5 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 71.6575 | 23.8368 | 567316.2871 | 47.2764 | 47.2764 | 120.3564 | 0.6 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 73.4646 | 25.644 | 610326.7845 | 50.8606 | 50.8606 | 126.5866 | 0.7 | 79.88 | 24.88 | 940464 | 78.372 | 78.372 | 75.2718 | 27.4511 | 653337.2819 | 54.4448 | 54.4448 | 132.8168 | 0.8 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 77.0789 | 29.2583 | 696347.7793 | 58.029 | 58.029 | 139.047 | 0.9 | 81.56 | 26.56 | 1003968 | 83.664 | 83.664 | 78.8861 | 31.0655 | 739358.2768 | 61.6132 | 61.6132 | 145.2772 | 1 | 82.4 | 27.4 | 1035720 | 86.31 | 86.31 | 80.6933 | 32.8726 | 782368.7742 | 65.1974 | 65.1974 | 151.5074 | 80 | 50 | 32.4412 | 32 | 48.6
8/26/20XX 3:00:00 PM | 0.625 | 5 | 81.6 | 48.3 | 64.4562 | 80.9009 | 16.4447 | 40 | 81.6 |  | 81.6 | 78.1053 | 0.1 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 64.17 | 16.3494 | 389114.8333 | 32.4262 | 32.4262 | 94.6702 | 0.2 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 65.7184 | 17.8977 | 425965.8667 | 35.4972 | 35.4972 | 100.1352 | 0.3 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 67.2667 | 19.4461 | 462816.9 | 38.5681 | 38.5681 | 105.6001 | 0.4 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 68.8151 | 20.9945 | 499667.9334 | 41.639 | 41.639 | 111.065 | 0.5 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 70.3634 | 22.5428 | 536518.9667 | 44.7099 | 44.7099 | 116.5299 | 0.6 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 71.9118 | 24.0912 | 573370.0001 | 47.7808 | 47.7808 | 121.9948 | 0.7 | 79.32 | 24.32 | 919296 | 76.608 | 76.608 | 73.4602 | 25.6395 | 610221.0334 | 50.8518 | 50.8518 | 127.4598 | 0.8 | 80.08 | 25.08 | 948024 | 79.002 | 79.002 | 75.0085 | 27.1879 | 647072.0667 | 53.9227 | 53.9227 | 132.9247 | 0.9 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 76.5569 | 28.7363 | 683923.1001 | 56.9936 | 56.9936 | 138.3896 | 1 | 81.6 | 26.6 | 1005480 | 83.79 | 83.79 | 78.1053 | 30.2846 | 720774.1334 | 60.0645 | 60.0645 | 143.8545 | 80 | 50 | 31.839 | 32 | 48.3
8/26/20XX 4:00:00 PM | 0.66667 | 5 | 81.1 | 50.3 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 80.0646 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 64.3659 | 16.5453 | 393777.9677 | 32.8148 | 32.8148 | 94.9013 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 66.1102 | 18.2896 | 435292.1354 | 36.2743 | 36.2743 | 100.5973 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 67.8545 | 20.0339 | 476806.3031 | 39.7339 | 39.7339 | 106.2934 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 69.5988 | 21.7782 | 518320.4709 | 43.1934 | 43.1934 | 111.9894 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 71.3431 | 23.5225 | 559834.6386 | 46.6529 | 46.6529 | 117.6854 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 73.0874 | 25.2668 | 601348.8063 | 50.1124 | 50.1124 | 123.3814 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 74.8317 | 27.011 | 642862.974 | 53.5719 | 53.5719 | 129.0774 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 76.576 | 28.7553 | 684377.1417 | 57.0314 | 57.0314 | 134.7734 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 78.3203 | 30.4996 | 725891.3094 | 60.4909 | 60.4909 | 140.4694 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 80.0646 | 32.2439 | 767405.4772 | 63.9505 | 63.9505 | 146.1655 | 80 | 50 | 32.0239 | 32 | 50.3
8/26/20XX 5:00:00 PM | 0.70833 | 5 | 79.9 | 51.6 | 76.4687 | 92.1119 | 15.6433 | 50 | 79.9 |  | 79.9 | 78.9716 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 64.2566 | 16.436 | 391176.7024 | 32.5981 | 32.5981 | 94.3066 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 65.8916 | 18.071 | 430089.6048 | 35.8408 | 35.8408 | 99.4078 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 67.5266 | 19.706 | 469002.5071 | 39.0835 | 39.0835 | 104.509 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 69.1616 | 21.341 | 507915.4095 | 42.3263 | 42.3263 | 109.6103 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 70.7966 | 22.976 | 546828.3119 | 45.569 | 45.569 | 114.7115 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 72.4316 | 24.611 | 585741.2143 | 48.8118 | 48.8118 | 119.8128 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 74.0666 | 26.246 | 624654.1167 | 52.0545 | 52.0545 | 124.914 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 75.7016 | 27.881 | 663567.019 | 55.2973 | 55.2973 | 130.0153 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 77.3366 | 29.516 | 702479.9214 | 58.54 | 58.54 | 135.1165 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 78.9716 | 31.151 | 741392.8238 | 61.7827 | 61.7827 | 140.2177 | 80 | 50 | 31.5584 | 32 | 51.6
8/26/20XX 6:00:00 PM | 0.75 | 5 | 78.9 | 52.9 | 73.9565 | 89.0782 | 15.1216 | 50 | 78.9 |  | 78.9 | 78.3418 | 0.1 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 64.1937 | 16.373 | 389677.8378 | 32.4732 | 32.4732 | 93.8667 | 0.2 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 65.7657 | 17.945 | 427091.8755 | 35.591 | 35.591 | 98.528 | 0.3 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 67.3377 | 19.5171 | 464505.9133 | 38.7088 | 38.7088 | 103.1893 | 0.4 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 68.9097 | 21.0891 | 501919.9511 | 41.8267 | 41.8267 | 107.8507 | 0.5 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 70.4817 | 22.6611 | 539333.9889 | 44.9445 | 44.9445 | 112.512 | 0.6 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 72.0537 | 24.2331 | 576748.0266 | 48.0623 | 48.0623 | 117.1733 | 0.7 | 77.43 | 22.43 | 847854 | 70.6545 | 70.6545 | 73.6258 | 25.8051 | 614162.0644 | 51.1802 | 51.1802 | 121.8347 | 0.8 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 75.1978 | 27.3771 | 651576.1022 | 54.298 | 54.298 | 126.496 | 0.9 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 76.7698 | 28.9492 | 688990.14 | 57.4158 | 57.4158 | 131.1573 | 1 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 78.3418 | 30.5212 | 726404.1777 | 60.5337 | 60.5337 | 135.8187 | 80 | 55 | 31.2147 | 32 | 52.9
8/26/20XX 7:00:00 PM | 0.79167 | 5 | 77.3 | 56.2 | 70.0801 | 84.3976 | 14.3175 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/26/20XX 8:00:00 PM | 0.83333 | 5 | 76.6 | 57.3 | 68.4384 | 82.4157 | 13.9773 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/26/20XX 9:00:00 PM | 0.875 | 5 | 75 | 61.2 | 78.0327 | 91.3149 | 13.2822 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/26/20XX 10:00:00 PM | 0.91667 | 5 | 73.8 | 64.9 | 74.8769 | 87.6104 | 12.7335 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/26/20XX 11:00:00 PM | 0.95833 | 5 | 72.8 | 68.5 | 72.3311 | 84.6221 | 12.291 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/26/20XX 12:00:00 AM | 0 | 6 | 72.8 | 65.5 | 72.3311 | 84.6221 | 12.291 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/27/20XX 1:00:00 AM | 0.041667 | 6 | 71.7 | 69.7 | 69.6172 | 81.4366 | 11.8194 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/27/20XX 2:00:00 AM | 0.083333 | 6 | 70.5 | 73.3 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/27/20XX 3:00:00 AM | 0.125 | 6 | 70.8 | 71.9 | 78.908 | 90.4259 | 11.5179 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/27/20XX 4:00:00 AM | 0.16667 | 6 | 70.4 | 73.6 | 77.8062 | 89.1597 | 11.3535 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/27/20XX 5:00:00 AM | 0.20833 | 6 | 69.7 | 74.7 | 75.9105 | 86.9813 | 11.0709 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/27/20XX 6:00:00 AM | 0.25 | 6 | 70 | 72.9 | 76.7179 | 87.9091 | 11.1912 | 70 | 70 |  | 70 | 79.9634 | 0.1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 64.3558 | 16.5352 | 393537.1728 | 32.7948 | 32.7948 | 91.3848 | 0.2 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 66.09 | 18.2694 | 434810.5456 | 36.2342 | 36.2342 | 93.5642 | 0.3 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 67.8242 | 20.0035 | 476083.9185 | 39.6737 | 39.6737 | 95.7437 | 0.4 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 69.5583 | 21.7377 | 517357.2913 | 43.1131 | 43.1131 | 97.9231 | 0.5 | 72 | 17 | 642600 | 53.55 | 53.55 | 71.2925 | 23.4719 | 558630.6641 | 46.5526 | 46.5526 | 100.1026 | 0.6 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 73.0267 | 25.2061 | 599904.0369 | 49.992 | 49.992 | 102.282 | 0.7 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 74.7609 | 26.9402 | 641177.4097 | 53.4315 | 53.4315 | 104.4615 | 0.8 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 76.495 | 28.6744 | 682450.7826 | 56.8709 | 56.8709 | 106.6409 | 0.9 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 78.2292 | 30.4086 | 723724.1554 | 60.3103 | 60.3103 | 108.8203 | 1 | 70 | 15 | 567000 | 47.25 | 47.25 | 79.9634 | 32.1428 | 764997.5282 | 63.7498 | 63.7498 | 110.9998 | 70 | 75 | 29.2877 | 30 | 72.9
8/27/20XX 7:00:00 AM | 0.29167 | 6 | 70.6 | 72.3 | 78.3554 | 89.7909 | 11.4354 | 70 | 70.6 |  | 70.6 | 80.9856 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 64.458 | 16.6374 | 395969.9815 | 32.9975 | 32.9975 | 91.7765 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 66.2944 | 18.4738 | 439676.1631 | 36.6397 | 36.6397 | 94.3477 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 68.1308 | 20.3102 | 483382.3446 | 40.2819 | 40.2819 | 96.9189 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 69.9672 | 22.1466 | 527088.5261 | 43.924 | 43.924 | 99.49 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 71.8036 | 23.983 | 570794.7077 | 47.5662 | 47.5662 | 102.0612 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 73.64 | 25.8194 | 614500.8892 | 51.2084 | 51.2084 | 104.6324 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 75.4764 | 27.6558 | 658207.0707 | 54.8506 | 54.8506 | 107.2036 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 77.3128 | 29.4922 | 701913.2523 | 58.4928 | 58.4928 | 109.7748 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 79.1492 | 31.3285 | 745619.4338 | 62.135 | 62.135 | 112.346 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 80.9856 | 33.1649 | 789325.6154 | 65.7771 | 65.7771 | 114.9171 | 70 | 70 | 29.5944 | 30 | 72.3
8/27/20XX 8:00:00 AM | 0.33333 | 6 | 72.3 | 67.4 | 71.0864 | 83.1611 | 12.0747 | 60 | 72.3 |  | 72.3 | 80.0216 | 0.1 | 73.83 | 18.83 | 711774 | 59.3145 | 59.3145 | 64.3616 | 16.541 | 393675.8358 | 32.8063 | 32.8063 | 92.1208 | 0.2 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 66.1016 | 18.281 | 435087.8716 | 36.2573 | 36.2573 | 95.0363 | 0.3 | 73.49 | 18.49 | 698922 | 58.2435 | 58.2435 | 67.8416 | 20.021 | 476499.9074 | 39.7083 | 39.7083 | 97.9518 | 0.4 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 69.5816 | 21.761 | 517911.9432 | 43.1593 | 43.1593 | 100.8673 | 0.5 | 73.15 | 18.15 | 686070 | 57.1725 | 57.1725 | 71.3216 | 23.501 | 559323.979 | 46.6103 | 46.6103 | 103.7828 | 0.6 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 73.0616 | 25.241 | 600736.0148 | 50.0613 | 50.0613 | 106.6983 | 0.7 | 72.81 | 17.81 | 673218 | 56.1015 | 56.1015 | 74.8016 | 26.981 | 642148.0506 | 53.5123 | 53.5123 | 109.6138 | 0.8 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 76.5416 | 28.721 | 683560.0865 | 56.9633 | 56.9633 | 112.5293 | 0.9 | 72.47 | 17.47 | 660366 | 55.0305 | 55.0305 | 78.2816 | 30.461 | 724972.1223 | 60.4143 | 60.4143 | 115.4448 | 1 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 80.0216 | 32.201 | 766384.1581 | 63.8653 | 63.8653 | 118.3603 | 70 | 65 | 29.8605 | 30 | 67.4
8/27/20XX 9:00:00 AM | 0.375 | 6 | 74.6 | 62 | 76.9684 | 90.0655 | 13.0971 | 60 | 74.6 |  | 74.6 | 79.5878 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 64.3183 | 16.4976 | 392643.3038 | 32.7203 | 32.7203 | 92.7593 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 66.0149 | 18.1942 | 433022.8077 | 36.0852 | 36.0852 | 96.3132 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 67.7115 | 19.8909 | 473402.3115 | 39.4502 | 39.4502 | 99.8672 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 69.4081 | 21.5875 | 513781.8153 | 42.8152 | 42.8152 | 103.4212 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 71.1047 | 23.2841 | 554161.3191 | 46.1801 | 46.1801 | 106.9751 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 72.8013 | 24.9807 | 594540.823 | 49.5451 | 49.5451 | 110.5291 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 74.498 | 26.6773 | 634920.3268 | 52.91 | 52.91 | 114.083 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 76.1946 | 28.3739 | 675299.8306 | 56.275 | 56.275 | 117.637 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 77.8912 | 30.0706 | 715679.3344 | 59.6399 | 59.6399 | 121.1909 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 79.5878 | 31.7672 | 756058.8383 | 63.0049 | 63.0049 | 124.7449 | 75 | 60 | 30.3563 | 30 | 62
8/27/20XX 10:00:00 AM | 0.41667 | 6 | 76.9 | 58.6 | 69.138 | 83.2602 | 14.1222 | 50 | 76.9 |  | 76.9 | 81.2831 | 0.1 | 74.29 | 19.29 | 729162 | 60.7635 | 60.7635 | 64.4878 | 16.6671 | 396678.0784 | 33.0565 | 33.0565 | 93.82 | 0.2 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 66.3539 | 18.5333 | 441092.3568 | 36.7577 | 36.7577 | 98.4347 | 0.3 | 74.87 | 19.87 | 751086 | 62.5905 | 62.5905 | 68.2201 | 20.3994 | 485506.6352 | 40.4589 | 40.4589 | 103.0494 | 0.4 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 70.0862 | 22.2656 | 529920.9136 | 44.1601 | 44.1601 | 107.6641 | 0.5 | 75.45 | 20.45 | 773010 | 64.4175 | 64.4175 | 71.9524 | 24.1317 | 574335.192 | 47.8613 | 47.8613 | 112.2788 | 0.6 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 73.8185 | 25.9979 | 618749.4704 | 51.5625 | 51.5625 | 116.8935 | 0.7 | 76.03 | 21.03 | 794934 | 66.2445 | 66.2445 | 75.6847 | 27.864 | 663163.7488 | 55.2636 | 55.2636 | 121.5081 | 0.8 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 77.5508 | 29.7302 | 707578.0272 | 58.9648 | 58.9648 | 126.1228 | 0.9 | 76.61 | 21.61 | 816858 | 68.0715 | 68.0715 | 79.4169 | 31.5963 | 751992.3056 | 62.666 | 62.666 | 130.7375 | 1 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 81.2831 | 33.4625 | 796406.584 | 66.3672 | 66.3672 | 135.3522 | 75 | 60 | 31.1854 | 32 | 58.6
8/27/20XX 11:00:00 AM | 0.45833 | 6 | 78.6 | 56.4 | 73.2164 | 88.1844 | 14.968 | 50 | 78.6 |  | 78.6 | 82.7959 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 64.6391 | 16.8184 | 400278.6318 | 33.3566 | 33.3566 | 94.6556 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 66.6565 | 18.8359 | 448293.4635 | 37.3578 | 37.3578 | 100.1058 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 68.6739 | 20.8533 | 496308.2953 | 41.359 | 41.359 | 105.556 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 70.6914 | 22.8707 | 544323.1271 | 45.3603 | 45.3603 | 111.0063 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 72.7088 | 24.8881 | 592337.9588 | 49.3615 | 49.3615 | 116.4565 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 74.7262 | 26.9056 | 640352.7906 | 53.3627 | 53.3627 | 121.9067 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 76.7436 | 28.923 | 688367.6223 | 57.364 | 57.364 | 127.357 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 78.7611 | 30.9404 | 736382.4541 | 61.3652 | 61.3652 | 132.8072 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 80.7785 | 32.9579 | 784397.2859 | 65.3664 | 65.3664 | 138.2574 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 82.7959 | 34.9753 | 832412.1176 | 69.3677 | 69.3677 | 143.7077 | 80 | 55 | 31.8392 | 32 | 56.4
8/27/20XX 12:00:00 PM | 0.5 | 6 | 79.9 | 54.1 | 76.4687 | 92.1119 | 15.6433 | 50 | 79.9 |  | 79.9 | 82.8824 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 64.6477 | 16.8271 | 400484.4539 | 33.3737 | 33.3737 | 95.0822 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 66.6738 | 18.8532 | 448705.1078 | 37.3921 | 37.3921 | 100.9591 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 68.6999 | 20.8792 | 496925.7617 | 41.4105 | 41.4105 | 106.836 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 70.7259 | 22.9053 | 545146.4156 | 45.4289 | 45.4289 | 112.7129 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 72.752 | 24.9314 | 593367.0695 | 49.4473 | 49.4473 | 118.5898 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 74.7781 | 26.9575 | 641587.7234 | 53.4656 | 53.4656 | 124.4666 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 76.8042 | 28.9835 | 689808.3773 | 57.484 | 57.484 | 130.3435 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 78.8303 | 31.0096 | 738029.0312 | 61.5024 | 61.5024 | 136.2204 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 80.8563 | 33.0357 | 786249.6851 | 65.5208 | 65.5208 | 142.0973 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 82.8824 | 35.0618 | 834470.339 | 69.5392 | 69.5392 | 147.9742 | 80 | 55 | 32.1716 | 32 | 54.1
8/27/20XX 1:00:00 PM | 0.54167 | 6 | 80.1 | 53.4 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 82.3343 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 64.5929 | 16.7723 | 399179.8675 | 33.265 | 33.265 | 95.0365 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 66.5642 | 18.7435 | 446095.9349 | 37.1747 | 37.1747 | 100.8677 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 68.5354 | 20.7148 | 493012.0024 | 41.0843 | 41.0843 | 106.6988 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 70.5067 | 22.6861 | 539928.0698 | 44.994 | 44.994 | 112.53 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 72.4779 | 24.6573 | 586844.1373 | 48.9037 | 48.9037 | 118.3612 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 74.4492 | 26.6286 | 633760.2047 | 52.8134 | 52.8134 | 124.1924 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 76.4205 | 28.5998 | 680676.2722 | 56.723 | 56.723 | 130.0235 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 78.3917 | 30.5711 | 727592.3397 | 60.6327 | 60.6327 | 135.8547 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 80.363 | 32.5424 | 774508.4071 | 64.5424 | 64.5424 | 141.6859 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 82.3343 | 34.5136 | 821424.4746 | 68.452 | 68.452 | 147.517 | 80 | 55 | 32.1347 | 32 | 53.4
8/27/20XX 2:00:00 PM | 0.58333 | 6 | 81.1 | 52.4 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 83.4853 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 64.708 | 16.8874 | 401919.2593 | 33.4933 | 33.4933 | 95.5798 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 66.7944 | 18.9737 | 451574.7185 | 37.6312 | 37.6312 | 101.9542 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 68.8807 | 21.0601 | 501230.1778 | 41.7692 | 41.7692 | 108.3287 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 70.9671 | 23.1465 | 550885.6371 | 45.9071 | 45.9071 | 114.7031 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 73.0535 | 25.2328 | 600541.0964 | 50.0451 | 50.0451 | 121.0776 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 75.1398 | 27.3192 | 650196.5556 | 54.183 | 54.183 | 127.452 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 77.2262 | 29.4055 | 699852.0149 | 58.321 | 58.321 | 133.8265 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 79.3125 | 31.4919 | 749507.4742 | 62.459 | 62.459 | 140.201 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 81.3989 | 33.5783 | 799162.9334 | 66.5969 | 66.5969 | 146.5754 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 83.4853 | 35.6646 | 848818.3927 | 70.7349 | 70.7349 | 152.9499 | 80 | 50 | 32.5605 | 32 | 52.4
8/27/20XX 3:00:00 PM | 0.625 | 6 | 80.4 | 52.6 | 77.751 | 93.6607 | 15.9097 | 50 | 80.4 |  | 80.4 | 81.8875 | 0.1 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 64.5482 | 16.7276 | 398116.5144 | 33.1764 | 33.1764 | 95.0424 | 0.2 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 66.4748 | 18.6542 | 443969.2288 | 36.9974 | 36.9974 | 100.8794 | 0.3 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 68.4014 | 20.5808 | 489821.9431 | 40.8185 | 40.8185 | 106.7165 | 0.4 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 70.328 | 22.5073 | 535674.6575 | 44.6396 | 44.6396 | 112.5536 | 0.5 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 72.2546 | 24.4339 | 581527.3719 | 48.4606 | 48.4606 | 118.3906 | 0.6 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 74.1811 | 26.3605 | 627380.0863 | 52.2817 | 52.2817 | 124.2277 | 0.7 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 76.1077 | 28.2871 | 673232.8006 | 56.1027 | 56.1027 | 130.0647 | 0.8 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 78.0343 | 30.2137 | 719085.515 | 59.9238 | 59.9238 | 135.9018 | 0.9 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 79.9609 | 32.1403 | 764938.2294 | 63.7449 | 63.7449 | 141.7389 | 1 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 81.8875 | 34.0668 | 810790.9438 | 67.5659 | 67.5659 | 147.5759 | 80 | 55 | 32.1382 | 32 | 52.6
8/27/20XX 4:00:00 PM | 0.66667 | 6 | 79.8 | 53.5 | 76.2143 | 91.8048 | 15.5904 | 50 | 79.8 |  | 79.8 | 81.671 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 64.5266 | 16.7059 | 397601.2313 | 33.1334 | 33.1334 | 94.8104 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 66.4315 | 18.6109 | 442938.6626 | 36.9116 | 36.9116 | 100.4156 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 68.3364 | 20.5158 | 488276.0939 | 40.6897 | 40.6897 | 106.0207 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 70.2414 | 22.4207 | 533613.5252 | 44.4678 | 44.4678 | 111.6258 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 72.1463 | 24.3257 | 578950.9564 | 48.2459 | 48.2459 | 117.2309 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 74.0512 | 26.2306 | 624288.3877 | 52.024 | 52.024 | 122.836 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 75.9562 | 28.1355 | 669625.819 | 55.8022 | 55.8022 | 128.4412 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 77.8611 | 30.0405 | 714963.2503 | 59.5803 | 59.5803 | 134.0463 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 79.766 | 31.9454 | 760300.6816 | 63.3584 | 63.3584 | 139.6514 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 81.671 | 33.8503 | 805638.1129 | 67.1365 | 67.1365 | 145.2565 | 80 | 55 | 31.9572 | 32 | 53.5
8/27/20XX 5:00:00 PM | 0.70833 | 6 | 79.1 | 55 | 74.4534 | 89.6782 | 15.2248 | 50 | 79.1 |  | 79.1 | 82.0658 | 0.1 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 64.566 | 16.7454 | 398540.9143 | 33.2117 | 33.2117 | 94.6682 | 0.2 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 66.5105 | 18.6898 | 444818.0285 | 37.0682 | 37.0682 | 100.1312 | 0.3 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 68.4549 | 20.6342 | 491095.1428 | 40.9246 | 40.9246 | 105.5941 | 0.4 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 70.3993 | 22.5787 | 537372.257 | 44.781 | 44.781 | 111.057 | 0.5 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 72.3437 | 24.5231 | 583649.3713 | 48.6374 | 48.6374 | 116.5199 | 0.6 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 74.2881 | 26.4675 | 629926.4855 | 52.4939 | 52.4939 | 121.9829 | 0.7 | 77.57 | 22.57 | 853146 | 71.0955 | 71.0955 | 76.2325 | 28.4119 | 676203.5998 | 56.3503 | 56.3503 | 127.4458 | 0.8 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 78.177 | 30.3563 | 722480.7141 | 60.2067 | 60.2067 | 132.9087 | 0.9 | 78.59 | 23.59 | 891702 | 74.3085 | 74.3085 | 80.1214 | 32.3007 | 768757.8283 | 64.0632 | 64.0632 | 138.3717 | 1 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 82.0658 | 34.2452 | 815034.9426 | 67.9196 | 67.9196 | 143.8346 | 80 | 55 | 31.8474 | 32 | 55
8/27/20XX 6:00:00 PM | 0.75 | 6 | 77.7 | 59.4 | 71.0329 | 85.548 | 14.515 | 50 | 77.7 |  | 77.7 | 84.6771 | 0.1 | 74.37 | 19.37 | 732186 | 61.0155 | 61.0155 | 64.8272 | 17.0065 | 404755.7083 | 33.7296 | 33.7296 | 94.7451 | 0.2 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 67.0327 | 19.2121 | 457247.6165 | 38.104 | 38.104 | 100.285 | 0.3 | 75.11 | 20.11 | 760158 | 63.3465 | 63.3465 | 69.2383 | 21.4176 | 509739.5248 | 42.4783 | 42.4783 | 105.8248 | 0.4 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 71.4438 | 23.6232 | 562231.433 | 46.8526 | 46.8526 | 111.3646 | 0.5 | 75.85 | 20.85 | 788130 | 65.6775 | 65.6775 | 73.6493 | 25.8287 | 614723.3413 | 51.2269 | 51.2269 | 116.9044 | 0.6 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 75.8549 | 28.0343 | 667215.2496 | 55.6013 | 55.6013 | 122.4443 | 0.7 | 76.59 | 21.59 | 816102 | 68.0085 | 68.0085 | 78.0604 | 30.2398 | 719707.1578 | 59.9756 | 59.9756 | 127.9841 | 0.8 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 80.266 | 32.4453 | 772199.0661 | 64.3499 | 64.3499 | 133.5239 | 0.9 | 77.33 | 22.33 | 844074 | 70.3395 | 70.3395 | 82.4715 | 34.6509 | 824690.9744 | 68.7242 | 68.7242 | 139.0637 | 1 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 84.6771 | 36.8564 | 877182.8826 | 73.0986 | 73.0986 | 144.6036 | 80 | 60 | 31.9132 | 32 | 59.4
8/27/20XX 7:00:00 PM | 0.79167 | 6 | 76.4 | 62.8 | 81.8567 | 95.8042 | 13.9475 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/27/20XX 8:00:00 PM | 0.83333 | 6 | 76 | 63.2 | 80.7483 | 94.5029 | 13.7546 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/27/20XX 9:00:00 PM | 0.875 | 6 | 75.5 | 63.8 | 79.3806 | 92.8973 | 13.5167 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/27/20XX 10:00:00 PM | 0.91667 | 6 | 74.6 | 65.7 | 76.9684 | 90.0655 | 13.0971 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/27/20XX 11:00:00 PM | 0.95833 | 6 | 74 | 69.4 | 75.3952 | 88.2187 | 12.8236 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/27/20XX 12:00:00 AM | 0 | 7 | 73.4 | 69.4 | 73.8495 | 86.4044 | 12.5549 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/28/20XX 1:00:00 AM | 0.041667 | 7 | 72.4 | 74.1 | 83.4515 | 95.6486 | 12.1971 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/28/20XX 2:00:00 AM | 0.083333 | 7 | 72.1 | 74.5 | 82.5828 | 94.6498 | 12.0671 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/28/20XX 3:00:00 AM | 0.125 | 7 | 71.7 | 75.3 | 81.4366 | 93.3322 | 11.8956 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/28/20XX 4:00:00 AM | 0.16667 | 7 | 71 | 76.4 | 79.4639 | 91.0648 | 11.6009 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/28/20XX 5:00:00 AM | 0.20833 | 7 | 70.1 | 78.6 | 76.9888 | 88.2203 | 11.2316 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/28/20XX 6:00:00 AM | 0.25 | 7 | 69.8 | 79.3 | 76.1788 | 87.2896 | 11.1108 | 70 | 69.8 |  | 69.8 | 86.5119 | 0.1 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 65.0107 | 17.19 | 409122.5885 | 34.0935 | 34.0935 | 92.6205 | 0.2 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 67.3997 | 19.579 | 465981.3771 | 38.8318 | 38.8318 | 96.0358 | 0.3 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 69.7887 | 21.9681 | 522840.1656 | 43.57 | 43.57 | 99.451 | 0.4 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 72.1777 | 24.3571 | 579698.9542 | 48.3082 | 48.3082 | 102.8662 | 0.5 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 74.5668 | 26.7461 | 636557.7427 | 53.0465 | 53.0465 | 106.2815 | 0.6 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 76.9558 | 29.1351 | 693416.5313 | 57.7847 | 57.7847 | 109.6967 | 0.7 | 71.06 | 16.06 | 607068 | 50.589 | 50.589 | 79.3448 | 31.5242 | 750275.3198 | 62.5229 | 62.5229 | 113.1119 | 0.8 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 81.7338 | 33.9132 | 807134.1084 | 67.2612 | 67.2612 | 116.5272 | 0.9 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 84.1229 | 36.3022 | 863992.8969 | 71.9994 | 71.9994 | 119.9424 | 1 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 86.5119 | 38.6912 | 920851.6854 | 76.7376 | 76.7376 | 123.3576 | 70 | 80 | 30.2612 | 30 | 79.3
8/28/20XX 7:00:00 AM | 0.29167 | 7 | 70.5 | 78.5 | 78.0804 | 89.4748 | 11.3944 | 70 | 70.5 |  | 70.5 | 87.7656 | 0.1 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 65.136 | 17.3154 | 412106.5513 | 34.3422 | 34.3422 | 93.0897 | 0.2 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 67.6504 | 19.8298 | 471949.3025 | 39.3291 | 39.3291 | 96.9741 | 0.3 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 70.1648 | 22.3442 | 531792.0538 | 44.316 | 44.316 | 100.8585 | 0.4 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 72.6792 | 24.8586 | 591634.8051 | 49.3029 | 49.3029 | 104.7429 | 0.5 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 75.1936 | 27.373 | 651477.5563 | 54.2898 | 54.2898 | 108.6273 | 0.6 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 77.708 | 29.8874 | 711320.3076 | 59.2767 | 59.2767 | 112.5117 | 0.7 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 80.2224 | 32.4018 | 771163.0589 | 64.2636 | 64.2636 | 116.3961 | 0.8 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 82.7368 | 34.9162 | 831005.8101 | 69.2505 | 69.2505 | 120.2805 | 0.9 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 85.2512 | 37.4306 | 890848.5614 | 74.2374 | 74.2374 | 124.1649 | 1 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 87.7656 | 39.945 | 950691.3127 | 79.2243 | 79.2243 | 128.0493 | 70 | 80 | 30.6289 | 30 | 78.5
8/28/20XX 8:00:00 AM | 0.33333 | 7 | 71.7 | 74.8 | 81.4366 | 93.3322 | 11.8956 | 70 | 71.7 |  | 71.7 | 87.1465 | 0.1 | 73.77 | 18.77 | 709506 | 59.1255 | 59.1255 | 65.0741 | 17.2535 | 410633.0151 | 34.2194 | 34.2194 | 93.3449 | 0.2 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 67.5266 | 19.706 | 469002.2302 | 39.0835 | 39.0835 | 97.4845 | 0.3 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 69.9791 | 22.1585 | 527371.4453 | 43.9476 | 43.9476 | 101.6241 | 0.4 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 72.4316 | 24.611 | 585740.6604 | 48.8117 | 48.8117 | 105.7637 | 0.5 | 72.85 | 17.85 | 674730 | 56.2275 | 56.2275 | 74.8841 | 27.0634 | 644109.8755 | 53.6758 | 53.6758 | 109.9033 | 0.6 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 77.3366 | 29.5159 | 702479.0906 | 58.5399 | 58.5399 | 114.0429 | 0.7 | 72.39 | 17.39 | 657342 | 54.7785 | 54.7785 | 79.789 | 31.9684 | 760848.3057 | 63.404 | 63.404 | 118.1825 | 0.8 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 82.2415 | 34.4209 | 819217.5208 | 68.2681 | 68.2681 | 122.3221 | 0.9 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 84.694 | 36.8734 | 877586.7359 | 73.1322 | 73.1322 | 126.4617 | 1 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 87.1465 | 39.3259 | 935955.951 | 77.9963 | 77.9963 | 130.6013 | 70 | 75 | 30.8269 | 30 | 74.8
8/28/20XX 9:00:00 AM | 0.375 | 7 | 73.8 | 70.3 | 87.6104 | 100.4307 | 12.8203 | 70 | 73.8 |  | 73.8 | 87.995 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 65.159 | 17.3383 | 412652.3315 | 34.3877 | 34.3877 | 94.1747 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 67.6963 | 19.8757 | 473040.863 | 39.4201 | 39.4201 | 99.1441 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 70.2336 | 22.413 | 533429.3945 | 44.4524 | 44.4524 | 104.1134 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 72.771 | 24.9503 | 593817.926 | 49.4848 | 49.4848 | 109.0828 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 75.3083 | 27.4877 | 654206.4575 | 54.5172 | 54.5172 | 114.0522 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 77.8456 | 30.025 | 714594.989 | 59.5496 | 59.5496 | 119.0216 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 80.383 | 32.5623 | 774983.5205 | 64.582 | 64.582 | 123.991 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 82.9203 | 35.0997 | 835372.052 | 69.6143 | 69.6143 | 128.9603 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 85.4576 | 37.637 | 895760.5835 | 74.6467 | 74.6467 | 133.9297 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 87.995 | 40.1743 | 956149.115 | 79.6791 | 79.6791 | 138.8991 | 75 | 70 | 31.4752 | 32 | 70.3
8/28/20XX 10:00:00 AM | 0.41667 | 7 | 75.8 | 64.3 | 80.1988 | 93.8579 | 13.6591 | 60 | 75.8 |  | 75.8 | 86.0722 | 0.1 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 64.9667 | 17.1461 | 408076.199 | 34.0063 | 34.0063 | 94.4233 | 0.2 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 67.3117 | 19.4911 | 463888.5981 | 38.6574 | 38.6574 | 99.6414 | 0.3 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 69.6568 | 21.8362 | 519700.9971 | 43.3084 | 43.3084 | 104.8594 | 0.4 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 72.0019 | 24.1812 | 575513.3961 | 47.9594 | 47.9594 | 110.0774 | 0.5 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 74.3469 | 26.5263 | 631325.7951 | 52.6105 | 52.6105 | 115.2955 | 0.6 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 76.692 | 28.8714 | 687138.1942 | 57.2615 | 57.2615 | 120.5135 | 0.7 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 79.037 | 31.2164 | 742950.5932 | 61.9125 | 61.9125 | 125.7315 | 0.8 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 81.3821 | 33.5615 | 798762.9922 | 66.5636 | 66.5636 | 130.9496 | 0.9 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 83.7272 | 35.9065 | 854575.3913 | 71.2146 | 71.2146 | 136.1676 | 1 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 86.0722 | 38.2516 | 910387.7903 | 75.8656 | 75.8656 | 141.3856 | 75 | 65 | 31.6654 | 32 | 64.3
8/28/20XX 11:00:00 AM | 0.45833 | 7 | 77.9 | 59.3 | 71.5134 | 86.1281 | 14.6147 | 50 | 77.9 |  | 77.9 | 85.105 | 0.1 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 64.87 | 17.0493 | 405774.2991 | 33.8145 | 33.8145 | 94.893 | 0.2 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 67.1183 | 19.2977 | 459284.7982 | 38.2737 | 38.2737 | 100.5807 | 0.3 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 69.3667 | 21.546 | 512795.2973 | 42.7329 | 42.7329 | 106.2684 | 0.4 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 71.615 | 23.7944 | 566305.7964 | 47.1921 | 47.1921 | 111.9561 | 0.5 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 73.8633 | 26.0427 | 619816.2955 | 51.6514 | 51.6514 | 117.6439 | 0.6 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 76.1117 | 28.291 | 673326.7946 | 56.1106 | 56.1106 | 123.3316 | 0.7 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 78.36 | 30.5394 | 726837.2937 | 60.5698 | 60.5698 | 129.0193 | 0.8 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 80.6084 | 32.7877 | 780347.7928 | 65.029 | 65.029 | 134.707 | 0.9 | 77.51 | 22.51 | 850878 | 70.9065 | 70.9065 | 82.8567 | 35.0361 | 833858.2919 | 69.4882 | 69.4882 | 140.3947 | 1 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 85.105 | 37.2844 | 887368.791 | 73.9474 | 73.9474 | 146.0824 | 80 | 60 | 32.0293 | 32 | 59.3
8/28/20XX 12:00:00 PM | 0.5 | 7 | 78.5 | 57.9 | 72.9711 | 87.8882 | 14.9171 | 50 | 78.5 |  | 78.5 | 84.7556 | 0.1 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 64.835 | 17.0144 | 404942.578 | 33.7452 | 33.7452 | 95.0127 | 0.2 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 67.0484 | 19.2278 | 457621.356 | 38.1351 | 38.1351 | 100.8201 | 0.3 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 69.2618 | 21.4412 | 510300.1339 | 42.525 | 42.525 | 106.6275 | 0.4 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 71.4752 | 23.6546 | 562978.9119 | 46.9149 | 46.9149 | 112.4349 | 0.5 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 73.6886 | 25.868 | 615657.6899 | 51.3048 | 51.3048 | 118.2423 | 0.6 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 75.902 | 28.0814 | 668336.4679 | 55.6947 | 55.6947 | 124.0497 | 0.7 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 78.1154 | 30.2948 | 721015.2458 | 60.0846 | 60.0846 | 129.8571 | 0.8 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 80.3288 | 32.5082 | 773694.0238 | 64.4745 | 64.4745 | 135.6645 | 0.9 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 82.5422 | 34.7215 | 826372.8018 | 68.8644 | 68.8644 | 141.4719 | 1 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 84.7556 | 36.9349 | 879051.5798 | 73.2543 | 73.2543 | 147.2793 | 80 | 60 | 32.1218 | 32 | 57.9
8/28/20XX 1:00:00 PM | 0.54167 | 7 | 79.3 | 53.9 | 74.9531 | 90.2816 | 15.3285 | 50 | 79.3 |  | 79.3 | 80.9312 | 0.1 | 74.53 | 19.53 | 738234 | 61.5195 | 61.5195 | 64.4526 | 16.632 | 395840.498 | 32.9867 | 32.9867 | 94.5062 | 0.2 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 66.2835 | 18.4629 | 439417.196 | 36.6181 | 36.6181 | 99.8071 | 0.3 | 75.59 | 20.59 | 778302 | 64.8585 | 64.8585 | 68.1145 | 20.2939 | 482993.8941 | 40.2495 | 40.2495 | 105.108 | 0.4 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 69.9454 | 22.1248 | 526570.5921 | 43.8809 | 43.8809 | 110.4089 | 0.5 | 76.65 | 21.65 | 818370 | 68.1975 | 68.1975 | 71.7764 | 23.9558 | 570147.2901 | 47.5123 | 47.5123 | 115.7098 | 0.6 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 73.6074 | 25.7867 | 613723.9881 | 51.1437 | 51.1437 | 121.0107 | 0.7 | 77.71 | 22.71 | 858438 | 71.5365 | 71.5365 | 75.4383 | 27.6177 | 657300.6861 | 54.7751 | 54.7751 | 126.3116 | 0.8 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 77.2693 | 29.4486 | 700877.3842 | 58.4064 | 58.4064 | 131.6124 | 0.9 | 78.77 | 23.77 | 898506 | 74.8755 | 74.8755 | 79.1002 | 31.2796 | 744454.0822 | 62.0378 | 62.0378 | 136.9133 | 1 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 80.9312 | 33.1105 | 788030.7802 | 65.6692 | 65.6692 | 142.2142 | 80 | 55 | 31.7186 | 32 | 53.9
8/28/20XX 2:00:00 PM | 0.58333 | 7 | 79.3 | 52.9 | 74.9531 | 90.2816 | 15.3285 | 50 | 79.3 |  | 79.3 | 79.3983 | 0.1 | 74.53 | 19.53 | 738234 | 61.5195 | 61.5195 | 64.2993 | 16.4787 | 392192.3157 | 32.6827 | 32.6827 | 94.2022 | 0.2 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 65.977 | 18.1563 | 432120.8313 | 36.0101 | 36.0101 | 99.1991 | 0.3 | 75.59 | 20.59 | 778302 | 64.8585 | 64.8585 | 67.6546 | 19.834 | 472049.347 | 39.3374 | 39.3374 | 104.1959 | 0.4 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 69.3323 | 21.5117 | 511977.8626 | 42.6648 | 42.6648 | 109.1928 | 0.5 | 76.65 | 21.65 | 818370 | 68.1975 | 68.1975 | 71.01 | 23.1893 | 551906.3783 | 45.9922 | 45.9922 | 114.1897 | 0.6 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 72.6876 | 24.867 | 591834.8939 | 49.3196 | 49.3196 | 119.1866 | 0.7 | 77.71 | 22.71 | 858438 | 71.5365 | 71.5365 | 74.3653 | 26.5447 | 631763.4096 | 52.647 | 52.647 | 124.1835 | 0.8 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 76.043 | 28.2223 | 671691.9253 | 55.9743 | 55.9743 | 129.1803 | 0.9 | 78.77 | 23.77 | 898506 | 74.8755 | 74.8755 | 77.7207 | 29.9 | 711620.4409 | 59.3017 | 59.3017 | 134.1772 | 1 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 79.3983 | 31.5777 | 751548.9566 | 62.6291 | 62.6291 | 139.1741 | 80 | 55 | 31.4783 | 32 | 52.9
8/28/20XX 3:00:00 PM | 0.625 | 7 | 78.8 | 52.7 | 73.7091 | 88.7794 | 15.0703 | 50 | 78.8 |  | 78.8 | 77.7781 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 64.1373 | 16.3166 | 388336.2381 | 32.3614 | 32.3614 | 93.7234 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 65.6529 | 17.8323 | 424408.6762 | 35.3674 | 35.3674 | 98.2414 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 67.1686 | 19.3479 | 460481.1143 | 38.3734 | 38.3734 | 102.7594 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 68.6842 | 20.8636 | 496553.5524 | 41.3795 | 41.3795 | 107.2775 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 70.1999 | 22.3792 | 532625.9905 | 44.3855 | 44.3855 | 111.7955 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 71.7155 | 23.8949 | 568698.4287 | 47.3915 | 47.3915 | 116.3135 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 73.2312 | 25.4105 | 604770.8668 | 50.3976 | 50.3976 | 120.8316 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 74.7468 | 26.9262 | 640843.3049 | 53.4036 | 53.4036 | 125.3496 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 76.2625 | 28.4418 | 676915.743 | 56.4096 | 56.4096 | 129.8676 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 77.7781 | 29.9575 | 712988.1811 | 59.4157 | 59.4157 | 134.3857 | 80 | 55 | 31.1019 | 32 | 52.7
8/28/20XX 4:00:00 PM | 0.66667 | 7 | 78.3 | 53.7 | 72.4824 | 87.2982 | 14.8157 | 50 | 78.3 |  | 78.3 | 77.9643 | 0.1 | 74.43 | 19.43 | 734454 | 61.2045 | 61.2045 | 64.1559 | 16.3353 | 388779.2526 | 32.3983 | 32.3983 | 93.6028 | 0.2 | 74.86 | 19.86 | 750708 | 62.559 | 62.559 | 65.6902 | 17.8695 | 425294.7052 | 35.4412 | 35.4412 | 98.0002 | 0.3 | 75.29 | 20.29 | 766962 | 63.9135 | 63.9135 | 67.2244 | 19.4038 | 461810.1577 | 38.4842 | 38.4842 | 102.3977 | 0.4 | 75.72 | 20.72 | 783216 | 65.268 | 65.268 | 68.7587 | 20.9381 | 498325.6103 | 41.5271 | 41.5271 | 106.7951 | 0.5 | 76.15 | 21.15 | 799470 | 66.6225 | 66.6225 | 70.2929 | 22.4723 | 534841.0629 | 44.5701 | 44.5701 | 111.1926 | 0.6 | 76.58 | 21.58 | 815724 | 67.977 | 67.977 | 71.8272 | 24.0066 | 571356.5155 | 47.613 | 47.613 | 115.59 | 0.7 | 77.01 | 22.01 | 831978 | 69.3315 | 69.3315 | 73.3615 | 25.5408 | 607871.9681 | 50.656 | 50.656 | 119.9875 | 0.8 | 77.44 | 22.44 | 848232 | 70.686 | 70.686 | 74.8957 | 27.0751 | 644387.4207 | 53.699 | 53.699 | 124.385 | 0.9 | 77.87 | 22.87 | 864486 | 72.0405 | 72.0405 | 76.43 | 28.6094 | 680902.8732 | 56.7419 | 56.7419 | 128.7824 | 1 | 78.3 | 23.3 | 880740 | 73.395 | 73.395 | 77.9643 | 30.1436 | 717418.3258 | 59.7849 | 59.7849 | 133.1799 | 80 | 55 | 31.0086 | 32 | 53.7
8/28/20XX 5:00:00 PM | 0.70833 | 7 | 78 | 53 | 71.7546 | 86.4193 | 14.6647 | 50 | 78 |  | 78 | 76.154 | 0.1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 63.9749 | 16.1542 | 384470.9399 | 32.0392 | 32.0392 | 93.1492 | 0.2 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 65.3281 | 17.5075 | 416678.0798 | 34.7232 | 34.7232 | 97.0932 | 0.3 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 66.6814 | 18.8607 | 448885.2197 | 37.4071 | 37.4071 | 101.0371 | 0.4 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 68.0346 | 20.214 | 481092.3596 | 40.091 | 40.091 | 104.981 | 0.5 | 76 | 21 | 793800 | 66.15 | 66.15 | 69.3878 | 21.5672 | 513299.4995 | 42.775 | 42.775 | 108.925 | 0.6 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 70.7411 | 22.9204 | 545506.6394 | 45.4589 | 45.4589 | 112.8689 | 0.7 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 72.0943 | 24.2737 | 577713.7793 | 48.1428 | 48.1428 | 116.8128 | 0.8 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 73.4476 | 25.6269 | 609920.9191 | 50.8267 | 50.8267 | 120.7567 | 0.9 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 74.8008 | 26.9802 | 642128.059 | 53.5107 | 53.5107 | 124.7007 | 1 | 78 | 23 | 869400 | 72.45 | 72.45 | 76.154 | 28.3334 | 674335.1989 | 56.1946 | 56.1946 | 128.6446 | 80 | 55 | 30.6515 | 30 | 53
8/28/20XX 6:00:00 PM | 0.75 | 7 | 76.8 | 55.5 | 68.9041 | 82.9779 | 14.0738 | 50 | 76.8 |  | 76.8 | 76.6447 | 0.1 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 64.0239 | 16.2033 | 385638.6842 | 32.1366 | 32.1366 | 92.8686 | 0.2 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.4262 | 17.6056 | 419013.5684 | 34.9178 | 34.9178 | 96.5318 | 0.3 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 66.8286 | 19.0079 | 452388.4526 | 37.699 | 37.699 | 100.195 | 0.4 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 68.2309 | 20.4102 | 485763.3368 | 40.4803 | 40.4803 | 103.8583 | 0.5 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 69.6332 | 21.8125 | 519138.221 | 43.2615 | 43.2615 | 107.5215 | 0.6 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 71.0355 | 23.2148 | 552513.1051 | 46.0428 | 46.0428 | 111.1848 | 0.7 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 72.4378 | 24.6171 | 585887.9893 | 48.824 | 48.824 | 114.848 | 0.8 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 73.8401 | 26.0194 | 619262.8735 | 51.6052 | 51.6052 | 118.5112 | 0.9 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 75.2424 | 27.4218 | 652637.7577 | 54.3865 | 54.3865 | 122.1745 | 1 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 76.6447 | 28.8241 | 686012.6419 | 57.1677 | 57.1677 | 125.8377 | 75 | 55 | 30.4345 | 30 | 55.5
8/28/20XX 7:00:00 PM | 0.79167 | 7 | 75.7 | 58.6 | 66.3753 | 79.9253 | 13.55 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/28/20XX 8:00:00 PM | 0.83333 | 7 | 74.5 | 61.3 | 76.7042 | 89.7555 | 13.0512 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/28/20XX 9:00:00 PM | 0.875 | 7 | 73.6 | 62.9 | 74.3617 | 87.0056 | 12.6439 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/28/20XX 10:00:00 PM | 0.91667 | 7 | 72.7 | 65.1 | 72.0807 | 84.3281 | 12.2474 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/28/20XX 11:00:00 PM | 0.95833 | 7 | 72.2 | 65.8 | 70.8397 | 82.8715 | 12.0318 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/28/20XX 12:00:00 AM | 0 | 1 | 71.3 | 68.2 | 68.6524 | 80.3042 | 11.6518 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/29/20XX 1:00:00 AM | 0.041667 | 1 | 70.7 | 70 | 78.6313 | 90.1079 | 11.4766 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/29/20XX 2:00:00 AM | 0.083333 | 1 | 70.5 | 70.6 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/29/20XX 3:00:00 AM | 0.125 | 1 | 69.9 | 71.3 | 76.4479 | 87.5989 | 11.151 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/29/20XX 4:00:00 AM | 0.16667 | 1 | 69.7 | 72.5 | 75.9105 | 86.9813 | 11.0709 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/29/20XX 5:00:00 AM | 0.20833 | 1 | 68.9 | 74.1 | 73.7935 | 84.5492 | 10.7557 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/29/20XX 6:00:00 AM | 0.25 | 1 | 68.6 | 74.4 | 73.0131 | 83.6528 | 10.6396 | 70 | 68.6 |  | 68.6 | 77.6946 | 0.1 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 64.1289 | 16.3083 | 388137.3799 | 32.3448 | 32.3448 | 90.4938 | 0.2 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 65.6362 | 17.8156 | 424010.9598 | 35.3342 | 35.3342 | 91.7822 | 0.3 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 67.1435 | 19.3229 | 459884.5398 | 38.3237 | 38.3237 | 93.0707 | 0.4 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 68.6508 | 20.8302 | 495758.1197 | 41.3132 | 41.3132 | 94.3592 | 0.5 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 70.1581 | 22.3375 | 531631.6996 | 44.3026 | 44.3026 | 95.6476 | 0.6 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 71.6654 | 23.8448 | 567505.2795 | 47.2921 | 47.2921 | 96.9361 | 0.7 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 73.1727 | 25.3521 | 603378.8595 | 50.2816 | 50.2816 | 98.2246 | 0.8 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 74.68 | 26.8593 | 639252.4394 | 53.271 | 53.271 | 99.513 | 0.9 | 69.14 | 14.14 | 534492 | 44.541 | 44.541 | 76.1873 | 28.3666 | 675126.0193 | 56.2605 | 56.2605 | 100.8015 | 1 | 68.6 | 13.6 | 514080 | 42.84 | 42.84 | 77.6946 | 29.8739 | 710999.5992 | 59.25 | 59.25 | 102.09 | 70 | 75 | 28.5905 | 28 | 74.4
8/29/20XX 7:00:00 AM | 0.29167 | 1 | 69.7 | 72.4 | 75.9105 | 86.9813 | 11.0709 | 70 | 69.7 |  | 69.7 | 78.5675 | 0.1 | 73.57 | 18.57 | 701946 | 58.4955 | 58.4955 | 64.2162 | 16.3956 | 390214.894 | 32.5179 | 32.5179 | 91.0134 | 0.2 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 65.8108 | 17.9902 | 428165.988 | 35.6805 | 35.6805 | 92.8215 | 0.3 | 72.71 | 17.71 | 669438 | 55.7865 | 55.7865 | 67.4054 | 19.5848 | 466117.0821 | 38.8431 | 38.8431 | 94.6296 | 0.4 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 69 | 21.1793 | 504068.1761 | 42.0057 | 42.0057 | 96.4377 | 0.5 | 71.85 | 16.85 | 636930 | 53.0775 | 53.0775 | 70.5946 | 22.7739 | 542019.2701 | 45.1683 | 45.1683 | 98.2458 | 0.6 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 72.1891 | 24.3685 | 579970.3641 | 48.3309 | 48.3309 | 100.0539 | 0.7 | 70.99 | 15.99 | 604422 | 50.3685 | 50.3685 | 73.7837 | 25.9631 | 617921.4581 | 51.4935 | 51.4935 | 101.862 | 0.8 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 75.3783 | 27.5577 | 655872.5522 | 54.656 | 54.656 | 103.67 | 0.9 | 70.13 | 15.13 | 571914 | 47.6595 | 47.6595 | 76.9729 | 29.1523 | 693823.6462 | 57.8186 | 57.8186 | 105.4781 | 1 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 78.5675 | 30.7468 | 731774.7402 | 60.9812 | 60.9812 | 107.2862 | 70 | 70 | 28.9962 | 28 | 72.4
8/29/20XX 8:00:00 AM | 0.33333 | 1 | 71.1 | 69.1 | 68.1744 | 79.7432 | 11.5688 | 60 | 71.1 |  | 71.1 | 78.702 | 0.1 | 73.71 | 18.71 | 707238 | 58.9365 | 58.9365 | 64.2297 | 16.409 | 390535.0369 | 32.5446 | 32.5446 | 91.4811 | 0.2 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 65.8377 | 18.0171 | 428806.2739 | 35.7339 | 35.7339 | 93.7569 | 0.3 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 67.4457 | 19.6251 | 467077.5108 | 38.9231 | 38.9231 | 96.0326 | 0.4 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 69.0538 | 21.2331 | 505348.7478 | 42.1124 | 42.1124 | 98.3084 | 0.5 | 72.55 | 17.55 | 663390 | 55.2825 | 55.2825 | 70.6618 | 22.8412 | 543619.9847 | 45.3017 | 45.3017 | 100.5842 | 0.6 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 72.2698 | 24.4492 | 581891.2216 | 48.4909 | 48.4909 | 102.8599 | 0.7 | 71.97 | 16.97 | 641466 | 53.4555 | 53.4555 | 73.8779 | 26.0572 | 620162.4586 | 51.6802 | 51.6802 | 105.1357 | 0.8 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 75.4859 | 27.6653 | 658433.6955 | 54.8695 | 54.8695 | 107.4115 | 0.9 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 77.0939 | 29.2733 | 696704.9325 | 58.0587 | 58.0587 | 109.6872 | 1 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 78.702 | 30.8814 | 734976.1694 | 61.248 | 61.248 | 111.963 | 70 | 70 | 29.3602 | 30 | 69.1
8/29/20XX 9:00:00 AM | 0.375 | 1 | 73 | 65.6 | 72.8342 | 85.2126 | 12.3784 | 60 | 73 |  | 73 | 79.7661 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.3361 | 16.5155 | 393067.7191 | 32.7556 | 32.7556 | 92.2906 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 66.0505 | 18.2299 | 433871.6381 | 36.156 | 36.156 | 95.376 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 67.765 | 19.9444 | 474675.5572 | 39.5563 | 39.5563 | 98.4613 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 69.4794 | 21.6588 | 515479.4762 | 42.9566 | 42.9566 | 101.5466 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 71.1939 | 23.3733 | 556283.3953 | 46.3569 | 46.3569 | 104.6319 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 72.9083 | 25.0877 | 597087.3143 | 49.7573 | 49.7573 | 107.7173 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 74.6228 | 26.8022 | 637891.2334 | 53.1576 | 53.1576 | 110.8026 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 76.3372 | 28.5166 | 678695.1524 | 56.5579 | 56.5579 | 113.8879 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 78.0517 | 30.2311 | 719499.0715 | 59.9583 | 59.9583 | 116.9733 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 79.7661 | 31.9455 | 760302.9905 | 63.3586 | 63.3586 | 120.0586 | 75 | 65 | 29.9921 | 30 | 65.6
8/29/20XX 10:00:00 AM | 0.41667 | 1 | 75.5 | 59.9 | 65.924 | 79.3806 | 13.4566 | 50 | 75.5 |  | 75.5 | 79.2461 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 64.2841 | 16.4634 | 391829.9233 | 32.6525 | 32.6525 | 92.975 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 65.9465 | 18.1259 | 431396.0467 | 35.9497 | 35.9497 | 96.7447 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 67.609 | 19.7883 | 470962.17 | 39.2468 | 39.2468 | 100.5143 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 69.2714 | 21.4508 | 510528.2933 | 42.544 | 42.544 | 104.284 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 70.9338 | 23.1132 | 550094.4167 | 45.8412 | 45.8412 | 108.0537 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 72.5963 | 24.7757 | 589660.54 | 49.1384 | 49.1384 | 111.8234 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 74.2587 | 26.4381 | 629226.6633 | 52.4356 | 52.4356 | 115.5931 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 75.9212 | 28.1005 | 668792.7867 | 55.7327 | 55.7327 | 119.3627 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 77.5836 | 29.763 | 708358.91 | 59.0299 | 59.0299 | 123.1324 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 79.2461 | 31.4254 | 747925.0333 | 62.3271 | 62.3271 | 126.9021 | 75 | 60 | 30.5233 | 30 | 59.9
8/29/20XX 11:00:00 AM | 0.45833 | 1 | 77.5 | 54.8 | 70.5552 | 84.9711 | 14.416 | 50 | 77.5 |  | 77.5 | 77.4748 | 0.1 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 64.107 | 16.2863 | 387614.3951 | 32.3012 | 32.3012 | 93.2537 | 0.2 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 65.5923 | 17.7716 | 422964.9902 | 35.2471 | 35.2471 | 97.3021 | 0.3 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 67.0776 | 19.257 | 458315.5853 | 38.193 | 38.193 | 101.3505 | 0.4 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 68.5629 | 20.7423 | 493666.1804 | 41.1388 | 41.1388 | 105.3988 | 0.5 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 70.0482 | 22.2276 | 529016.7755 | 44.0847 | 44.0847 | 109.4472 | 0.6 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 71.5335 | 23.7129 | 564367.3706 | 47.0306 | 47.0306 | 113.4956 | 0.7 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 73.0189 | 25.1982 | 599717.9656 | 49.9765 | 49.9765 | 117.544 | 0.8 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 74.5042 | 26.6836 | 635068.5607 | 52.9224 | 52.9224 | 121.5924 | 0.9 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 75.9895 | 28.1689 | 670419.1558 | 55.8683 | 55.8683 | 125.6408 | 1 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 77.4748 | 29.6542 | 705769.7509 | 58.8141 | 58.8141 | 129.6891 | 75 | 55 | 30.7359 | 30 | 54.8
8/29/20XX 12:00:00 PM | 0.5 | 1 | 79.1 | 53.4 | 74.4534 | 89.6782 | 15.2248 | 50 | 79.1 |  | 79.1 | 79.6298 | 0.1 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 64.3225 | 16.5018 | 392743.3257 | 32.7286 | 32.7286 | 94.1851 | 0.2 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 66.0233 | 18.2026 | 433222.8514 | 36.1019 | 36.1019 | 99.1649 | 0.3 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 67.7241 | 19.9035 | 473702.3772 | 39.4752 | 39.4752 | 104.1447 | 0.4 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 69.4249 | 21.6043 | 514181.9029 | 42.8485 | 42.8485 | 109.1245 | 0.5 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 71.1257 | 23.3051 | 554661.4286 | 46.2218 | 46.2218 | 114.1043 | 0.6 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 72.8266 | 25.0059 | 595140.9543 | 49.5951 | 49.5951 | 119.0841 | 0.7 | 77.57 | 22.57 | 853146 | 71.0955 | 71.0955 | 74.5274 | 26.7067 | 635620.4801 | 52.9684 | 52.9684 | 124.0639 | 0.8 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 76.2282 | 28.4076 | 676100.0058 | 56.3417 | 56.3417 | 129.0437 | 0.9 | 78.59 | 23.59 | 891702 | 74.3085 | 74.3085 | 77.929 | 30.1084 | 716579.5315 | 59.715 | 59.715 | 134.0235 | 1 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 79.6298 | 31.8092 | 757059.0572 | 63.0883 | 63.0883 | 139.0033 | 80 | 55 | 31.4656 | 32 | 53.4
8/29/20XX 1:00:00 PM | 0.54167 | 1 | 79.9 | 50.6 | 76.4687 | 92.1119 | 15.6433 | 50 | 79.9 |  | 79.9 | 77.4073 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 64.1002 | 16.2796 | 387453.6018 | 32.2878 | 32.2878 | 93.9963 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 65.5788 | 17.7581 | 422643.4035 | 35.2203 | 35.2203 | 98.7873 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 67.0573 | 19.2367 | 457833.2053 | 38.1528 | 38.1528 | 103.5783 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 68.5359 | 20.7153 | 493023.0071 | 41.0853 | 41.0853 | 108.3693 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 70.0144 | 22.1938 | 528212.8089 | 44.0177 | 44.0177 | 113.1602 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 71.493 | 23.6724 | 563402.6106 | 46.9502 | 46.9502 | 117.9512 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 72.9716 | 25.1509 | 598592.4124 | 49.8827 | 49.8827 | 122.7422 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 74.4501 | 26.6295 | 633782.2142 | 52.8152 | 52.8152 | 127.5332 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 75.9287 | 28.1081 | 668972.016 | 55.7477 | 55.7477 | 132.3242 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 77.4073 | 29.5866 | 704161.8177 | 58.6802 | 58.6802 | 137.1152 | 80 | 50 | 31.3132 | 32 | 50.6
8/29/20XX 2:00:00 PM | 0.58333 | 1 | 80.5 | 49.8 | 62.1659 | 78.0095 | 15.8436 | 40 | 80.5 |  | 80.5 | 77.6927 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 64.1287 | 16.3081 | 388132.8306 | 32.3444 | 32.3444 | 94.2419 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 65.6358 | 17.8152 | 424001.8611 | 35.3335 | 35.3335 | 99.2785 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 67.1429 | 19.3223 | 459870.8917 | 38.3226 | 38.3226 | 104.3151 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 68.65 | 20.8294 | 495739.9222 | 41.3117 | 41.3117 | 109.3517 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 70.1571 | 22.3365 | 531608.9528 | 44.3007 | 44.3007 | 114.3882 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 71.6642 | 23.8436 | 567477.9834 | 47.2898 | 47.2898 | 119.4248 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 73.1713 | 25.3507 | 603347.0139 | 50.2789 | 50.2789 | 124.4614 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 74.6784 | 26.8578 | 639216.0445 | 53.268 | 53.268 | 129.498 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 76.1856 | 28.3649 | 675085.075 | 56.2571 | 56.2571 | 134.5346 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 77.6927 | 29.872 | 710954.1056 | 59.2462 | 59.2462 | 139.5712 | 80 | 50 | 31.5049 | 32 | 49.8
8/29/20XX 3:00:00 PM | 0.625 | 1 | 80.5 | 50.3 | 78.0095 | 93.973 | 15.9635 | 50 | 80.5 |  | 80.5 | 78.4884 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 64.2083 | 16.3877 | 390026.7764 | 32.5022 | 32.5022 | 94.3997 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 65.795 | 17.9744 | 427789.7529 | 35.6491 | 35.6491 | 99.5941 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 67.3817 | 19.561 | 465552.7293 | 38.7961 | 38.7961 | 104.7886 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 68.9684 | 21.1477 | 503315.7057 | 41.943 | 41.943 | 109.983 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 70.555 | 22.7344 | 541078.6821 | 45.0899 | 45.0899 | 115.1774 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 72.1417 | 24.3211 | 578841.6586 | 48.2368 | 48.2368 | 120.3718 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 73.7284 | 25.9078 | 616604.635 | 51.3837 | 51.3837 | 125.5662 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 75.3151 | 27.4944 | 654367.6114 | 54.5306 | 54.5306 | 130.7606 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 76.9017 | 29.0811 | 692130.5879 | 57.6775 | 57.6775 | 135.955 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 78.4884 | 30.6678 | 729893.5643 | 60.8245 | 60.8245 | 141.1495 | 80 | 50 | 31.6297 | 32 | 50.3
8/29/20XX 4:00:00 PM | 0.66667 | 1 | 79.7 | 52.5 | 75.9607 | 91.4984 | 15.5378 | 50 | 79.7 |  | 79.7 | 79.8451 | 0.1 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 64.344 | 16.5233 | 393255.6743 | 32.7713 | 32.7713 | 94.4168 | 0.2 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 66.0663 | 18.2457 | 434247.5487 | 36.1873 | 36.1873 | 99.6283 | 0.3 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 67.7887 | 19.968 | 475239.423 | 39.6033 | 39.6033 | 104.8398 | 0.4 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 69.511 | 21.6904 | 516231.2973 | 43.0193 | 43.0193 | 110.0513 | 0.5 | 76.85 | 21.85 | 825930 | 68.8275 | 68.8275 | 71.2334 | 23.4127 | 557223.1717 | 46.4353 | 46.4353 | 115.2628 | 0.6 | 77.42 | 22.42 | 847476 | 70.623 | 70.623 | 72.9557 | 25.1351 | 598215.046 | 49.8513 | 49.8513 | 120.4743 | 0.7 | 77.99 | 22.99 | 869022 | 72.4185 | 72.4185 | 74.6781 | 26.8574 | 639206.9204 | 53.2672 | 53.2672 | 125.6857 | 0.8 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 76.4004 | 28.5798 | 680198.7947 | 56.6832 | 56.6832 | 130.8972 | 0.9 | 79.13 | 24.13 | 912114 | 76.0095 | 76.0095 | 78.1228 | 30.3021 | 721190.669 | 60.0992 | 60.0992 | 136.1087 | 1 | 79.7 | 24.7 | 933660 | 77.805 | 77.805 | 79.8451 | 32.0245 | 762182.5434 | 63.5152 | 63.5152 | 141.3202 | 80 | 50 | 31.6464 | 32 | 52.5
8/29/20XX 5:00:00 PM | 0.70833 | 1 | 78.5 | 53.1 | 72.9711 | 87.8882 | 14.9171 | 50 | 78.5 |  | 78.5 | 77.5954 | 0.1 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 64.119 | 16.2984 | 387901.2967 | 32.3251 | 32.3251 | 93.5926 | 0.2 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 65.6164 | 17.7957 | 423538.7935 | 35.2949 | 35.2949 | 97.9799 | 0.3 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 67.1138 | 19.2931 | 459176.2902 | 38.2647 | 38.2647 | 102.3672 | 0.4 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 68.6111 | 20.7905 | 494813.787 | 41.2345 | 41.2345 | 106.7545 | 0.5 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 70.1085 | 22.2879 | 530451.2837 | 44.2043 | 44.2043 | 111.1418 | 0.6 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 71.6059 | 23.7852 | 566088.7805 | 47.1741 | 47.1741 | 115.5291 | 0.7 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 73.1032 | 25.2826 | 601726.2772 | 50.1439 | 50.1439 | 119.9164 | 0.8 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 74.6006 | 26.78 | 637363.774 | 53.1136 | 53.1136 | 124.3036 | 0.9 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 76.098 | 28.2774 | 673001.2707 | 56.0834 | 56.0834 | 128.6909 | 1 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 77.5954 | 29.7747 | 708638.7674 | 59.0532 | 59.0532 | 133.0782 | 80 | 55 | 30.9997 | 30 | 53.1
8/29/20XX 6:00:00 PM | 0.75 | 1 | 77.4 | 54.2 | 70.3173 | 84.6839 | 14.3667 | 50 | 77.4 |  | 77.4 | 76.3513 | 0.1 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 63.9946 | 16.174 | 384940.3634 | 32.0784 | 32.0784 | 92.9994 | 0.2 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 65.3676 | 17.5469 | 417616.9269 | 34.8014 | 34.8014 | 96.7934 | 0.3 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 66.7405 | 18.9199 | 450293.4903 | 37.5245 | 37.5245 | 100.5875 | 0.4 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 68.1135 | 20.2929 | 482970.0537 | 40.2475 | 40.2475 | 104.3815 | 0.5 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 69.4865 | 21.6658 | 515646.6171 | 42.9706 | 42.9706 | 108.1756 | 0.6 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 70.8594 | 23.0388 | 548323.1806 | 45.6936 | 45.6936 | 111.9696 | 0.7 | 76.38 | 21.38 | 808164 | 67.347 | 67.347 | 72.2324 | 24.4118 | 580999.744 | 48.4166 | 48.4166 | 115.7636 | 0.8 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 73.6054 | 25.7847 | 613676.3074 | 51.1397 | 51.1397 | 119.5577 | 0.9 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 74.9783 | 27.1577 | 646352.8709 | 53.8627 | 53.8627 | 123.3517 | 1 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 76.3513 | 28.5306 | 679029.4343 | 56.5858 | 56.5858 | 127.1458 | 75 | 55 | 30.5355 | 30 | 54.2
8/29/20XX 7:00:00 PM | 0.79167 | 1 | 75.9 | 57 | 66.8292 | 80.4731 | 13.644 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/29/20XX 8:00:00 PM | 0.83333 | 1 | 74.7 | 60.8 | 77.2333 | 90.3765 | 13.1432 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/29/20XX 9:00:00 PM | 0.875 | 1 | 73.8 | 61.2 | 74.8769 | 87.6104 | 12.7335 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/29/20XX 10:00:00 PM | 0.91667 | 1 | 73.4 | 62.7 | 73.8495 | 86.4044 | 12.5549 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/29/20XX 11:00:00 PM | 0.95833 | 1 | 72 | 65.7 | 70.3485 | 82.2949 | 11.9464 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/29/20XX 12:00:00 AM | 0 | 2 | 71.4 | 67.7 | 68.8925 | 80.586 | 11.6935 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/30/20XX 1:00:00 AM | 0.041667 | 2 | 70.4 | 69.8 | 66.524 | 77.8062 | 11.2822 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/30/20XX 2:00:00 AM | 0.083333 | 2 | 70.3 | 70 | 77.5329 | 88.8456 | 11.3127 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/30/20XX 3:00:00 AM | 0.125 | 2 | 69.4 | 73.1 | 75.1104 | 86.0621 | 10.9517 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/30/20XX 4:00:00 AM | 0.16667 | 2 | 69.1 | 73 | 74.3178 | 85.1515 | 10.8337 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/30/20XX 5:00:00 AM | 0.20833 | 2 | 68.6 | 74.7 | 73.0131 | 83.6528 | 10.6396 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/30/20XX 6:00:00 AM | 0.25 | 2 | 68.1 | 76.8 | 71.7287 | 82.1774 | 10.4487 | 70 | 68.1 |  | 68.1 | 78.8338 | 0.1 | 73.41 | 18.41 | 695898 | 57.9915 | 57.9915 | 64.2428 | 16.4222 | 390848.7615 | 32.5707 | 32.5707 | 90.5622 | 0.2 | 72.82 | 17.82 | 673596 | 56.133 | 56.133 | 65.8641 | 18.0434 | 429433.723 | 35.7861 | 35.7861 | 91.9191 | 0.3 | 72.23 | 17.23 | 651294 | 54.2745 | 54.2745 | 67.4853 | 19.6647 | 468018.6846 | 39.0016 | 39.0016 | 93.2761 | 0.4 | 71.64 | 16.64 | 628992 | 52.416 | 52.416 | 69.1065 | 21.2859 | 506603.6461 | 42.217 | 42.217 | 94.633 | 0.5 | 71.05 | 16.05 | 606690 | 50.5575 | 50.5575 | 70.7277 | 22.9071 | 545188.6076 | 45.4324 | 45.4324 | 95.9899 | 0.6 | 70.46 | 15.46 | 584388 | 48.699 | 48.699 | 72.3489 | 24.5283 | 583773.5691 | 48.6478 | 48.6478 | 97.3468 | 0.7 | 69.87 | 14.87 | 562086 | 46.8405 | 46.8405 | 73.9702 | 26.1495 | 622358.5306 | 51.8632 | 51.8632 | 98.7037 | 0.8 | 69.28 | 14.28 | 539784 | 44.982 | 44.982 | 75.5914 | 27.7707 | 660943.4922 | 55.0786 | 55.0786 | 100.0606 | 0.9 | 68.69 | 13.69 | 517482 | 43.1235 | 43.1235 | 77.2126 | 29.392 | 699528.4537 | 58.294 | 58.294 | 101.4175 | 1 | 68.1 | 13.1 | 495180 | 41.265 | 41.265 | 78.8338 | 31.0132 | 738113.4152 | 61.5095 | 61.5095 | 102.7745 | 70 | 75 | 28.6458 | 28 | 76.8
8/30/20XX 7:00:00 AM | 0.29167 | 2 | 69.3 | 73.1 | 74.8454 | 85.7577 | 10.9122 | 70 | 69.3 |  | 69.3 | 78.2282 | 0.1 | 73.53 | 18.53 | 700434 | 58.3695 | 58.3695 | 64.1823 | 16.3617 | 389407.4534 | 32.4506 | 32.4506 | 90.8201 | 0.2 | 73.06 | 18.06 | 682668 | 56.889 | 56.889 | 65.7429 | 17.9223 | 426551.1068 | 35.5459 | 35.5459 | 92.4349 | 0.3 | 72.59 | 17.59 | 664902 | 55.4085 | 55.4085 | 67.3036 | 19.483 | 463694.7602 | 38.6412 | 38.6412 | 94.0497 | 0.4 | 72.12 | 17.12 | 647136 | 53.928 | 53.928 | 68.8643 | 21.0436 | 500838.4136 | 41.7365 | 41.7365 | 95.6645 | 0.5 | 71.65 | 16.65 | 629370 | 52.4475 | 52.4475 | 70.4249 | 22.6043 | 537982.067 | 44.8318 | 44.8318 | 97.2793 | 0.6 | 71.18 | 16.18 | 611604 | 50.967 | 50.967 | 71.9856 | 24.1649 | 575125.7204 | 47.9271 | 47.9271 | 98.8941 | 0.7 | 70.71 | 15.71 | 593838 | 49.4865 | 49.4865 | 73.5462 | 25.7256 | 612269.3738 | 51.0224 | 51.0224 | 100.5089 | 0.8 | 70.24 | 15.24 | 576072 | 48.006 | 48.006 | 75.1069 | 27.2863 | 649413.0271 | 54.1178 | 54.1178 | 102.1238 | 0.9 | 69.77 | 14.77 | 558306 | 46.5255 | 46.5255 | 76.6676 | 28.8469 | 686556.6805 | 57.2131 | 57.2131 | 103.7386 | 1 | 69.3 | 14.3 | 540540 | 45.045 | 45.045 | 78.2282 | 30.4076 | 723700.3339 | 60.3084 | 60.3084 | 105.3534 | 70 | 75 | 28.8452 | 28 | 73.1
8/30/20XX 8:00:00 AM | 0.33333 | 2 | 71.1 | 68.4 | 68.1744 | 79.7432 | 11.5688 | 60 | 71.1 |  | 71.1 | 77.8922 | 0.1 | 73.71 | 18.71 | 707238 | 58.9365 | 58.9365 | 64.1487 | 16.3281 | 388607.6755 | 32.384 | 32.384 | 91.3205 | 0.2 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 65.6757 | 17.8551 | 424951.5509 | 35.4126 | 35.4126 | 93.4356 | 0.3 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 67.2028 | 19.3822 | 461295.4264 | 38.4413 | 38.4413 | 95.5508 | 0.4 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 68.7298 | 20.9092 | 497639.3019 | 41.4699 | 41.4699 | 97.6659 | 0.5 | 72.55 | 17.55 | 663390 | 55.2825 | 55.2825 | 70.2569 | 22.4363 | 533983.1774 | 44.4986 | 44.4986 | 99.7811 | 0.6 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 71.784 | 23.9633 | 570327.0528 | 47.5273 | 47.5273 | 101.8963 | 0.7 | 71.97 | 16.97 | 641466 | 53.4555 | 53.4555 | 73.311 | 25.4904 | 606670.9283 | 50.5559 | 50.5559 | 104.0114 | 0.8 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 74.8381 | 27.0174 | 643014.8038 | 53.5846 | 53.5846 | 106.1266 | 0.9 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 76.3651 | 28.5445 | 679358.6792 | 56.6132 | 56.6132 | 108.2417 | 1 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 77.8922 | 30.0715 | 715702.5547 | 59.6419 | 59.6419 | 110.3569 | 70 | 70 | 29.2337 | 30 | 68.4
8/30/20XX 9:00:00 AM | 0.375 | 2 | 73.3 | 62.8 | 73.5946 | 86.1051 | 12.5105 | 60 | 73.3 |  | 73.3 | 77.0975 | 0.1 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 64.0692 | 16.2486 | 386716.3794 | 32.2264 | 32.2264 | 91.8559 | 0.2 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 65.5168 | 17.6962 | 421168.9587 | 35.0974 | 35.0974 | 94.5064 | 0.3 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 66.9644 | 19.1438 | 455621.5381 | 37.9685 | 37.9685 | 97.157 | 0.4 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 68.412 | 20.5913 | 490074.1174 | 40.8395 | 40.8395 | 99.8075 | 0.5 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 69.8596 | 22.0389 | 524526.6968 | 43.7106 | 43.7106 | 102.4581 | 0.6 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 71.3072 | 23.4865 | 558979.2761 | 46.5816 | 46.5816 | 105.1086 | 0.7 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 72.7547 | 24.9341 | 593431.8555 | 49.4527 | 49.4527 | 107.7592 | 0.8 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 74.2023 | 26.3817 | 627884.4348 | 52.3237 | 52.3237 | 110.4097 | 0.9 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 75.6499 | 27.8293 | 662337.0142 | 55.1948 | 55.1948 | 113.0603 | 1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 77.0975 | 29.2769 | 696789.5936 | 58.0658 | 58.0658 | 115.7108 | 75 | 65 | 29.6483 | 30 | 62.8
8/30/20XX 10:00:00 AM | 0.41667 | 2 | 76.4 | 56.6 | 67.9753 | 81.8567 | 13.8813 | 50 | 76.4 |  | 76.4 | 77.137 | 0.1 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 64.0732 | 16.2525 | 386810.3976 | 32.2342 | 32.2342 | 92.8402 | 0.2 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 65.5247 | 17.7041 | 421356.9952 | 35.1131 | 35.1131 | 96.4751 | 0.3 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 66.9762 | 19.1556 | 455903.5929 | 37.992 | 37.992 | 100.11 | 0.4 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 68.4278 | 20.6072 | 490450.1905 | 40.8708 | 40.8708 | 103.7448 | 0.5 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 69.8793 | 22.0587 | 524996.7881 | 43.7497 | 43.7497 | 107.3797 | 0.6 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 71.3309 | 23.5102 | 559543.3857 | 46.6286 | 46.6286 | 111.0146 | 0.7 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 72.7824 | 24.9618 | 594089.9833 | 49.5075 | 49.5075 | 114.6495 | 0.8 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 74.2339 | 26.4133 | 628636.5809 | 52.3864 | 52.3864 | 118.2844 | 0.9 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 75.6855 | 27.8648 | 663183.1786 | 55.2653 | 55.2653 | 121.9193 | 1 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 77.137 | 29.3164 | 697729.7762 | 58.1441 | 58.1441 | 125.5541 | 75 | 55 | 30.4136 | 30 | 56.6
8/30/20XX 11:00:00 AM | 0.45833 | 2 | 79.2 | 51.4 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 76.8416 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 64.0436 | 16.223 | 386107.3417 | 32.1756 | 32.1756 | 93.6636 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 65.4656 | 17.645 | 419950.8833 | 34.9959 | 34.9959 | 98.1219 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 66.8876 | 19.067 | 453794.425 | 37.8162 | 37.8162 | 102.5802 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 68.3096 | 20.489 | 487637.9667 | 40.6365 | 40.6365 | 107.0385 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 69.7316 | 21.911 | 521481.5084 | 43.4568 | 43.4568 | 111.4968 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 71.1536 | 23.333 | 555325.05 | 46.2771 | 46.2771 | 115.9551 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 72.5756 | 24.755 | 589168.5917 | 49.0974 | 49.0974 | 120.4134 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 73.9976 | 26.177 | 623012.1334 | 51.9177 | 51.9177 | 124.8717 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 75.4196 | 27.599 | 656855.6751 | 54.738 | 54.738 | 129.33 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 76.8416 | 29.021 | 690699.2167 | 57.5583 | 57.5583 | 133.7883 | 80 | 50 | 31.053 | 32 | 51.4
8/30/20XX 12:00:00 PM | 0.5 | 2 | 81.2 | 47.1 | 63.6155 | 79.8394 | 16.2239 | 40 | 81.2 |  | 81.2 | 75.1345 | 0.1 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 63.8729 | 16.0523 | 382044.4314 | 31.837 | 31.837 | 93.955 | 0.2 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 65.1242 | 17.3036 | 411825.0629 | 34.3188 | 34.3188 | 98.7048 | 0.3 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 66.3755 | 18.5549 | 441605.6943 | 36.8005 | 36.8005 | 103.4545 | 0.4 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 67.6268 | 19.8061 | 471386.3258 | 39.2822 | 39.2822 | 108.2042 | 0.5 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 68.8781 | 21.0574 | 501166.9572 | 41.7639 | 41.7639 | 112.9539 | 0.6 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 70.1294 | 22.3087 | 530947.5887 | 44.2456 | 44.2456 | 117.7036 | 0.7 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 71.3806 | 23.56 | 560728.2201 | 46.7274 | 46.7274 | 122.4534 | 0.8 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 72.6319 | 24.8113 | 590508.8516 | 49.2091 | 49.2091 | 127.2031 | 0.9 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 73.8832 | 26.0626 | 620289.483 | 51.6908 | 51.6908 | 131.9528 | 1 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 75.1345 | 27.3139 | 650070.1145 | 54.1725 | 54.1725 | 136.7025 | 80 | 45 | 31.275 | 32 | 47.1
8/30/20XX 1:00:00 PM | 0.54167 | 2 | 82 | 44.4 | 65.3059 | 81.9738 | 16.6679 | 40 | 82 |  | 82 | 72.6398 | 0.1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 63.6234 | 15.8028 | 376107.0064 | 31.3423 | 31.3423 | 93.7123 | 0.2 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 64.6253 | 16.8046 | 399950.2129 | 33.3292 | 33.3292 | 98.2192 | 0.3 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 65.6271 | 17.8064 | 423793.4193 | 35.3161 | 35.3161 | 102.7261 | 0.4 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 66.6289 | 18.8083 | 447636.6258 | 37.3031 | 37.3031 | 107.2331 | 0.5 | 78 | 23 | 869400 | 72.45 | 72.45 | 67.6307 | 19.8101 | 471479.8322 | 39.29 | 39.29 | 111.74 | 0.6 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 68.6325 | 20.8119 | 495323.0387 | 41.2769 | 41.2769 | 116.2469 | 0.7 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 69.6343 | 21.8137 | 519166.2451 | 43.2639 | 43.2639 | 120.7539 | 0.8 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 70.6362 | 22.8155 | 543009.4516 | 45.2508 | 45.2508 | 125.2608 | 0.9 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 71.638 | 23.8173 | 566852.658 | 47.2377 | 47.2377 | 129.7677 | 1 | 82 | 27 | 1020600 | 85.05 | 85.05 | 72.6398 | 24.8192 | 590695.8644 | 49.2247 | 49.2247 | 134.2747 | 80 | 45 | 31.0793 | 32 | 44.4
8/30/20XX 2:00:00 PM | 0.58333 | 2 | 82.5 | 44.5 | 66.3809 | 83.3313 | 16.9504 | 40 | 82.5 |  | 82.5 | 74.0086 | 0.1 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 63.7603 | 15.9397 | 379364.7845 | 31.6137 | 31.6137 | 94.1412 | 0.2 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 64.899 | 17.0784 | 406465.7689 | 33.8721 | 33.8721 | 99.0771 | 0.3 | 76.55 | 21.55 | 814590 | 67.8825 | 67.8825 | 66.0377 | 18.2171 | 433566.7534 | 36.1306 | 36.1306 | 104.0131 | 0.4 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 67.1764 | 19.3558 | 460667.7379 | 38.389 | 38.389 | 108.949 | 0.5 | 78.25 | 23.25 | 878850 | 73.2375 | 73.2375 | 68.3151 | 20.4945 | 487768.7223 | 40.6474 | 40.6474 | 113.8849 | 0.6 | 79.1 | 24.1 | 910980 | 75.915 | 75.915 | 69.4538 | 21.6332 | 514869.7068 | 42.9058 | 42.9058 | 118.8208 | 0.7 | 79.95 | 24.95 | 943110 | 78.5925 | 78.5925 | 70.5925 | 22.7719 | 541970.6913 | 45.1642 | 45.1642 | 123.7567 | 0.8 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 71.7312 | 23.9106 | 569071.6757 | 47.4226 | 47.4226 | 128.6926 | 0.9 | 81.65 | 26.65 | 1007370 | 83.9475 | 83.9475 | 72.8699 | 25.0493 | 596172.6602 | 49.6811 | 49.6811 | 133.6286 | 1 | 82.5 | 27.5 | 1039500 | 86.625 | 86.625 | 74.0086 | 26.188 | 623273.6446 | 51.9395 | 51.9395 | 138.5645 | 80 | 45 | 31.4165 | 32 | 44.5
8/30/20XX 3:00:00 PM | 0.625 | 2 | 82.4 | 45.8 | 66.1648 | 83.0584 | 16.8936 | 40 | 82.4 |  | 82.4 | 75.9631 | 0.1 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 63.9558 | 16.1351 | 384016.3914 | 32.0014 | 32.0014 | 94.4974 | 0.2 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 65.2899 | 17.4693 | 415768.9828 | 34.6474 | 34.6474 | 99.7894 | 0.3 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 66.6241 | 18.8034 | 447521.5742 | 37.2935 | 37.2935 | 105.0815 | 0.4 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 67.9582 | 20.1376 | 479274.1655 | 39.9395 | 39.9395 | 110.3735 | 0.5 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 69.2923 | 21.4717 | 511026.7569 | 42.5856 | 42.5856 | 115.6656 | 0.6 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 70.6265 | 22.8059 | 542779.3483 | 45.2316 | 45.2316 | 120.9576 | 0.7 | 79.88 | 24.88 | 940464 | 78.372 | 78.372 | 71.9606 | 24.14 | 574531.9397 | 47.8777 | 47.8777 | 126.2497 | 0.8 | 80.72 | 25.72 | 972216 | 81.018 | 81.018 | 73.2948 | 25.4741 | 606284.5311 | 50.5237 | 50.5237 | 131.5417 | 0.9 | 81.56 | 26.56 | 1003968 | 83.664 | 83.664 | 74.6289 | 26.8083 | 638037.1225 | 53.1698 | 53.1698 | 136.8338 | 1 | 82.4 | 27.4 | 1035720 | 86.31 | 86.31 | 75.9631 | 28.1424 | 669789.7138 | 55.8158 | 55.8158 | 142.1258 | 80 | 45 | 31.6988 | 32 | 45.8
8/30/20XX 4:00:00 PM | 0.66667 | 2 | 81.8 | 47.1 | 64.8799 | 81.4359 | 16.556 | 40 | 81.8 |  | 81.8 | 76.6347 | 0.1 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 64.0229 | 16.2023 | 385614.7846 | 32.1346 | 32.1346 | 94.4416 | 0.2 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 65.4242 | 17.6036 | 418965.7693 | 34.9138 | 34.9138 | 99.6778 | 0.3 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 66.8255 | 19.0049 | 452316.7539 | 37.6931 | 37.6931 | 104.9141 | 0.4 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 68.2268 | 20.4062 | 485667.7386 | 40.4723 | 40.4723 | 110.1503 | 0.5 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 69.6281 | 21.8075 | 519018.7232 | 43.2516 | 43.2516 | 115.3866 | 0.6 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 71.0294 | 23.2088 | 552369.7078 | 46.0308 | 46.0308 | 120.6228 | 0.7 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 72.4307 | 24.6101 | 585720.6925 | 48.8101 | 48.8101 | 125.8591 | 0.8 | 80.24 | 25.24 | 954072 | 79.506 | 79.506 | 73.832 | 26.0114 | 619071.6771 | 51.5893 | 51.5893 | 131.0953 | 0.9 | 81.02 | 26.02 | 983556 | 81.963 | 81.963 | 75.2333 | 27.4127 | 652422.6617 | 54.3686 | 54.3686 | 136.3316 | 1 | 81.8 | 26.8 | 1013040 | 84.42 | 84.42 | 76.6347 | 28.814 | 685773.6464 | 57.1478 | 57.1478 | 141.5678 | 80 | 45 | 31.6573 | 32 | 47.1
8/30/20XX 5:00:00 PM | 0.70833 | 2 | 80.4 | 49.9 | 61.9611 | 77.751 | 15.7899 | 40 | 80.4 |  | 80.4 | 77.5931 | 0.1 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 64.1188 | 16.2981 | 387895.7806 | 32.3246 | 32.3246 | 94.1906 | 0.2 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 65.6159 | 17.7953 | 423527.7612 | 35.294 | 35.294 | 99.176 | 0.3 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 67.1131 | 19.2924 | 459159.7417 | 38.2633 | 38.2633 | 104.1613 | 0.4 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 68.6102 | 20.7896 | 494791.7223 | 41.2326 | 41.2326 | 109.1466 | 0.5 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 70.1073 | 22.2867 | 530423.7029 | 44.202 | 44.202 | 114.132 | 0.6 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 71.6045 | 23.7839 | 566055.6835 | 47.1713 | 47.1713 | 119.1173 | 0.7 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 73.1016 | 25.281 | 601687.6641 | 50.1406 | 50.1406 | 124.1026 | 0.8 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 74.5988 | 26.7781 | 637319.6446 | 53.11 | 53.11 | 129.088 | 0.9 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 76.0959 | 28.2753 | 672951.6252 | 56.0793 | 56.0793 | 134.0733 | 1 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 77.5931 | 29.7724 | 708583.6058 | 59.0486 | 59.0486 | 139.0586 | 80 | 50 | 31.4647 | 32 | 49.9
8/30/20XX 6:00:00 PM | 0.75 | 2 | 78.9 | 52.7 | 73.9565 | 89.0782 | 15.1216 | 50 | 78.9 |  | 78.9 | 78.0394 | 0.1 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 64.1634 | 16.3428 | 388958.049 | 32.4132 | 32.4132 | 93.8067 | 0.2 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 65.7052 | 17.8846 | 425652.2979 | 35.471 | 35.471 | 98.408 | 0.3 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 67.247 | 19.4263 | 462346.5469 | 38.5289 | 38.5289 | 103.0094 | 0.4 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 68.7887 | 20.9681 | 499040.7958 | 41.5867 | 41.5867 | 107.6107 | 0.5 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 70.3305 | 22.5099 | 535735.0448 | 44.6446 | 44.6446 | 112.2121 | 0.6 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 71.8723 | 24.0517 | 572429.2937 | 47.7024 | 47.7024 | 116.8134 | 0.7 | 77.43 | 22.43 | 847854 | 70.6545 | 70.6545 | 73.4141 | 25.5934 | 609123.5427 | 50.7603 | 50.7603 | 121.4148 | 0.8 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 74.9558 | 27.1352 | 645817.7916 | 53.8181 | 53.8181 | 126.0161 | 0.9 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 76.4976 | 28.677 | 682512.0406 | 56.876 | 56.876 | 130.6175 | 1 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 78.0394 | 30.2188 | 719206.2896 | 59.9339 | 59.9339 | 135.2189 | 80 | 55 | 31.1673 | 32 | 52.7
8/30/20XX 7:00:00 PM | 0.79167 | 2 | 77.7 | 53.7 | 71.0329 | 85.548 | 14.515 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/30/20XX 8:00:00 PM | 0.83333 | 2 | 77.1 | 55.4 | 69.6077 | 83.8273 | 14.2196 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/30/20XX 9:00:00 PM | 0.875 | 2 | 75.9 | 59.5 | 66.8292 | 80.4731 | 13.644 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/30/20XX 10:00:00 PM | 0.91667 | 2 | 74.8 | 63.2 | 77.499 | 90.6884 | 13.1894 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/30/20XX 11:00:00 PM | 0.95833 | 2 | 74.2 | 64.5 | 75.9165 | 88.8307 | 12.9142 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/30/20XX 12:00:00 AM | 0 | 3 | 73.8 | 65.5 | 74.8769 | 87.6104 | 12.7335 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/31/20XX 1:00:00 AM | 0.041667 | 3 | 73 | 67.8 | 72.8342 | 85.2126 | 12.3784 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/31/20XX 2:00:00 AM | 0.083333 | 3 | 72.6 | 68.9 | 71.831 | 84.035 | 12.204 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/31/20XX 3:00:00 AM | 0.125 | 3 | 71.9 | 71 | 82.008 | 93.989 | 11.9811 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/31/20XX 4:00:00 AM | 0.16667 | 3 | 71.6 | 72.4 | 81.1522 | 93.0054 | 11.8531 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/31/20XX 5:00:00 AM | 0.20833 | 3 | 71 | 74.2 | 79.4639 | 91.0648 | 11.6009 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/31/20XX 6:00:00 AM | 0.25 | 3 | 71.3 | 74.3 | 80.3042 | 92.0306 | 11.7264 | 70 | 71.3 |  | 71.3 | 85.3466 | 0.1 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 64.8941 | 17.0735 | 406349.1787 | 33.8624 | 33.8624 | 92.8619 | 0.2 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 67.1666 | 19.346 | 460434.5574 | 38.3695 | 38.3695 | 96.5185 | 0.3 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 69.4391 | 21.6185 | 514519.936 | 42.8767 | 42.8767 | 100.1752 | 0.4 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 71.7116 | 23.891 | 568605.3147 | 47.3838 | 47.3838 | 103.8318 | 0.5 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 73.9841 | 26.1635 | 622690.6934 | 51.8909 | 51.8909 | 107.4884 | 0.6 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 76.2566 | 28.436 | 676776.0721 | 56.398 | 56.398 | 111.145 | 0.7 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 78.5291 | 30.7085 | 730861.4507 | 60.9051 | 60.9051 | 114.8016 | 0.8 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 80.8016 | 32.981 | 784946.8294 | 65.4122 | 65.4122 | 118.4582 | 0.9 | 71.57 | 16.57 | 626346 | 52.1955 | 52.1955 | 83.0741 | 35.2535 | 839032.2081 | 69.9194 | 69.9194 | 122.1149 | 1 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 85.3466 | 37.5259 | 893117.5868 | 74.4265 | 74.4265 | 125.7715 | 70 | 75 | 30.4474 | 30 | 74.3
8/31/20XX 7:00:00 AM | 0.29167 | 3 | 71.9 | 73.9 | 82.008 | 93.989 | 11.9811 | 70 | 71.9 |  | 71.9 | 86.6806 | 0.1 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 65.0275 | 17.2069 | 409524.0883 | 34.127 | 34.127 | 93.3155 | 0.2 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 67.4334 | 19.6128 | 466784.3765 | 38.8987 | 38.8987 | 97.4257 | 0.3 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 69.8393 | 22.0187 | 524044.6648 | 43.6704 | 43.6704 | 101.5359 | 0.4 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 72.2452 | 24.4246 | 581304.953 | 48.4421 | 48.4421 | 105.6461 | 0.5 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 74.6511 | 26.8305 | 638565.2413 | 53.2138 | 53.2138 | 109.7563 | 0.6 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 77.057 | 29.2364 | 695825.5295 | 57.9855 | 57.9855 | 113.8665 | 0.7 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 79.4629 | 31.6423 | 753085.8178 | 62.7572 | 62.7572 | 117.9767 | 0.8 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 81.8688 | 34.0482 | 810346.1061 | 67.5288 | 67.5288 | 122.0868 | 0.9 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 84.2747 | 36.4541 | 867606.3943 | 72.3005 | 72.3005 | 126.197 | 1 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 86.6806 | 38.8599 | 924866.6826 | 77.0722 | 77.0722 | 130.3072 | 70 | 75 | 30.8031 | 30 | 73.9
8/31/20XX 8:00:00 AM | 0.33333 | 3 | 73.5 | 70.6 | 86.7045 | 99.389 | 12.6844 | 70 | 73.5 |  | 73.5 | 87.4656 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 65.106 | 17.2854 | 411392.4192 | 34.2827 | 34.2827 | 93.9752 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 67.5904 | 19.7698 | 470521.0385 | 39.2101 | 39.2101 | 98.7451 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 70.0748 | 22.2542 | 529649.6577 | 44.1375 | 44.1375 | 103.515 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 72.5592 | 24.7386 | 588778.277 | 49.0649 | 49.0649 | 108.2849 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 75.0436 | 27.223 | 647906.8962 | 53.9922 | 53.9922 | 113.0547 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 77.528 | 29.7074 | 707035.5155 | 58.9196 | 58.9196 | 117.8246 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 80.0124 | 32.1918 | 766164.1347 | 63.847 | 63.847 | 122.5945 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 82.4968 | 34.6762 | 825292.754 | 68.7744 | 68.7744 | 127.3644 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 84.9812 | 37.1606 | 884421.3732 | 73.7018 | 73.7018 | 132.1343 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 87.4656 | 39.645 | 943549.9925 | 78.6292 | 78.6292 | 136.9042 | 75 | 70 | 31.3187 | 32 | 70.6
8/31/20XX 9:00:00 AM | 0.375 | 3 | 75.5 | 66.6 | 79.3806 | 92.8973 | 13.5167 | 60 | 75.5 |  | 75.5 | 88.3016 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 65.1896 | 17.369 | 413382.2414 | 34.4485 | 34.4485 | 94.771 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 67.7576 | 19.937 | 474500.6827 | 39.5417 | 39.5417 | 100.3367 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 70.3256 | 22.505 | 535619.1241 | 44.6349 | 44.6349 | 105.9024 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 72.8936 | 25.073 | 596737.5654 | 49.7281 | 49.7281 | 111.4681 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 75.4616 | 27.641 | 657856.0068 | 54.8213 | 54.8213 | 117.0338 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 78.0296 | 30.209 | 718974.4481 | 59.9145 | 59.9145 | 122.5995 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 80.5976 | 32.777 | 780092.8895 | 65.0077 | 65.0077 | 128.1652 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 83.1656 | 35.345 | 841211.3308 | 70.1009 | 70.1009 | 133.7309 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 85.7336 | 37.913 | 902329.7722 | 75.1941 | 75.1941 | 139.2966 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 88.3016 | 40.481 | 963448.2135 | 80.2874 | 80.2874 | 144.8624 | 75 | 65 | 31.9407 | 32 | 66.6
8/31/20XX 10:00:00 AM | 0.41667 | 3 | 78.2 | 62 | 87.0044 | 101.8479 | 14.8435 | 60 | 78.2 |  | 78.2 | 89.9731 | 0.1 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 65.3568 | 17.5361 | 417360.2842 | 34.78 | 34.78 | 95.953 | 0.2 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 68.0919 | 20.2713 | 482456.7684 | 40.2047 | 40.2047 | 102.7007 | 0.3 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 70.8271 | 23.0064 | 547553.2526 | 45.6294 | 45.6294 | 109.4484 | 0.4 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 73.5622 | 25.7416 | 612649.7368 | 51.0541 | 51.0541 | 116.1961 | 0.5 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 76.2974 | 28.4767 | 677746.221 | 56.4789 | 56.4789 | 122.9439 | 0.6 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 79.0325 | 31.2119 | 742842.7051 | 61.9036 | 61.9036 | 129.6916 | 0.7 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 81.7677 | 33.947 | 807939.1893 | 67.3283 | 67.3283 | 136.4393 | 0.8 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 84.5028 | 36.6822 | 873035.6735 | 72.753 | 72.753 | 143.187 | 0.9 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 87.2379 | 39.4173 | 938132.1577 | 78.1777 | 78.1777 | 149.9347 | 1 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 89.9731 | 42.1525 | 1003228.6419 | 83.6024 | 83.6024 | 156.6824 | 80 | 60 | 32.8657 | 32 | 62
8/31/20XX 11:00:00 AM | 0.45833 | 3 | 80.9 | 56.8 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 90.0533 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 65.3648 | 17.5442 | 417551.1178 | 34.7959 | 34.7959 | 96.8194 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 68.108 | 20.2873 | 482838.4355 | 40.2365 | 40.2365 | 104.4335 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 70.8511 | 23.0305 | 548125.7533 | 45.6771 | 45.6771 | 112.0476 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 73.5943 | 25.7737 | 613413.0711 | 51.1178 | 51.1178 | 119.6618 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 76.3375 | 28.5168 | 678700.3889 | 56.5584 | 56.5584 | 127.2759 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 79.0806 | 31.26 | 743987.7066 | 61.999 | 61.999 | 134.89 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 81.8238 | 34.0032 | 809275.0244 | 67.4396 | 67.4396 | 142.5041 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 84.5669 | 36.7463 | 874562.3422 | 72.8802 | 72.8802 | 150.1182 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 87.3101 | 39.4895 | 939849.6599 | 78.3208 | 78.3208 | 157.7323 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 90.0533 | 42.2326 | 1005136.9777 | 83.7614 | 83.7614 | 165.3464 | 80 | 55 | 33.5417 | 34 | 56.8
8/31/20XX 12:00:00 PM | 0.5 | 3 | 83.1 | 51.1 | 84.9846 | 102.3992 | 17.4147 | 50 | 83.1 |  | 83.1 | 86.9002 | 0.1 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 65.0495 | 17.2289 | 410046.7285 | 34.1706 | 34.1706 | 96.8871 | 0.2 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 67.4773 | 19.6567 | 467829.657 | 38.9858 | 38.9858 | 104.5688 | 0.3 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 69.9052 | 22.0846 | 525612.5855 | 43.801 | 43.801 | 112.2505 | 0.4 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 72.333 | 24.5124 | 583395.514 | 48.6163 | 48.6163 | 119.9323 | 0.5 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 74.7609 | 26.9403 | 641178.4425 | 53.4315 | 53.4315 | 127.614 | 0.6 | 79.46 | 24.46 | 924588 | 77.049 | 77.049 | 77.1888 | 29.3681 | 698961.371 | 58.2468 | 58.2468 | 135.2958 | 0.7 | 80.37 | 25.37 | 958986 | 79.9155 | 79.9155 | 79.6166 | 31.796 | 756744.2995 | 63.062 | 63.062 | 142.9775 | 0.8 | 81.28 | 26.28 | 993384 | 82.782 | 82.782 | 82.0445 | 34.2238 | 814527.228 | 67.8773 | 67.8773 | 150.6593 | 0.9 | 82.19 | 27.19 | 1027782 | 85.6485 | 85.6485 | 84.4723 | 36.6517 | 872310.1564 | 72.6925 | 72.6925 | 158.341 | 1 | 83.1 | 28.1 | 1062180 | 88.515 | 88.515 | 86.9002 | 39.0795 | 930093.0849 | 77.5078 | 77.5078 | 166.0228 | 85 | 50 | 33.5873 | 34 | 51.1
8/31/20XX 1:00:00 PM | 0.54167 | 3 | 84.1 | 49.4 | 69.9179 | 87.7992 | 17.8813 | 40 | 84.1 |  | 84.1 | 86.7263 | 0.1 | 75.01 | 20.01 | 756378 | 63.0315 | 63.0315 | 65.0321 | 17.2115 | 409632.9059 | 34.1361 | 34.1361 | 97.1676 | 0.2 | 76.02 | 21.02 | 794556 | 66.213 | 66.213 | 67.4426 | 19.6219 | 467002.0118 | 38.9168 | 38.9168 | 105.1298 | 0.3 | 77.03 | 22.03 | 832734 | 69.3945 | 69.3945 | 69.853 | 22.0324 | 524371.1177 | 43.6976 | 43.6976 | 113.0921 | 0.4 | 78.04 | 23.04 | 870912 | 72.576 | 72.576 | 72.2635 | 24.4429 | 581740.2237 | 48.4784 | 48.4784 | 121.0544 | 0.5 | 79.05 | 24.05 | 909090 | 75.7575 | 75.7575 | 74.674 | 26.8533 | 639109.3296 | 53.2591 | 53.2591 | 129.0166 | 0.6 | 80.06 | 25.06 | 947268 | 78.939 | 78.939 | 77.0844 | 29.2638 | 696478.4355 | 58.0399 | 58.0399 | 136.9789 | 0.7 | 81.07 | 26.07 | 985446 | 82.1205 | 82.1205 | 79.4949 | 31.6743 | 753847.5414 | 62.8206 | 62.8206 | 144.9411 | 0.8 | 82.08 | 27.08 | 1023624 | 85.302 | 85.302 | 81.9054 | 34.0847 | 811216.6473 | 67.6014 | 67.6014 | 152.9034 | 0.9 | 83.09 | 28.09 | 1061802 | 88.4835 | 88.4835 | 84.3158 | 36.4952 | 868585.7532 | 72.3821 | 72.3821 | 160.8656 | 1 | 84.1 | 29.1 | 1099980 | 91.665 | 91.665 | 86.7263 | 38.9057 | 925954.8592 | 77.1629 | 77.1629 | 168.8279 | 85 | 50 | 33.8055 | 34 | 49.4
8/31/20XX 2:00:00 PM | 0.58333 | 3 | 84.3 | 48.2 | 70.3706 | 88.3711 | 18.0005 | 40 | 84.3 |  | 84.3 | 85.131 | 0.1 | 75.03 | 20.03 | 757134 | 63.0945 | 63.0945 | 64.8726 | 17.0519 | 405836.0447 | 33.8197 | 33.8197 | 96.9142 | 0.2 | 76.06 | 21.06 | 796068 | 66.339 | 66.339 | 67.1235 | 19.3029 | 459408.2895 | 38.284 | 38.284 | 104.623 | 0.3 | 77.09 | 22.09 | 835002 | 69.5835 | 69.5835 | 69.3744 | 21.5538 | 512980.5342 | 42.7484 | 42.7484 | 112.3319 | 0.4 | 78.12 | 23.12 | 873936 | 72.828 | 72.828 | 71.6254 | 23.8047 | 566552.7789 | 47.2127 | 47.2127 | 120.0407 | 0.5 | 79.15 | 24.15 | 912870 | 76.0725 | 76.0725 | 73.8763 | 26.0557 | 620125.0237 | 51.6771 | 51.6771 | 127.7496 | 0.6 | 80.18 | 25.18 | 951804 | 79.317 | 79.317 | 76.1272 | 28.3066 | 673697.2684 | 56.1414 | 56.1414 | 135.4584 | 0.7 | 81.21 | 26.21 | 990738 | 82.5615 | 82.5615 | 78.3782 | 30.5575 | 727269.5132 | 60.6058 | 60.6058 | 143.1673 | 0.8 | 82.24 | 27.24 | 1029672 | 85.806 | 85.806 | 80.6291 | 32.8085 | 780841.7579 | 65.0701 | 65.0701 | 150.8761 | 0.9 | 83.27 | 28.27 | 1068606 | 89.0505 | 89.0505 | 82.88 | 35.0594 | 834414.0026 | 69.5345 | 69.5345 | 158.585 | 1 | 84.3 | 29.3 | 1107540 | 92.295 | 92.295 | 85.131 | 37.3103 | 887986.2474 | 73.9989 | 73.9989 | 166.2939 | 85 | 50 | 33.604 | 34 | 48.2
8/31/20XX 3:00:00 PM | 0.625 | 3 | 83 | 50.4 | 84.7072 | 102.0641 | 17.3569 | 50 | 83 |  | 83 | 85.4015 | 0.1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 64.8996 | 17.079 | 406479.7856 | 33.8733 | 33.8733 | 96.5583 | 0.2 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 67.1776 | 19.357 | 460695.7712 | 38.3913 | 38.3913 | 103.9113 | 0.3 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 69.4556 | 21.6349 | 514911.7568 | 42.9093 | 42.9093 | 111.2643 | 0.4 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 71.7336 | 23.9129 | 569127.7423 | 47.4273 | 47.4273 | 118.6173 | 0.5 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 74.0115 | 26.1909 | 623343.7279 | 51.9453 | 51.9453 | 125.9703 | 0.6 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 76.2895 | 28.4689 | 677559.7135 | 56.4633 | 56.4633 | 133.3233 | 0.7 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 78.5675 | 30.7469 | 731775.6991 | 60.9813 | 60.9813 | 140.6763 | 0.8 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 80.8455 | 33.0249 | 785991.6847 | 65.4993 | 65.4993 | 148.0293 | 0.9 | 82.1 | 27.1 | 1024380 | 85.365 | 85.365 | 83.1235 | 35.3028 | 840207.6703 | 70.0173 | 70.0173 | 155.3823 | 1 | 83 | 28 | 1058400 | 88.2 | 88.2 | 85.4015 | 37.5808 | 894423.6558 | 74.5353 | 74.5353 | 162.7353 | 85 | 50 | 33.3274 | 34 | 50.4
8/31/20XX 4:00:00 PM | 0.66667 | 3 | 81.3 | 53.5 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 85.8433 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 64.9438 | 17.1232 | 407531.4222 | 33.961 | 33.961 | 96.1105 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 67.266 | 19.4453 | 462799.0443 | 38.5666 | 38.5666 | 103.0156 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 69.5881 | 21.7675 | 518066.6665 | 43.1722 | 43.1722 | 109.9207 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 71.9103 | 24.0897 | 573334.2887 | 47.7779 | 47.7779 | 116.8259 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 74.2325 | 26.4118 | 628601.9108 | 52.3835 | 52.3835 | 123.731 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 76.5546 | 28.734 | 683869.533 | 56.9891 | 56.9891 | 130.6361 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 78.8768 | 31.0562 | 739137.1552 | 61.5948 | 61.5948 | 137.5413 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 81.199 | 33.3784 | 794404.7773 | 66.2004 | 66.2004 | 144.4464 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 83.5212 | 35.7005 | 849672.3995 | 70.806 | 70.806 | 151.3515 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 85.8433 | 38.0227 | 904940.0217 | 75.4117 | 75.4117 | 158.2567 | 80 | 55 | 32.9795 | 32 | 53.5
8/31/20XX 5:00:00 PM | 0.70833 | 3 | 80.1 | 56.9 | 76.9795 | 92.7289 | 15.7494 | 50 | 80.1 |  | 80.1 | 87.8466 | 0.1 | 74.61 | 19.61 | 741258 | 61.7715 | 61.7715 | 65.1441 | 17.3235 | 412299.1213 | 34.3583 | 34.3583 | 96.1298 | 0.2 | 75.22 | 20.22 | 764316 | 63.693 | 63.693 | 67.6666 | 19.846 | 472334.4426 | 39.3612 | 39.3612 | 103.0542 | 0.3 | 75.83 | 20.83 | 787374 | 65.6145 | 65.6145 | 70.1891 | 22.3685 | 532369.7639 | 44.3641 | 44.3641 | 109.9786 | 0.4 | 76.44 | 21.44 | 810432 | 67.536 | 67.536 | 72.7116 | 24.891 | 592405.0852 | 49.3671 | 49.3671 | 116.9031 | 0.5 | 77.05 | 22.05 | 833490 | 69.4575 | 69.4575 | 75.2341 | 27.4135 | 652440.4065 | 54.37 | 54.37 | 123.8275 | 0.6 | 77.66 | 22.66 | 856548 | 71.379 | 71.379 | 77.7566 | 29.936 | 712475.7278 | 59.373 | 59.373 | 130.752 | 0.7 | 78.27 | 23.27 | 879606 | 73.3005 | 73.3005 | 80.2791 | 32.4584 | 772511.0491 | 64.3759 | 64.3759 | 137.6764 | 0.8 | 78.88 | 23.88 | 902664 | 75.222 | 75.222 | 82.8016 | 34.9809 | 832546.3704 | 69.3789 | 69.3789 | 144.6009 | 0.9 | 79.49 | 24.49 | 925722 | 77.1435 | 77.1435 | 85.3241 | 37.5034 | 892581.6917 | 74.3818 | 74.3818 | 151.5253 | 1 | 80.1 | 25.1 | 948780 | 79.065 | 79.065 | 87.8466 | 40.0259 | 952617.013 | 79.3848 | 79.3848 | 158.4498 | 80 | 55 | 32.9991 | 32 | 56.9
8/31/20XX 6:00:00 PM | 0.75 | 3 | 78.8 | 56.5 | 73.7091 | 88.7794 | 15.0703 | 50 | 78.8 |  | 78.8 | 83.5048 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 64.71 | 16.8893 | 401965.783 | 33.4971 | 33.4971 | 94.8591 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 66.7983 | 18.9776 | 451667.7661 | 37.639 | 37.639 | 100.513 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 68.8866 | 21.066 | 501369.7491 | 41.7808 | 41.7808 | 106.1668 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 70.9749 | 23.1543 | 551071.7321 | 45.9226 | 45.9226 | 111.8206 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 73.0632 | 25.2426 | 600773.7151 | 50.0645 | 50.0645 | 117.4745 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 75.1515 | 27.3309 | 650475.6982 | 54.2063 | 54.2063 | 123.1283 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 77.2399 | 29.4192 | 700177.6812 | 58.3481 | 58.3481 | 128.7821 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 79.3282 | 31.5075 | 749879.6642 | 62.49 | 62.49 | 134.436 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 81.4165 | 33.5959 | 799581.6472 | 66.6318 | 66.6318 | 140.0898 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 83.5048 | 35.6842 | 849283.6303 | 70.7736 | 70.7736 | 145.7436 | 80 | 55 | 31.9994 | 32 | 56.5
8/31/20XX 7:00:00 PM | 0.79167 | 3 | 78 | 58.2 | 71.7546 | 86.4193 | 14.6647 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/31/20XX 8:00:00 PM | 0.83333 | 3 | 77.5 | 57.5 | 70.5552 | 84.9711 | 14.416 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/31/20XX 9:00:00 PM | 0.875 | 3 | 76.8 | 59.1 | 68.9041 | 82.9779 | 14.0738 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/31/20XX 10:00:00 PM | 0.91667 | 3 | 76.2 | 60.3 | 81.3009 | 95.1517 | 13.8508 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/31/20XX 11:00:00 PM | 0.95833 | 3 | 75.1 | 62.8 | 78.3007 | 91.6296 | 13.3289 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8/31/20XX 12:00:00 AM | 0 | 4 | 74.4 | 64.8 | 76.4409 | 89.4463 | 13.0054 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/1/20XX 1:00:00 AM | 0.041667 | 4 | 73.6 | 67.2 | 74.3617 | 87.0056 | 12.6439 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/1/20XX 2:00:00 AM | 0.083333 | 4 | 73.3 | 66.9 | 73.5946 | 86.1051 | 12.5105 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/1/20XX 3:00:00 AM | 0.125 | 4 | 72.6 | 68.7 | 71.831 | 84.035 | 12.204 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/1/20XX 4:00:00 AM | 0.16667 | 4 | 71.3 | 71.7 | 80.3042 | 92.0306 | 11.7264 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/1/20XX 5:00:00 AM | 0.20833 | 4 | 70.5 | 73.3 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/1/20XX 6:00:00 AM | 0.25 | 4 | 70.6 | 73.6 | 78.3554 | 89.7909 | 11.4354 | 70 | 70.6 |  | 70.6 | 82.4722 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 64.6067 | 16.7861 | 399508.1023 | 33.2923 | 33.2923 | 92.0713 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 66.5917 | 18.7711 | 446752.4045 | 37.2294 | 37.2294 | 94.9374 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 68.5768 | 20.7562 | 493996.7068 | 41.1664 | 41.1664 | 97.8034 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 70.5619 | 22.7412 | 541241.009 | 45.1034 | 45.1034 | 100.6694 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 72.5469 | 24.7263 | 588485.3113 | 49.0404 | 49.0404 | 103.5354 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 74.532 | 26.7113 | 635729.6136 | 52.9775 | 52.9775 | 106.4015 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 76.517 | 28.6964 | 682973.9158 | 56.9145 | 56.9145 | 109.2675 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 78.5021 | 30.6814 | 730218.2181 | 60.8515 | 60.8515 | 112.1335 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 80.4871 | 32.6665 | 777462.5203 | 64.7885 | 64.7885 | 114.9995 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 82.4722 | 34.6515 | 824706.8226 | 68.7256 | 68.7256 | 117.8656 | 70 | 75 | 29.8266 | 30 | 73.6
9/1/20XX 7:00:00 AM | 0.29167 | 4 | 71.6 | 71 | 81.1522 | 93.0054 | 11.8531 | 70 | 71.6 |  | 71.6 | 82.3375 | 0.1 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 64.5932 | 16.7726 | 399187.6425 | 33.2656 | 33.2656 | 92.3596 | 0.2 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 66.5648 | 18.7442 | 446111.485 | 37.176 | 37.176 | 95.514 | 0.3 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 68.5364 | 20.7158 | 493035.3275 | 41.0863 | 41.0863 | 98.6683 | 0.4 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 70.508 | 22.6874 | 539959.17 | 44.9966 | 44.9966 | 101.8226 | 0.5 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 72.4796 | 24.659 | 586883.0125 | 48.9069 | 48.9069 | 104.9769 | 0.6 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 74.4512 | 26.6305 | 633806.855 | 52.8172 | 52.8172 | 108.1312 | 0.7 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 76.4228 | 28.6021 | 680730.6976 | 56.7276 | 56.7276 | 111.2856 | 0.8 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 78.3944 | 30.5737 | 727654.5401 | 60.6379 | 60.6379 | 114.4399 | 0.9 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 80.3659 | 32.5453 | 774578.3826 | 64.5482 | 64.5482 | 117.5942 | 1 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 82.3375 | 34.5169 | 821502.2251 | 68.4585 | 68.4585 | 120.7485 | 70 | 70 | 30.0508 | 30 | 71
9/1/20XX 8:00:00 AM | 0.33333 | 4 | 72.7 | 67.4 | 72.0807 | 84.3281 | 12.2474 | 60 | 72.7 |  | 72.7 | 81.1438 | 0.1 | 73.87 | 18.87 | 713286 | 59.4405 | 59.4405 | 64.4738 | 16.6532 | 396346.5169 | 33.0289 | 33.0289 | 92.4694 | 0.2 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 66.3261 | 18.5054 | 440429.2339 | 36.7024 | 36.7024 | 95.7334 | 0.3 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 68.1783 | 20.3576 | 484511.9508 | 40.376 | 40.376 | 98.9975 | 0.4 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 70.0305 | 22.2099 | 528594.6678 | 44.0496 | 44.0496 | 102.2616 | 0.5 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 71.8827 | 24.0621 | 572677.3847 | 47.7231 | 47.7231 | 105.5256 | 0.6 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 73.7349 | 25.9143 | 616760.1016 | 51.3967 | 51.3967 | 108.7897 | 0.7 | 73.09 | 18.09 | 683802 | 56.9835 | 56.9835 | 75.5871 | 27.7665 | 660842.8186 | 55.0702 | 55.0702 | 112.0537 | 0.8 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 77.4394 | 29.6187 | 704925.5355 | 58.7438 | 58.7438 | 115.3178 | 0.9 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 79.2916 | 31.4709 | 749008.2525 | 62.4174 | 62.4174 | 118.5819 | 1 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 81.1438 | 33.3231 | 793090.9694 | 66.0909 | 66.0909 | 121.8459 | 75 | 65 | 30.1339 | 30 | 67.4
9/1/20XX 9:00:00 AM | 0.375 | 4 | 74.2 | 64.6 | 75.9165 | 88.8307 | 12.9142 | 60 | 74.2 |  | 74.2 | 81.857 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 64.5452 | 16.7245 | 398044.0341 | 33.1703 | 33.1703 | 93.0833 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 66.4687 | 18.6481 | 443824.2683 | 36.9854 | 36.9854 | 96.9614 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 68.3923 | 20.5716 | 489604.5024 | 40.8004 | 40.8004 | 100.8394 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 70.3158 | 22.4952 | 535384.7366 | 44.6154 | 44.6154 | 104.7174 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 72.2393 | 24.4187 | 581164.9707 | 48.4304 | 48.4304 | 108.5954 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 74.1629 | 26.3422 | 626945.2048 | 52.2454 | 52.2454 | 112.4734 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 76.0864 | 28.2658 | 672725.439 | 56.0605 | 56.0605 | 116.3515 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 78.0099 | 30.1893 | 718505.6731 | 59.8755 | 59.8755 | 120.2295 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 79.9335 | 32.1129 | 764285.9072 | 63.6905 | 63.6905 | 124.1075 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 81.857 | 34.0364 | 810066.1414 | 67.5055 | 67.5055 | 127.9855 | 75 | 65 | 30.6132 | 30 | 64.6
9/1/20XX 10:00:00 AM | 0.41667 | 4 | 76.6 | 60.9 | 82.4157 | 96.4605 | 14.0448 | 60 | 76.6 |  | 76.6 | 83.6797 | 0.1 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 64.7274 | 16.9068 | 402382.0007 | 33.5318 | 33.5318 | 94.2008 | 0.2 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 66.8332 | 19.0126 | 452500.2014 | 37.7084 | 37.7084 | 99.1964 | 0.3 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 68.9391 | 21.1184 | 502618.4022 | 41.8849 | 41.8849 | 104.1919 | 0.4 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 71.0449 | 23.2242 | 552736.6029 | 46.0614 | 46.0614 | 109.1874 | 0.5 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 73.1507 | 25.33 | 602854.8036 | 50.2379 | 50.2379 | 114.1829 | 0.6 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 75.2565 | 27.4358 | 652973.0043 | 54.4144 | 54.4144 | 119.1784 | 0.7 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 77.3623 | 29.5416 | 703091.2051 | 58.5909 | 58.5909 | 124.1739 | 0.8 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 79.4681 | 31.6475 | 753209.4058 | 62.7675 | 62.7675 | 129.1695 | 0.9 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 81.5739 | 33.7533 | 803327.6065 | 66.944 | 66.944 | 134.165 | 1 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 83.6797 | 35.8591 | 853445.8072 | 71.1205 | 71.1205 | 139.1605 | 75 | 60 | 31.4871 | 32 | 60.9
9/1/20XX 11:00:00 AM | 0.45833 | 4 | 78.8 | 54.1 | 73.7091 | 88.7794 | 15.0703 | 50 | 78.8 |  | 78.8 | 79.888 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 64.3483 | 16.5276 | 393357.6494 | 32.7798 | 32.7798 | 94.1418 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 66.0749 | 18.2543 | 434451.4988 | 36.2043 | 36.2043 | 99.0783 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 67.8015 | 19.9809 | 475545.3482 | 39.6288 | 39.6288 | 104.0148 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 69.5282 | 21.7075 | 516639.1976 | 43.0533 | 43.0533 | 108.9513 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 71.2548 | 23.4342 | 557733.047 | 46.4778 | 46.4778 | 113.8878 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 72.9814 | 25.1608 | 598826.8964 | 49.9022 | 49.9022 | 118.8242 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 74.7081 | 26.8874 | 639920.7458 | 53.3267 | 53.3267 | 123.7607 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 76.4347 | 28.6141 | 681014.5952 | 56.7512 | 56.7512 | 128.6972 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 78.1613 | 30.3407 | 722108.4445 | 60.1757 | 60.1757 | 133.6337 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 79.888 | 32.0673 | 763202.2939 | 63.6002 | 63.6002 | 138.5702 | 80 | 55 | 31.4325 | 32 | 54.1
9/1/20XX 12:00:00 PM | 0.5 | 4 | 80.6 | 49.3 | 62.3713 | 78.2688 | 15.8975 | 40 | 80.6 |  | 80.6 | 77.156 | 0.1 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 64.0751 | 16.2544 | 386855.56 | 32.238 | 32.238 | 94.167 | 0.2 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 65.5285 | 17.7079 | 421447.3199 | 35.1206 | 35.1206 | 99.1286 | 0.3 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 66.9819 | 19.1613 | 456039.0799 | 38.0033 | 38.0033 | 104.0903 | 0.4 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 68.4354 | 20.6147 | 490630.8399 | 40.8859 | 40.8859 | 109.0519 | 0.5 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 69.8888 | 22.0682 | 525222.5999 | 43.7685 | 43.7685 | 114.0135 | 0.6 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 71.3422 | 23.5216 | 559814.3598 | 46.6512 | 46.6512 | 118.9752 | 0.7 | 78.62 | 23.62 | 892836 | 74.403 | 74.403 | 72.7957 | 24.975 | 594406.1198 | 49.5338 | 49.5338 | 123.9368 | 0.8 | 79.28 | 24.28 | 917784 | 76.482 | 76.482 | 74.2491 | 26.4285 | 628997.8798 | 52.4165 | 52.4165 | 128.8985 | 0.9 | 79.94 | 24.94 | 942732 | 78.561 | 78.561 | 75.7026 | 27.8819 | 663589.6398 | 55.2991 | 55.2991 | 133.8601 | 1 | 80.6 | 25.6 | 967680 | 80.64 | 80.64 | 77.156 | 29.3354 | 698181.3997 | 58.1818 | 58.1818 | 138.8218 | 80 | 50 | 31.4452 | 32 | 49.3
9/1/20XX 1:00:00 PM | 0.54167 | 4 | 81.6 | 47.3 | 64.4562 | 80.9009 | 16.4447 | 40 | 81.6 |  | 81.6 | 76.4608 | 0.1 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 64.0055 | 16.1849 | 385201.0015 | 32.1001 | 32.1001 | 94.3441 | 0.2 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 65.3895 | 17.5688 | 418138.203 | 34.8449 | 34.8449 | 99.4829 | 0.3 | 76.28 | 21.28 | 804384 | 67.032 | 67.032 | 66.7734 | 18.9527 | 451075.4045 | 37.5896 | 37.5896 | 104.6216 | 0.4 | 77.04 | 22.04 | 833112 | 69.426 | 69.426 | 68.1573 | 20.3367 | 484012.606 | 40.3344 | 40.3344 | 109.7604 | 0.5 | 77.8 | 22.8 | 861840 | 71.82 | 71.82 | 69.5412 | 21.7206 | 516949.8075 | 43.0792 | 43.0792 | 114.8992 | 0.6 | 78.56 | 23.56 | 890568 | 74.214 | 74.214 | 70.9251 | 23.1045 | 549887.009 | 45.8239 | 45.8239 | 120.0379 | 0.7 | 79.32 | 24.32 | 919296 | 76.608 | 76.608 | 72.309 | 24.4884 | 582824.2105 | 48.5687 | 48.5687 | 125.1767 | 0.8 | 80.08 | 25.08 | 948024 | 79.002 | 79.002 | 73.693 | 25.8723 | 615761.412 | 51.3135 | 51.3135 | 130.3155 | 0.9 | 80.84 | 25.84 | 976752 | 81.396 | 81.396 | 75.0769 | 27.2562 | 648698.6135 | 54.0582 | 54.0582 | 135.4542 | 1 | 81.6 | 26.6 | 1005480 | 83.79 | 83.79 | 76.4608 | 28.6402 | 681635.8151 | 56.803 | 56.803 | 140.593 | 80 | 45 | 31.581 | 32 | 47.3
9/1/20XX 2:00:00 PM | 0.58333 | 4 | 80.9 | 50.7 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 80.1835 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 64.3778 | 16.5572 | 394061.0761 | 32.8384 | 32.8384 | 94.8619 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 66.134 | 18.3134 | 435858.3522 | 36.3215 | 36.3215 | 100.5185 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 67.8902 | 20.0696 | 477655.6282 | 39.8046 | 39.8046 | 106.1751 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 69.6464 | 21.8258 | 519452.9043 | 43.2877 | 43.2877 | 111.8317 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 71.4026 | 23.5819 | 561250.1804 | 46.7708 | 46.7708 | 117.4883 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 73.1588 | 25.3381 | 603047.4565 | 50.254 | 50.254 | 123.145 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 74.9149 | 27.0943 | 644844.7326 | 53.7371 | 53.7371 | 128.8016 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 76.6711 | 28.8505 | 686642.0086 | 57.2202 | 57.2202 | 134.4582 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 78.4273 | 30.6067 | 728439.2847 | 60.7033 | 60.7033 | 140.1148 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 80.1835 | 32.3629 | 770236.5608 | 64.1864 | 64.1864 | 145.7714 | 80 | 50 | 31.9935 | 32 | 50.7
9/1/20XX 3:00:00 PM | 0.625 | 4 | 80.5 | 51.8 | 78.0095 | 93.973 | 15.9635 | 50 | 80.5 |  | 80.5 | 80.8829 | 0.1 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 64.4478 | 16.6271 | 395725.7322 | 32.9771 | 32.9771 | 94.8746 | 0.2 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 66.2739 | 18.4533 | 439187.6643 | 36.599 | 36.599 | 100.544 | 0.3 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 68.1 | 20.2794 | 482649.5965 | 40.2208 | 40.2208 | 106.2133 | 0.4 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 69.9262 | 22.1055 | 526111.5287 | 43.8426 | 43.8426 | 111.8826 | 0.5 | 77.25 | 22.25 | 841050 | 70.0875 | 70.0875 | 71.7523 | 23.9317 | 569573.4609 | 47.4645 | 47.4645 | 117.552 | 0.6 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 73.5784 | 25.7578 | 613035.393 | 51.0863 | 51.0863 | 123.2213 | 0.7 | 78.55 | 23.55 | 890190 | 74.1825 | 74.1825 | 75.4046 | 27.5839 | 656497.3252 | 54.7081 | 54.7081 | 128.8906 | 0.8 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 77.2307 | 29.4101 | 699959.2574 | 58.3299 | 58.3299 | 134.5599 | 0.9 | 79.85 | 24.85 | 939330 | 78.2775 | 78.2775 | 79.0568 | 31.2362 | 743421.1895 | 61.9518 | 61.9518 | 140.2293 | 1 | 80.5 | 25.5 | 963900 | 80.325 | 80.325 | 80.8829 | 33.0623 | 786883.1217 | 65.5736 | 65.5736 | 145.8986 | 80 | 50 | 32.0052 | 32 | 51.8
9/1/20XX 4:00:00 PM | 0.66667 | 4 | 78.5 | 58.4 | 72.9711 | 87.8882 | 14.9171 | 50 | 78.5 |  | 78.5 | 85.5014 | 0.1 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 64.9096 | 17.089 | 406717.7114 | 33.8931 | 33.8931 | 95.1606 | 0.2 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 67.1976 | 19.377 | 461171.6229 | 38.431 | 38.431 | 101.116 | 0.3 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 69.4856 | 21.6649 | 515625.5343 | 42.9688 | 42.9688 | 107.0713 | 0.4 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 71.7736 | 23.9529 | 570079.4457 | 47.5066 | 47.5066 | 113.0266 | 0.5 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 74.0615 | 26.2409 | 624533.3572 | 52.0444 | 52.0444 | 118.9819 | 0.6 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 76.3495 | 28.5289 | 678987.2686 | 56.5823 | 56.5823 | 124.9373 | 0.7 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 78.6375 | 30.8169 | 733441.1801 | 61.1201 | 61.1201 | 130.8926 | 0.8 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 80.9255 | 33.1048 | 787895.0915 | 65.6579 | 65.6579 | 136.8479 | 0.9 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 83.2134 | 35.3928 | 842349.0029 | 70.1958 | 70.1958 | 142.8033 | 1 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 85.5014 | 37.6808 | 896802.9144 | 74.7336 | 74.7336 | 148.7586 | 80 | 60 | 32.2387 | 32 | 58.4
9/1/20XX 5:00:00 PM | 0.70833 | 4 | 77.2 | 59.8 | 69.8436 | 84.112 | 14.2685 | 50 | 77.2 |  | 77.2 | 83.8266 | 0.1 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 64.7421 | 16.9215 | 402731.7281 | 33.561 | 33.561 | 94.419 | 0.2 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 66.8626 | 19.042 | 453199.6561 | 37.7666 | 37.7666 | 99.6326 | 0.3 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 68.9831 | 21.1625 | 503667.5842 | 41.9723 | 41.9723 | 104.8463 | 0.4 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 71.1036 | 23.283 | 554135.5122 | 46.178 | 46.178 | 110.06 | 0.5 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 73.2241 | 25.4035 | 604603.4403 | 50.3836 | 50.3836 | 115.2736 | 0.6 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 75.3446 | 27.524 | 655071.3683 | 54.5893 | 54.5893 | 120.4873 | 0.7 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 77.4651 | 29.6445 | 705539.2964 | 58.7949 | 58.7949 | 125.7009 | 0.8 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 79.5856 | 31.765 | 756007.2244 | 63.0006 | 63.0006 | 130.9146 | 0.9 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 81.7061 | 33.8855 | 806475.1525 | 67.2063 | 67.2063 | 136.1283 | 1 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 83.8266 | 36.006 | 856943.0805 | 71.4119 | 71.4119 | 141.3419 | 75 | 60 | 31.6573 | 32 | 59.8
9/1/20XX 6:00:00 PM | 0.75 | 4 | 76 | 62.1 | 80.7483 | 94.5029 | 13.7546 | 60 | 76 |  | 76 | 83.6367 | 0.1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 64.7231 | 16.9025 | 402279.7363 | 33.5233 | 33.5233 | 94.0033 | 0.2 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 66.8247 | 19.004 | 452295.6726 | 37.6913 | 37.6913 | 98.8013 | 0.3 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 68.9262 | 21.1055 | 502311.6089 | 41.8593 | 41.8593 | 103.5993 | 0.4 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 71.0277 | 23.207 | 552327.5452 | 46.0273 | 46.0273 | 108.3973 | 0.5 | 75 | 20 | 756000 | 63 | 63 | 73.1292 | 25.3085 | 602343.4814 | 50.1953 | 50.1953 | 113.1953 | 0.6 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 75.2307 | 27.4101 | 652359.4177 | 54.3633 | 54.3633 | 117.9933 | 0.7 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 77.3322 | 29.5116 | 702375.354 | 58.5313 | 58.5313 | 122.7913 | 0.8 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 79.4337 | 31.6131 | 752391.2903 | 62.6993 | 62.6993 | 127.5893 | 0.9 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 81.5352 | 33.7146 | 802407.2266 | 66.8673 | 66.8673 | 132.3873 | 1 | 76 | 21 | 793800 | 66.15 | 66.15 | 83.6367 | 35.8161 | 852423.1629 | 71.0353 | 71.0353 | 137.1853 | 75 | 60 | 31.3332 | 32 | 62.1
9/1/20XX 7:00:00 PM | 0.79167 | 4 | 74.6 | 66 | 76.9684 | 90.0655 | 13.0971 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/1/20XX 8:00:00 PM | 0.83333 | 4 | 74 | 68.5 | 75.3952 | 88.2187 | 12.8236 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/1/20XX 9:00:00 PM | 0.875 | 4 | 73.5 | 68.9 | 74.1052 | 86.7045 | 12.5993 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/1/20XX 10:00:00 PM | 0.91667 | 4 | 73.2 | 69.6 | 73.3404 | 85.8067 | 12.4664 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/1/20XX 11:00:00 PM | 0.95833 | 4 | 72.6 | 69 | 71.831 | 84.035 | 12.204 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/1/20XX 12:00:00 AM | 0 | 5 | 71.8 | 69.2 | 69.8602 | 81.7218 | 11.8616 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/2/20XX 1:00:00 AM | 0.041667 | 5 | 71.1 | 71 | 79.7432 | 91.3858 | 11.6426 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/2/20XX 2:00:00 AM | 0.083333 | 5 | 70.7 | 71.6 | 78.6313 | 90.1079 | 11.4766 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/2/20XX 3:00:00 AM | 0.125 | 5 | 70.4 | 72.1 | 77.8062 | 89.1597 | 11.3535 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/2/20XX 4:00:00 AM | 0.16667 | 5 | 69.8 | 75 | 76.1788 | 87.2896 | 11.1108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/2/20XX 5:00:00 AM | 0.20833 | 5 | 69.2 | 76.8 | 74.5812 | 85.4541 | 10.8729 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/2/20XX 6:00:00 AM | 0.25 | 5 | 69.1 | 78 | 74.3178 | 85.1515 | 10.8337 | 70 | 69.1 |  | 69.1 | 82.9848 | 0.1 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 64.6579 | 16.8373 | 400728.1222 | 33.394 | 33.394 | 91.7005 | 0.2 | 73.02 | 18.02 | 681156 | 56.763 | 56.763 | 66.6943 | 18.8736 | 449192.4444 | 37.4327 | 37.4327 | 94.1957 | 0.3 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 68.7306 | 20.9099 | 497656.7667 | 41.4714 | 41.4714 | 96.6909 | 0.4 | 72.04 | 17.04 | 644112 | 53.676 | 53.676 | 70.7669 | 22.9463 | 546121.0889 | 45.5101 | 45.5101 | 99.1861 | 0.5 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 72.8032 | 24.9826 | 594585.4111 | 49.5488 | 49.5488 | 101.6813 | 0.6 | 71.06 | 16.06 | 607068 | 50.589 | 50.589 | 74.8395 | 27.0189 | 643049.7333 | 53.5875 | 53.5875 | 104.1765 | 0.7 | 70.57 | 15.57 | 588546 | 49.0455 | 49.0455 | 76.8758 | 29.0552 | 691514.0555 | 57.6262 | 57.6262 | 106.6717 | 0.8 | 70.08 | 15.08 | 570024 | 47.502 | 47.502 | 78.9122 | 31.0915 | 739978.3777 | 61.6649 | 61.6649 | 109.1669 | 0.9 | 69.59 | 14.59 | 551502 | 45.9585 | 45.9585 | 80.9485 | 33.1278 | 788442.7 | 65.7036 | 65.7036 | 111.6621 | 1 | 69.1 | 14.1 | 532980 | 44.415 | 44.415 | 82.9848 | 35.1642 | 836907.0222 | 69.7423 | 69.7423 | 114.1573 | 70 | 80 | 29.5388 | 30 | 78
9/2/20XX 7:00:00 AM | 0.29167 | 5 | 70.8 | 74.5 | 78.908 | 90.4259 | 11.5179 | 70 | 70.8 |  | 70.8 | 84.091 | 0.1 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 64.7686 | 16.9479 | 403360.9823 | 33.6134 | 33.6134 | 92.4554 | 0.2 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 66.9155 | 19.0949 | 454458.1647 | 37.8715 | 37.8715 | 95.7055 | 0.3 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 69.0625 | 21.2418 | 505555.347 | 42.1296 | 42.1296 | 98.9556 | 0.4 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 71.2094 | 23.3888 | 556652.5294 | 46.3877 | 46.3877 | 102.2057 | 0.5 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 73.3563 | 25.5357 | 607749.7117 | 50.6458 | 50.6458 | 105.4558 | 0.6 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 75.5033 | 27.6826 | 658846.894 | 54.9039 | 54.9039 | 108.7059 | 0.7 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 77.6502 | 29.8296 | 709944.0764 | 59.162 | 59.162 | 111.956 | 0.8 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 79.7972 | 31.9765 | 761041.2587 | 63.4201 | 63.4201 | 115.2061 | 0.9 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 81.9441 | 34.1235 | 812138.4411 | 67.6782 | 67.6782 | 118.4562 | 1 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 84.091 | 36.2704 | 863235.6234 | 71.9363 | 71.9363 | 121.7063 | 70 | 75 | 30.1286 | 30 | 74.5
9/2/20XX 8:00:00 AM | 0.33333 | 5 | 72.6 | 68.5 | 71.831 | 84.035 | 12.204 | 60 | 72.6 |  | 72.6 | 82.2044 | 0.1 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 64.5799 | 16.7593 | 398870.8585 | 33.2392 | 33.2392 | 92.6482 | 0.2 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 66.5382 | 18.7176 | 445477.9169 | 37.1232 | 37.1232 | 96.0912 | 0.3 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 68.4965 | 20.6758 | 492084.9754 | 41.0071 | 41.0071 | 99.5341 | 0.4 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 70.4548 | 22.6341 | 538692.0338 | 44.891 | 44.891 | 102.977 | 0.5 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 72.413 | 24.5924 | 585299.0923 | 48.7749 | 48.7749 | 106.4199 | 0.6 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 74.3713 | 26.5507 | 631906.1507 | 52.6588 | 52.6588 | 109.8628 | 0.7 | 73.02 | 18.02 | 681156 | 56.763 | 56.763 | 76.3296 | 28.509 | 678513.2092 | 56.5428 | 56.5428 | 113.3058 | 0.8 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 78.2879 | 30.4672 | 725120.2677 | 60.4267 | 60.4267 | 116.7487 | 0.9 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 80.2462 | 32.4255 | 771727.3261 | 64.3106 | 64.3106 | 120.1916 | 1 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 82.2044 | 34.3838 | 818334.3846 | 68.1945 | 68.1945 | 123.6345 | 75 | 70 | 30.2752 | 30 | 68.5
9/2/20XX 9:00:00 AM | 0.375 | 5 | 74.4 | 65.9 | 76.4409 | 89.4463 | 13.0054 | 60 | 74.4 |  | 74.4 | 84.1141 | 0.1 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 64.7709 | 16.9502 | 403415.8272 | 33.618 | 33.618 | 93.594 | 0.2 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 66.9201 | 19.0995 | 454567.8543 | 37.8807 | 37.8807 | 97.9827 | 0.3 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 69.0694 | 21.2487 | 505719.8815 | 42.1433 | 42.1433 | 102.3713 | 0.4 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 71.2186 | 23.398 | 556871.9087 | 46.406 | 46.406 | 106.76 | 0.5 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 73.3679 | 25.5472 | 608023.9358 | 50.6687 | 50.6687 | 111.1487 | 0.6 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 75.5171 | 27.6965 | 659175.963 | 54.9313 | 54.9313 | 115.5373 | 0.7 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 77.6663 | 29.8457 | 710327.9902 | 59.194 | 59.194 | 119.926 | 0.8 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 79.8156 | 31.995 | 761480.0173 | 63.4567 | 63.4567 | 124.3147 | 0.9 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 81.9648 | 34.1442 | 812632.0445 | 67.7193 | 67.7193 | 128.7033 | 1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 84.1141 | 36.2934 | 863784.0717 | 71.982 | 71.982 | 133.092 | 75 | 65 | 31.0154 | 32 | 65.9
9/2/20XX 10:00:00 AM | 0.41667 | 5 | 77.4 | 59.1 | 70.3173 | 84.6839 | 14.3667 | 50 | 77.4 |  | 77.4 | 83.3909 | 0.1 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 64.6986 | 16.8779 | 401694.7638 | 33.4746 | 33.4746 | 94.3956 | 0.2 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 66.7755 | 18.9549 | 451125.7275 | 37.5938 | 37.5938 | 99.5858 | 0.3 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 68.8524 | 21.0318 | 500556.6913 | 41.7131 | 41.7131 | 104.7761 | 0.4 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 70.9294 | 23.1087 | 549987.6551 | 45.8323 | 45.8323 | 109.9663 | 0.5 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 73.0063 | 25.1857 | 599418.6188 | 49.9516 | 49.9516 | 115.1566 | 0.6 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 75.0832 | 27.2626 | 648849.5826 | 54.0708 | 54.0708 | 120.3468 | 0.7 | 76.38 | 21.38 | 808164 | 67.347 | 67.347 | 77.1602 | 29.3395 | 698280.5463 | 58.19 | 58.19 | 125.537 | 0.8 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 79.2371 | 31.4165 | 747711.5101 | 62.3093 | 62.3093 | 130.7273 | 0.9 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 81.314 | 33.4934 | 797142.4739 | 66.4285 | 66.4285 | 135.9175 | 1 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 83.3909 | 35.5703 | 846573.4376 | 70.5478 | 70.5478 | 141.1078 | 75 | 60 | 31.6381 | 32 | 59.1
9/2/20XX 11:00:00 AM | 0.45833 | 5 | 79.5 | 55.1 | 75.4555 | 90.8883 | 15.4328 | 50 | 79.5 |  | 79.5 | 83.3262 | 0.1 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 64.6921 | 16.8715 | 401540.6998 | 33.4617 | 33.4617 | 95.0442 | 0.2 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 66.7625 | 18.9419 | 450817.5995 | 37.5681 | 37.5681 | 100.8831 | 0.3 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 68.833 | 21.0124 | 500094.4993 | 41.6745 | 41.6745 | 106.722 | 0.4 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 70.9035 | 23.0828 | 549371.399 | 45.7809 | 45.7809 | 112.5609 | 0.5 | 76.75 | 21.75 | 822150 | 68.5125 | 68.5125 | 72.9739 | 25.1533 | 598648.2988 | 49.8874 | 49.8874 | 118.3999 | 0.6 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 75.0444 | 27.2237 | 647925.1985 | 53.9938 | 53.9938 | 124.2388 | 0.7 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 77.1148 | 29.2942 | 697202.0983 | 58.1002 | 58.1002 | 130.0777 | 0.8 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 79.1853 | 31.3647 | 746478.998 | 62.2066 | 62.2066 | 135.9166 | 0.9 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 81.2558 | 33.4351 | 795755.8978 | 66.313 | 66.313 | 141.7555 | 1 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 83.3262 | 35.5056 | 845032.7975 | 70.4194 | 70.4194 | 147.5944 | 80 | 55 | 32.1431 | 32 | 55.1
9/2/20XX 12:00:00 PM | 0.5 | 5 | 80.9 | 53.3 | 79.0509 | 95.2309 | 16.1799 | 50 | 80.9 |  | 80.9 | 84.3903 | 0.1 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 64.7985 | 16.9779 | 404073.225 | 33.6728 | 33.6728 | 95.6963 | 0.2 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 66.9754 | 19.1547 | 455882.65 | 37.9902 | 37.9902 | 102.1872 | 0.3 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 69.1522 | 21.3316 | 507692.075 | 42.3077 | 42.3077 | 108.6782 | 0.4 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 71.3291 | 23.5085 | 559501.5 | 46.6251 | 46.6251 | 115.1691 | 0.5 | 77.45 | 22.45 | 848610 | 70.7175 | 70.7175 | 73.506 | 25.6853 | 611310.925 | 50.9426 | 50.9426 | 121.6601 | 0.6 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 75.6828 | 27.8622 | 663120.35 | 55.26 | 55.26 | 128.151 | 0.7 | 78.83 | 23.83 | 900774 | 75.0645 | 75.0645 | 77.8597 | 30.0391 | 714929.775 | 59.5775 | 59.5775 | 134.642 | 0.8 | 79.52 | 24.52 | 926856 | 77.238 | 77.238 | 80.0366 | 32.2159 | 766739.2 | 63.8949 | 63.8949 | 141.1329 | 0.9 | 80.21 | 25.21 | 952938 | 79.4115 | 79.4115 | 82.2134 | 34.3928 | 818548.625 | 68.2124 | 68.2124 | 147.6239 | 1 | 80.9 | 25.9 | 979020 | 81.585 | 81.585 | 84.3903 | 36.5697 | 870358.05 | 72.5298 | 72.5298 | 154.1148 | 80 | 55 | 32.6534 | 32 | 53.3
9/2/20XX 1:00:00 PM | 0.54167 | 5 | 79.9 | 56.3 | 76.4687 | 92.1119 | 15.6433 | 50 | 79.9 |  | 79.9 | 86.3239 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 64.9919 | 17.1712 | 408675.2752 | 34.0563 | 34.0563 | 95.7648 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 67.3621 | 19.5415 | 465086.7505 | 38.7572 | 38.7572 | 102.3242 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 69.7323 | 21.9117 | 521498.2257 | 43.4582 | 43.4582 | 108.8837 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 72.1026 | 24.2819 | 577909.7009 | 48.1591 | 48.1591 | 115.4431 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 74.4728 | 26.6522 | 634321.1762 | 52.8601 | 52.8601 | 122.0026 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 76.843 | 29.0224 | 690732.6514 | 57.5611 | 57.5611 | 128.5621 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 79.2132 | 31.3926 | 747144.1267 | 62.262 | 62.262 | 135.1215 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 81.5835 | 33.7628 | 803555.6019 | 66.963 | 66.963 | 141.681 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 83.9537 | 36.1331 | 859967.0771 | 71.6639 | 71.6639 | 148.2404 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 86.3239 | 38.5033 | 916378.5524 | 76.3649 | 76.3649 | 154.7999 | 80 | 55 | 32.7112 | 32 | 56.3
9/2/20XX 2:00:00 PM | 0.58333 | 5 | 79.8 | 58.9 | 76.2143 | 91.8048 | 15.5904 | 50 | 79.8 |  | 79.8 | 90.0898 | 0.1 | 74.58 | 19.58 | 740124 | 61.677 | 61.677 | 65.3685 | 17.5478 | 417638.0683 | 34.8032 | 34.8032 | 96.4802 | 0.2 | 75.16 | 20.16 | 762048 | 63.504 | 63.504 | 68.1153 | 20.2946 | 483012.3365 | 40.251 | 40.251 | 103.755 | 0.3 | 75.74 | 20.74 | 783972 | 65.331 | 65.331 | 70.8621 | 23.0415 | 548386.6048 | 45.6989 | 45.6989 | 111.0299 | 0.4 | 76.32 | 21.32 | 805896 | 67.158 | 67.158 | 73.6089 | 25.7883 | 613760.873 | 51.1467 | 51.1467 | 118.3047 | 0.5 | 76.9 | 21.9 | 827820 | 68.985 | 68.985 | 76.3557 | 28.5351 | 679135.1413 | 56.5946 | 56.5946 | 125.5796 | 0.6 | 77.48 | 22.48 | 849744 | 70.812 | 70.812 | 79.1025 | 31.2819 | 744509.4095 | 62.0425 | 62.0425 | 132.8545 | 0.7 | 78.06 | 23.06 | 871668 | 72.639 | 72.639 | 81.8494 | 34.0287 | 809883.6778 | 67.4903 | 67.4903 | 140.1293 | 0.8 | 78.64 | 23.64 | 893592 | 74.466 | 74.466 | 84.5962 | 36.7755 | 875257.946 | 72.9382 | 72.9382 | 147.4042 | 0.9 | 79.22 | 24.22 | 915516 | 76.293 | 76.293 | 87.343 | 39.5224 | 940632.2143 | 78.386 | 78.386 | 154.679 | 1 | 79.8 | 24.8 | 937440 | 78.12 | 78.12 | 90.0898 | 42.2692 | 1006006.4825 | 83.8339 | 83.8339 | 161.9539 | 80 | 60 | 33.2772 | 34 | 58.9
9/2/20XX 3:00:00 PM | 0.625 | 5 | 79.6 | 59.2 | 75.7077 | 91.1929 | 15.4852 | 50 | 79.6 |  | 79.6 | 89.9541 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.3549 | 17.5342 | 417315.1226 | 34.7763 | 34.7763 | 96.3903 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 68.0881 | 20.2675 | 482366.4452 | 40.1972 | 40.1972 | 103.5752 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 70.8214 | 23.0007 | 547417.7679 | 45.6181 | 45.6181 | 110.7601 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 73.5546 | 25.734 | 612469.0905 | 51.0391 | 51.0391 | 117.9451 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 76.2879 | 28.4672 | 677520.4131 | 56.46 | 56.46 | 125.13 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 79.0211 | 31.2005 | 742571.7357 | 61.881 | 61.881 | 132.315 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 81.7544 | 33.9337 | 807623.0583 | 67.3019 | 67.3019 | 139.4999 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 84.4876 | 36.667 | 872674.3809 | 72.7229 | 72.7229 | 146.6849 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 87.2209 | 39.4002 | 937725.7036 | 78.1438 | 78.1438 | 153.8698 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 89.9541 | 42.1335 | 1002777.0262 | 83.5648 | 83.5648 | 161.0548 | 80 | 60 | 33.2067 | 34 | 59.2
9/2/20XX 4:00:00 PM | 0.66667 | 5 | 79.2 | 58.1 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 87.0769 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 65.0672 | 17.2465 | 410467.3355 | 34.2056 | 34.2056 | 95.6936 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 67.5127 | 19.6921 | 468670.871 | 39.0559 | 39.0559 | 102.1819 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 69.9582 | 22.1376 | 526874.4064 | 43.9062 | 43.9062 | 108.6702 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 72.4037 | 24.5831 | 585077.9419 | 48.7565 | 48.7565 | 115.1585 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 74.8493 | 27.0286 | 643281.4774 | 53.6068 | 53.6068 | 121.6468 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 77.2948 | 29.4742 | 701485.0129 | 58.4571 | 58.4571 | 128.1351 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 79.7403 | 31.9197 | 759688.5483 | 63.3074 | 63.3074 | 134.6234 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 82.1858 | 34.3652 | 817892.0838 | 68.1577 | 68.1577 | 141.1117 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 84.6314 | 36.8107 | 876095.6193 | 73.008 | 73.008 | 147.6 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 87.0769 | 39.2563 | 934299.1548 | 77.8583 | 77.8583 | 154.0883 | 80 | 60 | 32.6574 | 32 | 58.1
9/2/20XX 5:00:00 PM | 0.70833 | 5 | 77.9 | 60.8 | 86.1281 | 100.819 | 14.691 | 60 | 77.9 |  | 77.9 | 87.3033 | 0.1 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 65.0898 | 17.2692 | 411006.2631 | 34.2505 | 34.2505 | 95.329 | 0.2 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 67.558 | 19.7373 | 469748.7262 | 39.1457 | 39.1457 | 101.4527 | 0.3 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 70.0261 | 22.2055 | 528491.1894 | 44.0409 | 44.0409 | 107.5764 | 0.4 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 72.4943 | 24.6737 | 587233.6525 | 48.9361 | 48.9361 | 113.7001 | 0.5 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 74.9625 | 27.1419 | 645976.1156 | 53.8313 | 53.8313 | 119.8238 | 0.6 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 77.4307 | 29.61 | 704718.5787 | 58.7265 | 58.7265 | 125.9475 | 0.7 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 79.8988 | 32.0782 | 763461.0418 | 63.6218 | 63.6218 | 132.0713 | 0.8 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 82.367 | 34.5464 | 822203.5049 | 68.517 | 68.517 | 138.195 | 0.9 | 77.51 | 22.51 | 850878 | 70.9065 | 70.9065 | 84.8352 | 37.0145 | 880945.9681 | 73.4122 | 73.4122 | 144.3187 | 1 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 87.3033 | 39.4827 | 939688.4312 | 78.3074 | 78.3074 | 150.4424 | 80 | 60 | 32.3737 | 32 | 60.8
9/2/20XX 6:00:00 PM | 0.75 | 5 | 77 | 62.7 | 83.5433 | 97.7844 | 14.241 | 60 | 77 |  | 77 | 87.3884 | 0.1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 65.0983 | 17.2777 | 411208.734 | 34.2674 | 34.2674 | 95.0624 | 0.2 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 67.575 | 19.7544 | 470153.668 | 39.1795 | 39.1795 | 100.9195 | 0.3 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 70.0517 | 22.231 | 529098.6019 | 44.0916 | 44.0916 | 106.7766 | 0.4 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 72.5283 | 24.7077 | 588043.5359 | 49.0036 | 49.0036 | 112.6336 | 0.5 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 75.005 | 27.1844 | 646988.4699 | 53.9157 | 53.9157 | 118.4907 | 0.6 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 77.4817 | 29.6611 | 705933.4039 | 58.8278 | 58.8278 | 124.3478 | 0.7 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 79.9584 | 32.1377 | 764878.3378 | 63.7399 | 63.7399 | 130.2049 | 0.8 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 82.4351 | 34.6144 | 823823.2718 | 68.6519 | 68.6519 | 136.0619 | 0.9 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 84.9117 | 37.0911 | 882768.2058 | 73.564 | 73.564 | 141.919 | 1 | 77 | 22 | 831600 | 69.3 | 69.3 | 87.3884 | 39.5678 | 941713.1398 | 78.4761 | 78.4761 | 147.7761 | 75 | 65 | 32.1661 | 32 | 62.7
9/2/20XX 7:00:00 PM | 0.79167 | 5 | 75 | 67.7 | 78.0327 | 91.3149 | 13.2822 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/2/20XX 8:00:00 PM | 0.83333 | 5 | 74.5 | 69.2 | 76.7042 | 89.7555 | 13.0512 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/2/20XX 9:00:00 PM | 0.875 | 5 | 73.6 | 70.7 | 87.0056 | 99.7352 | 12.7296 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/2/20XX 10:00:00 PM | 0.91667 | 5 | 73.1 | 71.6 | 85.5092 | 98.0145 | 12.5053 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/2/20XX 11:00:00 PM | 0.95833 | 5 | 72.9 | 71.7 | 84.9169 | 97.3334 | 12.4165 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/2/20XX 12:00:00 AM | 0 | 6 | 72.3 | 75.1 | 83.1611 | 95.3147 | 12.1536 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/3/20XX 1:00:00 AM | 0.041667 | 6 | 71.6 | 75.8 | 81.1522 | 93.0054 | 11.8531 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/3/20XX 2:00:00 AM | 0.083333 | 6 | 71.4 | 76.3 | 80.586 | 92.3545 | 11.7685 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/3/20XX 3:00:00 AM | 0.125 | 6 | 70.7 | 77 | 78.6313 | 90.1079 | 11.4766 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/3/20XX 4:00:00 AM | 0.16667 | 6 | 70.2 | 79.1 | 77.2604 | 88.5325 | 11.2721 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/3/20XX 5:00:00 AM | 0.20833 | 6 | 70 | 79.8 | 76.7179 | 87.9091 | 11.1912 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/3/20XX 6:00:00 AM | 0.25 | 6 | 69.6 | 80.7 | 86.674 | 97.707 | 11.0331 | 80 | 69.6 |  | 69.6 | 87.4463 | 0.1 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 65.1041 | 17.2835 | 411346.4959 | 34.2789 | 34.2789 | 92.7429 | 0.2 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 67.5866 | 19.7659 | 470429.1917 | 39.2024 | 39.2024 | 96.2804 | 0.3 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 70.069 | 22.2484 | 529511.8876 | 44.126 | 44.126 | 99.818 | 0.4 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 72.5515 | 24.7309 | 588594.5834 | 49.0495 | 49.0495 | 103.3555 | 0.5 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 75.034 | 27.2133 | 647677.2793 | 53.9731 | 53.9731 | 106.8931 | 0.6 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 77.5164 | 29.6958 | 706759.9752 | 58.8967 | 58.8967 | 110.4307 | 0.7 | 70.92 | 15.92 | 601776 | 50.148 | 50.148 | 79.9989 | 32.1783 | 765842.671 | 63.8202 | 63.8202 | 113.9682 | 0.8 | 70.48 | 15.48 | 585144 | 48.762 | 48.762 | 82.4814 | 34.6607 | 824925.3669 | 68.7438 | 68.7438 | 117.5058 | 0.9 | 70.04 | 15.04 | 568512 | 47.376 | 47.376 | 84.9638 | 37.1432 | 884008.0627 | 73.6673 | 73.6673 | 121.0433 | 1 | 69.6 | 14.6 | 551880 | 45.99 | 45.99 | 87.4463 | 39.6257 | 943090.7586 | 78.5909 | 78.5909 | 124.5809 | 70 | 80 | 30.358 | 30 | 80.7
9/3/20XX 7:00:00 AM | 0.29167 | 6 | 70.8 | 79 | 78.908 | 90.4259 | 11.5179 | 70 | 70.8 |  | 70.8 | 89.2741 | 0.1 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 65.2869 | 17.4662 | 415696.647 | 34.6414 | 34.6414 | 93.4834 | 0.2 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 67.9521 | 20.1315 | 479129.4941 | 39.9275 | 39.9275 | 97.7615 | 0.3 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 70.6174 | 22.7967 | 542562.3411 | 45.2135 | 45.2135 | 102.0395 | 0.4 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 73.2826 | 25.462 | 605995.1881 | 50.4996 | 50.4996 | 106.3176 | 0.5 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 75.9479 | 28.1272 | 669428.0352 | 55.7857 | 55.7857 | 110.5957 | 0.6 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 78.6131 | 30.7925 | 732860.8822 | 61.0717 | 61.0717 | 114.8737 | 0.7 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 81.2784 | 33.4577 | 796293.7292 | 66.3578 | 66.3578 | 119.1518 | 0.8 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 83.9436 | 36.123 | 859726.5763 | 71.6439 | 71.6439 | 123.4299 | 0.9 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 86.6088 | 38.7882 | 923159.4233 | 76.93 | 76.93 | 127.708 | 1 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 89.2741 | 41.4535 | 986592.2703 | 82.216 | 82.216 | 131.986 | 70 | 80 | 30.9382 | 30 | 79
9/3/20XX 8:00:00 AM | 0.33333 | 6 | 71.9 | 77.5 | 82.008 | 93.989 | 11.9811 | 70 | 71.9 |  | 71.9 | 90.9938 | 0.1 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 65.4588 | 17.6382 | 419789.4804 | 34.9825 | 34.9825 | 94.171 | 0.2 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 68.2961 | 20.4754 | 487315.1608 | 40.6096 | 40.6096 | 99.1366 | 0.3 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 71.1333 | 23.3126 | 554840.8412 | 46.2367 | 46.2367 | 104.1022 | 0.4 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 73.9705 | 26.1499 | 622366.5215 | 51.8639 | 51.8639 | 109.0679 | 0.5 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 76.8077 | 28.9871 | 689892.2019 | 57.491 | 57.491 | 114.0335 | 0.6 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 79.6449 | 31.8243 | 757417.8823 | 63.1182 | 63.1182 | 118.9992 | 0.7 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 82.4821 | 34.6615 | 824943.5627 | 68.7453 | 68.7453 | 123.9648 | 0.8 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 85.3193 | 37.4987 | 892469.2431 | 74.3724 | 74.3724 | 128.9304 | 0.9 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 88.1566 | 40.3359 | 959994.9235 | 79.9996 | 79.9996 | 133.8961 | 1 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 90.9938 | 43.1731 | 1027520.6039 | 85.6267 | 85.6267 | 138.8617 | 70 | 75 | 31.4772 | 32 | 77.5
9/3/20XX 9:00:00 AM | 0.375 | 6 | 73.7 | 73.3 | 87.3075 | 100.0824 | 12.7749 | 70 | 73.7 |  | 73.7 | 91.5232 | 0.1 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 65.5118 | 17.6912 | 421049.6012 | 35.0875 | 35.0875 | 94.843 | 0.2 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 68.402 | 20.5813 | 489835.4025 | 40.8196 | 40.8196 | 100.4806 | 0.3 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 71.2921 | 23.4715 | 558621.2037 | 46.5518 | 46.5518 | 106.1183 | 0.4 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 74.1823 | 26.3616 | 627407.0049 | 52.2839 | 52.2839 | 111.7559 | 0.5 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 77.0724 | 29.2518 | 696192.8061 | 58.0161 | 58.0161 | 117.3936 | 0.6 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 79.9626 | 32.142 | 764978.6074 | 63.7482 | 63.7482 | 123.0312 | 0.7 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 82.8528 | 35.0321 | 833764.4086 | 69.4804 | 69.4804 | 128.6689 | 0.8 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 85.7429 | 37.9223 | 902550.2098 | 75.2125 | 75.2125 | 134.3065 | 0.9 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 88.6331 | 40.8124 | 971336.011 | 80.9447 | 80.9447 | 139.9442 | 1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 91.5232 | 43.7026 | 1040121.8123 | 86.6768 | 86.6768 | 145.5818 | 75 | 75 | 32.0024 | 32 | 73.3
9/3/20XX 10:00:00 AM | 0.41667 | 6 | 75.2 | 67.9 | 78.5695 | 91.9451 | 13.3756 | 60 | 75.2 |  | 75.2 | 89.1362 | 0.1 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.2731 | 17.4525 | 415368.5663 | 34.614 | 34.614 | 94.842 | 0.2 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 67.9246 | 20.1039 | 478473.3326 | 39.8728 | 39.8728 | 100.4788 | 0.3 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 70.576 | 22.7554 | 541578.0989 | 45.1315 | 45.1315 | 106.1155 | 0.4 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 73.2275 | 25.4068 | 604682.8653 | 50.3902 | 50.3902 | 111.7522 | 0.5 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 75.8789 | 28.0583 | 667787.6316 | 55.649 | 55.649 | 117.389 | 0.6 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 78.5304 | 30.7098 | 730892.3979 | 60.9077 | 60.9077 | 123.0257 | 0.7 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 81.1819 | 33.3612 | 793997.1642 | 66.1664 | 66.1664 | 128.6624 | 0.8 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 83.8333 | 36.0127 | 857101.9305 | 71.4252 | 71.4252 | 134.2992 | 0.9 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 86.4848 | 38.6641 | 920206.6968 | 76.6839 | 76.6839 | 139.9359 | 1 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 89.1362 | 41.3156 | 983311.4631 | 81.9426 | 81.9426 | 145.5726 | 75 | 70 | 31.9976 | 32 | 67.9
9/3/20XX 11:00:00 AM | 0.45833 | 6 | 77.5 | 63 | 84.9711 | 99.4607 | 14.4896 | 60 | 77.5 |  | 77.5 | 89.318 | 0.1 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 65.2913 | 17.4706 | 415801.1518 | 34.6501 | 34.6501 | 95.6026 | 0.2 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 67.9609 | 20.1403 | 479338.5037 | 39.9449 | 39.9449 | 101.9999 | 0.3 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 70.6305 | 22.8099 | 542875.8555 | 45.2397 | 45.2397 | 108.3972 | 0.4 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 73.3002 | 25.4795 | 606413.2074 | 50.5344 | 50.5344 | 114.7944 | 0.5 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 75.9698 | 28.1492 | 669950.5592 | 55.8292 | 55.8292 | 121.1917 | 0.6 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 78.6395 | 30.8188 | 733487.911 | 61.124 | 61.124 | 127.589 | 0.7 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 81.3091 | 33.4885 | 797025.2629 | 66.4188 | 66.4188 | 133.9863 | 0.8 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 83.9787 | 36.1581 | 860562.6147 | 71.7136 | 71.7136 | 140.3836 | 0.9 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 86.6484 | 38.8277 | 924099.9665 | 77.0083 | 77.0083 | 146.7808 | 1 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 89.318 | 41.4974 | 987637.3184 | 82.3031 | 82.3031 | 153.1781 | 75 | 65 | 32.5911 | 32 | 63
9/3/20XX 12:00:00 PM | 0.5 | 6 | 79.2 | 57.7 | 74.7029 | 89.9794 | 15.2766 | 50 | 79.2 |  | 79.2 | 86.4658 | 0.1 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 65.0061 | 17.1854 | 409013.0075 | 34.0844 | 34.0844 | 95.5724 | 0.2 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 67.3905 | 19.5698 | 465762.215 | 38.8135 | 38.8135 | 101.9395 | 0.3 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 69.7749 | 21.9543 | 522511.4225 | 43.5426 | 43.5426 | 108.3066 | 0.4 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 72.1593 | 24.3387 | 579260.63 | 48.2717 | 48.2717 | 114.6737 | 0.5 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 74.5437 | 26.7231 | 636009.8374 | 53.0008 | 53.0008 | 121.0408 | 0.6 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 76.9282 | 29.1075 | 692759.0449 | 57.7299 | 57.7299 | 127.4079 | 0.7 | 77.64 | 22.64 | 855792 | 71.316 | 71.316 | 79.3126 | 31.4919 | 749508.2524 | 62.459 | 62.459 | 133.775 | 0.8 | 78.16 | 23.16 | 875448 | 72.954 | 72.954 | 81.697 | 33.8764 | 806257.4599 | 67.1881 | 67.1881 | 140.1421 | 0.9 | 78.68 | 23.68 | 895104 | 74.592 | 74.592 | 84.0814 | 36.2608 | 863006.6674 | 71.9172 | 71.9172 | 146.5092 | 1 | 79.2 | 24.2 | 914760 | 76.23 | 76.23 | 86.4658 | 38.6452 | 919755.8749 | 76.6463 | 76.6463 | 152.8763 | 80 | 60 | 32.5617 | 32 | 57.7
9/3/20XX 1:00:00 PM | 0.54167 | 6 | 80 | 56.2 | 76.7237 | 92.42 | 15.6963 | 50 | 80 |  | 80 | 86.4554 | 0.1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 65.005 | 17.1844 | 408988.171 | 34.0823 | 34.0823 | 95.8223 | 0.2 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 67.3884 | 19.5678 | 465712.5421 | 38.8094 | 38.8094 | 102.4394 | 0.3 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 69.7718 | 21.9511 | 522436.9131 | 43.5364 | 43.5364 | 109.0564 | 0.4 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 72.1551 | 24.3345 | 579161.2841 | 48.2634 | 48.2634 | 115.6734 | 0.5 | 77 | 22 | 831600 | 69.3 | 69.3 | 74.5385 | 26.7179 | 635885.6551 | 52.9905 | 52.9905 | 122.2905 | 0.6 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 76.9219 | 29.1013 | 692610.0262 | 57.7175 | 57.7175 | 128.9075 | 0.7 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 79.3053 | 31.4846 | 749334.3972 | 62.4445 | 62.4445 | 135.5245 | 0.8 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 81.6886 | 33.868 | 806058.7682 | 67.1716 | 67.1716 | 142.1416 | 0.9 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 84.072 | 36.2514 | 862783.1393 | 71.8986 | 71.8986 | 148.7586 | 1 | 80 | 25 | 945000 | 78.75 | 78.75 | 86.4554 | 38.6348 | 919507.5103 | 76.6256 | 76.6256 | 155.3756 | 80 | 55 | 32.7564 | 32 | 56.2
9/3/20XX 2:00:00 PM | 0.58333 | 6 | 80.8 | 53.2 | 78.7895 | 94.9151 | 16.1256 | 50 | 80.8 |  | 80.8 | 83.9497 | 0.1 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 64.7544 | 16.9338 | 403024.5834 | 33.5854 | 33.5854 | 95.5774 | 0.2 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 66.8872 | 19.0666 | 453785.3669 | 37.8154 | 37.8154 | 101.9494 | 0.3 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 69.0201 | 21.1994 | 504546.1503 | 42.0455 | 42.0455 | 108.3215 | 0.4 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 71.1529 | 23.3322 | 555306.9337 | 46.2756 | 46.2756 | 114.6936 | 0.5 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 73.2857 | 25.465 | 606067.7172 | 50.5056 | 50.5056 | 121.0656 | 0.6 | 78.08 | 23.08 | 872424 | 72.702 | 72.702 | 75.4185 | 27.5978 | 656828.5006 | 54.7357 | 54.7357 | 127.4377 | 0.7 | 78.76 | 23.76 | 898128 | 74.844 | 74.844 | 77.5513 | 29.7306 | 707589.284 | 58.9658 | 58.9658 | 133.8098 | 0.8 | 79.44 | 24.44 | 923832 | 76.986 | 76.986 | 79.6841 | 31.8634 | 758350.0675 | 63.1958 | 63.1958 | 140.1818 | 0.9 | 80.12 | 25.12 | 949536 | 79.128 | 79.128 | 81.8169 | 33.9963 | 809110.8509 | 67.4259 | 67.4259 | 146.5539 | 1 | 80.8 | 25.8 | 975240 | 81.27 | 81.27 | 83.9497 | 36.1291 | 859871.6343 | 71.656 | 71.656 | 152.926 | 80 | 55 | 32.5598 | 32 | 53.2
9/3/20XX 3:00:00 PM | 0.625 | 6 | 80.2 | 54.1 | 77.2359 | 93.0386 | 15.8027 | 50 | 80.2 |  | 80.2 | 83.715 | 0.1 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 64.731 | 16.9103 | 402466.0813 | 33.5388 | 33.5388 | 95.3418 | 0.2 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 66.8403 | 19.0197 | 452668.3626 | 37.7224 | 37.7224 | 101.4784 | 0.3 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 68.9497 | 21.129 | 502870.6439 | 41.9059 | 41.9059 | 107.6149 | 0.4 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 71.059 | 23.2384 | 553072.9252 | 46.0894 | 46.0894 | 113.7514 | 0.5 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 73.1683 | 25.3477 | 603275.2065 | 50.2729 | 50.2729 | 119.8879 | 0.6 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 75.2777 | 27.457 | 653477.4878 | 54.4565 | 54.4565 | 126.0245 | 0.7 | 78.34 | 23.34 | 882252 | 73.521 | 73.521 | 77.387 | 29.5664 | 703679.7691 | 58.64 | 58.64 | 132.161 | 0.8 | 78.96 | 23.96 | 905688 | 75.474 | 75.474 | 79.4963 | 31.6757 | 753882.0504 | 62.8235 | 62.8235 | 138.2975 | 0.9 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 81.6057 | 33.7851 | 804084.3317 | 67.007 | 67.007 | 144.434 | 1 | 80.2 | 25.2 | 952560 | 79.38 | 79.38 | 83.715 | 35.8944 | 854286.613 | 71.1906 | 71.1906 | 150.5706 | 80 | 55 | 32.3758 | 32 | 54.1
9/3/20XX 4:00:00 PM | 0.66667 | 6 | 79.5 | 55 | 75.4555 | 90.8883 | 15.4328 | 50 | 79.5 |  | 79.5 | 83.1719 | 0.1 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 64.6767 | 16.856 | 401173.3984 | 33.4311 | 33.4311 | 95.0136 | 0.2 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 66.7317 | 18.9111 | 450082.9969 | 37.5069 | 37.5069 | 100.8219 | 0.3 | 75.65 | 20.65 | 780570 | 65.0475 | 65.0475 | 68.7867 | 20.9661 | 498992.5953 | 41.5827 | 41.5827 | 106.6302 | 0.4 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 70.8417 | 23.0211 | 547902.1937 | 45.6585 | 45.6585 | 112.4385 | 0.5 | 76.75 | 21.75 | 822150 | 68.5125 | 68.5125 | 72.8968 | 25.0761 | 596811.7922 | 49.7343 | 49.7343 | 118.2468 | 0.6 | 77.3 | 22.3 | 842940 | 70.245 | 70.245 | 74.9518 | 27.1312 | 645721.3906 | 53.8101 | 53.8101 | 124.0551 | 0.7 | 77.85 | 22.85 | 863730 | 71.9775 | 71.9775 | 77.0068 | 29.1862 | 694630.9891 | 57.8859 | 57.8859 | 129.8634 | 0.8 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 79.0618 | 31.2412 | 743540.5875 | 61.9617 | 61.9617 | 135.6717 | 0.9 | 78.95 | 23.95 | 905310 | 75.4425 | 75.4425 | 81.1169 | 33.2962 | 792450.1859 | 66.0375 | 66.0375 | 141.48 | 1 | 79.5 | 24.5 | 926100 | 77.175 | 77.175 | 83.1719 | 35.3513 | 841359.7844 | 70.1133 | 70.1133 | 147.2883 | 80 | 55 | 32.1189 | 32 | 55
9/3/20XX 5:00:00 PM | 0.70833 | 6 | 78.5 | 57.1 | 72.9711 | 87.8882 | 14.9171 | 50 | 78.5 |  | 78.5 | 83.5622 | 0.1 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 64.7157 | 16.8951 | 402102.3644 | 33.5085 | 33.5085 | 94.776 | 0.2 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 66.8097 | 18.9891 | 451940.9289 | 37.6617 | 37.6617 | 100.3467 | 0.3 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 68.9038 | 21.0832 | 501779.4933 | 41.815 | 41.815 | 105.9175 | 0.4 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 70.9979 | 23.1772 | 551618.0577 | 45.9682 | 45.9682 | 111.4882 | 0.5 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 73.0919 | 25.2713 | 601456.6222 | 50.1214 | 50.1214 | 117.0589 | 0.6 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 75.186 | 27.3653 | 651295.1866 | 54.2746 | 54.2746 | 122.6296 | 0.7 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 77.28 | 29.4594 | 701133.7511 | 58.4278 | 58.4278 | 128.2003 | 0.8 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 79.3741 | 31.5535 | 750972.3155 | 62.581 | 62.581 | 133.771 | 0.9 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 81.4681 | 33.6475 | 800810.8799 | 66.7342 | 66.7342 | 139.3417 | 1 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 83.5622 | 35.7416 | 850649.4444 | 70.8875 | 70.8875 | 144.9125 | 80 | 55 | 31.9348 | 32 | 57.1
9/3/20XX 6:00:00 PM | 0.75 | 6 | 78 | 55.5 | 71.7546 | 86.4193 | 14.6647 | 50 | 78 |  | 78 | 79.8202 | 0.1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 64.3415 | 16.5209 | 393196.4485 | 32.7664 | 32.7664 | 93.8764 | 0.2 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 66.0614 | 18.2407 | 434129.0971 | 36.1774 | 36.1774 | 98.5474 | 0.3 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 67.7812 | 19.9606 | 475061.7456 | 39.5885 | 39.5885 | 103.2185 | 0.4 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 69.5011 | 21.6804 | 515994.3941 | 42.9995 | 42.9995 | 107.8895 | 0.5 | 76 | 21 | 793800 | 66.15 | 66.15 | 71.2209 | 23.4003 | 556927.0427 | 46.4106 | 46.4106 | 112.5606 | 0.6 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 72.9408 | 25.1202 | 597859.6912 | 49.8216 | 49.8216 | 117.2316 | 0.7 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 74.6606 | 26.84 | 638792.3397 | 53.2327 | 53.2327 | 121.9027 | 0.8 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 76.3805 | 28.5599 | 679724.9883 | 56.6437 | 56.6437 | 126.5737 | 0.9 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 78.1004 | 30.2797 | 720657.6368 | 60.0548 | 60.0548 | 131.2448 | 1 | 78 | 23 | 869400 | 72.45 | 72.45 | 79.8202 | 31.9996 | 761590.2853 | 63.4659 | 63.4659 | 135.9159 | 80 | 55 | 31.2259 | 32 | 55.5
9/3/20XX 7:00:00 PM | 0.79167 | 6 | 76.7 | 59.8 | 68.6709 | 82.6964 | 14.0254 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/3/20XX 8:00:00 PM | 0.83333 | 6 | 75.5 | 63.3 | 79.3806 | 92.8973 | 13.5167 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/3/20XX 9:00:00 PM | 0.875 | 6 | 75.1 | 64.4 | 78.3007 | 91.6296 | 13.3289 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/3/20XX 10:00:00 PM | 0.91667 | 6 | 73.8 | 67.8 | 74.8769 | 87.6104 | 12.7335 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/3/20XX 11:00:00 PM | 0.95833 | 6 | 73.3 | 68.8 | 73.5946 | 86.1051 | 12.5105 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/3/20XX 12:00:00 AM | 0 | 7 | 72.3 | 70.5 | 83.1611 | 95.3147 | 12.1536 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/4/20XX 1:00:00 AM | 0.041667 | 7 | 71.8 | 70.2 | 81.7218 | 93.6601 | 11.9383 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/4/20XX 2:00:00 AM | 0.083333 | 7 | 71.7 | 71.3 | 81.4366 | 93.3322 | 11.8956 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/4/20XX 3:00:00 AM | 0.125 | 7 | 70.7 | 72.3 | 78.6313 | 90.1079 | 11.4766 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/4/20XX 4:00:00 AM | 0.16667 | 7 | 70.1 | 71.6 | 76.9888 | 88.2203 | 11.2316 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/4/20XX 5:00:00 AM | 0.20833 | 7 | 69.7 | 71 | 75.9105 | 86.9813 | 11.0709 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/4/20XX 6:00:00 AM | 0.25 | 7 | 69.3 | 72.5 | 74.8454 | 85.7577 | 10.9122 | 70 | 69.3 |  | 69.3 | 77.5735 | 0.1 | 73.53 | 18.53 | 700434 | 58.3695 | 58.3695 | 64.1168 | 16.2962 | 387849.1846 | 32.3208 | 32.3208 | 90.6903 | 0.2 | 73.06 | 18.06 | 682668 | 56.889 | 56.889 | 65.612 | 17.7914 | 423434.5691 | 35.2862 | 35.2862 | 92.1752 | 0.3 | 72.59 | 17.59 | 664902 | 55.4085 | 55.4085 | 67.1072 | 19.2866 | 459019.9537 | 38.2517 | 38.2517 | 93.6602 | 0.4 | 72.12 | 17.12 | 647136 | 53.928 | 53.928 | 68.6024 | 20.7817 | 494605.3382 | 41.2171 | 41.2171 | 95.1451 | 0.5 | 71.65 | 16.65 | 629370 | 52.4475 | 52.4475 | 70.0976 | 22.2769 | 530190.7228 | 44.1826 | 44.1826 | 96.6301 | 0.6 | 71.18 | 16.18 | 611604 | 50.967 | 50.967 | 71.5927 | 23.7721 | 565776.1073 | 47.148 | 47.148 | 98.115 | 0.7 | 70.71 | 15.71 | 593838 | 49.4865 | 49.4865 | 73.0879 | 25.2673 | 601361.4919 | 50.1135 | 50.1135 | 99.6 | 0.8 | 70.24 | 15.24 | 576072 | 48.006 | 48.006 | 74.5831 | 26.7625 | 636946.8764 | 53.0789 | 53.0789 | 101.0849 | 0.9 | 69.77 | 14.77 | 558306 | 46.5255 | 46.5255 | 76.0783 | 28.2577 | 672532.261 | 56.0444 | 56.0444 | 102.5699 | 1 | 69.3 | 14.3 | 540540 | 45.045 | 45.045 | 77.5735 | 29.7528 | 708117.6455 | 59.0098 | 59.0098 | 104.0548 | 70 | 70 | 28.743 | 28 | 72.5
9/4/20XX 7:00:00 AM | 0.29167 | 7 | 70.6 | 70.5 | 78.3554 | 89.7909 | 11.4354 | 70 | 70.6 |  | 70.6 | 78.9272 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 64.2522 | 16.4316 | 391071.0451 | 32.5893 | 32.5893 | 91.3683 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 65.8827 | 18.0621 | 429878.2903 | 35.8232 | 35.8232 | 93.5312 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 67.5133 | 19.6927 | 468685.5354 | 39.0571 | 39.0571 | 95.6941 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 69.1439 | 21.3232 | 507492.7806 | 42.2911 | 42.2911 | 97.8571 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 70.7744 | 22.9538 | 546300.0257 | 45.525 | 45.525 | 100.02 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 72.405 | 24.5843 | 585107.2709 | 48.7589 | 48.7589 | 102.1829 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 74.0355 | 26.2149 | 623914.516 | 51.9929 | 51.9929 | 104.3459 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 75.6661 | 27.8455 | 662721.7612 | 55.2268 | 55.2268 | 106.5088 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 77.2966 | 29.476 | 701529.0063 | 58.4608 | 58.4608 | 108.6718 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 78.9272 | 31.1066 | 740336.2515 | 61.6947 | 61.6947 | 110.8347 | 70 | 70 | 29.2729 | 30 | 70.5
9/4/20XX 8:00:00 AM | 0.33333 | 7 | 72.3 | 67.5 | 71.0864 | 83.1611 | 12.0747 | 60 | 72.3 |  | 72.3 | 80.1424 | 0.1 | 73.83 | 18.83 | 711774 | 59.3145 | 59.3145 | 64.3737 | 16.5531 | 393963.2126 | 32.8303 | 32.8303 | 92.1448 | 0.2 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 66.1258 | 18.3052 | 435662.6252 | 36.3052 | 36.3052 | 95.0842 | 0.3 | 73.49 | 18.49 | 698922 | 58.2435 | 58.2435 | 67.8779 | 20.0572 | 477362.0377 | 39.7802 | 39.7802 | 98.0237 | 0.4 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 69.6299 | 21.8093 | 519061.4503 | 43.2551 | 43.2551 | 100.9631 | 0.5 | 73.15 | 18.15 | 686070 | 57.1725 | 57.1725 | 71.382 | 23.5614 | 560760.8629 | 46.7301 | 46.7301 | 103.9026 | 0.6 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 73.1341 | 25.3135 | 602460.2755 | 50.205 | 50.205 | 106.842 | 0.7 | 72.81 | 17.81 | 673218 | 56.1015 | 56.1015 | 74.8862 | 27.0655 | 644159.6881 | 53.68 | 53.68 | 109.7815 | 0.8 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 76.6382 | 28.8176 | 685859.1006 | 57.1549 | 57.1549 | 112.7209 | 0.9 | 72.47 | 17.47 | 660366 | 55.0305 | 55.0305 | 78.3903 | 30.5697 | 727558.5132 | 60.6299 | 60.6299 | 115.6604 | 1 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 80.1424 | 32.3218 | 769257.9258 | 64.1048 | 64.1048 | 118.5998 | 70 | 65 | 29.8793 | 30 | 67.5
9/4/20XX 9:00:00 AM | 0.375 | 7 | 74.4 | 63.1 | 76.4409 | 89.4463 | 13.0054 | 60 | 74.4 |  | 74.4 | 80.4726 | 0.1 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 64.4067 | 16.5861 | 394749.0216 | 32.8958 | 32.8958 | 92.8718 | 0.2 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 66.1918 | 18.3712 | 437234.2432 | 36.4362 | 36.4362 | 96.5382 | 0.3 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 67.9769 | 20.1563 | 479719.4648 | 39.9766 | 39.9766 | 100.2046 | 0.4 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 69.762 | 21.9414 | 522204.6864 | 43.5171 | 43.5171 | 103.8711 | 0.5 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 71.5471 | 23.7265 | 564689.908 | 47.0575 | 47.0575 | 107.5375 | 0.6 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 73.3322 | 25.5116 | 607175.1296 | 50.5979 | 50.5979 | 111.2039 | 0.7 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 75.1173 | 27.2967 | 649660.3512 | 54.1384 | 54.1384 | 114.8704 | 0.8 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 76.9024 | 29.0817 | 692145.5728 | 57.6788 | 57.6788 | 118.5368 | 0.9 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 78.6875 | 30.8668 | 734630.7944 | 61.2192 | 61.2192 | 122.2032 | 1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 80.4726 | 32.6519 | 777116.016 | 64.7597 | 64.7597 | 125.8697 | 75 | 65 | 30.4457 | 30 | 63.1
9/4/20XX 10:00:00 AM | 0.41667 | 7 | 76.6 | 58 | 68.4384 | 82.4157 | 13.9773 | 50 | 76.6 |  | 76.6 | 79.6202 | 0.1 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 64.3215 | 16.5009 | 392720.4268 | 32.7267 | 32.7267 | 93.3957 | 0.2 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 66.0213 | 18.2007 | 433177.0535 | 36.0981 | 36.0981 | 97.5861 | 0.3 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 67.7212 | 19.9006 | 473633.6803 | 39.4695 | 39.4695 | 101.7765 | 0.4 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 69.4211 | 21.6004 | 514090.307 | 42.8409 | 42.8409 | 105.9669 | 0.5 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 71.1209 | 23.3003 | 554546.9338 | 46.2122 | 46.2122 | 110.1572 | 0.6 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 72.8208 | 25.0001 | 595003.5605 | 49.5836 | 49.5836 | 114.3476 | 0.7 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 74.5206 | 26.7 | 635460.1873 | 52.955 | 52.955 | 118.538 | 0.8 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 76.2205 | 28.3999 | 675916.814 | 56.3264 | 56.3264 | 122.7284 | 0.9 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 77.9204 | 30.0997 | 716373.4408 | 59.6978 | 59.6978 | 126.9188 | 1 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 79.6202 | 31.7996 | 756830.0676 | 63.0692 | 63.0692 | 131.1092 | 75 | 60 | 30.8514 | 30 | 58
9/4/20XX 11:00:00 AM | 0.45833 | 7 | 78.9 | 54.9 | 73.9565 | 89.0782 | 15.1216 | 50 | 78.9 |  | 78.9 | 81.3661 | 0.1 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 64.4961 | 16.6755 | 396875.7259 | 33.073 | 33.073 | 94.4665 | 0.2 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 66.3705 | 18.5499 | 441487.6519 | 36.7906 | 36.7906 | 99.7276 | 0.3 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 68.245 | 20.4244 | 486099.5778 | 40.5083 | 40.5083 | 104.9888 | 0.4 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 70.1194 | 22.2988 | 530711.5038 | 44.226 | 44.226 | 110.25 | 0.5 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 71.9939 | 24.1733 | 575323.4297 | 47.9436 | 47.9436 | 115.5111 | 0.6 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 73.8683 | 26.0477 | 619935.3557 | 51.6613 | 51.6613 | 120.7723 | 0.7 | 77.43 | 22.43 | 847854 | 70.6545 | 70.6545 | 75.7428 | 27.9222 | 664547.2816 | 55.3789 | 55.3789 | 126.0334 | 0.8 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 77.6172 | 29.7966 | 709159.2075 | 59.0966 | 59.0966 | 131.2946 | 0.9 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 79.4917 | 31.6711 | 753771.1335 | 62.8143 | 62.8143 | 136.5558 | 1 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 81.3661 | 33.5455 | 798383.0594 | 66.5319 | 66.5319 | 141.8169 | 80 | 55 | 31.6887 | 32 | 54.9
9/4/20XX 12:00:00 PM | 0.5 | 7 | 81.3 | 50.2 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 80.4317 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 64.4026 | 16.582 | 394651.7523 | 32.8876 | 32.8876 | 95.0371 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 66.1836 | 18.363 | 437039.7045 | 36.42 | 36.42 | 100.869 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 67.9647 | 20.144 | 479427.6568 | 39.9523 | 39.9523 | 106.7008 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 69.7457 | 21.925 | 521815.6091 | 43.4846 | 43.4846 | 112.5326 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 71.5267 | 23.706 | 564203.5614 | 47.017 | 47.017 | 118.3645 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 73.3077 | 25.487 | 606591.5136 | 50.5493 | 50.5493 | 124.1963 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 75.0887 | 27.268 | 648979.4659 | 54.0816 | 54.0816 | 130.0281 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 76.8697 | 29.0491 | 691367.4182 | 57.614 | 57.614 | 135.86 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 78.6507 | 30.8301 | 733755.3705 | 61.1463 | 61.1463 | 141.6918 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 80.4317 | 32.6111 | 776143.3227 | 64.6786 | 64.6786 | 147.5236 | 80 | 50 | 32.1305 | 32 | 50.2
9/4/20XX 1:00:00 PM | 0.54167 | 7 | 81.3 | 51.4 | 80.1037 | 96.5026 | 16.3989 | 50 | 81.3 |  | 81.3 | 82.3996 | 0.1 | 74.73 | 19.73 | 745794 | 62.1495 | 62.1495 | 64.5994 | 16.7788 | 399335.2686 | 33.2779 | 33.2779 | 95.4274 | 0.2 | 75.46 | 20.46 | 773388 | 64.449 | 64.449 | 66.5772 | 18.7566 | 446406.7372 | 37.2006 | 37.2006 | 101.6496 | 0.3 | 76.19 | 21.19 | 800982 | 66.7485 | 66.7485 | 68.555 | 20.7344 | 493478.2058 | 41.1232 | 41.1232 | 107.8717 | 0.4 | 76.92 | 21.92 | 828576 | 69.048 | 69.048 | 70.5328 | 22.7122 | 540549.6744 | 45.0458 | 45.0458 | 114.0938 | 0.5 | 77.65 | 22.65 | 856170 | 71.3475 | 71.3475 | 72.5106 | 24.69 | 587621.143 | 48.9684 | 48.9684 | 120.3159 | 0.6 | 78.38 | 23.38 | 883764 | 73.647 | 73.647 | 74.4884 | 26.6678 | 634692.6116 | 52.8911 | 52.8911 | 126.5381 | 0.7 | 79.11 | 24.11 | 911358 | 75.9465 | 75.9465 | 76.4662 | 28.6455 | 681764.0802 | 56.8137 | 56.8137 | 132.7602 | 0.8 | 79.84 | 24.84 | 938952 | 78.246 | 78.246 | 78.444 | 30.6233 | 728835.5488 | 60.7363 | 60.7363 | 138.9823 | 0.9 | 80.57 | 25.57 | 966546 | 80.5455 | 80.5455 | 80.4218 | 32.6011 | 775907.0174 | 64.6589 | 64.6589 | 145.2044 | 1 | 81.3 | 26.3 | 994140 | 82.845 | 82.845 | 82.3996 | 34.5789 | 822978.486 | 68.5815 | 68.5815 | 151.4265 | 80 | 50 | 32.4392 | 32 | 51.4
9/4/20XX 2:00:00 PM | 0.58333 | 7 | 81.9 | 49.5 | 65.0926 | 81.7045 | 16.6119 | 40 | 81.9 |  | 81.9 | 80.8739 | 0.1 | 74.79 | 19.79 | 748062 | 62.3385 | 62.3385 | 64.4469 | 16.6262 | 395704.1709 | 32.9753 | 32.9753 | 95.3138 | 0.2 | 75.58 | 20.58 | 777924 | 64.827 | 64.827 | 66.2721 | 18.4515 | 439144.5419 | 36.5954 | 36.5954 | 101.4224 | 0.3 | 76.37 | 21.37 | 807786 | 67.3155 | 67.3155 | 68.0973 | 20.2767 | 482584.9128 | 40.2154 | 40.2154 | 107.5309 | 0.4 | 77.16 | 22.16 | 837648 | 69.804 | 69.804 | 69.9225 | 22.1019 | 526025.2837 | 43.8354 | 43.8354 | 113.6394 | 0.5 | 77.95 | 22.95 | 867510 | 72.2925 | 72.2925 | 71.7478 | 23.9271 | 569465.6547 | 47.4555 | 47.4555 | 119.748 | 0.6 | 78.74 | 23.74 | 897372 | 74.781 | 74.781 | 73.573 | 25.7524 | 612906.0256 | 51.0755 | 51.0755 | 125.8565 | 0.7 | 79.53 | 24.53 | 927234 | 77.2695 | 77.2695 | 75.3982 | 27.5776 | 656346.3966 | 54.6955 | 54.6955 | 131.965 | 0.8 | 80.32 | 25.32 | 957096 | 79.758 | 79.758 | 77.2234 | 29.4028 | 699786.7675 | 58.3156 | 58.3156 | 138.0736 | 0.9 | 81.11 | 26.11 | 986958 | 82.2465 | 82.2465 | 79.0487 | 31.228 | 743227.1384 | 61.9356 | 61.9356 | 144.1821 | 1 | 81.9 | 26.9 | 1016820 | 84.735 | 84.735 | 80.8739 | 33.0533 | 786667.5094 | 65.5556 | 65.5556 | 150.2906 | 80 | 50 | 32.347 | 32 | 49.5
9/4/20XX 3:00:00 PM | 0.625 | 7 | 81.1 | 50.9 | 79.5759 | 95.865 | 16.2891 | 50 | 81.1 |  | 81.1 | 81.0419 | 0.1 | 74.71 | 19.71 | 745038 | 62.0865 | 62.0865 | 64.4637 | 16.643 | 396104.051 | 33.0087 | 33.0087 | 95.0952 | 0.2 | 75.42 | 20.42 | 771876 | 64.323 | 64.323 | 66.3057 | 18.4851 | 439944.302 | 36.662 | 36.662 | 100.985 | 0.3 | 76.13 | 21.13 | 798714 | 66.5595 | 66.5595 | 68.1477 | 20.3271 | 483784.5531 | 40.3154 | 40.3154 | 106.8749 | 0.4 | 76.84 | 21.84 | 825552 | 68.796 | 68.796 | 69.9897 | 22.1691 | 527624.8041 | 43.9687 | 43.9687 | 112.7647 | 0.5 | 77.55 | 22.55 | 852390 | 71.0325 | 71.0325 | 71.8318 | 24.0111 | 571465.0551 | 47.6221 | 47.6221 | 118.6546 | 0.6 | 78.26 | 23.26 | 879228 | 73.269 | 73.269 | 73.6738 | 25.8532 | 615305.3061 | 51.2754 | 51.2754 | 124.5444 | 0.7 | 78.97 | 23.97 | 906066 | 75.5055 | 75.5055 | 75.5158 | 27.6952 | 659145.5571 | 54.9288 | 54.9288 | 130.4343 | 0.8 | 79.68 | 24.68 | 932904 | 77.742 | 77.742 | 77.3579 | 29.5372 | 702985.8081 | 58.5822 | 58.5822 | 136.3242 | 0.9 | 80.39 | 25.39 | 959742 | 79.9785 | 79.9785 | 79.1999 | 31.3792 | 746826.0592 | 62.2355 | 62.2355 | 142.214 | 1 | 81.1 | 26.1 | 986580 | 82.215 | 82.215 | 81.0419 | 33.2213 | 790666.3102 | 65.8889 | 65.8889 | 148.1039 | 80 | 50 | 32.1772 | 32 | 50.9
9/4/20XX 4:00:00 PM | 0.66667 | 7 | 80.4 | 52.5 | 77.751 | 93.6607 | 15.9097 | 50 | 80.4 |  | 80.4 | 81.7284 | 0.1 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 64.5323 | 16.7117 | 397737.863 | 33.1448 | 33.1448 | 95.0108 | 0.2 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 66.443 | 18.6223 | 443211.9261 | 36.9343 | 36.9343 | 100.8163 | 0.3 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 68.3537 | 20.533 | 488685.9891 | 40.7238 | 40.7238 | 106.6218 | 0.4 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 70.2643 | 22.4437 | 534160.0521 | 44.5133 | 44.5133 | 112.4273 | 0.5 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 72.175 | 24.3544 | 579634.1151 | 48.3028 | 48.3028 | 118.2328 | 0.6 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 74.0857 | 26.265 | 625108.1782 | 52.0923 | 52.0923 | 124.0383 | 0.7 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 75.9964 | 28.1757 | 670582.2412 | 55.8819 | 55.8819 | 129.8439 | 0.8 | 79.12 | 24.12 | 911736 | 75.978 | 75.978 | 77.907 | 30.0864 | 716056.3042 | 59.6714 | 59.6714 | 135.6494 | 0.9 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 79.8177 | 31.9971 | 761530.3672 | 63.4609 | 63.4609 | 141.4549 | 1 | 80.4 | 25.4 | 960120 | 80.01 | 80.01 | 81.7284 | 33.9077 | 807004.4303 | 67.2504 | 67.2504 | 147.2604 | 80 | 50 | 32.1133 | 32 | 52.5
9/4/20XX 5:00:00 PM | 0.70833 | 7 | 79.3 | 55 | 74.9531 | 90.2816 | 15.3285 | 50 | 79.3 |  | 79.3 | 82.6173 | 0.1 | 74.53 | 19.53 | 738234 | 61.5195 | 61.5195 | 64.6212 | 16.8006 | 399853.4986 | 33.3211 | 33.3211 | 94.8406 | 0.2 | 75.06 | 20.06 | 758268 | 63.189 | 63.189 | 66.6208 | 18.8001 | 447443.1972 | 37.2869 | 37.2869 | 100.4759 | 0.3 | 75.59 | 20.59 | 778302 | 64.8585 | 64.8585 | 68.6203 | 20.7997 | 495032.8959 | 41.2527 | 41.2527 | 106.1112 | 0.4 | 76.12 | 21.12 | 798336 | 66.528 | 66.528 | 70.6199 | 22.7993 | 542622.5945 | 45.2185 | 45.2185 | 111.7465 | 0.5 | 76.65 | 21.65 | 818370 | 68.1975 | 68.1975 | 72.6195 | 24.7988 | 590212.2931 | 49.1844 | 49.1844 | 117.3819 | 0.6 | 77.18 | 22.18 | 838404 | 69.867 | 69.867 | 74.619 | 26.7984 | 637801.9917 | 53.1502 | 53.1502 | 123.0172 | 0.7 | 77.71 | 22.71 | 858438 | 71.5365 | 71.5365 | 76.6186 | 28.798 | 685391.6903 | 57.116 | 57.116 | 128.6525 | 0.8 | 78.24 | 23.24 | 878472 | 73.206 | 73.206 | 78.6182 | 30.7975 | 732981.3889 | 61.0818 | 61.0818 | 134.2878 | 0.9 | 78.77 | 23.77 | 898506 | 74.8755 | 74.8755 | 80.6177 | 32.7971 | 780571.0876 | 65.0476 | 65.0476 | 139.9231 | 1 | 79.3 | 24.3 | 918540 | 76.545 | 76.545 | 82.6173 | 34.7967 | 828160.7862 | 69.0134 | 69.0134 | 145.5584 | 80 | 55 | 31.9829 | 32 | 55
9/4/20XX 6:00:00 PM | 0.75 | 7 | 78.1 | 58 | 71.9966 | 86.7115 | 14.7149 | 50 | 78.1 |  | 78.1 | 83.7685 | 0.1 | 74.41 | 19.41 | 733698 | 61.1415 | 61.1415 | 64.7363 | 16.9157 | 402593.2899 | 33.5494 | 33.5494 | 94.6909 | 0.2 | 74.82 | 19.82 | 749196 | 62.433 | 62.433 | 66.851 | 19.0304 | 452922.7798 | 37.7436 | 37.7436 | 100.1766 | 0.3 | 75.23 | 20.23 | 764694 | 63.7245 | 63.7245 | 68.9657 | 21.1451 | 503252.2697 | 41.9377 | 41.9377 | 105.6622 | 0.4 | 75.64 | 20.64 | 780192 | 65.016 | 65.016 | 71.0804 | 23.2597 | 553581.7596 | 46.1318 | 46.1318 | 111.1478 | 0.5 | 76.05 | 21.05 | 795690 | 66.3075 | 66.3075 | 73.1951 | 25.3744 | 603911.2495 | 50.3259 | 50.3259 | 116.6334 | 0.6 | 76.46 | 21.46 | 811188 | 67.599 | 67.599 | 75.3097 | 27.4891 | 654240.7394 | 54.5201 | 54.5201 | 122.1191 | 0.7 | 76.87 | 21.87 | 826686 | 68.8905 | 68.8905 | 77.4244 | 29.6038 | 704570.2293 | 58.7142 | 58.7142 | 127.6047 | 0.8 | 77.28 | 22.28 | 842184 | 70.182 | 70.182 | 79.5391 | 31.7185 | 754899.7192 | 62.9083 | 62.9083 | 133.0903 | 0.9 | 77.69 | 22.69 | 857682 | 71.4735 | 71.4735 | 81.6538 | 33.8332 | 805229.2091 | 67.1024 | 67.1024 | 138.5759 | 1 | 78.1 | 23.1 | 873180 | 72.765 | 72.765 | 83.7685 | 35.9478 | 855558.699 | 71.2966 | 71.2966 | 144.0616 | 80 | 60 | 31.869 | 32 | 58
9/4/20XX 7:00:00 PM | 0.79167 | 7 | 76.9 | 59.9 | 69.138 | 83.2602 | 14.1222 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/4/20XX 8:00:00 PM | 0.83333 | 7 | 75.9 | 61.4 | 80.4731 | 94.1799 | 13.7068 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/4/20XX 9:00:00 PM | 0.875 | 7 | 75.2 | 63.6 | 78.5695 | 91.9451 | 13.3756 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/4/20XX 10:00:00 PM | 0.91667 | 7 | 74 | 63.4 | 75.3952 | 88.2187 | 12.8236 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/4/20XX 11:00:00 PM | 0.95833 | 7 | 73.3 | 64.5 | 73.5946 | 86.1051 | 12.5105 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/4/20XX 12:00:00 AM | 0 | 1 | 72.6 | 66.2 | 71.831 | 84.035 | 12.204 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/5/20XX 1:00:00 AM | 0.041667 | 1 | 71.9 | 67.1 | 70.104 | 82.008 | 11.904 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/5/20XX 2:00:00 AM | 0.083333 | 1 | 71.3 | 68.6 | 68.6524 | 80.3042 | 11.6518 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/5/20XX 3:00:00 AM | 0.125 | 1 | 70.9 | 71.9 | 79.1855 | 90.7449 | 11.5593 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/5/20XX 4:00:00 AM | 0.16667 | 1 | 70.4 | 73.3 | 77.8062 | 89.1597 | 11.3535 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/5/20XX 5:00:00 AM | 0.20833 | 1 | 70.2 | 74.4 | 77.2604 | 88.5325 | 11.2721 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/5/20XX 6:00:00 AM | 0.25 | 1 | 70 | 75.5 | 76.7179 | 87.9091 | 11.1912 | 70 | 70 |  | 70 | 82.8731 | 0.1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 64.6468 | 16.8261 | 400462.2895 | 33.3719 | 33.3719 | 91.9619 | 0.2 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 66.6719 | 18.8513 | 448660.779 | 37.3884 | 37.3884 | 94.7184 | 0.3 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 68.6971 | 20.8764 | 496859.2685 | 41.4049 | 41.4049 | 97.4749 | 0.4 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 70.7222 | 22.9016 | 545057.7579 | 45.4215 | 45.4215 | 100.2315 | 0.5 | 72 | 17 | 642600 | 53.55 | 53.55 | 72.7474 | 24.9267 | 593256.2474 | 49.438 | 49.438 | 102.988 | 0.6 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 74.7725 | 26.9519 | 641454.7369 | 53.4546 | 53.4546 | 105.7446 | 0.7 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 76.7977 | 28.977 | 689653.2264 | 57.4711 | 57.4711 | 108.5011 | 0.8 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 78.8228 | 31.0022 | 737851.7159 | 61.4876 | 61.4876 | 111.2576 | 0.9 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 80.848 | 33.0273 | 786050.2054 | 65.5042 | 65.5042 | 114.0142 | 1 | 70 | 15 | 567000 | 47.25 | 47.25 | 82.8731 | 35.0525 | 834248.6948 | 69.5207 | 69.5207 | 116.7707 | 70 | 75 | 29.7421 | 30 | 75.5
9/5/20XX 7:00:00 AM | 0.29167 | 1 | 71 | 73.5 | 79.4639 | 91.0648 | 11.6009 | 70 | 71 |  | 71 | 83.5242 | 0.1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.7119 | 16.8913 | 402012.0133 | 33.501 | 33.501 | 92.406 | 0.2 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 66.8022 | 18.9815 | 451760.2267 | 37.6467 | 37.6467 | 95.6067 | 0.3 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 68.8924 | 21.0718 | 501508.44 | 41.7924 | 41.7924 | 98.8074 | 0.4 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 70.9827 | 23.162 | 551256.6534 | 45.9381 | 45.9381 | 102.0081 | 0.5 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 73.0729 | 25.2523 | 601004.8667 | 50.0837 | 50.0837 | 105.2087 | 0.6 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 75.1632 | 27.3426 | 650753.0801 | 54.2294 | 54.2294 | 108.4094 | 0.7 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 77.2535 | 29.4328 | 700501.2934 | 58.3751 | 58.3751 | 111.6101 | 0.8 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 79.3437 | 31.5231 | 750249.5068 | 62.5208 | 62.5208 | 114.8108 | 0.9 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 81.434 | 33.6133 | 799997.7201 | 66.6665 | 66.6665 | 118.0115 | 1 | 71 | 16 | 604800 | 50.4 | 50.4 | 83.5242 | 35.7036 | 849745.9335 | 70.8122 | 70.8122 | 121.2122 | 70 | 75 | 30.0891 | 30 | 73.5
9/5/20XX 8:00:00 AM | 0.33333 | 1 | 72.4 | 71 | 83.4515 | 95.6486 | 12.1971 | 70 | 72.4 |  | 72.4 | 84.6712 | 0.1 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 64.8266 | 17.006 | 404741.8098 | 33.7285 | 33.7285 | 93.0745 | 0.2 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 67.0315 | 19.2109 | 457219.8197 | 38.1017 | 38.1017 | 96.9437 | 0.3 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 69.2365 | 21.4159 | 509697.8295 | 42.4748 | 42.4748 | 100.8128 | 0.4 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 71.4415 | 23.6208 | 562175.8393 | 46.848 | 46.848 | 104.682 | 0.5 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 73.6464 | 25.8258 | 614653.8492 | 51.2212 | 51.2212 | 108.5512 | 0.6 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 75.8514 | 28.0308 | 667131.859 | 55.5943 | 55.5943 | 112.4203 | 0.7 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 78.0563 | 30.2357 | 719609.8688 | 59.9675 | 59.9675 | 116.2895 | 0.8 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 80.2613 | 32.4407 | 772087.8787 | 64.3407 | 64.3407 | 120.1587 | 0.9 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 82.4663 | 34.6456 | 824565.8885 | 68.7138 | 68.7138 | 124.0278 | 1 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 84.6712 | 36.8506 | 877043.8984 | 73.087 | 73.087 | 127.897 | 70 | 70 | 30.6118 | 30 | 71
9/5/20XX 9:00:00 AM | 0.375 | 1 | 74.7 | 66 | 77.2333 | 90.3765 | 13.1432 | 60 | 74.7 |  | 74.7 | 85.1192 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 64.8714 | 17.0508 | 405808.0525 | 33.8173 | 33.8173 | 93.8878 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 67.1211 | 19.3005 | 459352.3049 | 38.2794 | 38.2794 | 98.5704 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 69.3709 | 21.5503 | 512896.5574 | 42.7414 | 42.7414 | 103.2529 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 71.6207 | 23.8 | 566440.8099 | 47.2034 | 47.2034 | 107.9354 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 73.8704 | 26.0498 | 619985.0624 | 51.6654 | 51.6654 | 112.6179 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 76.1202 | 28.2996 | 673529.3148 | 56.1274 | 56.1274 | 117.3004 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 78.3699 | 30.5493 | 727073.5673 | 60.5895 | 60.5895 | 121.983 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 80.6197 | 32.7991 | 780617.8198 | 65.0515 | 65.0515 | 126.6655 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 82.8695 | 35.0488 | 834162.0723 | 69.5135 | 69.5135 | 131.348 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 85.1192 | 37.2986 | 887706.3247 | 73.9755 | 73.9755 | 136.0305 | 75 | 65 | 31.2463 | 32 | 66
9/5/20XX 10:00:00 AM | 0.41667 | 1 | 76.5 | 62.7 | 82.1358 | 96.1318 | 13.9961 | 60 | 76.5 |  | 76.5 | 85.9147 | 0.1 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 64.9509 | 17.1303 | 407701.318 | 33.9751 | 33.9751 | 94.6126 | 0.2 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 67.2802 | 19.4596 | 463138.836 | 38.5949 | 38.5949 | 100.0199 | 0.3 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 69.6096 | 21.7889 | 518576.354 | 43.2147 | 43.2147 | 105.4272 | 0.4 | 75 | 20 | 756000 | 63 | 63 | 71.9389 | 24.1182 | 574013.872 | 47.8345 | 47.8345 | 110.8345 | 0.5 | 75.25 | 20.25 | 765450 | 63.7875 | 63.7875 | 74.2682 | 26.4475 | 629451.3899 | 52.4543 | 52.4543 | 116.2418 | 0.6 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 76.5975 | 28.7768 | 684888.9079 | 57.0741 | 57.0741 | 121.6491 | 0.7 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 78.9268 | 31.1062 | 740326.4259 | 61.6939 | 61.6939 | 127.0564 | 0.8 | 76 | 21 | 793800 | 66.15 | 66.15 | 81.2561 | 33.4355 | 795763.9439 | 66.3137 | 66.3137 | 132.4637 | 0.9 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 83.5854 | 35.7648 | 851201.4619 | 70.9335 | 70.9335 | 137.871 | 1 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 85.9147 | 38.0941 | 906638.9799 | 75.5532 | 75.5532 | 143.2782 | 75 | 65 | 31.8125 | 32 | 62.7
9/5/20XX 11:00:00 AM | 0.45833 | 1 | 77.4 | 58.9 | 70.3173 | 84.6839 | 14.3667 | 50 | 77.4 |  | 77.4 | 83.1036 | 0.1 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 64.6698 | 16.8492 | 401010.9107 | 33.4176 | 33.4176 | 94.3386 | 0.2 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 66.718 | 18.8974 | 449758.0214 | 37.4798 | 37.4798 | 99.4718 | 0.3 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 68.7662 | 20.9456 | 498505.1321 | 41.5421 | 41.5421 | 104.6051 | 0.4 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 70.8144 | 22.9938 | 547252.2428 | 45.6044 | 45.6044 | 109.7384 | 0.5 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 72.8626 | 25.042 | 595999.3534 | 49.6666 | 49.6666 | 114.8716 | 0.6 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 74.9108 | 27.0902 | 644746.4641 | 53.7289 | 53.7289 | 120.0049 | 0.7 | 76.38 | 21.38 | 808164 | 67.347 | 67.347 | 76.959 | 29.1384 | 693493.5748 | 57.7911 | 57.7911 | 125.1381 | 0.8 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 79.0072 | 31.1866 | 742240.6855 | 61.8534 | 61.8534 | 130.2714 | 0.9 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 81.0554 | 33.2348 | 790987.7962 | 65.9156 | 65.9156 | 135.4046 | 1 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 83.1036 | 35.283 | 839734.9069 | 69.9779 | 69.9779 | 140.5379 | 75 | 60 | 31.5931 | 32 | 58.9
9/5/20XX 12:00:00 PM | 0.5 | 1 | 79.6 | 54.5 | 75.7077 | 91.1929 | 15.4852 | 50 | 79.6 |  | 79.6 | 82.6761 | 0.1 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 64.6271 | 16.8064 | 399993.3586 | 33.3328 | 33.3328 | 94.9468 | 0.2 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 66.6325 | 18.8119 | 447722.9172 | 37.3102 | 37.3102 | 100.6882 | 0.3 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 68.638 | 20.8173 | 495452.4758 | 41.2877 | 41.2877 | 106.4297 | 0.4 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 70.6434 | 22.8228 | 543182.0344 | 45.2652 | 45.2652 | 112.1712 | 0.5 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 72.6489 | 24.8282 | 590911.593 | 49.2426 | 49.2426 | 117.9126 | 0.6 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 74.6543 | 26.8337 | 638641.1516 | 53.2201 | 53.2201 | 123.6541 | 0.7 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 76.6597 | 28.8391 | 686370.7102 | 57.1976 | 57.1976 | 129.3956 | 0.8 | 78.48 | 23.48 | 887544 | 73.962 | 73.962 | 78.6652 | 30.8445 | 734100.2688 | 61.175 | 61.175 | 135.137 | 0.9 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 80.6706 | 32.85 | 781829.8274 | 65.1525 | 65.1525 | 140.8785 | 1 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 82.6761 | 34.8554 | 829559.386 | 69.1299 | 69.1299 | 146.6199 | 80 | 55 | 32.0657 | 32 | 54.5
9/5/20XX 1:00:00 PM | 0.54167 | 1 | 81 | 51 | 79.313 | 95.5475 | 16.2344 | 50 | 81 |  | 81 | 80.9365 | 0.1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 64.4531 | 16.6325 | 395853.1596 | 32.9878 | 32.9878 | 95.0428 | 0.2 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 66.2846 | 18.464 | 439442.5191 | 36.6202 | 36.6202 | 100.8802 | 0.3 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 68.1161 | 20.2955 | 483031.8787 | 40.2527 | 40.2527 | 106.7177 | 0.4 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 69.9476 | 22.1269 | 526621.2383 | 43.8851 | 43.8851 | 112.5551 | 0.5 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 71.7791 | 23.9584 | 570210.5978 | 47.5175 | 47.5175 | 118.3925 | 0.6 | 78.2 | 23.2 | 876960 | 73.08 | 73.08 | 73.6105 | 25.7899 | 613799.9574 | 51.15 | 51.15 | 124.23 | 0.7 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 75.442 | 27.6214 | 657389.317 | 54.7824 | 54.7824 | 130.0674 | 0.8 | 79.6 | 24.6 | 929880 | 77.49 | 77.49 | 77.2735 | 29.4529 | 700978.6765 | 58.4149 | 58.4149 | 135.9049 | 0.9 | 80.3 | 25.3 | 956340 | 79.695 | 79.695 | 79.105 | 31.2844 | 744568.0361 | 62.0473 | 62.0473 | 141.7423 | 1 | 81 | 26 | 982800 | 81.9 | 81.9 | 80.9365 | 33.1159 | 788157.3956 | 65.6798 | 65.6798 | 147.5798 | 80 | 50 | 32.1362 | 32 | 51
9/5/20XX 2:00:00 PM | 0.58333 | 1 | 81.4 | 51.5 | 80.3687 | 96.8227 | 16.454 | 50 | 81.4 |  | 81.4 | 82.8368 | 0.1 | 74.74 | 19.74 | 746172 | 62.181 | 62.181 | 64.6432 | 16.8225 | 400375.9189 | 33.3647 | 33.3647 | 95.5457 | 0.2 | 75.48 | 20.48 | 774144 | 64.512 | 64.512 | 66.6647 | 18.844 | 448488.0378 | 37.374 | 37.374 | 101.886 | 0.3 | 76.22 | 21.22 | 802116 | 66.843 | 66.843 | 68.6862 | 20.8656 | 496600.1567 | 41.3833 | 41.3833 | 108.2263 | 0.4 | 76.96 | 21.96 | 830088 | 69.174 | 69.174 | 70.7077 | 22.8871 | 544712.2756 | 45.3927 | 45.3927 | 114.5667 | 0.5 | 77.7 | 22.7 | 858060 | 71.505 | 71.505 | 72.7292 | 24.9086 | 592824.3945 | 49.402 | 49.402 | 120.907 | 0.6 | 78.44 | 23.44 | 886032 | 73.836 | 73.836 | 74.7507 | 26.9301 | 640936.5134 | 53.4114 | 53.4114 | 127.2474 | 0.7 | 79.18 | 24.18 | 914004 | 76.167 | 76.167 | 76.7723 | 28.9516 | 689048.6323 | 57.4207 | 57.4207 | 133.5877 | 0.8 | 79.92 | 24.92 | 941976 | 78.498 | 78.498 | 78.7938 | 30.9731 | 737160.7512 | 61.4301 | 61.4301 | 139.9281 | 0.9 | 80.66 | 25.66 | 969948 | 80.829 | 80.829 | 80.8153 | 32.9947 | 785272.8701 | 65.4394 | 65.4394 | 146.2684 | 1 | 81.4 | 26.4 | 997920 | 83.16 | 83.16 | 82.8368 | 35.0162 | 833384.989 | 69.4487 | 69.4487 | 152.6087 | 80 | 50 | 32.5324 | 32 | 51.5
9/5/20XX 3:00:00 PM | 0.625 | 1 | 81.2 | 51 | 79.8394 | 96.1834 | 16.3439 | 50 | 81.2 |  | 81.2 | 81.4738 | 0.1 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 64.5069 | 16.6862 | 397132.0429 | 33.0943 | 33.0943 | 95.2123 | 0.2 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 66.3921 | 18.5714 | 442000.2858 | 36.8334 | 36.8334 | 101.2194 | 0.3 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 68.2773 | 20.4567 | 486868.5288 | 40.5724 | 40.5724 | 107.2264 | 0.4 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 70.1625 | 22.3419 | 531736.7717 | 44.3114 | 44.3114 | 113.2334 | 0.5 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 72.0477 | 24.2271 | 576605.0146 | 48.0504 | 48.0504 | 119.2404 | 0.6 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 73.933 | 26.1123 | 621473.2575 | 51.7894 | 51.7894 | 125.2474 | 0.7 | 79.04 | 24.04 | 908712 | 75.726 | 75.726 | 75.8182 | 27.9975 | 666341.5004 | 55.5285 | 55.5285 | 131.2545 | 0.8 | 79.76 | 24.76 | 935928 | 77.994 | 77.994 | 77.7034 | 29.8828 | 711209.7433 | 59.2675 | 59.2675 | 137.2615 | 0.9 | 80.48 | 25.48 | 963144 | 80.262 | 80.262 | 79.5886 | 31.768 | 756077.9863 | 63.0065 | 63.0065 | 143.2685 | 1 | 81.2 | 26.2 | 990360 | 82.53 | 82.53 | 81.4738 | 33.6532 | 800946.2292 | 66.7455 | 66.7455 | 149.2755 | 80 | 50 | 32.2695 | 32 | 51
9/5/20XX 4:00:00 PM | 0.66667 | 1 | 80.2 | 52.7 | 77.2359 | 93.0386 | 15.8027 | 50 | 80.2 |  | 80.2 | 81.5027 | 0.1 | 74.62 | 19.62 | 741636 | 61.803 | 61.803 | 64.5097 | 16.6891 | 397200.6242 | 33.1001 | 33.1001 | 94.9031 | 0.2 | 75.24 | 20.24 | 765072 | 63.756 | 63.756 | 66.3978 | 18.5772 | 442137.4485 | 36.8448 | 36.8448 | 100.6008 | 0.3 | 75.86 | 20.86 | 788508 | 65.709 | 65.709 | 68.2859 | 20.4653 | 487074.2727 | 40.5895 | 40.5895 | 106.2985 | 0.4 | 76.48 | 21.48 | 811944 | 67.662 | 67.662 | 70.174 | 22.3534 | 532011.097 | 44.3343 | 44.3343 | 111.9963 | 0.5 | 77.1 | 22.1 | 835380 | 69.615 | 69.615 | 72.0621 | 24.2415 | 576947.9212 | 48.079 | 48.079 | 117.694 | 0.6 | 77.72 | 22.72 | 858816 | 71.568 | 71.568 | 73.9502 | 26.1296 | 621884.7455 | 51.8237 | 51.8237 | 123.3917 | 0.7 | 78.34 | 23.34 | 882252 | 73.521 | 73.521 | 75.8383 | 28.0177 | 666821.5697 | 55.5685 | 55.5685 | 129.0895 | 0.8 | 78.96 | 23.96 | 905688 | 75.474 | 75.474 | 77.7264 | 29.9058 | 711758.3939 | 59.3132 | 59.3132 | 134.7872 | 0.9 | 79.58 | 24.58 | 929124 | 77.427 | 77.427 | 79.6145 | 31.7939 | 756695.2182 | 63.0579 | 63.0579 | 140.4849 | 1 | 80.2 | 25.2 | 952560 | 79.38 | 79.38 | 81.5027 | 33.682 | 801632.0424 | 66.8027 | 66.8027 | 146.1827 | 80 | 55 | 32.0288 | 32 | 52.7
9/5/20XX 5:00:00 PM | 0.70833 | 1 | 78.8 | 55.2 | 73.7091 | 88.7794 | 15.0703 | 50 | 78.8 |  | 78.8 | 81.5457 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 64.514 | 16.6934 | 397303.044 | 33.1086 | 33.1086 | 94.4706 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 66.4064 | 18.5858 | 442342.288 | 36.8619 | 36.8619 | 99.7359 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 68.2988 | 20.4782 | 487381.5319 | 40.6151 | 40.6151 | 105.0011 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 70.1913 | 22.3706 | 532420.7759 | 44.3684 | 44.3684 | 110.2664 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 72.0837 | 24.263 | 577460.0199 | 48.1217 | 48.1217 | 115.5317 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 73.9761 | 26.1554 | 622499.2639 | 51.8749 | 51.8749 | 120.7969 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 75.8685 | 28.0478 | 667538.5078 | 55.6282 | 55.6282 | 126.0622 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 77.7609 | 29.9402 | 712577.7518 | 59.3815 | 59.3815 | 131.3275 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 79.6533 | 31.8326 | 757616.9958 | 63.1347 | 63.1347 | 136.5927 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 81.5457 | 33.7251 | 802656.2398 | 66.888 | 66.888 | 141.858 | 80 | 55 | 31.6923 | 32 | 55.2
9/5/20XX 6:00:00 PM | 0.75 | 1 | 77.4 | 57.7 | 70.3173 | 84.6839 | 14.3667 | 50 | 77.4 |  | 77.4 | 81.3796 | 0.1 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 64.4974 | 16.6768 | 396907.7922 | 33.0756 | 33.0756 | 93.9966 | 0.2 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 66.3732 | 18.5526 | 441551.7845 | 36.796 | 36.796 | 98.788 | 0.3 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 68.249 | 20.4284 | 486195.7767 | 40.5163 | 40.5163 | 103.5793 | 0.4 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 70.1248 | 22.3042 | 530839.769 | 44.2366 | 44.2366 | 108.3706 | 0.5 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 72.0006 | 24.18 | 575483.7612 | 47.957 | 47.957 | 113.162 | 0.6 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 73.8764 | 26.0558 | 620127.7534 | 51.6773 | 51.6773 | 117.9533 | 0.7 | 76.38 | 21.38 | 808164 | 67.347 | 67.347 | 75.7522 | 27.9316 | 664771.7457 | 55.3976 | 55.3976 | 122.7446 | 0.8 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 77.628 | 29.8074 | 709415.7379 | 59.118 | 59.118 | 127.536 | 0.9 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 79.5038 | 31.6832 | 754059.7302 | 62.8383 | 62.8383 | 132.3273 | 1 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 81.3796 | 33.559 | 798703.7224 | 66.5586 | 66.5586 | 137.1186 | 75 | 60 | 31.3231 | 32 | 57.7
9/5/20XX 7:00:00 PM | 0.79167 | 1 | 75.9 | 59.2 | 66.8292 | 80.4731 | 13.644 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/5/20XX 8:00:00 PM | 0.83333 | 1 | 74.3 | 63.6 | 76.1783 | 89.138 | 12.9597 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/5/20XX 9:00:00 PM | 0.875 | 1 | 73.9 | 63.1 | 75.1356 | 87.9141 | 12.7785 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/5/20XX 10:00:00 PM | 0.91667 | 1 | 73.4 | 62.5 | 73.8495 | 86.4044 | 12.5549 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/5/20XX 11:00:00 PM | 0.95833 | 1 | 72.8 | 63.8 | 72.3311 | 84.6221 | 12.291 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/5/20XX 12:00:00 AM | 0 | 2 | 72.3 | 65.6 | 71.0864 | 83.1611 | 12.0747 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/6/20XX 1:00:00 AM | 0.041667 | 2 | 70.7 | 68.8 | 67.227 | 78.6313 | 11.4043 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/6/20XX 2:00:00 AM | 0.083333 | 2 | 69.9 | 70.4 | 76.4479 | 87.5989 | 11.151 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/6/20XX 3:00:00 AM | 0.125 | 2 | 68.9 | 73.7 | 73.7935 | 84.5492 | 10.7557 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/6/20XX 4:00:00 AM | 0.16667 | 2 | 68.3 | 74.5 | 72.24 | 82.7647 | 10.5247 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/6/20XX 5:00:00 AM | 0.20833 | 2 | 68.1 | 73 | 71.7287 | 82.1774 | 10.4487 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/6/20XX 6:00:00 AM | 0.25 | 2 | 67.6 | 74.8 | 70.4642 | 80.7252 | 10.261 | 70 | 67.6 |  | 67.6 | 75.3895 | 0.1 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 63.8984 | 16.0778 | 382651.3169 | 31.8876 | 31.8876 | 89.7216 | 0.2 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 65.1752 | 17.3546 | 413038.8339 | 34.4199 | 34.4199 | 90.2379 | 0.3 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 66.452 | 18.6314 | 443426.3508 | 36.9522 | 36.9522 | 90.7542 | 0.4 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 67.7288 | 19.9081 | 473813.8678 | 39.4845 | 39.4845 | 91.2705 | 0.5 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 69.0056 | 21.1849 | 504201.3847 | 42.0168 | 42.0168 | 91.7868 | 0.6 | 70.16 | 15.16 | 573048 | 47.754 | 47.754 | 70.2824 | 22.4617 | 534588.9017 | 44.5491 | 44.5491 | 92.3031 | 0.7 | 69.52 | 14.52 | 548856 | 45.738 | 45.738 | 71.5591 | 23.7385 | 564976.4186 | 47.0814 | 47.0814 | 92.8194 | 0.8 | 68.88 | 13.88 | 524664 | 43.722 | 43.722 | 72.8359 | 25.0153 | 595363.9356 | 49.6137 | 49.6137 | 93.3357 | 0.9 | 68.24 | 13.24 | 500472 | 41.706 | 41.706 | 74.1127 | 26.2921 | 625751.4525 | 52.146 | 52.146 | 93.852 | 1 | 67.6 | 12.6 | 476280 | 39.69 | 39.69 | 75.3895 | 27.5689 | 656138.9695 | 54.6782 | 54.6782 | 94.3682 | 70 | 75 | 27.9859 | 28 | 74.8
9/6/20XX 7:00:00 AM | 0.29167 | 2 | 68.8 | 73.2 | 73.5326 | 84.2494 | 10.7169 | 70 | 68.8 |  | 68.8 | 76.962 | 0.1 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 64.0557 | 16.235 | 386393.7977 | 32.1995 | 32.1995 | 90.4115 | 0.2 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 65.4897 | 17.6691 | 420523.7955 | 35.0436 | 35.0436 | 91.6176 | 0.3 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 66.9237 | 19.1031 | 454653.7932 | 37.8878 | 37.8878 | 92.8238 | 0.4 | 71.92 | 16.92 | 639576 | 53.298 | 53.298 | 68.3578 | 20.5371 | 488783.791 | 40.732 | 40.732 | 94.03 | 0.5 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 69.7918 | 21.9712 | 522913.7887 | 43.5761 | 43.5761 | 95.2361 | 0.6 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 71.2258 | 23.4052 | 557043.7865 | 46.4203 | 46.4203 | 96.4423 | 0.7 | 70.36 | 15.36 | 580608 | 48.384 | 48.384 | 72.6599 | 24.8392 | 591173.7842 | 49.2645 | 49.2645 | 97.6485 | 0.8 | 69.84 | 14.84 | 560952 | 46.746 | 46.746 | 74.0939 | 26.2733 | 625303.782 | 52.1086 | 52.1086 | 98.8546 | 0.9 | 69.32 | 14.32 | 541296 | 45.108 | 45.108 | 75.5279 | 27.7073 | 659433.7797 | 54.9528 | 54.9528 | 100.0608 | 1 | 68.8 | 13.8 | 521640 | 43.47 | 43.47 | 76.962 | 29.1413 | 693563.7775 | 57.797 | 57.797 | 101.267 | 70 | 75 | 28.5251 | 28 | 73.2
9/6/20XX 8:00:00 AM | 0.33333 | 2 | 69.8 | 70.4 | 76.1788 | 87.2896 | 11.1108 | 70 | 69.8 |  | 69.8 | 76.6232 | 0.1 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 64.0218 | 16.2012 | 385587.5875 | 32.1323 | 32.1323 | 90.6593 | 0.2 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 65.422 | 17.6013 | 418911.3749 | 34.9093 | 34.9093 | 92.1133 | 0.3 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 66.8221 | 19.0015 | 452235.1624 | 37.6863 | 37.6863 | 93.5673 | 0.4 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 68.2223 | 20.4016 | 485558.9499 | 40.4632 | 40.4632 | 95.0212 | 0.5 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 69.6224 | 21.8018 | 518882.7373 | 43.2402 | 43.2402 | 96.4752 | 0.6 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 71.0226 | 23.202 | 552206.5248 | 46.0172 | 46.0172 | 97.9292 | 0.7 | 71.06 | 16.06 | 607068 | 50.589 | 50.589 | 72.4227 | 24.6021 | 585530.3123 | 48.7942 | 48.7942 | 99.3832 | 0.8 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 73.8229 | 26.0023 | 618854.0997 | 51.5712 | 51.5712 | 100.8372 | 0.9 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 75.2231 | 27.4024 | 652177.8872 | 54.3482 | 54.3482 | 102.2912 | 1 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 76.6232 | 28.8026 | 685501.6747 | 57.1251 | 57.1251 | 103.7451 | 70 | 70 | 28.7171 | 28 | 70.4
9/6/20XX 9:00:00 AM | 0.375 | 2 | 71.2 | 67.3 | 68.413 | 80.0233 | 11.6102 | 60 | 71.2 |  | 71.2 | 76.8885 | 0.1 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 64.0483 | 16.2277 | 386218.9647 | 32.1849 | 32.1849 | 91.1529 | 0.2 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 65.475 | 17.6544 | 420174.1294 | 35.0145 | 35.0145 | 93.1005 | 0.3 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 66.9017 | 19.0811 | 454129.2942 | 37.8441 | 37.8441 | 95.0481 | 0.4 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 68.3284 | 20.5078 | 488084.4589 | 40.6737 | 40.6737 | 96.9957 | 0.5 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 69.7551 | 21.9344 | 522039.6236 | 43.5033 | 43.5033 | 98.9433 | 0.6 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 71.1818 | 23.3611 | 555994.7883 | 46.3329 | 46.3329 | 100.8909 | 0.7 | 72.04 | 17.04 | 644112 | 53.676 | 53.676 | 72.6084 | 24.7878 | 589949.9531 | 49.1625 | 49.1625 | 102.8385 | 0.8 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 74.0351 | 26.2145 | 623905.1178 | 51.9921 | 51.9921 | 104.7861 | 0.9 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 75.4618 | 27.6412 | 657860.2825 | 54.8217 | 54.8217 | 106.7337 | 1 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 76.8885 | 29.0679 | 691815.4472 | 57.6513 | 57.6513 | 108.6813 | 70 | 65 | 29.1013 | 30 | 67.3
9/6/20XX 10:00:00 AM | 0.41667 | 2 | 72.8 | 63.9 | 72.3311 | 84.6221 | 12.291 | 60 | 72.8 |  | 72.8 | 77.1246 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 64.0719 | 16.2513 | 386780.8396 | 32.2317 | 32.2317 | 91.7037 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 65.5222 | 17.7016 | 421297.8792 | 35.1082 | 35.1082 | 94.2022 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 66.9725 | 19.1519 | 455814.9188 | 37.9846 | 37.9846 | 96.7006 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 68.4228 | 20.6022 | 490331.9583 | 40.861 | 40.861 | 99.199 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 69.8731 | 22.0525 | 524848.9979 | 43.7374 | 43.7374 | 101.6974 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 71.3234 | 23.5028 | 559366.0375 | 46.6138 | 46.6138 | 104.1958 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 72.7737 | 24.9531 | 593883.0771 | 49.4903 | 49.4903 | 106.6943 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 74.224 | 26.4034 | 628400.1167 | 52.3667 | 52.3667 | 109.1927 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 75.6743 | 27.8537 | 662917.1563 | 55.2431 | 55.2431 | 111.6911 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 77.1246 | 29.304 | 697434.1958 | 58.1195 | 58.1195 | 114.1895 | 75 | 65 | 29.5301 | 30 | 63.9
9/6/20XX 11:00:00 AM | 0.45833 | 2 | 74.8 | 59.8 | 64.365 | 77.499 | 13.134 | 50 | 74.8 |  | 74.8 | 77.2363 | 0.1 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 64.0831 | 16.2625 | 387046.6958 | 32.2539 | 32.2539 | 92.3559 | 0.2 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 65.5446 | 17.7239 | 421829.5915 | 35.1525 | 35.1525 | 95.5065 | 0.3 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 67.006 | 19.1854 | 456612.4873 | 38.051 | 38.051 | 98.657 | 0.4 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 68.4675 | 20.6469 | 491395.383 | 40.9496 | 40.9496 | 101.8076 | 0.5 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 69.929 | 22.1083 | 526178.2788 | 43.8482 | 43.8482 | 104.9582 | 0.6 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 71.3904 | 23.5698 | 560961.1745 | 46.7468 | 46.7468 | 108.1088 | 0.7 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 72.8519 | 25.0313 | 595744.0703 | 49.6453 | 49.6453 | 111.2593 | 0.8 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 74.3134 | 26.4927 | 630526.9661 | 52.5439 | 52.5439 | 114.4099 | 0.9 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 75.7748 | 27.9542 | 665309.8618 | 55.4425 | 55.4425 | 117.5605 | 1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 77.2363 | 29.4157 | 700092.7576 | 58.3411 | 58.3411 | 120.7111 | 75 | 60 | 30.0373 | 30 | 59.8
9/6/20XX 12:00:00 PM | 0.5 | 2 | 76.5 | 57.7 | 68.2065 | 82.1358 | 13.9292 | 50 | 76.5 |  | 76.5 | 78.932 | 0.1 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 64.2527 | 16.432 | 391082.5752 | 32.5902 | 32.5902 | 93.2277 | 0.2 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 65.8837 | 18.0631 | 429901.3504 | 35.8251 | 35.8251 | 97.2501 | 0.3 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 67.5148 | 19.6941 | 468720.1257 | 39.06 | 39.06 | 101.2725 | 0.4 | 75 | 20 | 756000 | 63 | 63 | 69.1458 | 21.3252 | 507538.9009 | 42.2949 | 42.2949 | 105.2949 | 0.5 | 75.25 | 20.25 | 765450 | 63.7875 | 63.7875 | 70.7768 | 22.9562 | 546357.6761 | 45.5298 | 45.5298 | 109.3173 | 0.6 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 72.4079 | 24.5872 | 585176.4513 | 48.7647 | 48.7647 | 113.3397 | 0.7 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 74.0389 | 26.2183 | 623995.2266 | 51.9996 | 51.9996 | 117.3621 | 0.8 | 76 | 21 | 793800 | 66.15 | 66.15 | 75.67 | 27.8493 | 662814.0018 | 55.2345 | 55.2345 | 121.3845 | 0.9 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 77.301 | 29.4804 | 701632.777 | 58.4694 | 58.4694 | 125.4069 | 1 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 78.932 | 31.1114 | 740451.5522 | 61.7043 | 61.7043 | 129.4293 | 75 | 60 | 30.7192 | 30 | 57.7
9/6/20XX 1:00:00 PM | 0.54167 | 2 | 77.2 | 56.7 | 69.8436 | 84.112 | 14.2685 | 50 | 77.2 |  | 77.2 | 79.4034 | 0.1 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 64.2998 | 16.4792 | 392204.4595 | 32.6837 | 32.6837 | 93.5417 | 0.2 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 65.978 | 18.1574 | 432145.119 | 36.0121 | 36.0121 | 97.8781 | 0.3 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 67.6562 | 19.8355 | 472085.7785 | 39.3405 | 39.3405 | 102.2145 | 0.4 | 75.28 | 20.28 | 766584 | 63.882 | 63.882 | 69.3343 | 21.5137 | 512026.438 | 42.6689 | 42.6689 | 106.5509 | 0.5 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 71.0125 | 23.1919 | 551967.0975 | 45.9973 | 45.9973 | 110.8873 | 0.6 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 72.6907 | 24.8701 | 591907.757 | 49.3256 | 49.3256 | 115.2236 | 0.7 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 74.3689 | 26.5483 | 631848.4165 | 52.654 | 52.654 | 119.56 | 0.8 | 76.56 | 21.56 | 814968 | 67.914 | 67.914 | 76.0471 | 28.2264 | 671789.076 | 55.9824 | 55.9824 | 123.8964 | 0.9 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 77.7252 | 29.9046 | 711729.7355 | 59.3108 | 59.3108 | 128.2328 | 1 | 77.2 | 22.2 | 839160 | 69.93 | 69.93 | 79.4034 | 31.5828 | 751670.395 | 62.6392 | 62.6392 | 132.5692 | 75 | 55 | 30.9645 | 30 | 56.7
9/6/20XX 2:00:00 PM | 0.58333 | 2 | 77 | 56.7 | 69.3725 | 83.5433 | 14.1708 | 50 | 77 |  | 77 | 78.867 | 0.1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 64.2462 | 16.4255 | 390927.6763 | 32.5773 | 32.5773 | 93.3723 | 0.2 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 65.8707 | 18.0501 | 429591.5527 | 35.7993 | 35.7993 | 97.5393 | 0.3 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 67.4952 | 19.6746 | 468255.429 | 39.0213 | 39.0213 | 101.7063 | 0.4 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 69.1198 | 21.2991 | 506919.3053 | 42.2433 | 42.2433 | 105.8733 | 0.5 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 70.7443 | 22.9237 | 545583.1817 | 45.4653 | 45.4653 | 110.0403 | 0.6 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 72.3688 | 24.5482 | 584247.058 | 48.6873 | 48.6873 | 114.2073 | 0.7 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 73.9934 | 26.1727 | 622910.9343 | 51.9092 | 51.9092 | 118.3742 | 0.8 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 75.6179 | 27.7973 | 661574.8107 | 55.1312 | 55.1312 | 122.5412 | 0.9 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 77.2424 | 29.4218 | 700238.687 | 58.3532 | 58.3532 | 126.7082 | 1 | 77 | 22 | 831600 | 69.3 | 69.3 | 78.867 | 31.0463 | 738902.5633 | 61.5752 | 61.5752 | 130.8752 | 75 | 55 | 30.8315 | 30 | 56.7
9/6/20XX 3:00:00 PM | 0.625 | 2 | 76.2 | 58.3 | 67.5149 | 81.3009 | 13.786 | 50 | 76.2 |  | 76.2 | 78.9572 | 0.1 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 64.2552 | 16.4346 | 391142.5682 | 32.5952 | 32.5952 | 93.1382 | 0.2 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 65.8888 | 18.0681 | 430021.3363 | 35.8351 | 35.8351 | 97.0711 | 0.3 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 67.5223 | 19.7017 | 468900.1045 | 39.075 | 39.075 | 101.004 | 0.4 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 69.1559 | 21.3352 | 507778.8726 | 42.3149 | 42.3149 | 104.9369 | 0.5 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 70.7894 | 22.9688 | 546657.6408 | 45.5548 | 45.5548 | 108.8698 | 0.6 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 72.423 | 24.6024 | 585536.409 | 48.7947 | 48.7947 | 112.8027 | 0.7 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 74.0566 | 26.2359 | 624415.1771 | 52.0346 | 52.0346 | 116.7356 | 0.8 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 75.6901 | 27.8695 | 663293.9453 | 55.2745 | 55.2745 | 120.6685 | 0.9 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 77.3237 | 29.5031 | 702172.7134 | 58.5144 | 58.5144 | 124.6014 | 1 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 78.9572 | 31.1366 | 741051.4816 | 61.7543 | 61.7543 | 128.5343 | 75 | 60 | 30.6496 | 30 | 58.3
9/6/20XX 4:00:00 PM | 0.66667 | 2 | 75 | 59.9 | 64.8072 | 78.0327 | 13.2255 | 50 | 75 |  | 75 | 77.9004 | 0.1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 64.1495 | 16.3289 | 388627.3212 | 32.3856 | 32.3856 | 92.5506 | 0.2 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 65.6774 | 17.8568 | 424990.8424 | 35.4159 | 35.4159 | 95.8959 | 0.3 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 67.2053 | 19.3846 | 461354.3635 | 38.4462 | 38.4462 | 99.2412 | 0.4 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 68.7331 | 20.9125 | 497717.8847 | 41.4765 | 41.4765 | 102.5865 | 0.5 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 70.261 | 22.4404 | 534081.4059 | 44.5068 | 44.5068 | 105.9318 | 0.6 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 71.7889 | 23.9683 | 570444.9271 | 47.5371 | 47.5371 | 109.2771 | 0.7 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 73.3168 | 25.4962 | 606808.4482 | 50.5674 | 50.5674 | 112.6224 | 0.8 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 74.8447 | 27.024 | 643171.9694 | 53.5977 | 53.5977 | 115.9677 | 0.9 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 76.3725 | 28.5519 | 679535.4906 | 56.628 | 56.628 | 119.313 | 1 | 75 | 20 | 756000 | 63 | 63 | 77.9004 | 30.0798 | 715899.0118 | 59.6583 | 59.6583 | 122.6583 | 75 | 60 | 30.1902 | 30 | 59.9
9/6/20XX 5:00:00 PM | 0.70833 | 2 | 74.3 | 60.6 | 76.1783 | 89.138 | 12.9597 | 60 | 74.3 |  | 74.3 | 76.9559 | 0.1 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 64.0551 | 16.2344 | 386379.3218 | 32.1983 | 32.1983 | 92.1428 | 0.2 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 65.4885 | 17.6679 | 420494.8437 | 35.0412 | 35.0412 | 95.0802 | 0.3 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 66.9219 | 19.1013 | 454610.3655 | 37.8842 | 37.8842 | 98.0177 | 0.4 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 68.3553 | 20.5347 | 488725.8874 | 40.7272 | 40.7272 | 100.9552 | 0.5 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 69.7888 | 21.9681 | 522841.4092 | 43.5701 | 43.5701 | 103.8926 | 0.6 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 71.2222 | 23.4016 | 556956.9311 | 46.4131 | 46.4131 | 106.8301 | 0.7 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 72.6556 | 24.835 | 591072.4529 | 49.256 | 49.256 | 109.7675 | 0.8 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 74.089 | 26.2684 | 625187.9748 | 52.099 | 52.099 | 112.705 | 0.9 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 75.5225 | 27.7018 | 659303.4966 | 54.942 | 54.942 | 115.6425 | 1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 76.9559 | 29.1353 | 693419.0185 | 57.7849 | 57.7849 | 118.5799 | 75 | 60 | 29.871 | 30 | 60.6
9/6/20XX 6:00:00 PM | 0.75 | 2 | 71.9 | 67.9 | 70.104 | 82.008 | 11.904 | 60 | 71.9 |  | 71.9 | 79.5081 | 0.1 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 64.3103 | 16.4896 | 392453.6439 | 32.7045 | 32.7045 | 91.893 | 0.2 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 65.9989 | 18.1783 | 432643.4878 | 36.0536 | 36.0536 | 94.5806 | 0.3 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 67.6876 | 19.8669 | 472833.3318 | 39.4028 | 39.4028 | 97.2683 | 0.4 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 69.3762 | 21.5556 | 513023.1757 | 42.7519 | 42.7519 | 99.9559 | 0.5 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 71.0649 | 23.2442 | 553213.0196 | 46.1011 | 46.1011 | 102.6436 | 0.6 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 72.7535 | 24.9329 | 593402.8635 | 49.4502 | 49.4502 | 105.3312 | 0.7 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 74.4422 | 26.6215 | 633592.7074 | 52.7994 | 52.7994 | 108.0189 | 0.8 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 76.1308 | 28.3102 | 673782.5514 | 56.1485 | 56.1485 | 110.7065 | 0.9 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 77.8195 | 29.9988 | 713972.3953 | 59.4977 | 59.4977 | 113.3942 | 1 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 79.5081 | 31.6875 | 754162.2392 | 62.8469 | 62.8469 | 116.0819 | 70 | 70 | 29.6822 | 30 | 67.9
9/6/20XX 7:00:00 PM | 0.79167 | 2 | 71.1 | 69.4 | 68.1744 | 79.7432 | 11.5688 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/6/20XX 8:00:00 PM | 0.83333 | 2 | 70.5 | 71.8 | 78.0804 | 89.4748 | 11.3944 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/6/20XX 9:00:00 PM | 0.875 | 2 | 69.9 | 72.7 | 76.4479 | 87.5989 | 11.151 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/6/20XX 10:00:00 PM | 0.91667 | 2 | 69.2 | 73.8 | 74.5812 | 85.4541 | 10.8729 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/6/20XX 11:00:00 PM | 0.95833 | 2 | 68.1 | 77.9 | 71.7287 | 82.1774 | 10.4487 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/6/20XX 12:00:00 AM | 0 | 3 | 67.9 | 78.7 | 71.2205 | 81.5937 | 10.3732 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/7/20XX 1:00:00 AM | 0.041667 | 3 | 67.7 | 80.3 | 81.0138 | 91.3046 | 10.2909 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/7/20XX 2:00:00 AM | 0.083333 | 3 | 67.1 | 81.6 | 79.2959 | 89.362 | 10.0661 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/7/20XX 3:00:00 AM | 0.125 | 3 | 66.9 | 82.5 | 78.7306 | 88.7227 | 9.9922 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/7/20XX 4:00:00 AM | 0.16667 | 3 | 67 | 81.7 | 79.0128 | 89.0419 | 10.0291 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/7/20XX 5:00:00 AM | 0.20833 | 3 | 66.6 | 82.9 | 77.8893 | 87.7716 | 9.8822 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/7/20XX 6:00:00 AM | 0.25 | 3 | 66.8 | 82.7 | 78.4493 | 88.4047 | 9.9554 | 80 | 66.8 |  | 66.8 | 81.1372 | 0.1 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 64.4732 | 16.6526 | 396330.8878 | 33.0276 | 33.0276 | 90.6096 | 0.2 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 66.3247 | 18.5041 | 440397.9756 | 36.6998 | 36.6998 | 92.0138 | 0.3 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 68.1763 | 20.3557 | 484465.0635 | 40.3721 | 40.3721 | 93.4181 | 0.4 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 70.0279 | 22.2072 | 528532.1513 | 44.0443 | 44.0443 | 94.8223 | 0.5 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 71.8794 | 24.0588 | 572599.2391 | 47.7166 | 47.7166 | 96.2266 | 0.6 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 73.731 | 25.9103 | 616666.3269 | 51.3889 | 51.3889 | 97.6309 | 0.7 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 75.5825 | 27.7619 | 660733.4148 | 55.0611 | 55.0611 | 99.0351 | 0.8 | 68.24 | 13.24 | 500472 | 41.706 | 41.706 | 77.4341 | 29.6135 | 704800.5026 | 58.7334 | 58.7334 | 100.4394 | 0.9 | 67.52 | 12.52 | 473256 | 39.438 | 39.438 | 79.2857 | 31.465 | 748867.5904 | 62.4056 | 62.4056 | 101.8436 | 1 | 66.8 | 11.8 | 446040 | 37.17 | 37.17 | 81.1372 | 33.3166 | 792934.6782 | 66.0779 | 66.0779 | 103.2479 | 65 | 85 | 28.6865 | 28 | 82.7
9/7/20XX 7:00:00 AM | 0.29167 | 3 | 67.6 | 80.6 | 80.7252 | 90.9783 | 10.2531 | 80 | 67.6 |  | 67.6 | 81.3404 | 0.1 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 64.4935 | 16.6729 | 396814.4219 | 33.0679 | 33.0679 | 90.9019 | 0.2 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 66.3654 | 18.5447 | 441365.0438 | 36.7804 | 36.7804 | 92.5984 | 0.3 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 68.2373 | 20.4166 | 485915.6656 | 40.493 | 40.493 | 94.295 | 0.4 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 70.1091 | 22.2885 | 530466.2875 | 44.2055 | 44.2055 | 95.9915 | 0.5 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 71.981 | 24.1604 | 575016.9094 | 47.9181 | 47.9181 | 97.6881 | 0.6 | 70.16 | 15.16 | 573048 | 47.754 | 47.754 | 73.8529 | 26.0322 | 619567.5313 | 51.6306 | 51.6306 | 99.3846 | 0.7 | 69.52 | 14.52 | 548856 | 45.738 | 45.738 | 75.7248 | 27.9041 | 664118.1532 | 55.3432 | 55.3432 | 101.0812 | 0.8 | 68.88 | 13.88 | 524664 | 43.722 | 43.722 | 77.5966 | 29.776 | 708668.775 | 59.0557 | 59.0557 | 102.7777 | 0.9 | 68.24 | 13.24 | 500472 | 41.706 | 41.706 | 79.4685 | 31.6479 | 753219.3969 | 62.7683 | 62.7683 | 104.4743 | 1 | 67.6 | 12.6 | 476280 | 39.69 | 39.69 | 81.3404 | 33.5197 | 797770.0188 | 66.4808 | 66.4808 | 106.1708 | 70 | 80 | 28.9143 | 28 | 80.6
9/7/20XX 8:00:00 AM | 0.33333 | 3 | 68.8 | 76.1 | 73.5326 | 84.2494 | 10.7169 | 70 | 68.8 |  | 68.8 | 80.0699 | 0.1 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 64.3665 | 16.5458 | 393790.5859 | 32.8159 | 32.8159 | 91.0279 | 0.2 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 66.1113 | 18.2906 | 435317.3717 | 36.2764 | 36.2764 | 92.8504 | 0.3 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 67.8561 | 20.0355 | 476844.1576 | 39.737 | 39.737 | 94.673 | 0.4 | 71.92 | 16.92 | 639576 | 53.298 | 53.298 | 69.6009 | 21.7803 | 518370.9435 | 43.1976 | 43.1976 | 96.4956 | 0.5 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 71.3457 | 23.5251 | 559897.7293 | 46.6581 | 46.6581 | 98.3181 | 0.6 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 73.0906 | 25.2699 | 601424.5152 | 50.1187 | 50.1187 | 100.1407 | 0.7 | 70.36 | 15.36 | 580608 | 48.384 | 48.384 | 74.8354 | 27.0148 | 642951.301 | 53.5793 | 53.5793 | 101.9633 | 0.8 | 69.84 | 14.84 | 560952 | 46.746 | 46.746 | 76.5802 | 28.7596 | 684478.0869 | 57.0398 | 57.0398 | 103.7858 | 0.9 | 69.32 | 14.32 | 541296 | 45.108 | 45.108 | 78.325 | 30.5044 | 726004.8728 | 60.5004 | 60.5004 | 105.6084 | 1 | 68.8 | 13.8 | 521640 | 43.47 | 43.47 | 80.0699 | 32.2492 | 767531.6586 | 63.961 | 63.961 | 107.431 | 70 | 75 | 29.0102 | 30 | 76.1
9/7/20XX 9:00:00 AM | 0.375 | 3 | 70.7 | 71.7 | 78.6313 | 90.1079 | 11.4766 | 70 | 70.7 |  | 70.7 | 80.5823 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 64.4177 | 16.5971 | 395010.1977 | 32.9175 | 32.9175 | 91.728 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 66.2138 | 18.3931 | 437756.5954 | 36.4797 | 36.4797 | 94.2507 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 68.0098 | 20.1892 | 480502.9931 | 40.0419 | 40.0419 | 96.7734 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 69.8059 | 21.9853 | 523249.3908 | 43.6041 | 43.6041 | 99.2961 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 71.602 | 23.7813 | 565995.7885 | 47.1663 | 47.1663 | 101.8188 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 73.398 | 25.5774 | 608742.1862 | 50.7285 | 50.7285 | 104.3415 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 75.1941 | 27.3735 | 651488.5839 | 54.2907 | 54.2907 | 106.8642 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 76.9902 | 29.1695 | 694234.9816 | 57.8529 | 57.8529 | 109.3869 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 78.7862 | 30.9656 | 736981.3793 | 61.4151 | 61.4151 | 111.9096 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 80.5823 | 32.7617 | 779727.777 | 64.9773 | 64.9773 | 114.4323 | 70 | 70 | 29.5559 | 30 | 71.7
9/7/20XX 10:00:00 AM | 0.41667 | 3 | 73.2 | 63.9 | 73.3404 | 85.8067 | 12.4664 | 60 | 73.2 |  | 73.2 | 78.2022 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 64.1797 | 16.3591 | 389345.6496 | 32.4455 | 32.4455 | 92.0435 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 65.7378 | 17.9171 | 426427.4992 | 35.5356 | 35.5356 | 94.8816 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 67.2958 | 19.4752 | 463509.3487 | 38.6258 | 38.6258 | 97.7198 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 68.8539 | 21.0332 | 500591.1983 | 41.7159 | 41.7159 | 100.5579 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 70.4119 | 22.5913 | 537673.0479 | 44.8061 | 44.8061 | 103.3961 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 71.97 | 24.1494 | 574754.8975 | 47.8962 | 47.8962 | 106.2342 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 73.5281 | 25.7074 | 611836.747 | 50.9864 | 50.9864 | 109.0724 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 75.0861 | 27.2655 | 648918.5966 | 54.0765 | 54.0765 | 111.9105 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 76.6442 | 28.8235 | 686000.4462 | 57.1667 | 57.1667 | 114.7487 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 78.2022 | 30.3816 | 723082.2958 | 60.2569 | 60.2569 | 117.5869 | 75 | 65 | 29.7965 | 30 | 63.9
9/7/20XX 11:00:00 AM | 0.45833 | 3 | 76.4 | 59.2 | 67.9753 | 81.8567 | 13.8813 | 50 | 76.4 |  | 76.4 | 80.7462 | 0.1 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 64.4341 | 16.6135 | 395400.1717 | 32.95 | 32.95 | 93.556 | 0.2 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 66.2465 | 18.4259 | 438536.5435 | 36.5447 | 36.5447 | 97.9067 | 0.3 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 68.059 | 20.2384 | 481672.9152 | 40.1394 | 40.1394 | 102.2574 | 0.4 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 69.8714 | 22.0508 | 524809.287 | 43.7341 | 43.7341 | 106.6081 | 0.5 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 71.6839 | 23.8633 | 567945.6587 | 47.3288 | 47.3288 | 110.9588 | 0.6 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 73.4963 | 25.6757 | 611082.0304 | 50.9235 | 50.9235 | 115.3095 | 0.7 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 75.3088 | 27.4882 | 654218.4022 | 54.5182 | 54.5182 | 119.6602 | 0.8 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 77.1213 | 29.3006 | 697354.7739 | 58.1129 | 58.1129 | 124.0109 | 0.9 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 78.9337 | 31.1131 | 740491.1457 | 61.7076 | 61.7076 | 128.3616 | 1 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 80.7462 | 32.9255 | 783627.5174 | 65.3023 | 65.3023 | 132.7123 | 75 | 60 | 30.9787 | 30 | 59.2
9/7/20XX 12:00:00 PM | 0.5 | 3 | 77.5 | 57.5 | 70.5552 | 84.9711 | 14.416 | 50 | 77.5 |  | 77.5 | 81.3671 | 0.1 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 64.4962 | 16.6756 | 396878.1024 | 33.0732 | 33.0732 | 94.0257 | 0.2 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 66.3707 | 18.5501 | 441492.4047 | 36.791 | 36.791 | 98.846 | 0.3 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 68.2453 | 20.4247 | 486106.7071 | 40.5089 | 40.5089 | 103.6664 | 0.4 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 70.1198 | 22.2992 | 530721.0094 | 44.2268 | 44.2268 | 108.4868 | 0.5 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 71.9944 | 24.1738 | 575335.3118 | 47.9446 | 47.9446 | 113.3071 | 0.6 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 73.8689 | 26.0483 | 619949.6141 | 51.6625 | 51.6625 | 118.1275 | 0.7 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 75.7435 | 27.9229 | 664563.9165 | 55.3803 | 55.3803 | 122.9478 | 0.8 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 77.618 | 29.7974 | 709178.2188 | 59.0982 | 59.0982 | 127.7682 | 0.9 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 79.4926 | 31.672 | 753792.5212 | 62.816 | 62.816 | 132.5885 | 1 | 77.5 | 22.5 | 850500 | 70.875 | 70.875 | 81.3671 | 33.5465 | 798406.8235 | 66.5339 | 66.5339 | 137.4089 | 75 | 55 | 31.3456 | 32 | 57.5
9/7/20XX 1:00:00 PM | 0.54167 | 3 | 78.8 | 55 | 73.7091 | 88.7794 | 15.0703 | 50 | 78.8 |  | 78.8 | 81.2443 | 0.1 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 64.4839 | 16.6633 | 396585.6995 | 33.0488 | 33.0488 | 94.4108 | 0.2 | 74.96 | 19.96 | 754488 | 62.874 | 62.874 | 66.3462 | 18.5255 | 440907.599 | 36.7423 | 36.7423 | 99.6163 | 0.3 | 75.44 | 20.44 | 772632 | 64.386 | 64.386 | 68.2084 | 20.3878 | 485229.4985 | 40.4358 | 40.4358 | 104.8218 | 0.4 | 75.92 | 20.92 | 790776 | 65.898 | 65.898 | 70.0707 | 22.2501 | 529551.398 | 44.1293 | 44.1293 | 110.0273 | 0.5 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 71.933 | 24.1123 | 573873.2975 | 47.8228 | 47.8228 | 115.2328 | 0.6 | 76.88 | 21.88 | 827064 | 68.922 | 68.922 | 73.7952 | 25.9746 | 618195.197 | 51.5163 | 51.5163 | 120.4383 | 0.7 | 77.36 | 22.36 | 845208 | 70.434 | 70.434 | 75.6575 | 27.8369 | 662517.0965 | 55.2098 | 55.2098 | 125.6438 | 0.8 | 77.84 | 22.84 | 863352 | 71.946 | 71.946 | 77.5197 | 29.6991 | 706838.996 | 58.9032 | 58.9032 | 130.8492 | 0.9 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 79.382 | 31.5614 | 751160.8956 | 62.5967 | 62.5967 | 136.0547 | 1 | 78.8 | 23.8 | 899640 | 74.97 | 74.97 | 81.2443 | 33.4236 | 795482.7951 | 66.2902 | 66.2902 | 141.2602 | 80 | 55 | 31.6451 | 32 | 55
9/7/20XX 2:00:00 PM | 0.58333 | 3 | 78.6 | 55.6 | 73.2164 | 88.1844 | 14.968 | 50 | 78.6 |  | 78.6 | 81.5985 | 0.1 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 64.5193 | 16.6987 | 397428.7247 | 33.1191 | 33.1191 | 94.4181 | 0.2 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 66.417 | 18.5964 | 442593.6494 | 36.8828 | 36.8828 | 99.6308 | 0.3 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 68.3147 | 20.4941 | 487758.5741 | 40.6465 | 40.6465 | 104.8435 | 0.4 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 70.2124 | 22.3917 | 532923.4988 | 44.4103 | 44.4103 | 110.0563 | 0.5 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 72.1101 | 24.2894 | 578088.4235 | 48.174 | 48.174 | 115.269 | 0.6 | 76.76 | 21.76 | 822528 | 68.544 | 68.544 | 74.0077 | 26.1871 | 623253.3482 | 51.9378 | 51.9378 | 120.4818 | 0.7 | 77.22 | 22.22 | 839916 | 69.993 | 69.993 | 75.9054 | 28.0848 | 668418.2729 | 55.7015 | 55.7015 | 125.6945 | 0.8 | 77.68 | 22.68 | 857304 | 71.442 | 71.442 | 77.8031 | 29.9825 | 713583.1976 | 59.4653 | 59.4653 | 130.9073 | 0.9 | 78.14 | 23.14 | 874692 | 72.891 | 72.891 | 79.7008 | 31.8802 | 758748.1223 | 63.229 | 63.229 | 136.12 | 1 | 78.6 | 23.6 | 892080 | 74.34 | 74.34 | 81.5985 | 33.7779 | 803913.047 | 66.9928 | 66.9928 | 141.3328 | 80 | 55 | 31.6516 | 32 | 55.6
9/7/20XX 3:00:00 PM | 0.625 | 3 | 78.4 | 56.8 | 72.7264 | 87.5927 | 14.8663 | 50 | 78.4 |  | 78.4 | 82.8355 | 0.1 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 64.643 | 16.8224 | 400372.85 | 33.3644 | 33.3644 | 94.6004 | 0.2 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 66.6644 | 18.8438 | 448481.8999 | 37.3735 | 37.3735 | 99.9955 | 0.3 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 68.6858 | 20.8652 | 496590.9499 | 41.3826 | 41.3826 | 105.3906 | 0.4 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 70.7072 | 22.8866 | 544699.9999 | 45.3917 | 45.3917 | 110.7857 | 0.5 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 72.7286 | 24.9079 | 592809.0498 | 49.4008 | 49.4008 | 116.1808 | 0.6 | 76.64 | 21.64 | 817992 | 68.166 | 68.166 | 74.75 | 26.9293 | 640918.0998 | 53.4098 | 53.4098 | 121.5758 | 0.7 | 77.08 | 22.08 | 834624 | 69.552 | 69.552 | 76.7714 | 28.9507 | 689027.1498 | 57.4189 | 57.4189 | 126.9709 | 0.8 | 77.52 | 22.52 | 851256 | 70.938 | 70.938 | 78.7927 | 30.9721 | 737136.1997 | 61.428 | 61.428 | 132.366 | 0.9 | 77.96 | 22.96 | 867888 | 72.324 | 72.324 | 80.8141 | 32.9935 | 785245.2497 | 65.4371 | 65.4371 | 137.7611 | 1 | 78.4 | 23.4 | 884520 | 73.71 | 73.71 | 82.8355 | 35.0149 | 833354.2996 | 69.4462 | 69.4462 | 143.1562 | 80 | 55 | 31.7964 | 32 | 56.8
9/7/20XX 4:00:00 PM | 0.66667 | 3 | 77.4 | 58.5 | 70.3173 | 84.6839 | 14.3667 | 50 | 77.4 |  | 77.4 | 82.5289 | 0.1 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 64.6124 | 16.7917 | 399643.2045 | 33.3036 | 33.3036 | 94.2246 | 0.2 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 66.6031 | 18.7825 | 447022.6091 | 37.2519 | 37.2519 | 99.2439 | 0.3 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 68.5938 | 20.7732 | 494402.0136 | 41.2002 | 41.2002 | 104.2632 | 0.4 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 70.5846 | 22.7639 | 541781.4182 | 45.1485 | 45.1485 | 109.2825 | 0.5 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 72.5753 | 24.7547 | 589160.8227 | 49.0967 | 49.0967 | 114.3017 | 0.6 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 74.566 | 26.7454 | 636540.2272 | 53.045 | 53.045 | 119.321 | 0.7 | 76.38 | 21.38 | 808164 | 67.347 | 67.347 | 76.5568 | 28.7361 | 683919.6318 | 56.9933 | 56.9933 | 124.3403 | 0.8 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 78.5475 | 30.7269 | 731299.0363 | 60.9416 | 60.9416 | 129.3596 | 0.9 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 80.5382 | 32.7176 | 778678.4408 | 64.8899 | 64.8899 | 134.3789 | 1 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 82.5289 | 34.7083 | 826057.8454 | 68.8382 | 68.8382 | 139.3982 | 75 | 60 | 31.5031 | 32 | 58.5
9/7/20XX 5:00:00 PM | 0.70833 | 3 | 76.6 | 60.5 | 82.4157 | 96.4605 | 14.0448 | 60 | 76.6 |  | 76.6 | 83.1179 | 0.1 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 64.6713 | 16.8506 | 401044.9371 | 33.4204 | 33.4204 | 94.0894 | 0.2 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 66.7209 | 18.9003 | 449826.0742 | 37.4855 | 37.4855 | 98.9735 | 0.3 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 68.7705 | 20.9499 | 498607.2113 | 41.5506 | 41.5506 | 103.8576 | 0.4 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 70.8201 | 22.9995 | 547388.3485 | 45.6157 | 45.6157 | 108.7417 | 0.5 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 72.8698 | 25.0491 | 596169.4856 | 49.6808 | 49.6808 | 113.6258 | 0.6 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 74.9194 | 27.0988 | 644950.6227 | 53.7459 | 53.7459 | 118.5099 | 0.7 | 75.82 | 20.82 | 786996 | 65.583 | 65.583 | 76.969 | 29.1484 | 693731.7598 | 57.811 | 57.811 | 123.394 | 0.8 | 76.08 | 21.08 | 796824 | 66.402 | 66.402 | 79.0187 | 31.198 | 742512.8969 | 61.8761 | 61.8761 | 128.2781 | 0.9 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 81.0683 | 33.2476 | 791294.034 | 65.9412 | 65.9412 | 133.1622 | 1 | 76.6 | 21.6 | 816480 | 68.04 | 68.04 | 83.1179 | 35.2973 | 840075.1711 | 70.0063 | 70.0063 | 138.0463 | 75 | 60 | 31.3991 | 32 | 60.5
9/7/20XX 6:00:00 PM | 0.75 | 3 | 75 | 63.4 | 78.0327 | 91.3149 | 13.2822 | 60 | 75 |  | 75 | 82.5486 | 0.1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 64.6143 | 16.7937 | 399690.0788 | 33.3075 | 33.3075 | 93.4725 | 0.2 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 66.607 | 18.7864 | 447116.3577 | 37.2597 | 37.2597 | 97.7397 | 0.3 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 68.5997 | 20.7791 | 494542.6365 | 41.2119 | 41.2119 | 102.0069 | 0.4 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 70.5924 | 22.7718 | 541968.9154 | 45.1641 | 45.1641 | 106.2741 | 0.5 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 72.5851 | 24.7645 | 589395.1942 | 49.1163 | 49.1163 | 110.5413 | 0.6 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 74.5778 | 26.7572 | 636821.4731 | 53.0685 | 53.0685 | 114.8085 | 0.7 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 76.5705 | 28.7499 | 684247.7519 | 57.0206 | 57.0206 | 119.0756 | 0.8 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 78.5632 | 30.7426 | 731674.0308 | 60.9728 | 60.9728 | 123.3428 | 0.9 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 80.5559 | 32.7353 | 779100.3096 | 64.925 | 64.925 | 127.61 | 1 | 75 | 20 | 756000 | 63 | 63 | 82.5486 | 34.728 | 826526.5885 | 68.8772 | 68.8772 | 131.8772 | 75 | 65 | 30.9176 | 30 | 63.4
9/7/20XX 7:00:00 PM | 0.79167 | 3 | 74.1 | 64.3 | 75.6554 | 88.5243 | 12.8688 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/7/20XX 8:00:00 PM | 0.83333 | 3 | 73.2 | 65.9 | 73.3404 | 85.8067 | 12.4664 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/7/20XX 9:00:00 PM | 0.875 | 3 | 72.4 | 67.2 | 71.3339 | 83.4515 | 12.1177 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/7/20XX 10:00:00 PM | 0.91667 | 3 | 71.6 | 68.1 | 69.3749 | 81.1522 | 11.7773 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/7/20XX 11:00:00 PM | 0.95833 | 3 | 71 | 69.5 | 67.9365 | 79.4639 | 11.5275 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/7/20XX 12:00:00 AM | 0 | 4 | 71 | 68.7 | 67.9365 | 79.4639 | 11.5275 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/8/20XX 1:00:00 AM | 0.041667 | 4 | 69.9 | 71.2 | 76.4479 | 87.5989 | 11.151 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/8/20XX 2:00:00 AM | 0.083333 | 4 | 69.6 | 72.2 | 75.643 | 86.674 | 11.031 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/8/20XX 3:00:00 AM | 0.125 | 4 | 69.2 | 74.7 | 74.5812 | 85.4541 | 10.8729 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/8/20XX 4:00:00 AM | 0.16667 | 4 | 68.8 | 75.1 | 73.5326 | 84.2494 | 10.7169 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/8/20XX 5:00:00 AM | 0.20833 | 4 | 68.7 | 75.6 | 73.2724 | 83.9506 | 10.6782 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/8/20XX 6:00:00 AM | 0.25 | 4 | 68.5 | 76 | 72.7546 | 83.3558 | 10.6012 | 70 | 68.5 |  | 68.5 | 79.1153 | 0.1 | 73.45 | 18.45 | 697410 | 58.1175 | 58.1175 | 64.271 | 16.4504 | 391518.8261 | 32.6266 | 32.6266 | 90.7441 | 0.2 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 65.9204 | 18.0997 | 430773.8522 | 35.8978 | 35.8978 | 92.2828 | 0.3 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 67.5697 | 19.7491 | 470028.8782 | 39.1691 | 39.1691 | 93.8216 | 0.4 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 69.2191 | 21.3985 | 509283.9043 | 42.4403 | 42.4403 | 95.3603 | 0.5 | 71.25 | 16.25 | 614250 | 51.1875 | 51.1875 | 70.8685 | 23.0479 | 548538.9304 | 45.7116 | 45.7116 | 96.8991 | 0.6 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 72.5179 | 24.6972 | 587793.9565 | 48.9828 | 48.9828 | 98.4378 | 0.7 | 70.15 | 15.15 | 572670 | 47.7225 | 47.7225 | 74.1672 | 26.3466 | 627048.9826 | 52.2541 | 52.2541 | 99.9766 | 0.8 | 69.6 | 14.6 | 551880 | 45.99 | 45.99 | 75.8166 | 27.996 | 666304.0087 | 55.5253 | 55.5253 | 101.5153 | 0.9 | 69.05 | 14.05 | 531090 | 44.2575 | 44.2575 | 77.466 | 29.6453 | 705559.0347 | 58.7966 | 58.7966 | 103.0541 | 1 | 68.5 | 13.5 | 510300 | 42.525 | 42.525 | 79.1153 | 31.2947 | 744814.0608 | 62.0678 | 62.0678 | 104.5928 | 70 | 75 | 28.7877 | 28 | 76
9/8/20XX 7:00:00 AM | 0.29167 | 4 | 69.4 | 75.2 | 75.1104 | 86.0621 | 10.9517 | 70 | 69.4 |  | 69.4 | 80.8053 | 0.1 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 64.44 | 16.6194 | 395540.9931 | 32.9617 | 32.9617 | 91.3627 | 0.2 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 66.2584 | 18.4377 | 438818.1863 | 36.5682 | 36.5682 | 93.5202 | 0.3 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 68.0767 | 20.2561 | 482095.3794 | 40.1746 | 40.1746 | 95.6776 | 0.4 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 69.8951 | 22.0745 | 525372.5726 | 43.781 | 43.781 | 97.835 | 0.5 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 71.7135 | 23.8928 | 568649.7657 | 47.3875 | 47.3875 | 99.9925 | 0.6 | 71.24 | 16.24 | 613872 | 51.156 | 51.156 | 73.5318 | 25.7112 | 611926.9588 | 50.9939 | 50.9939 | 102.1499 | 0.7 | 70.78 | 15.78 | 596484 | 49.707 | 49.707 | 75.3502 | 27.5296 | 655204.152 | 54.6003 | 54.6003 | 104.3073 | 0.8 | 70.32 | 15.32 | 579096 | 48.258 | 48.258 | 77.1686 | 29.348 | 698481.3451 | 58.2068 | 58.2068 | 106.4648 | 0.9 | 69.86 | 14.86 | 561708 | 46.809 | 46.809 | 78.987 | 31.1663 | 741758.5383 | 61.8132 | 61.8132 | 108.6222 | 1 | 69.4 | 14.4 | 544320 | 45.36 | 45.36 | 80.8053 | 32.9847 | 785035.7314 | 65.4196 | 65.4196 | 110.7796 | 70 | 75 | 29.2721 | 30 | 75.2
9/8/20XX 8:00:00 AM | 0.33333 | 4 | 70.4 | 73.5 | 77.8062 | 89.1597 | 11.3535 | 70 | 70.4 |  | 70.4 | 81.78 | 0.1 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 64.5375 | 16.7168 | 397860.626 | 33.1551 | 33.1551 | 91.8711 | 0.2 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 66.4533 | 18.6327 | 443457.452 | 36.9548 | 36.9548 | 94.5368 | 0.3 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 68.3691 | 20.5485 | 489054.2779 | 40.7545 | 40.7545 | 97.2025 | 0.4 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 70.285 | 22.4643 | 534651.1039 | 44.5543 | 44.5543 | 99.8683 | 0.5 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 72.2008 | 24.3802 | 580247.9299 | 48.354 | 48.354 | 102.534 | 0.6 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 74.1166 | 26.296 | 625844.7559 | 52.1537 | 52.1537 | 105.1997 | 0.7 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 76.0325 | 28.2118 | 671441.5819 | 55.9535 | 55.9535 | 107.8655 | 0.8 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 77.9483 | 30.1277 | 717038.4079 | 59.7532 | 59.7532 | 110.5312 | 0.9 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 79.8641 | 32.0435 | 762635.2338 | 63.5529 | 63.5529 | 113.1969 | 1 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 81.78 | 33.9593 | 808232.0598 | 67.3527 | 67.3527 | 115.8627 | 70 | 75 | 29.6694 | 30 | 73.5
9/8/20XX 9:00:00 AM | 0.375 | 4 | 72.5 | 69.6 | 71.5821 | 83.7428 | 12.1608 | 60 | 72.5 |  | 72.5 | 83.2564 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 64.6851 | 16.8645 | 401374.5558 | 33.4479 | 33.4479 | 92.8254 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 66.7486 | 18.928 | 450485.3116 | 37.5404 | 37.5404 | 96.4454 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 68.8121 | 20.9914 | 499596.0673 | 41.633 | 41.633 | 100.0655 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 70.8755 | 23.0549 | 548706.8231 | 45.7256 | 45.7256 | 103.6856 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 72.939 | 25.1184 | 597817.5789 | 49.8181 | 49.8181 | 107.3056 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 75.0025 | 27.1819 | 646928.3347 | 53.9107 | 53.9107 | 110.9257 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 77.066 | 29.2453 | 696039.0905 | 58.0033 | 58.0033 | 114.5458 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 79.1294 | 31.3088 | 745149.8463 | 62.0958 | 62.0958 | 118.1658 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 81.1929 | 33.3723 | 794260.602 | 66.1884 | 66.1884 | 121.7859 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 83.2564 | 35.4358 | 843371.3578 | 70.2809 | 70.2809 | 125.4059 | 70 | 70 | 30.4152 | 30 | 69.6
9/8/20XX 10:00:00 AM | 0.41667 | 4 | 74.8 | 64.7 | 77.499 | 90.6884 | 13.1894 | 60 | 74.8 |  | 74.8 | 83.698 | 0.1 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 64.7293 | 16.9086 | 402425.5583 | 33.5355 | 33.5355 | 93.6375 | 0.2 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 66.8369 | 19.0163 | 452587.3166 | 37.7156 | 37.7156 | 98.0696 | 0.3 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 68.9445 | 21.1239 | 502749.0748 | 41.8958 | 41.8958 | 102.5018 | 0.4 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 71.0522 | 23.2315 | 552910.8331 | 46.0759 | 46.0759 | 106.9339 | 0.5 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 73.1598 | 25.3392 | 603072.5914 | 50.256 | 50.256 | 111.366 | 0.6 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 75.2675 | 27.4468 | 653234.3497 | 54.4362 | 54.4362 | 115.7982 | 0.7 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 77.3751 | 29.5545 | 703396.1079 | 58.6163 | 58.6163 | 120.2303 | 0.8 | 74.64 | 19.64 | 742392 | 61.866 | 61.866 | 79.4827 | 31.6621 | 753557.8662 | 62.7965 | 62.7965 | 124.6625 | 0.9 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 81.5904 | 33.7697 | 803719.6245 | 66.9766 | 66.9766 | 129.0946 | 1 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 83.698 | 35.8774 | 853881.3828 | 71.1568 | 71.1568 | 133.5268 | 75 | 65 | 31.0484 | 32 | 64.7
9/8/20XX 11:00:00 AM | 0.45833 | 4 | 77.4 | 59.8 | 70.3173 | 84.6839 | 14.3667 | 50 | 77.4 |  | 77.4 | 84.3966 | 0.1 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 64.7991 | 16.9785 | 404088.2495 | 33.674 | 33.674 | 94.595 | 0.2 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 66.9766 | 19.156 | 455912.6991 | 37.9927 | 37.9927 | 99.9847 | 0.3 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 69.1541 | 21.3335 | 507737.1486 | 42.3114 | 42.3114 | 105.3744 | 0.4 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 71.3316 | 23.511 | 559561.5981 | 46.6301 | 46.6301 | 110.7641 | 0.5 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 73.5091 | 25.6885 | 611386.0476 | 50.9488 | 50.9488 | 116.1538 | 0.6 | 76.04 | 21.04 | 795312 | 66.276 | 66.276 | 75.6866 | 27.866 | 663210.4972 | 55.2675 | 55.2675 | 121.5435 | 0.7 | 76.38 | 21.38 | 808164 | 67.347 | 67.347 | 77.8641 | 30.0435 | 715034.9467 | 59.5862 | 59.5862 | 126.9332 | 0.8 | 76.72 | 21.72 | 821016 | 68.418 | 68.418 | 80.0416 | 32.221 | 766859.3962 | 63.9049 | 63.9049 | 132.3229 | 0.9 | 77.06 | 22.06 | 833868 | 69.489 | 69.489 | 82.2191 | 34.3985 | 818683.8457 | 68.2237 | 68.2237 | 137.7127 | 1 | 77.4 | 22.4 | 846720 | 70.56 | 70.56 | 84.3966 | 36.576 | 870508.2953 | 72.5424 | 72.5424 | 143.1024 | 75 | 60 | 31.7957 | 32 | 59.8
9/8/20XX 12:00:00 PM | 0.5 | 4 | 78.5 | 57.2 | 72.9711 | 87.8882 | 14.9171 | 50 | 78.5 |  | 78.5 | 83.7114 | 0.1 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 64.7306 | 16.91 | 402457.3911 | 33.5381 | 33.5381 | 94.8056 | 0.2 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 66.8396 | 19.0189 | 452650.9823 | 37.7209 | 37.7209 | 100.4059 | 0.3 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 68.9486 | 21.1279 | 502844.5734 | 41.9037 | 41.9037 | 106.0062 | 0.4 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 71.0575 | 23.2369 | 553038.1645 | 46.0865 | 46.0865 | 111.6065 | 0.5 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 73.1665 | 25.3459 | 603231.7556 | 50.2693 | 50.2693 | 117.2068 | 0.6 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 75.2755 | 27.4548 | 653425.3468 | 54.4521 | 54.4521 | 122.8071 | 0.7 | 77.15 | 22.15 | 837270 | 69.7725 | 69.7725 | 77.3845 | 29.5638 | 703618.9379 | 58.6349 | 58.6349 | 128.4074 | 0.8 | 77.6 | 22.6 | 854280 | 71.19 | 71.19 | 79.4934 | 31.6728 | 753812.529 | 62.8177 | 62.8177 | 134.0077 | 0.9 | 78.05 | 23.05 | 871290 | 72.6075 | 72.6075 | 81.6024 | 33.7818 | 804006.1202 | 67.0005 | 67.0005 | 139.608 | 1 | 78.5 | 23.5 | 888300 | 74.025 | 74.025 | 83.7114 | 35.8907 | 854199.7113 | 71.1833 | 71.1833 | 145.2083 | 80 | 55 | 31.9582 | 32 | 57.2
9/8/20XX 1:00:00 PM | 0.54167 | 4 | 79.4 | 55.4 | 75.2039 | 90.5845 | 15.3806 | 50 | 79.4 |  | 79.4 | 83.5094 | 0.1 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 64.7104 | 16.8898 | 401976.7646 | 33.4981 | 33.4981 | 95.0491 | 0.2 | 75.08 | 20.08 | 759024 | 63.252 | 63.252 | 66.7992 | 18.9786 | 451689.7291 | 37.6408 | 37.6408 | 100.8928 | 0.3 | 75.62 | 20.62 | 779436 | 64.953 | 64.953 | 68.888 | 21.0673 | 501402.6937 | 41.7836 | 41.7836 | 106.7366 | 0.4 | 76.16 | 21.16 | 799848 | 66.654 | 66.654 | 70.9768 | 23.1561 | 551115.6583 | 45.9263 | 45.9263 | 112.5803 | 0.5 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 73.0655 | 25.2449 | 600828.6228 | 50.0691 | 50.0691 | 118.4241 | 0.6 | 77.24 | 22.24 | 840672 | 70.056 | 70.056 | 75.1543 | 27.3337 | 650541.5874 | 54.2118 | 54.2118 | 124.2678 | 0.7 | 77.78 | 22.78 | 861084 | 71.757 | 71.757 | 77.2431 | 29.4225 | 700254.5519 | 58.3545 | 58.3545 | 130.1115 | 0.8 | 78.32 | 23.32 | 881496 | 73.458 | 73.458 | 79.3319 | 31.5112 | 749967.5165 | 62.4973 | 62.4973 | 135.9553 | 0.9 | 78.86 | 23.86 | 901908 | 75.159 | 75.159 | 81.4207 | 33.6 | 799680.4811 | 66.64 | 66.64 | 141.799 | 1 | 79.4 | 24.4 | 922320 | 76.86 | 76.86 | 83.5094 | 35.6888 | 849393.4456 | 70.7828 | 70.7828 | 147.6428 | 80 | 55 | 32.1473 | 32 | 55.4
9/8/20XX 2:00:00 PM | 0.58333 | 4 | 79.9 | 53.5 | 76.4687 | 92.1119 | 15.6433 | 50 | 79.9 |  | 79.9 | 81.9438 | 0.1 | 74.59 | 19.59 | 740502 | 61.7085 | 61.7085 | 64.5539 | 16.7332 | 398250.5935 | 33.1875 | 33.1875 | 94.896 | 0.2 | 75.18 | 20.18 | 762804 | 63.567 | 63.567 | 66.4861 | 18.6654 | 444237.3871 | 37.0198 | 37.0198 | 100.5868 | 0.3 | 75.77 | 20.77 | 785106 | 65.4255 | 65.4255 | 68.4183 | 20.5977 | 490224.1806 | 40.852 | 40.852 | 106.2775 | 0.4 | 76.36 | 21.36 | 807408 | 67.284 | 67.284 | 70.3505 | 22.5299 | 536210.9741 | 44.6842 | 44.6842 | 111.9682 | 0.5 | 76.95 | 21.95 | 829710 | 69.1425 | 69.1425 | 72.2827 | 24.4621 | 582197.7677 | 48.5165 | 48.5165 | 117.659 | 0.6 | 77.54 | 22.54 | 852012 | 71.001 | 71.001 | 74.2149 | 26.3943 | 628184.5612 | 52.3487 | 52.3487 | 123.3497 | 0.7 | 78.13 | 23.13 | 874314 | 72.8595 | 72.8595 | 76.1472 | 28.3265 | 674171.3547 | 56.1809 | 56.1809 | 129.0404 | 0.8 | 78.72 | 23.72 | 896616 | 74.718 | 74.718 | 78.0794 | 30.2587 | 720158.1483 | 60.0132 | 60.0132 | 134.7312 | 0.9 | 79.31 | 24.31 | 918918 | 76.5765 | 76.5765 | 80.0116 | 32.191 | 766144.9418 | 63.8454 | 63.8454 | 140.4219 | 1 | 79.9 | 24.9 | 941220 | 78.435 | 78.435 | 81.9438 | 34.1232 | 812131.7353 | 67.6776 | 67.6776 | 146.1126 | 80 | 55 | 32.0245 | 32 | 53.5
9/8/20XX 3:00:00 PM | 0.625 | 4 | 78.9 | 54.2 | 73.9565 | 89.0782 | 15.1216 | 50 | 78.9 |  | 78.9 | 80.3076 | 0.1 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 64.3902 | 16.5696 | 394356.4651 | 32.863 | 32.863 | 94.2565 | 0.2 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 66.1588 | 18.3382 | 436449.1302 | 36.3708 | 36.3708 | 99.3078 | 0.3 | 75.47 | 20.47 | 773766 | 64.4805 | 64.4805 | 67.9274 | 20.1068 | 478541.7952 | 39.8785 | 39.8785 | 104.359 | 0.4 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 69.696 | 21.8754 | 520634.4603 | 43.3862 | 43.3862 | 109.4102 | 0.5 | 76.45 | 21.45 | 810810 | 67.5675 | 67.5675 | 71.4646 | 23.644 | 562727.1254 | 46.8939 | 46.8939 | 114.4614 | 0.6 | 76.94 | 21.94 | 829332 | 69.111 | 69.111 | 73.2332 | 25.4126 | 604819.7905 | 50.4016 | 50.4016 | 119.5126 | 0.7 | 77.43 | 22.43 | 847854 | 70.6545 | 70.6545 | 75.0018 | 27.1812 | 646912.4556 | 53.9094 | 53.9094 | 124.5639 | 0.8 | 77.92 | 22.92 | 866376 | 72.198 | 72.198 | 76.7704 | 28.9498 | 689005.1207 | 57.4171 | 57.4171 | 129.6151 | 0.9 | 78.41 | 23.41 | 884898 | 73.7415 | 73.7415 | 78.539 | 30.7184 | 731097.7857 | 60.9248 | 60.9248 | 134.6663 | 1 | 78.9 | 23.9 | 903420 | 75.285 | 75.285 | 80.3076 | 32.487 | 773190.4508 | 64.4325 | 64.4325 | 139.7175 | 80 | 55 | 31.5228 | 32 | 54.2
9/8/20XX 4:00:00 PM | 0.66667 | 4 | 77.9 | 55.3 | 71.5134 | 86.1281 | 14.6147 | 50 | 77.9 |  | 77.9 | 79.2592 | 0.1 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 64.2854 | 16.4648 | 391861.121 | 32.6551 | 32.6551 | 93.7336 | 0.2 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 65.9491 | 18.1285 | 431458.4419 | 35.9549 | 35.9549 | 98.2619 | 0.3 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 67.6129 | 19.7923 | 471055.7629 | 39.2546 | 39.2546 | 102.7901 | 0.4 | 75.56 | 20.56 | 777168 | 64.764 | 64.764 | 69.2766 | 21.456 | 510653.0838 | 42.5544 | 42.5544 | 107.3184 | 0.5 | 75.95 | 20.95 | 791910 | 65.9925 | 65.9925 | 70.9404 | 23.1198 | 550250.4048 | 45.8542 | 45.8542 | 111.8467 | 0.6 | 76.34 | 21.34 | 806652 | 67.221 | 67.221 | 72.6042 | 24.7835 | 589847.7257 | 49.154 | 49.154 | 116.375 | 0.7 | 76.73 | 21.73 | 821394 | 68.4495 | 68.4495 | 74.2679 | 26.4473 | 629445.0467 | 52.4538 | 52.4538 | 120.9033 | 0.8 | 77.12 | 22.12 | 836136 | 69.678 | 69.678 | 75.9317 | 28.111 | 669042.3677 | 55.7535 | 55.7535 | 125.4315 | 0.9 | 77.51 | 22.51 | 850878 | 70.9065 | 70.9065 | 77.5954 | 29.7748 | 708639.6886 | 59.0533 | 59.0533 | 129.9598 | 1 | 77.9 | 22.9 | 865620 | 72.135 | 72.135 | 79.2592 | 31.4385 | 748237.0096 | 62.3531 | 62.3531 | 134.4881 | 80 | 55 | 31.1135 | 32 | 55.3
9/8/20XX 5:00:00 PM | 0.70833 | 4 | 76.2 | 56.2 | 67.5149 | 81.3009 | 13.786 | 50 | 76.2 |  | 76.2 | 76.0622 | 0.1 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 63.9657 | 16.1451 | 384252.3376 | 32.021 | 32.021 | 92.564 | 0.2 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 65.3097 | 17.4891 | 416240.8752 | 34.6867 | 34.6867 | 95.9227 | 0.3 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 66.6538 | 18.8332 | 448229.4128 | 37.3525 | 37.3525 | 99.2815 | 0.4 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 67.9979 | 20.1772 | 480217.9504 | 40.0182 | 40.0182 | 102.6402 | 0.5 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 69.3419 | 21.5213 | 512206.488 | 42.6839 | 42.6839 | 105.9989 | 0.6 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 70.686 | 22.8653 | 544195.0256 | 45.3496 | 45.3496 | 109.3576 | 0.7 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 72.03 | 24.2094 | 576183.5632 | 48.0153 | 48.0153 | 112.7163 | 0.8 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 73.3741 | 25.5534 | 608172.1008 | 50.681 | 50.681 | 116.075 | 0.9 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 74.7181 | 26.8975 | 640160.6384 | 53.3467 | 53.3467 | 119.4337 | 1 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 76.0622 | 28.2416 | 672149.176 | 56.0124 | 56.0124 | 122.7924 | 75 | 55 | 30.1964 | 30 | 56.2
9/8/20XX 6:00:00 PM | 0.75 | 4 | 73.8 | 62.3 | 74.8769 | 87.6104 | 12.7335 | 60 | 73.8 |  | 73.8 | 77.8056 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 64.14 | 16.3194 | 388401.6058 | 32.3668 | 32.3668 | 92.1538 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 65.6584 | 17.8378 | 424539.4115 | 35.3783 | 35.3783 | 95.1023 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 67.1768 | 19.3562 | 460677.2173 | 38.3898 | 38.3898 | 98.0508 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 68.6952 | 20.8746 | 496815.0231 | 41.4013 | 41.4013 | 100.9993 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 70.2136 | 22.393 | 532952.8289 | 44.4127 | 44.4127 | 103.9477 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 71.732 | 23.9114 | 569090.6346 | 47.4242 | 47.4242 | 106.8962 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 73.2504 | 25.4298 | 605228.4404 | 50.4357 | 50.4357 | 109.8447 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 74.7688 | 26.9482 | 641366.2462 | 53.4472 | 53.4472 | 112.7932 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 76.2872 | 28.4666 | 677504.052 | 56.4587 | 56.4587 | 115.7417 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 77.8056 | 29.985 | 713641.8577 | 59.4702 | 59.4702 | 118.6902 | 75 | 60 | 29.8815 | 30 | 62.3
9/8/20XX 7:00:00 PM | 0.79167 | 4 | 72.6 | 64.9 | 71.831 | 84.035 | 12.204 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/8/20XX 8:00:00 PM | 0.83333 | 4 | 70.9 | 67.4 | 67.6992 | 79.1855 | 11.4863 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/8/20XX 9:00:00 PM | 0.875 | 4 | 70.4 | 66.9 | 66.524 | 77.8062 | 11.2822 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/8/20XX 10:00:00 PM | 0.91667 | 4 | 69.6 | 66.9 | 64.6807 | 75.643 | 10.9623 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/8/20XX 11:00:00 PM | 0.95833 | 4 | 69.2 | 67.5 | 63.776 | 74.5812 | 10.8052 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/8/20XX 12:00:00 AM | 0 | 5 | 68.8 | 65.4 | 62.8824 | 73.5326 | 10.6502 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/9/20XX 1:00:00 AM | 0.041667 | 5 | 68.2 | 66.1 | 61.5627 | 71.984 | 10.4213 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/9/20XX 2:00:00 AM | 0.083333 | 5 | 67.2 | 68.2 | 59.4176 | 69.467 | 10.0494 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/9/20XX 3:00:00 AM | 0.125 | 5 | 66.4 | 70.9 | 67.51 | 77.333 | 9.823 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/9/20XX 4:00:00 AM | 0.16667 | 5 | 65.8 | 72.7 | 66.0748 | 75.6853 | 9.6105 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/9/20XX 5:00:00 AM | 0.20833 | 5 | 65.1 | 76.2 | 64.435 | 73.8031 | 9.3681 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/9/20XX 6:00:00 AM | 0.25 | 5 | 65 | 75.8 | 64.2037 | 73.5377 | 9.3339 | 70 | 65 |  | 65 | 69.6174 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 69.6174 | 21.7968 | 518763.5057 | 43.2303 | 43.2303 | 74.7303 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 69.6174 | 21.7968 | 518763.5057 | 43.2303 | 43.2303 | 74.7303 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 69.6174 | 21.7968 | 518763.5057 | 43.2303 | 43.2303 | 74.7303 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 69.6174 | 21.7968 | 518763.5057 | 43.2303 | 43.2303 | 74.7303 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 69.6174 | 21.7968 | 518763.5057 | 43.2303 | 43.2303 | 74.7303 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 69.6174 | 21.7968 | 518763.5057 | 43.2303 | 43.2303 | 74.7303 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 69.6174 | 21.7968 | 518763.5057 | 43.2303 | 43.2303 | 74.7303 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 69.6174 | 21.7968 | 518763.5057 | 43.2303 | 43.2303 | 74.7303 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 69.6174 | 21.7968 | 518763.5057 | 43.2303 | 43.2303 | 74.7303 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 69.6174 | 21.7968 | 518763.5057 | 43.2303 | 43.2303 | 74.7303 | 65 | 75 | 26.4499 | 26 | 75.8
9/9/20XX 7:00:00 AM | 0.29167 | 5 | 65.8 | 73.8 | 66.0748 | 75.6853 | 9.6105 | 70 | 65.8 |  | 65.8 | 69.7268 | 0.1 | 73.18 | 18.18 | 687204 | 57.267 | 57.267 | 63.3321 | 15.5115 | 369174.039 | 30.7645 | 30.7645 | 88.0315 | 0.2 | 72.36 | 17.36 | 656208 | 54.684 | 54.684 | 64.0427 | 16.222 | 386084.278 | 32.1737 | 32.1737 | 86.8577 | 0.3 | 71.54 | 16.54 | 625212 | 52.101 | 52.101 | 64.7532 | 16.9325 | 402994.517 | 33.5829 | 33.5829 | 85.6839 | 0.4 | 70.72 | 15.72 | 594216 | 49.518 | 49.518 | 65.4637 | 17.6431 | 419904.756 | 34.9921 | 34.9921 | 84.5101 | 0.5 | 69.9 | 14.9 | 563220 | 46.935 | 46.935 | 66.1742 | 18.3536 | 436814.995 | 36.4012 | 36.4012 | 83.3362 | 0.6 | 69.08 | 14.08 | 532224 | 44.352 | 44.352 | 66.8847 | 19.0641 | 453725.234 | 37.8104 | 37.8104 | 82.1624 | 0.7 | 68.26 | 13.26 | 501228 | 41.769 | 41.769 | 67.5952 | 19.7746 | 470635.473 | 39.2196 | 39.2196 | 80.9886 | 0.8 | 67.44 | 12.44 | 470232 | 39.186 | 39.186 | 68.3057 | 20.4851 | 487545.712 | 40.6288 | 40.6288 | 79.8148 | 0.9 | 66.62 | 11.62 | 439236 | 36.603 | 36.603 | 69.0163 | 21.1956 | 504455.951 | 42.038 | 42.038 | 78.641 | 1 | 65.8 | 10.8 | 408240 | 34.02 | 34.02 | 69.7268 | 21.9061 | 521366.19 | 43.4472 | 43.4472 | 77.4672 | 65 | 75 | 26.6625 | 26 | 73.8
9/9/20XX 8:00:00 AM | 0.33333 | 5 | 67.1 | 70.1 | 69.2196 | 79.2959 | 10.0763 | 70 | 67.1 |  | 67.1 | 69.3204 | 0.1 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 63.2915 | 15.4709 | 368206.8021 | 30.6839 | 30.6839 | 88.3604 | 0.2 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 63.9614 | 16.1407 | 384149.8042 | 32.0125 | 32.0125 | 87.5155 | 0.3 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 64.6313 | 16.8106 | 400092.8063 | 33.3411 | 33.3411 | 86.6706 | 0.4 | 71.24 | 16.24 | 613872 | 51.156 | 51.156 | 65.3011 | 17.4805 | 416035.8084 | 34.6697 | 34.6697 | 85.8257 | 0.5 | 70.55 | 15.55 | 587790 | 48.9825 | 48.9825 | 65.971 | 18.1504 | 431978.8105 | 35.9982 | 35.9982 | 84.9807 | 0.6 | 69.86 | 14.86 | 561708 | 46.809 | 46.809 | 66.6409 | 18.8202 | 447921.8126 | 37.3268 | 37.3268 | 84.1358 | 0.7 | 69.17 | 14.17 | 535626 | 44.6355 | 44.6355 | 67.3108 | 19.4901 | 463864.8147 | 38.6554 | 38.6554 | 83.2909 | 0.8 | 68.48 | 13.48 | 509544 | 42.462 | 42.462 | 67.9806 | 20.16 | 479807.8168 | 39.984 | 39.984 | 82.446 | 0.9 | 67.79 | 12.79 | 483462 | 40.2885 | 40.2885 | 68.6505 | 20.8299 | 495750.8189 | 41.3126 | 41.3126 | 81.6011 | 1 | 67.1 | 12.1 | 457380 | 38.115 | 38.115 | 69.3204 | 21.4997 | 511693.821 | 42.6412 | 42.6412 | 80.7562 | 65 | 70 | 26.9168 | 26 | 70.1
9/9/20XX 9:00:00 AM | 0.375 | 5 | 68.8 | 67.6 | 62.8824 | 73.5326 | 10.6502 | 60 | 68.8 |  | 68.8 | 70.9765 | 0.1 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 63.4571 | 15.6365 | 372148.4275 | 31.0124 | 31.0124 | 89.2244 | 0.2 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 64.2926 | 16.472 | 392033.055 | 32.6694 | 32.6694 | 89.2434 | 0.3 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 65.1281 | 17.3075 | 411917.6824 | 34.3265 | 34.3265 | 89.2625 | 0.4 | 71.92 | 16.92 | 639576 | 53.298 | 53.298 | 65.9636 | 18.143 | 431802.3099 | 35.9835 | 35.9835 | 89.2815 | 0.5 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 66.7991 | 18.9784 | 451686.9374 | 37.6406 | 37.6406 | 89.3006 | 0.6 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 67.6346 | 19.8139 | 471571.5649 | 39.2976 | 39.2976 | 89.3196 | 0.7 | 70.36 | 15.36 | 580608 | 48.384 | 48.384 | 68.4701 | 20.6494 | 491456.1923 | 40.9547 | 40.9547 | 89.3387 | 0.8 | 69.84 | 14.84 | 560952 | 46.746 | 46.746 | 69.3055 | 21.4849 | 511340.8198 | 42.6117 | 42.6117 | 89.3577 | 0.9 | 69.32 | 14.32 | 541296 | 45.108 | 45.108 | 70.141 | 22.3204 | 531225.4473 | 44.2688 | 44.2688 | 89.3768 | 1 | 68.8 | 13.8 | 521640 | 43.47 | 43.47 | 70.9765 | 23.1559 | 551110.0748 | 45.9258 | 45.9258 | 89.3958 | 70 | 70 | 27.5908 | 28 | 67.6
9/9/20XX 10:00:00 AM | 0.41667 | 5 | 70.4 | 64.4 | 66.524 | 77.8062 | 11.2822 | 60 | 70.4 |  | 70.4 | 71.4882 | 0.1 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 63.5083 | 15.6877 | 373366.2229 | 31.1139 | 31.1139 | 89.8299 | 0.2 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 64.3949 | 16.5743 | 394468.6457 | 32.8724 | 32.8724 | 90.4544 | 0.3 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 65.2816 | 17.461 | 415571.0686 | 34.6309 | 34.6309 | 91.0789 | 0.4 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 66.1683 | 18.3476 | 436673.4915 | 36.3895 | 36.3895 | 91.7035 | 0.5 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 67.0549 | 19.2343 | 457775.9143 | 38.148 | 38.148 | 92.328 | 0.6 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 67.9416 | 20.1209 | 478878.3372 | 39.9065 | 39.9065 | 92.9525 | 0.7 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 68.8282 | 21.0076 | 499980.7601 | 41.6651 | 41.6651 | 93.5771 | 0.8 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 69.7149 | 21.8943 | 521083.1829 | 43.4236 | 43.4236 | 94.2016 | 0.9 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 70.6015 | 22.7809 | 542185.6058 | 45.1821 | 45.1821 | 94.8261 | 1 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 71.4882 | 23.6676 | 563288.0286 | 46.9407 | 46.9407 | 95.4507 | 70 | 65 | 28.0619 | 28 | 64.4
9/9/20XX 11:00:00 AM | 0.45833 | 5 | 73.2 | 58.3 | 60.9187 | 73.3404 | 12.4216 | 50 | 73.2 |  | 73.2 | 71.2287 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 63.4823 | 15.6617 | 372748.575 | 31.0624 | 31.0624 | 90.6604 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 64.343 | 16.5224 | 393233.3501 | 32.7694 | 32.7694 | 92.1154 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 65.2037 | 17.3831 | 413718.1251 | 34.4765 | 34.4765 | 93.5705 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 66.0645 | 18.2438 | 434202.9001 | 36.1836 | 36.1836 | 95.0256 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 66.9252 | 19.1045 | 454687.6752 | 37.8906 | 37.8906 | 96.4806 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 67.7859 | 19.9652 | 475172.4502 | 39.5977 | 39.5977 | 97.9357 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 68.6466 | 20.8259 | 495657.2252 | 41.3048 | 41.3048 | 99.3908 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 69.5073 | 21.6866 | 516142.0003 | 43.0118 | 43.0118 | 100.8458 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 70.368 | 22.5473 | 536626.7753 | 44.7189 | 44.7189 | 102.3009 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 71.2287 | 23.408 | 557111.5503 | 46.426 | 46.426 | 103.756 | 75 | 60 | 28.7061 | 28 | 58.3
9/9/20XX 12:00:00 PM | 0.5 | 5 | 74.6 | 56.4 | 63.9253 | 76.9684 | 13.0431 | 50 | 74.6 |  | 74.6 | 72.2729 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 63.5868 | 15.7661 | 375233.7614 | 31.2695 | 31.2695 | 91.3085 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 64.5519 | 16.7312 | 398203.7228 | 33.1836 | 33.1836 | 93.4116 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 65.517 | 17.6964 | 421173.6842 | 35.0978 | 35.0978 | 95.5148 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 66.4821 | 18.6615 | 444143.6456 | 37.012 | 37.012 | 97.618 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 67.4473 | 19.6266 | 467113.607 | 38.9261 | 38.9261 | 99.7211 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 68.4124 | 20.5917 | 490083.5685 | 40.8403 | 40.8403 | 101.8243 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 69.3775 | 21.5569 | 513053.5299 | 42.7545 | 42.7545 | 103.9275 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 70.3426 | 22.522 | 536023.4913 | 44.6686 | 44.6686 | 106.0306 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 71.3078 | 23.4871 | 558993.4527 | 46.5828 | 46.5828 | 108.1338 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 72.2729 | 24.4522 | 581963.4141 | 48.497 | 48.497 | 110.237 | 75 | 55 | 29.2118 | 30 | 56.4
9/9/20XX 1:00:00 PM | 0.54167 | 5 | 74.7 | 56.3 | 64.1448 | 77.2333 | 13.0885 | 50 | 74.7 |  | 74.7 | 72.3906 | 0.1 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 63.5985 | 15.7779 | 375513.8387 | 31.2928 | 31.2928 | 91.3633 | 0.2 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 64.5754 | 16.7548 | 398763.8773 | 33.2303 | 33.2303 | 93.5213 | 0.3 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 65.5523 | 17.7317 | 422013.916 | 35.1678 | 35.1678 | 95.6793 | 0.4 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 66.5292 | 18.7086 | 445263.9546 | 37.1053 | 37.1053 | 97.8373 | 0.5 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 67.5061 | 19.6855 | 468513.9933 | 39.0428 | 39.0428 | 99.9953 | 0.6 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 68.483 | 20.6624 | 491764.0319 | 40.9803 | 40.9803 | 102.1533 | 0.7 | 74.49 | 19.49 | 736722 | 61.3935 | 61.3935 | 69.4599 | 21.6392 | 515014.0706 | 42.9178 | 42.9178 | 104.3113 | 0.8 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 70.4368 | 22.6161 | 538264.1093 | 44.8553 | 44.8553 | 106.4693 | 0.9 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 71.4137 | 23.593 | 561514.1479 | 46.7928 | 46.7928 | 108.6273 | 1 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 72.3906 | 24.5699 | 584764.1866 | 48.7303 | 48.7303 | 110.7853 | 75 | 55 | 29.2547 | 30 | 56.3
9/9/20XX 2:00:00 PM | 0.58333 | 5 | 74.6 | 57.2 | 63.9253 | 76.9684 | 13.0431 | 50 | 74.6 |  | 74.6 | 73.3163 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 63.6911 | 15.8705 | 377717.162 | 31.4764 | 31.4764 | 91.5154 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 64.7606 | 16.9399 | 403170.5241 | 33.5975 | 33.5975 | 93.8255 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 65.83 | 18.0094 | 428623.8861 | 35.7187 | 35.7187 | 96.1357 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 66.8995 | 19.0789 | 454077.2482 | 37.8398 | 37.8398 | 98.4458 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 67.969 | 20.1483 | 479530.6102 | 39.9609 | 39.9609 | 100.7559 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 69.0384 | 21.2178 | 504983.9723 | 42.082 | 42.082 | 103.066 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 70.1079 | 22.2873 | 530437.3343 | 44.2031 | 44.2031 | 105.3761 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 71.1774 | 23.3568 | 555890.6964 | 46.3242 | 46.3242 | 107.6862 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 72.2469 | 24.4262 | 581344.0584 | 48.4453 | 48.4453 | 109.9963 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 73.3163 | 25.4957 | 606797.4205 | 50.5665 | 50.5665 | 112.3065 | 75 | 55 | 29.375 | 30 | 57.2
9/9/20XX 3:00:00 PM | 0.625 | 5 | 74.4 | 57.8 | 63.4882 | 76.4409 | 12.9527 | 50 | 74.4 |  | 74.4 | 73.5913 | 0.1 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 63.7186 | 15.898 | 378371.6071 | 31.531 | 31.531 | 91.507 | 0.2 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 64.8156 | 16.9949 | 404479.4141 | 33.7066 | 33.7066 | 93.8086 | 0.3 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.9125 | 18.0919 | 430587.2212 | 35.8823 | 35.8823 | 96.1103 | 0.4 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 67.0095 | 19.1889 | 456695.0283 | 38.0579 | 38.0579 | 98.4119 | 0.5 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 68.1065 | 20.2858 | 482802.8354 | 40.2336 | 40.2336 | 100.7136 | 0.6 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 69.2034 | 21.3828 | 508910.6424 | 42.4092 | 42.4092 | 103.0152 | 0.7 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 70.3004 | 22.4798 | 535018.4495 | 44.5849 | 44.5849 | 105.3169 | 0.8 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 71.3974 | 23.5767 | 561126.2566 | 46.7605 | 46.7605 | 107.6185 | 0.9 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 72.4943 | 24.6737 | 587234.0637 | 48.9362 | 48.9362 | 109.9202 | 1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 73.5913 | 25.7707 | 613341.8707 | 51.1118 | 51.1118 | 112.2218 | 75 | 60 | 29.3691 | 30 | 57.8
9/9/20XX 4:00:00 PM | 0.66667 | 5 | 73.4 | 58.8 | 61.3407 | 73.8495 | 12.5088 | 50 | 73.4 |  | 73.4 | 72.3484 | 0.1 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 63.5943 | 15.7737 | 375413.6128 | 31.2845 | 31.2845 | 90.9455 | 0.2 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 64.567 | 16.7464 | 398563.4255 | 33.2136 | 33.2136 | 92.6856 | 0.3 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 65.5397 | 17.719 | 421713.2383 | 35.1428 | 35.1428 | 94.4258 | 0.4 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 66.5124 | 18.6917 | 444863.051 | 37.0719 | 37.0719 | 96.1659 | 0.5 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 67.485 | 19.6644 | 468012.8638 | 39.0011 | 39.0011 | 97.9061 | 0.6 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 68.4577 | 20.6371 | 491162.6766 | 40.9302 | 40.9302 | 99.6462 | 0.7 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 69.4304 | 21.6098 | 514312.4893 | 42.8594 | 42.8594 | 101.3864 | 0.8 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 70.4031 | 22.5824 | 537462.3021 | 44.7885 | 44.7885 | 103.1265 | 0.9 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 71.3758 | 23.5551 | 560612.1148 | 46.7177 | 46.7177 | 104.8667 | 1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 72.3484 | 24.5278 | 583761.9276 | 48.6468 | 48.6468 | 106.6068 | 75 | 60 | 28.9301 | 28 | 58.8
9/9/20XX 5:00:00 PM | 0.70833 | 5 | 73 | 58.4 | 60.4992 | 72.8342 | 12.335 | 50 | 73 |  | 73 | 70.8606 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 63.4455 | 15.6249 | 371872.6278 | 30.9894 | 30.9894 | 90.5244 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.2694 | 16.4488 | 391481.4556 | 32.6235 | 32.6235 | 91.8435 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 65.0933 | 17.2727 | 411090.2834 | 34.2575 | 34.2575 | 93.1625 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 65.9172 | 18.0966 | 430699.1112 | 35.8916 | 35.8916 | 94.4816 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 66.7411 | 18.9205 | 450307.939 | 37.5257 | 37.5257 | 95.8007 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 67.565 | 19.7444 | 469916.7668 | 39.1597 | 39.1597 | 97.1197 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 68.3889 | 20.5683 | 489525.5946 | 40.7938 | 40.7938 | 98.4388 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 69.2128 | 21.3922 | 509134.4224 | 42.4279 | 42.4279 | 99.7579 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 70.0367 | 22.2161 | 528743.2502 | 44.0619 | 44.0619 | 101.0769 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 70.8606 | 23.04 | 548352.078 | 45.696 | 45.696 | 102.396 | 75 | 60 | 28.5996 | 28 | 58.4
9/9/20XX 6:00:00 PM | 0.75 | 5 | 71.8 | 61.2 | 69.8602 | 81.7218 | 11.8616 | 60 | 71.8 |  | 71.8 | 71.2836 | 0.1 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 63.4878 | 15.6672 | 372879.3321 | 31.0733 | 31.0733 | 90.2303 | 0.2 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 64.354 | 16.5334 | 393494.8643 | 32.7912 | 32.7912 | 91.2552 | 0.3 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 65.2202 | 17.3996 | 414110.3964 | 34.5092 | 34.5092 | 92.2802 | 0.4 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 66.0864 | 18.2658 | 434725.9286 | 36.2272 | 36.2272 | 93.3052 | 0.5 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 66.9526 | 19.132 | 455341.4607 | 37.9451 | 37.9451 | 94.3301 | 0.6 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 67.8188 | 19.9982 | 475956.9928 | 39.6631 | 39.6631 | 95.3551 | 0.7 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 68.685 | 20.8644 | 496572.525 | 41.381 | 41.381 | 96.38 | 0.8 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 69.5512 | 21.7306 | 517188.0571 | 43.099 | 43.099 | 97.405 | 0.9 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 70.4174 | 22.5968 | 537803.5893 | 44.817 | 44.817 | 98.43 | 1 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 71.2836 | 23.463 | 558419.1214 | 46.5349 | 46.5349 | 99.4549 | 70 | 60 | 28.3723 | 28 | 61.2
9/9/20XX 7:00:00 PM | 0.79167 | 5 | 71.2 | 63.4 | 68.413 | 80.0233 | 11.6102 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/9/20XX 8:00:00 PM | 0.83333 | 5 | 70.4 | 62.9 | 66.524 | 77.8062 | 11.2822 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/9/20XX 9:00:00 PM | 0.875 | 5 | 70 | 67.7 | 65.5967 | 76.7179 | 11.1212 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/9/20XX 10:00:00 PM | 0.91667 | 5 | 68.6 | 70.1 | 73.0131 | 83.6528 | 10.6396 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/9/20XX 11:00:00 PM | 0.95833 | 5 | 68.1 | 72.8 | 71.7287 | 82.1774 | 10.4487 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/9/20XX 12:00:00 AM | 0 | 6 | 67.2 | 73.6 | 69.467 | 79.58 | 10.113 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/10/20XX 1:00:00 AM | 0.041667 | 6 | 66.2 | 77.5 | 67.0285 | 76.7802 | 9.7517 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/10/20XX 2:00:00 AM | 0.083333 | 6 | 65.5 | 78.7 | 65.3675 | 74.8734 | 9.5059 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/10/20XX 3:00:00 AM | 0.125 | 6 | 65.1 | 79.1 | 64.435 | 73.8031 | 9.3681 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/10/20XX 4:00:00 AM | 0.16667 | 6 | 64.8 | 78.2 | 63.7435 | 73.0095 | 9.266 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/10/20XX 5:00:00 AM | 0.20833 | 6 | 64.5 | 78.8 | 63.0587 | 72.2236 | 9.1649 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/10/20XX 6:00:00 AM | 0.25 | 6 | 64.6 | 78.4 | 63.2862 | 72.4847 | 9.1985 | 70 | 64.6 |  | 64.6 | 71.0129 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 71.0129 | 23.1923 | 551976.9038 | 45.9981 | 45.9981 | 76.2381 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 71.0129 | 23.1923 | 551976.9038 | 45.9981 | 45.9981 | 76.2381 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 71.0129 | 23.1923 | 551976.9038 | 45.9981 | 45.9981 | 76.2381 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 71.0129 | 23.1923 | 551976.9038 | 45.9981 | 45.9981 | 76.2381 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 71.0129 | 23.1923 | 551976.9038 | 45.9981 | 45.9981 | 76.2381 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 71.0129 | 23.1923 | 551976.9038 | 45.9981 | 45.9981 | 76.2381 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 71.0129 | 23.1923 | 551976.9038 | 45.9981 | 45.9981 | 76.2381 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 71.0129 | 23.1923 | 551976.9038 | 45.9981 | 45.9981 | 76.2381 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 71.0129 | 23.1923 | 551976.9038 | 45.9981 | 45.9981 | 76.2381 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 71.0129 | 23.1923 | 551976.9038 | 45.9981 | 45.9981 | 76.2381 | 65 | 80 | 26.5696 | 26 | 78.4
9/10/20XX 7:00:00 AM | 0.29167 | 6 | 65 | 78.7 | 64.2037 | 73.5377 | 9.3339 | 70 | 65 |  | 65 | 72.3243 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 72.3243 | 24.5036 | 583186.4244 | 48.5989 | 48.5989 | 80.0989 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 72.3243 | 24.5036 | 583186.4244 | 48.5989 | 48.5989 | 80.0989 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 72.3243 | 24.5036 | 583186.4244 | 48.5989 | 48.5989 | 80.0989 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 72.3243 | 24.5036 | 583186.4244 | 48.5989 | 48.5989 | 80.0989 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 72.3243 | 24.5036 | 583186.4244 | 48.5989 | 48.5989 | 80.0989 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 72.3243 | 24.5036 | 583186.4244 | 48.5989 | 48.5989 | 80.0989 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 72.3243 | 24.5036 | 583186.4244 | 48.5989 | 48.5989 | 80.0989 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 72.3243 | 24.5036 | 583186.4244 | 48.5989 | 48.5989 | 80.0989 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 72.3243 | 24.5036 | 583186.4244 | 48.5989 | 48.5989 | 80.0989 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 72.3243 | 24.5036 | 583186.4244 | 48.5989 | 48.5989 | 80.0989 | 65 | 80 | 26.8717 | 26 | 78.7
9/10/20XX 8:00:00 AM | 0.33333 | 6 | 66.5 | 75.5 | 67.7519 | 77.6107 | 9.8588 | 70 | 66.5 |  | 66.5 | 73.1742 | 0.1 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 63.6769 | 15.8563 | 377379.017 | 31.4483 | 31.4483 | 88.9358 | 0.2 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 64.7322 | 16.9115 | 402494.234 | 33.5412 | 33.5412 | 88.6662 | 0.3 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 65.7874 | 17.9668 | 427609.451 | 35.6341 | 35.6341 | 88.3966 | 0.4 | 71 | 16 | 604800 | 50.4 | 50.4 | 66.8427 | 19.022 | 452724.668 | 37.7271 | 37.7271 | 88.1271 | 0.5 | 70.25 | 15.25 | 576450 | 48.0375 | 48.0375 | 67.8979 | 20.0773 | 477839.885 | 39.82 | 39.82 | 87.8575 | 0.6 | 69.5 | 14.5 | 548100 | 45.675 | 45.675 | 68.9532 | 21.1326 | 502955.102 | 41.9129 | 41.9129 | 87.5879 | 0.7 | 68.75 | 13.75 | 519750 | 43.3125 | 43.3125 | 70.0085 | 22.1878 | 528070.319 | 44.0059 | 44.0059 | 87.3184 | 0.8 | 68 | 13 | 491400 | 40.95 | 40.95 | 71.0637 | 23.2431 | 553185.536 | 46.0988 | 46.0988 | 87.0488 | 0.9 | 67.25 | 12.25 | 463050 | 38.5875 | 38.5875 | 72.119 | 24.2984 | 578300.753 | 48.1917 | 48.1917 | 86.7792 | 1 | 66.5 | 11.5 | 434700 | 36.225 | 36.225 | 73.1742 | 25.3536 | 603415.97 | 50.2847 | 50.2847 | 86.5097 | 65 | 75 | 27.3712 | 28 | 75.5
9/10/20XX 9:00:00 AM | 0.375 | 6 | 68.6 | 71.5 | 73.0131 | 83.6528 | 10.6396 | 70 | 68.6 |  | 68.6 | 74.6091 | 0.1 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 63.8204 | 15.9997 | 380793.9105 | 31.7328 | 31.7328 | 89.8818 | 0.2 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 65.0191 | 17.1985 | 409324.0211 | 34.1103 | 34.1103 | 90.5583 | 0.3 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 66.2179 | 18.3972 | 437854.1316 | 36.4878 | 36.4878 | 91.2348 | 0.4 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 67.4166 | 19.596 | 466384.2421 | 38.8654 | 38.8654 | 91.9114 | 0.5 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 68.6154 | 20.7947 | 494914.3527 | 41.2429 | 41.2429 | 92.5879 | 0.6 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 69.8141 | 21.9935 | 523444.4632 | 43.6204 | 43.6204 | 93.2644 | 0.7 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 71.0128 | 23.1922 | 551974.5738 | 45.9979 | 45.9979 | 93.9409 | 0.8 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 72.2116 | 24.391 | 580504.6843 | 48.3754 | 48.3754 | 94.6174 | 0.9 | 69.14 | 14.14 | 534492 | 44.541 | 44.541 | 73.4103 | 25.5897 | 609034.7948 | 50.7529 | 50.7529 | 95.2939 | 1 | 68.6 | 13.6 | 514080 | 42.84 | 42.84 | 74.6091 | 26.7884 | 637564.9054 | 53.1304 | 53.1304 | 95.9704 | 70 | 70 | 28.1089 | 28 | 71.5
9/10/20XX 10:00:00 AM | 0.41667 | 6 | 70.7 | 67.5 | 67.227 | 78.6313 | 11.4043 | 60 | 70.7 |  | 70.7 | 75.7802 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 63.9375 | 16.1169 | 383581.2213 | 31.9651 | 31.9651 | 90.7756 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 65.2533 | 17.4327 | 414898.6426 | 34.5749 | 34.5749 | 92.3459 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 66.5692 | 18.7486 | 446216.0639 | 37.1847 | 37.1847 | 93.9162 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 67.8851 | 20.0644 | 477533.4852 | 39.7945 | 39.7945 | 95.4865 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 69.2009 | 21.3803 | 508850.9066 | 42.4042 | 42.4042 | 97.0567 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 70.5168 | 22.6961 | 540168.3279 | 45.014 | 45.014 | 98.627 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 71.8326 | 24.012 | 571485.7492 | 47.6238 | 47.6238 | 100.1973 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 73.1485 | 25.3279 | 602803.1705 | 50.2336 | 50.2336 | 101.7676 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 74.4644 | 26.6437 | 634120.5918 | 52.8434 | 52.8434 | 103.3379 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 75.7802 | 27.9596 | 665438.0131 | 55.4532 | 55.4532 | 104.9082 | 70 | 65 | 28.8058 | 28 | 67.5
9/10/20XX 11:00:00 AM | 0.45833 | 6 | 72 | 64.7 | 70.3485 | 82.2949 | 11.9464 | 60 | 72 |  | 72 | 75.9633 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 63.9558 | 16.1352 | 384016.9992 | 32.0014 | 32.0014 | 91.2214 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 65.29 | 17.4693 | 415770.1984 | 34.6475 | 34.6475 | 93.2375 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 66.6241 | 18.8035 | 447523.3975 | 37.2936 | 37.2936 | 95.2536 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 67.9583 | 20.1377 | 479276.5967 | 39.9397 | 39.9397 | 97.2697 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 69.2925 | 21.4718 | 511029.7959 | 42.5858 | 42.5858 | 99.2858 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 70.6266 | 22.806 | 542782.9951 | 45.2319 | 45.2319 | 101.3019 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 71.9608 | 24.1402 | 574536.1942 | 47.878 | 47.878 | 103.318 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 73.295 | 25.4743 | 606289.3934 | 50.5241 | 50.5241 | 105.3341 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 74.6291 | 26.8085 | 638042.5926 | 53.1702 | 53.1702 | 107.3502 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 75.9633 | 28.1427 | 669795.7918 | 55.8163 | 55.8163 | 109.3663 | 70 | 65 | 29.1526 | 30 | 64.7
9/10/20XX 12:00:00 PM | 0.5 | 6 | 73.5 | 61.3 | 74.1052 | 86.7045 | 12.5993 | 60 | 73.5 |  | 73.5 | 75.7431 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 63.9338 | 16.1131 | 383492.9387 | 31.9577 | 31.9577 | 91.6502 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 65.2459 | 17.4253 | 414722.0773 | 34.5602 | 34.5602 | 94.0952 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 66.5581 | 18.7374 | 445951.216 | 37.1626 | 37.1626 | 96.5401 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 67.8702 | 20.0496 | 477180.3547 | 39.765 | 39.765 | 98.985 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 69.1824 | 21.3617 | 508409.4933 | 42.3675 | 42.3675 | 101.43 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 70.4945 | 22.6739 | 539638.632 | 44.9699 | 44.9699 | 103.8749 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 71.8067 | 23.986 | 570867.7707 | 47.5723 | 47.5723 | 106.3198 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 73.1188 | 25.2982 | 602096.9093 | 50.1747 | 50.1747 | 108.7647 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 74.431 | 26.6103 | 633326.048 | 52.7772 | 52.7772 | 111.2097 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 75.7431 | 27.9225 | 664555.1867 | 55.3796 | 55.3796 | 113.6546 | 75 | 60 | 29.4854 | 30 | 61.3
9/10/20XX 1:00:00 PM | 0.54167 | 6 | 73.6 | 60.8 | 74.3617 | 87.0056 | 12.6439 | 60 | 73.6 |  | 73.6 | 75.3732 | 0.1 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 63.8968 | 16.0762 | 382612.4964 | 31.8844 | 31.8844 | 91.6084 | 0.2 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 65.1719 | 17.3513 | 412961.1929 | 34.4134 | 34.4134 | 94.0114 | 0.3 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 66.4471 | 18.6265 | 443309.8893 | 36.9425 | 36.9425 | 96.4145 | 0.4 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 67.7223 | 19.9016 | 473658.5858 | 39.4715 | 39.4715 | 98.8175 | 0.5 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 68.9974 | 21.1768 | 504007.2822 | 42.0006 | 42.0006 | 101.2206 | 0.6 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 70.2726 | 22.4519 | 534355.9786 | 44.5297 | 44.5297 | 103.6237 | 0.7 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 71.5477 | 23.7271 | 564704.6751 | 47.0587 | 47.0587 | 106.0267 | 0.8 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 72.8229 | 25.0022 | 595053.3715 | 49.5878 | 49.5878 | 108.4298 | 0.9 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 74.098 | 26.2774 | 625402.0679 | 52.1168 | 52.1168 | 110.8328 | 1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 75.3732 | 27.5526 | 655750.7644 | 54.6459 | 54.6459 | 113.2359 | 75 | 60 | 29.4521 | 30 | 60.8
9/10/20XX 2:00:00 PM | 0.58333 | 6 | 74.3 | 58.4 | 63.2706 | 76.1783 | 12.9077 | 50 | 74.3 |  | 74.3 | 74.1131 | 0.1 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 63.7708 | 15.9501 | 379613.4227 | 31.6345 | 31.6345 | 91.579 | 0.2 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 64.9199 | 17.0993 | 406963.0454 | 33.9136 | 33.9136 | 93.9526 | 0.3 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 66.0691 | 18.2484 | 434312.6682 | 36.1927 | 36.1927 | 96.3262 | 0.4 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 67.2182 | 19.3976 | 461662.2909 | 38.4719 | 38.4719 | 98.6999 | 0.5 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 68.3674 | 20.5467 | 489011.9136 | 40.751 | 40.751 | 101.0735 | 0.6 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 69.5165 | 21.6959 | 516361.5363 | 43.0301 | 43.0301 | 103.4471 | 0.7 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 70.6656 | 22.845 | 543711.1591 | 45.3093 | 45.3093 | 105.8208 | 0.8 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 71.8148 | 23.9942 | 571060.7818 | 47.5884 | 47.5884 | 108.1944 | 0.9 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 72.9639 | 25.1433 | 598410.4045 | 49.8675 | 49.8675 | 110.568 | 1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 74.1131 | 26.2924 | 625760.0272 | 52.1467 | 52.1467 | 112.9417 | 75 | 60 | 29.4263 | 30 | 58.4
9/10/20XX 3:00:00 PM | 0.625 | 6 | 73.9 | 60.7 | 75.1356 | 87.9141 | 12.7785 | 60 | 73.9 |  | 73.9 | 76.0301 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 63.9625 | 16.1418 | 384176.022 | 32.0147 | 32.0147 | 91.8332 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 65.3033 | 17.4827 | 416088.244 | 34.674 | 34.674 | 94.461 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 66.6442 | 18.8235 | 448000.466 | 37.3334 | 37.3334 | 97.0889 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 67.985 | 20.1644 | 479912.6879 | 39.9927 | 39.9927 | 99.7167 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 69.3259 | 21.5052 | 511824.9099 | 42.6521 | 42.6521 | 102.3446 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 70.6667 | 22.8461 | 543737.1319 | 45.3114 | 45.3114 | 104.9724 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 72.0076 | 24.1869 | 575649.3539 | 47.9708 | 47.9708 | 107.6003 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 73.3484 | 25.5278 | 607561.5759 | 50.6301 | 50.6301 | 110.2281 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 74.6893 | 26.8686 | 639473.7979 | 53.2895 | 53.2895 | 112.856 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 76.0301 | 28.2095 | 671386.0199 | 55.9488 | 55.9488 | 115.4838 | 75 | 60 | 29.6283 | 30 | 60.7
9/10/20XX 4:00:00 PM | 0.66667 | 6 | 73.4 | 61.4 | 73.8495 | 86.4044 | 12.5549 | 60 | 73.4 |  | 73.4 | 75.6072 | 0.1 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 63.9202 | 16.0996 | 383169.4101 | 31.9308 | 31.9308 | 91.5918 | 0.2 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.2187 | 17.3981 | 414075.0203 | 34.5063 | 34.5063 | 93.9783 | 0.3 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 66.5173 | 18.6967 | 444980.6304 | 37.0817 | 37.0817 | 96.3647 | 0.4 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 67.8159 | 19.9952 | 475886.2406 | 39.6572 | 39.6572 | 98.7512 | 0.5 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 69.1144 | 21.2938 | 506791.8507 | 42.2327 | 42.2327 | 101.1377 | 0.6 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 70.413 | 22.5923 | 537697.4609 | 44.8081 | 44.8081 | 103.5241 | 0.7 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 71.7115 | 23.8909 | 568603.071 | 47.3836 | 47.3836 | 105.9106 | 0.8 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 73.0101 | 25.1894 | 599508.6811 | 49.9591 | 49.9591 | 108.2971 | 0.9 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 74.3086 | 26.488 | 630414.2913 | 52.5345 | 52.5345 | 110.6835 | 1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 75.6072 | 27.7866 | 661319.9014 | 55.11 | 55.11 | 113.07 | 75 | 60 | 29.4397 | 30 | 61.4
9/10/20XX 5:00:00 PM | 0.70833 | 6 | 72.5 | 62.1 | 71.5821 | 83.7428 | 12.1608 | 60 | 72.5 |  | 72.5 | 74.1358 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 63.7731 | 15.9524 | 379667.5629 | 31.639 | 31.639 | 91.0165 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.9245 | 17.1038 | 407071.3259 | 33.9226 | 33.9226 | 92.8276 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 66.0759 | 18.2553 | 434475.0888 | 36.2063 | 36.2063 | 94.6388 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 67.2273 | 19.4067 | 461878.8517 | 38.4899 | 38.4899 | 96.4499 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 68.3787 | 20.5581 | 489282.6146 | 40.7736 | 40.7736 | 98.2611 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 69.5301 | 21.7095 | 516686.3776 | 43.0572 | 43.0572 | 100.0722 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 70.6816 | 22.8609 | 544090.1405 | 45.3408 | 45.3408 | 101.8833 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 71.833 | 24.0123 | 571493.9034 | 47.6245 | 47.6245 | 103.6945 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 72.9844 | 25.1638 | 598897.6663 | 49.9081 | 49.9081 | 105.5056 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 74.1358 | 26.3152 | 626301.4293 | 52.1918 | 52.1918 | 107.3168 | 70 | 60 | 28.9894 | 28 | 62.1
9/10/20XX 6:00:00 PM | 0.75 | 6 | 71.6 | 63.8 | 69.3749 | 81.1522 | 11.7773 | 60 | 71.6 |  | 71.6 | 73.8503 | 0.1 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 63.7445 | 15.9239 | 378987.993 | 31.5823 | 31.5823 | 90.6763 | 0.2 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 64.8674 | 17.0467 | 405712.1859 | 33.8093 | 33.8093 | 92.1473 | 0.3 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 65.9902 | 18.1696 | 432436.3789 | 36.0364 | 36.0364 | 93.6184 | 0.4 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 67.1131 | 19.2925 | 459160.5718 | 38.2634 | 38.2634 | 95.0894 | 0.5 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 68.236 | 20.4153 | 485884.7648 | 40.4904 | 40.4904 | 96.5604 | 0.6 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 69.3588 | 21.5382 | 512608.9578 | 42.7174 | 42.7174 | 98.0314 | 0.7 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 70.4817 | 22.6611 | 539333.1507 | 44.9444 | 44.9444 | 99.5024 | 0.8 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 71.6046 | 23.7839 | 566057.3437 | 47.1714 | 47.1714 | 100.9734 | 0.9 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 72.7274 | 24.9068 | 592781.5367 | 49.3985 | 49.3985 | 102.4445 | 1 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 73.8503 | 26.0297 | 619505.7296 | 51.6255 | 51.6255 | 103.9155 | 70 | 65 | 28.7245 | 28 | 63.8
9/10/20XX 7:00:00 PM | 0.79167 | 6 | 70.7 | 65.9 | 67.227 | 78.6313 | 11.4043 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/10/20XX 8:00:00 PM | 0.83333 | 6 | 70.2 | 67.7 | 66.0589 | 77.2604 | 11.2015 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/10/20XX 9:00:00 PM | 0.875 | 6 | 69.5 | 69 | 64.4535 | 75.3763 | 10.9228 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/10/20XX 10:00:00 PM | 0.91667 | 6 | 68.7 | 70.8 | 73.2724 | 83.9506 | 10.6782 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/10/20XX 11:00:00 PM | 0.95833 | 6 | 67.8 | 73.8 | 70.9676 | 81.3033 | 10.3357 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/10/20XX 12:00:00 AM | 0 | 7 | 67.3 | 75.7 | 69.7151 | 79.8649 | 10.1498 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/11/20XX 1:00:00 AM | 0.041667 | 7 | 67 | 75.6 | 68.973 | 79.0128 | 10.0398 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/11/20XX 2:00:00 AM | 0.083333 | 7 | 66.2 | 78 | 67.0285 | 76.7802 | 9.7517 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/11/20XX 3:00:00 AM | 0.125 | 7 | 65.4 | 79.6 | 65.1332 | 74.6045 | 9.4713 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/11/20XX 4:00:00 AM | 0.16667 | 7 | 64.6 | 80.5 | 72.4847 | 81.6621 | 9.1774 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/11/20XX 5:00:00 AM | 0.20833 | 7 | 64.2 | 81.5 | 71.4454 | 80.4876 | 9.0422 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/11/20XX 6:00:00 AM | 0.25 | 7 | 64.3 | 81.7 | 71.704 | 80.7798 | 9.0758 | 80 | 64.3 |  | 64.3 | 73.2469 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 73.2469 | 25.4262 | 605144.0807 | 50.4287 | 50.4287 | 79.7237 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 73.2469 | 25.4262 | 605144.0807 | 50.4287 | 50.4287 | 79.7237 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 73.2469 | 25.4262 | 605144.0807 | 50.4287 | 50.4287 | 79.7237 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 73.2469 | 25.4262 | 605144.0807 | 50.4287 | 50.4287 | 79.7237 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 73.2469 | 25.4262 | 605144.0807 | 50.4287 | 50.4287 | 79.7237 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 73.2469 | 25.4262 | 605144.0807 | 50.4287 | 50.4287 | 79.7237 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 73.2469 | 25.4262 | 605144.0807 | 50.4287 | 50.4287 | 79.7237 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 73.2469 | 25.4262 | 605144.0807 | 50.4287 | 50.4287 | 79.7237 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 73.2469 | 25.4262 | 605144.0807 | 50.4287 | 50.4287 | 79.7237 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 73.2469 | 25.4262 | 605144.0807 | 50.4287 | 50.4287 | 79.7237 | 65 | 80 | 26.8443 | 26 | 81.7
9/11/20XX 7:00:00 AM | 0.29167 | 7 | 65.3 | 79.5 | 64.8997 | 74.3365 | 9.4368 | 70 | 65.3 |  | 65.3 | 73.8647 | 0.1 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 63.7459 | 15.9253 | 379022.189 | 31.5852 | 31.5852 | 88.6947 | 0.2 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 64.8702 | 17.0496 | 405780.5781 | 33.815 | 33.815 | 88.184 | 0.3 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 65.9945 | 18.1739 | 432538.9671 | 36.0449 | 36.0449 | 87.6734 | 0.4 | 70.52 | 15.52 | 586656 | 48.888 | 48.888 | 67.1188 | 19.2982 | 459297.3562 | 38.2748 | 38.2748 | 87.1628 | 0.5 | 69.65 | 14.65 | 553770 | 46.1475 | 46.1475 | 68.2431 | 20.4225 | 486055.7452 | 40.5046 | 40.5046 | 86.6521 | 0.6 | 68.78 | 13.78 | 520884 | 43.407 | 43.407 | 69.3674 | 21.5468 | 512814.1342 | 42.7345 | 42.7345 | 86.1415 | 0.7 | 67.91 | 12.91 | 487998 | 40.6665 | 40.6665 | 70.4917 | 22.6711 | 539572.5233 | 44.9644 | 44.9644 | 85.6309 | 0.8 | 67.04 | 12.04 | 455112 | 37.926 | 37.926 | 71.616 | 23.7954 | 566330.9123 | 47.1942 | 47.1942 | 85.1202 | 0.9 | 66.17 | 11.17 | 422226 | 35.1855 | 35.1855 | 72.7404 | 24.9197 | 593089.3014 | 49.4241 | 49.4241 | 84.6096 | 1 | 65.3 | 10.3 | 389340 | 32.445 | 32.445 | 73.8647 | 26.044 | 619847.6904 | 51.654 | 51.654 | 84.099 | 65 | 80 | 27.1852 | 28 | 79.5
9/11/20XX 8:00:00 AM | 0.33333 | 7 | 66.7 | 76.1 | 68.238 | 78.1688 | 9.9308 | 70 | 66.7 |  | 66.7 | 74.2958 | 0.1 | 73.27 | 18.27 | 690606 | 57.5505 | 57.5505 | 63.7891 | 15.9684 | 380048.3756 | 31.6707 | 31.6707 | 89.2212 | 0.2 | 72.54 | 17.54 | 663012 | 55.251 | 55.251 | 64.9565 | 17.1358 | 407832.9513 | 33.9861 | 33.9861 | 89.2371 | 0.3 | 71.81 | 16.81 | 635418 | 52.9515 | 52.9515 | 66.1239 | 18.3033 | 435617.5269 | 36.3015 | 36.3015 | 89.253 | 0.4 | 71.08 | 16.08 | 607824 | 50.652 | 50.652 | 67.2913 | 19.4707 | 463402.1026 | 38.6168 | 38.6168 | 89.2688 | 0.5 | 70.35 | 15.35 | 580230 | 48.3525 | 48.3525 | 68.4587 | 20.6381 | 491186.6782 | 40.9322 | 40.9322 | 89.2847 | 0.6 | 69.62 | 14.62 | 552636 | 46.053 | 46.053 | 69.6261 | 21.8055 | 518971.2539 | 43.2476 | 43.2476 | 89.3006 | 0.7 | 68.89 | 13.89 | 525042 | 43.7535 | 43.7535 | 70.7936 | 22.9729 | 546755.8295 | 45.563 | 45.563 | 89.3165 | 0.8 | 68.16 | 13.16 | 497448 | 41.454 | 41.454 | 71.961 | 24.1404 | 574540.4052 | 47.8784 | 47.8784 | 89.3324 | 0.9 | 67.43 | 12.43 | 469854 | 39.1545 | 39.1545 | 73.1284 | 25.3078 | 602324.9808 | 50.1937 | 50.1937 | 89.3482 | 1 | 66.7 | 11.7 | 442260 | 36.855 | 36.855 | 74.2958 | 26.4752 | 630109.5565 | 52.5091 | 52.5091 | 89.3641 | 65 | 75 | 27.595 | 28 | 76.1
9/11/20XX 9:00:00 AM | 0.375 | 7 | 68.2 | 70.9 | 71.984 | 82.4706 | 10.4866 | 70 | 68.2 |  | 68.2 | 72.9278 | 0.1 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 63.6522 | 15.8316 | 376792.367 | 31.3994 | 31.3994 | 89.4224 | 0.2 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 64.6829 | 16.8622 | 401320.934 | 33.4434 | 33.4434 | 89.6394 | 0.3 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 65.7135 | 17.8928 | 425849.501 | 35.4875 | 35.4875 | 89.8565 | 0.4 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 66.7441 | 18.9234 | 450378.068 | 37.5315 | 37.5315 | 90.0735 | 0.5 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 67.7747 | 19.9541 | 474906.6351 | 39.5756 | 39.5756 | 90.2906 | 0.6 | 70.52 | 15.52 | 586656 | 48.888 | 48.888 | 68.8053 | 20.9847 | 499435.2021 | 41.6196 | 41.6196 | 90.5076 | 0.7 | 69.94 | 14.94 | 564732 | 47.061 | 47.061 | 69.8359 | 22.0153 | 523963.7691 | 43.6636 | 43.6636 | 90.7246 | 0.8 | 69.36 | 14.36 | 542808 | 45.234 | 45.234 | 70.8665 | 23.0459 | 548492.3361 | 45.7077 | 45.7077 | 90.9417 | 0.9 | 68.78 | 13.78 | 520884 | 43.407 | 43.407 | 71.8971 | 24.0765 | 573020.9031 | 47.7517 | 47.7517 | 91.1587 | 1 | 68.2 | 13.2 | 498960 | 41.58 | 41.58 | 72.9278 | 25.1071 | 597549.4701 | 49.7958 | 49.7958 | 91.3758 | 70 | 70 | 27.7486 | 28 | 70.9
9/11/20XX 10:00:00 AM | 0.41667 | 7 | 70.7 | 64.9 | 67.227 | 78.6313 | 11.4043 | 60 | 70.7 |  | 70.7 | 72.8151 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 63.641 | 15.8203 | 376524.2527 | 31.377 | 31.377 | 90.1875 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 64.6603 | 16.8397 | 400784.7054 | 33.3987 | 33.3987 | 91.1697 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 65.6797 | 17.859 | 425045.1581 | 35.4204 | 35.4204 | 92.1519 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 66.699 | 18.8784 | 449305.6109 | 37.4421 | 37.4421 | 93.1341 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 67.7184 | 19.8977 | 473566.0636 | 39.4638 | 39.4638 | 94.1163 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 68.7377 | 20.9171 | 497826.5163 | 41.4855 | 41.4855 | 95.0985 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 69.7571 | 21.9364 | 522086.969 | 43.5072 | 43.5072 | 96.0807 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 70.7764 | 22.9558 | 546347.4217 | 45.529 | 45.529 | 97.063 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 71.7958 | 23.9751 | 570607.8744 | 47.5507 | 47.5507 | 98.0452 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 72.8151 | 24.9945 | 594868.3271 | 49.5724 | 49.5724 | 99.0274 | 70 | 65 | 28.3426 | 28 | 64.9
9/11/20XX 11:00:00 AM | 0.45833 | 7 | 73.3 | 60.5 | 73.5946 | 86.1051 | 12.5105 | 60 | 73.3 |  | 73.3 | 74.2201 | 0.1 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 63.7815 | 15.9608 | 379868.1058 | 31.6557 | 31.6557 | 91.2852 | 0.2 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 64.9413 | 17.1207 | 407472.4116 | 33.956 | 33.956 | 93.365 | 0.3 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 66.1012 | 18.2805 | 435076.7174 | 36.2564 | 36.2564 | 95.4449 | 0.4 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 67.261 | 19.4404 | 462681.0232 | 38.5568 | 38.5568 | 97.5248 | 0.5 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 68.4209 | 20.6002 | 490285.329 | 40.8571 | 40.8571 | 99.6046 | 0.6 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 69.5807 | 21.7601 | 517889.6348 | 43.1575 | 43.1575 | 101.6845 | 0.7 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 70.7405 | 22.9199 | 545493.9406 | 45.4578 | 45.4578 | 103.7643 | 0.8 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 71.9004 | 24.0798 | 573098.2464 | 47.7582 | 47.7582 | 105.8442 | 0.9 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 73.0602 | 25.2396 | 600702.5522 | 50.0585 | 50.0585 | 107.924 | 1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 74.2201 | 26.3994 | 628306.858 | 52.3589 | 52.3589 | 110.0039 | 75 | 60 | 29.1983 | 30 | 60.5
9/11/20XX 12:00:00 PM | 0.5 | 7 | 74.6 | 59.1 | 63.9253 | 76.9684 | 13.0431 | 50 | 74.6 |  | 74.6 | 75.7945 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 63.9389 | 16.1183 | 383615.2386 | 31.9679 | 31.9679 | 92.0069 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.2562 | 17.4356 | 414966.6771 | 34.5806 | 34.5806 | 94.8086 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 66.5735 | 18.7529 | 446318.1157 | 37.1932 | 37.1932 | 97.6102 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 67.8908 | 20.0701 | 477669.5542 | 39.8058 | 39.8058 | 100.4118 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 69.2081 | 21.3874 | 509020.9928 | 42.4184 | 42.4184 | 103.2134 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 70.5254 | 22.7047 | 540372.4313 | 45.031 | 45.031 | 106.015 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 71.8426 | 24.022 | 571723.8699 | 47.6437 | 47.6437 | 108.8167 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 73.1599 | 25.3393 | 603075.3085 | 50.2563 | 50.2563 | 111.6183 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 74.4772 | 26.6566 | 634426.747 | 52.8689 | 52.8689 | 114.4199 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 75.7945 | 27.9739 | 665778.1856 | 55.4815 | 55.4815 | 117.2215 | 75 | 60 | 29.7628 | 30 | 59.1
9/11/20XX 1:00:00 PM | 0.54167 | 7 | 75.7 | 56.1 | 66.3753 | 79.9253 | 13.55 | 50 | 75.7 |  | 75.7 | 74.6408 | 0.1 | 74.17 | 19.17 | 724626 | 60.3855 | 60.3855 | 63.8235 | 16.0029 | 380869.4114 | 31.7391 | 31.7391 | 92.1246 | 0.2 | 74.34 | 19.34 | 731052 | 60.921 | 60.921 | 65.0255 | 17.2048 | 409475.0228 | 34.1229 | 34.1229 | 95.0439 | 0.3 | 74.51 | 19.51 | 737478 | 61.4565 | 61.4565 | 66.2274 | 18.4067 | 438080.6341 | 36.5067 | 36.5067 | 97.9632 | 0.4 | 74.68 | 19.68 | 743904 | 61.992 | 61.992 | 67.4293 | 19.6087 | 466686.2455 | 38.8905 | 38.8905 | 100.8825 | 0.5 | 74.85 | 19.85 | 750330 | 62.5275 | 62.5275 | 68.6312 | 20.8106 | 495291.8569 | 41.2743 | 41.2743 | 103.8018 | 0.6 | 75.02 | 20.02 | 756756 | 63.063 | 63.063 | 69.8331 | 22.0125 | 523897.4683 | 43.6581 | 43.6581 | 106.7211 | 0.7 | 75.19 | 20.19 | 763182 | 63.5985 | 63.5985 | 71.035 | 23.2144 | 552503.0796 | 46.0419 | 46.0419 | 109.6404 | 0.8 | 75.36 | 20.36 | 769608 | 64.134 | 64.134 | 72.237 | 24.4163 | 581108.691 | 48.4257 | 48.4257 | 112.5597 | 0.9 | 75.53 | 20.53 | 776034 | 64.6695 | 64.6695 | 73.4389 | 25.6182 | 609714.3024 | 50.8095 | 50.8095 | 115.479 | 1 | 75.7 | 20.7 | 782460 | 65.205 | 65.205 | 74.6408 | 26.8202 | 638319.9138 | 53.1933 | 53.1933 | 118.3983 | 75 | 55 | 29.8515 | 30 | 56.1
9/11/20XX 2:00:00 PM | 0.58333 | 7 | 76 | 56.7 | 67.0571 | 80.7483 | 13.6912 | 50 | 76 |  | 76 | 76.2302 | 0.1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 63.9825 | 16.1619 | 384652.1188 | 32.0543 | 32.0543 | 92.5343 | 0.2 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 65.3433 | 17.5227 | 417040.4376 | 34.7534 | 34.7534 | 95.8634 | 0.3 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 66.7042 | 18.8836 | 449428.7563 | 37.4524 | 37.4524 | 99.1924 | 0.4 | 74.8 | 19.8 | 748440 | 62.37 | 62.37 | 68.065 | 20.2444 | 481817.0751 | 40.1514 | 40.1514 | 102.5214 | 0.5 | 75 | 20 | 756000 | 63 | 63 | 69.4259 | 21.6053 | 514205.3939 | 42.8504 | 42.8504 | 105.8504 | 0.6 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 70.7868 | 22.9661 | 546593.7127 | 45.5495 | 45.5495 | 109.1795 | 0.7 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 72.1476 | 24.327 | 578982.0315 | 48.2485 | 48.2485 | 112.5085 | 0.8 | 75.6 | 20.6 | 778680 | 64.89 | 64.89 | 73.5085 | 25.6878 | 611370.3502 | 50.9475 | 50.9475 | 115.8375 | 0.9 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 74.8693 | 27.0487 | 643758.669 | 53.6466 | 53.6466 | 119.1666 | 1 | 76 | 21 | 793800 | 66.15 | 66.15 | 76.2302 | 28.4095 | 676146.9878 | 56.3456 | 56.3456 | 122.4956 | 75 | 55 | 30.1737 | 30 | 56.7
9/11/20XX 3:00:00 PM | 0.625 | 7 | 76.3 | 56.6 | 67.7448 | 81.5784 | 13.8336 | 50 | 76.3 |  | 76.3 | 76.8749 | 0.1 | 74.23 | 19.23 | 726894 | 60.5745 | 60.5745 | 64.047 | 16.2263 | 386186.6857 | 32.1822 | 32.1822 | 92.7567 | 0.2 | 74.46 | 19.46 | 735588 | 61.299 | 61.299 | 65.4723 | 17.6517 | 420109.5715 | 35.0091 | 35.0091 | 96.3081 | 0.3 | 74.69 | 19.69 | 744282 | 62.0235 | 62.0235 | 66.8976 | 19.077 | 454032.4572 | 37.836 | 37.836 | 99.8595 | 0.4 | 74.92 | 19.92 | 752976 | 62.748 | 62.748 | 68.323 | 20.5023 | 487955.3429 | 40.6629 | 40.6629 | 103.4109 | 0.5 | 75.15 | 20.15 | 761670 | 63.4725 | 63.4725 | 69.7483 | 21.9277 | 521878.2287 | 43.4899 | 43.4899 | 106.9624 | 0.6 | 75.38 | 20.38 | 770364 | 64.197 | 64.197 | 71.1736 | 23.353 | 555801.1144 | 46.3168 | 46.3168 | 110.5138 | 0.7 | 75.61 | 20.61 | 779058 | 64.9215 | 64.9215 | 72.599 | 24.7783 | 589724.0001 | 49.1437 | 49.1437 | 114.0652 | 0.8 | 75.84 | 20.84 | 787752 | 65.646 | 65.646 | 74.0243 | 26.2037 | 623646.8859 | 51.9706 | 51.9706 | 117.6166 | 0.9 | 76.07 | 21.07 | 796446 | 66.3705 | 66.3705 | 75.4496 | 27.629 | 657569.7716 | 54.7975 | 54.7975 | 121.168 | 1 | 76.3 | 21.3 | 805140 | 67.095 | 67.095 | 76.8749 | 29.0543 | 691492.6573 | 57.6244 | 57.6244 | 124.7194 | 75 | 55 | 30.3481 | 30 | 56.6
9/11/20XX 4:00:00 PM | 0.66667 | 7 | 76.5 | 54.8 | 68.2065 | 82.1358 | 13.9292 | 50 | 76.5 |  | 76.5 | 74.8926 | 0.1 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 63.8487 | 16.0281 | 381468.6168 | 31.7891 | 31.7891 | 92.4266 | 0.2 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 65.0758 | 17.2552 | 410673.4337 | 34.2228 | 34.2228 | 95.6478 | 0.3 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 66.3029 | 18.4823 | 439878.2505 | 36.6565 | 36.6565 | 98.869 | 0.4 | 75 | 20 | 756000 | 63 | 63 | 67.53 | 19.7094 | 469083.0674 | 39.0903 | 39.0903 | 102.0903 | 0.5 | 75.25 | 20.25 | 765450 | 63.7875 | 63.7875 | 68.7571 | 20.9365 | 498287.8842 | 41.524 | 41.524 | 105.3115 | 0.6 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 69.9842 | 22.1636 | 527492.701 | 43.9577 | 43.9577 | 108.5327 | 0.7 | 75.75 | 20.75 | 784350 | 65.3625 | 65.3625 | 71.2113 | 23.3907 | 556697.5179 | 46.3915 | 46.3915 | 111.754 | 0.8 | 76 | 21 | 793800 | 66.15 | 66.15 | 72.4384 | 24.6177 | 585902.3347 | 48.8252 | 48.8252 | 114.9752 | 0.9 | 76.25 | 21.25 | 803250 | 66.9375 | 66.9375 | 73.6655 | 25.8448 | 615107.1516 | 51.2589 | 51.2589 | 118.1964 | 1 | 76.5 | 21.5 | 812700 | 67.725 | 67.725 | 74.8926 | 27.0719 | 644311.9684 | 53.6927 | 53.6927 | 121.4177 | 75 | 55 | 30.0867 | 30 | 54.8
9/11/20XX 5:00:00 PM | 0.70833 | 7 | 75.5 | 58.2 | 65.924 | 79.3806 | 13.4566 | 50 | 75.5 |  | 75.5 | 76.9584 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 64.0553 | 16.2347 | 386385.3832 | 32.1988 | 32.1988 | 92.5213 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 65.489 | 17.6684 | 420506.9665 | 35.0422 | 35.0422 | 95.8372 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 66.9227 | 19.102 | 454628.5497 | 37.8857 | 37.8857 | 99.1532 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 68.3564 | 20.5357 | 488750.133 | 40.7292 | 40.7292 | 102.4692 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 69.79 | 21.9694 | 522871.7162 | 43.5726 | 43.5726 | 105.7851 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 71.2237 | 23.4031 | 556993.2995 | 46.4161 | 46.4161 | 109.1011 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 72.6574 | 24.8368 | 591114.8827 | 49.2596 | 49.2596 | 112.4171 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 74.0911 | 26.2704 | 625236.4659 | 52.103 | 52.103 | 115.733 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 75.5248 | 27.7041 | 659358.0492 | 54.9465 | 54.9465 | 119.049 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 76.9584 | 29.1378 | 693479.6324 | 57.79 | 57.79 | 122.365 | 75 | 60 | 30.1653 | 30 | 58.2
9/11/20XX 6:00:00 PM | 0.75 | 7 | 73.9 | 60.8 | 75.1356 | 87.9141 | 12.7785 | 60 | 73.9 |  | 73.9 | 76.1579 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 63.9753 | 16.1546 | 384480.1492 | 32.04 | 32.04 | 91.8585 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 65.3289 | 17.5083 | 416696.4984 | 34.7247 | 34.7247 | 94.5117 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 66.6825 | 18.8619 | 448912.8476 | 37.4094 | 37.4094 | 97.1649 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 68.0361 | 20.2155 | 481129.1969 | 40.0941 | 40.0941 | 99.8181 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 69.3898 | 21.5691 | 513345.5461 | 42.7788 | 42.7788 | 102.4713 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 70.7434 | 22.9228 | 545561.8953 | 45.4635 | 45.4635 | 105.1245 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 72.097 | 24.2764 | 577778.2445 | 48.1482 | 48.1482 | 107.7777 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 73.4507 | 25.63 | 609994.5937 | 50.8329 | 50.8329 | 110.4309 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 74.8043 | 26.9837 | 642210.9429 | 53.5176 | 53.5176 | 113.0841 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 76.1579 | 28.3373 | 674427.2921 | 56.2023 | 56.2023 | 115.7373 | 75 | 60 | 29.6482 | 30 | 60.8
9/11/20XX 7:00:00 PM | 0.79167 | 7 | 72.9 | 63.1 | 72.5823 | 84.9169 | 12.3346 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/11/20XX 8:00:00 PM | 0.83333 | 7 | 71.9 | 65.8 | 70.104 | 82.008 | 11.904 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/11/20XX 9:00:00 PM | 0.875 | 7 | 71.7 | 67.2 | 69.6172 | 81.4366 | 11.8194 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/11/20XX 10:00:00 PM | 0.91667 | 7 | 70.9 | 67.6 | 67.6992 | 79.1855 | 11.4863 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/11/20XX 11:00:00 PM | 0.95833 | 7 | 69.8 | 69.4 | 65.1373 | 76.1788 | 11.0415 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/11/20XX 12:00:00 AM | 0 | 1 | 69.1 | 70.4 | 74.3178 | 85.1515 | 10.8337 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/12/20XX 1:00:00 AM | 0.041667 | 1 | 68.5 | 72.5 | 72.7546 | 83.3558 | 10.6012 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/12/20XX 2:00:00 AM | 0.083333 | 1 | 67.9 | 73.4 | 71.2205 | 81.5937 | 10.3732 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/12/20XX 3:00:00 AM | 0.125 | 1 | 67.2 | 75.2 | 69.467 | 79.58 | 10.113 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/12/20XX 4:00:00 AM | 0.16667 | 1 | 66.2 | 77.7 | 67.0285 | 76.7802 | 9.7517 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/12/20XX 5:00:00 AM | 0.20833 | 1 | 65.9 | 78.7 | 66.3121 | 75.9577 | 9.6456 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/12/20XX 6:00:00 AM | 0.25 | 1 | 65.8 | 80 | 75.6853 | 85.2798 | 9.5945 | 80 | 65.8 |  | 65.8 | 75.6853 | 0.1 | 73.18 | 18.18 | 687204 | 57.267 | 57.267 | 63.928 | 16.1074 | 383355.3334 | 31.9463 | 31.9463 | 89.2133 | 0.2 | 72.36 | 17.36 | 656208 | 54.684 | 54.684 | 65.2344 | 17.4137 | 414446.8667 | 34.5372 | 34.5372 | 89.2212 | 0.3 | 71.54 | 16.54 | 625212 | 52.101 | 52.101 | 66.5407 | 18.7201 | 445538.4001 | 37.1282 | 37.1282 | 89.2292 | 0.4 | 70.72 | 15.72 | 594216 | 49.518 | 49.518 | 67.8471 | 20.0265 | 476629.9334 | 39.7192 | 39.7192 | 89.2372 | 0.5 | 69.9 | 14.9 | 563220 | 46.935 | 46.935 | 69.1535 | 21.3328 | 507721.4668 | 42.3101 | 42.3101 | 89.2451 | 0.6 | 69.08 | 14.08 | 532224 | 44.352 | 44.352 | 70.4598 | 22.6392 | 538813.0001 | 44.9011 | 44.9011 | 89.2531 | 0.7 | 68.26 | 13.26 | 501228 | 41.769 | 41.769 | 71.7662 | 23.9456 | 569904.5335 | 47.492 | 47.492 | 89.261 | 0.8 | 67.44 | 12.44 | 470232 | 39.186 | 39.186 | 73.0726 | 25.2519 | 600996.0669 | 50.083 | 50.083 | 89.269 | 0.9 | 66.62 | 11.62 | 439236 | 36.603 | 36.603 | 74.3789 | 26.5583 | 632087.6002 | 52.674 | 52.674 | 89.277 | 1 | 65.8 | 10.8 | 408240 | 34.02 | 34.02 | 75.6853 | 27.8647 | 663179.1336 | 55.2649 | 55.2649 | 89.2849 | 65 | 80 | 27.5914 | 28 | 80
9/12/20XX 7:00:00 AM | 0.29167 | 1 | 66.6 | 78.7 | 67.9946 | 77.8893 | 9.8947 | 70 | 66.6 |  | 66.6 | 76.603 | 0.1 | 73.26 | 18.26 | 690228 | 57.519 | 57.519 | 64.0198 | 16.1991 | 385539.4674 | 32.1283 | 32.1283 | 89.6473 | 0.2 | 72.52 | 17.52 | 662256 | 55.188 | 55.188 | 65.4179 | 17.5973 | 418815.1347 | 34.9013 | 34.9013 | 90.0893 | 0.3 | 71.78 | 16.78 | 634284 | 52.857 | 52.857 | 66.816 | 18.9954 | 452090.8021 | 37.6742 | 37.6742 | 90.5312 | 0.4 | 71.04 | 16.04 | 606312 | 50.526 | 50.526 | 68.2142 | 20.3935 | 485366.4694 | 40.4472 | 40.4472 | 90.9732 | 0.5 | 70.3 | 15.3 | 578340 | 48.195 | 48.195 | 69.6123 | 21.7917 | 518642.1368 | 43.2202 | 43.2202 | 91.4152 | 0.6 | 69.56 | 14.56 | 550368 | 45.864 | 45.864 | 71.0105 | 23.1898 | 551917.8042 | 45.9932 | 45.9932 | 91.8572 | 0.7 | 68.82 | 13.82 | 522396 | 43.533 | 43.533 | 72.4086 | 24.588 | 585193.4715 | 48.7661 | 48.7661 | 92.2991 | 0.8 | 68.08 | 13.08 | 494424 | 41.202 | 41.202 | 73.8067 | 25.9861 | 618469.1389 | 51.5391 | 51.5391 | 92.7411 | 0.9 | 67.34 | 12.34 | 466452 | 38.871 | 38.871 | 75.2049 | 27.3842 | 651744.8062 | 54.3121 | 54.3121 | 93.1831 | 1 | 66.6 | 11.6 | 438480 | 36.54 | 36.54 | 76.603 | 28.7824 | 685020.4736 | 57.085 | 57.085 | 93.625 | 65 | 80 | 27.9304 | 28 | 78.7
9/12/20XX 8:00:00 AM | 0.33333 | 1 | 68.4 | 73.3 | 72.4969 | 83.0598 | 10.5629 | 70 | 68.4 |  | 68.4 | 75.9827 | 0.1 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 63.9577 | 16.1371 | 384063.0977 | 32.0053 | 32.0053 | 90.0913 | 0.2 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 65.2938 | 17.4732 | 415862.3955 | 34.6552 | 34.6552 | 90.9772 | 0.3 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 66.6299 | 18.8093 | 447661.6932 | 37.3051 | 37.3051 | 91.8631 | 0.4 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 67.9661 | 20.1454 | 479460.9909 | 39.9551 | 39.9551 | 92.7491 | 0.5 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 69.3022 | 21.4815 | 511260.2886 | 42.605 | 42.605 | 93.635 | 0.6 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 70.6383 | 22.8176 | 543059.5864 | 45.255 | 45.255 | 94.521 | 0.7 | 70.08 | 15.08 | 570024 | 47.502 | 47.502 | 71.9744 | 24.1537 | 574858.8841 | 47.9049 | 47.9049 | 95.4069 | 0.8 | 69.52 | 14.52 | 548856 | 45.738 | 45.738 | 73.3105 | 25.4898 | 606658.1818 | 50.5548 | 50.5548 | 96.2928 | 0.9 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 74.6466 | 26.8259 | 638457.4795 | 53.2048 | 53.2048 | 97.1788 | 1 | 68.4 | 13.4 | 506520 | 42.21 | 42.21 | 75.9827 | 28.162 | 670256.7773 | 55.8547 | 55.8547 | 98.0647 | 70 | 75 | 28.2743 | 28 | 73.3
9/12/20XX 9:00:00 AM | 0.375 | 1 | 69.5 | 72.3 | 75.3763 | 86.3676 | 10.9913 | 70 | 69.5 |  | 69.5 | 77.9043 | 0.1 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 64.1499 | 16.3293 | 388636.5171 | 32.3864 | 32.3864 | 90.8189 | 0.2 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 65.6782 | 17.8575 | 425009.2341 | 35.4174 | 35.4174 | 92.4324 | 0.3 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 67.2064 | 19.3858 | 461381.9512 | 38.4485 | 38.4485 | 94.046 | 0.4 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 68.7347 | 20.9141 | 497754.6682 | 41.4796 | 41.4796 | 95.6596 | 0.5 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 70.263 | 22.4423 | 534127.3853 | 44.5106 | 44.5106 | 97.2731 | 0.6 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 71.7912 | 23.9706 | 570500.1023 | 47.5417 | 47.5417 | 98.8867 | 0.7 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 73.3195 | 25.4989 | 606872.8194 | 50.5727 | 50.5727 | 100.5002 | 0.8 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 74.8478 | 27.0271 | 643245.5365 | 53.6038 | 53.6038 | 102.1138 | 0.9 | 69.95 | 14.95 | 565110 | 47.0925 | 47.0925 | 76.376 | 28.5554 | 679618.2535 | 56.6349 | 56.6349 | 103.7274 | 1 | 69.5 | 14.5 | 548100 | 45.675 | 45.675 | 77.9043 | 30.0837 | 715990.9706 | 59.6659 | 59.6659 | 105.3409 | 70 | 70 | 28.8436 | 28 | 72.3
9/12/20XX 10:00:00 AM | 0.41667 | 1 | 71.5 | 67.8 | 69.1333 | 80.8687 | 11.7354 | 60 | 71.5 |  | 71.5 | 78.2869 | 0.1 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 64.1882 | 16.3675 | 389547.1823 | 32.4623 | 32.4623 | 91.5248 | 0.2 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 65.7547 | 17.9341 | 426830.5645 | 35.5692 | 35.5692 | 93.8442 | 0.3 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 67.3212 | 19.5006 | 464113.9468 | 38.6762 | 38.6762 | 96.1637 | 0.4 | 73 | 18 | 680400 | 56.7 | 56.7 | 68.8877 | 21.0671 | 501397.3291 | 41.7831 | 41.7831 | 98.4831 | 0.5 | 72.75 | 17.75 | 670950 | 55.9125 | 55.9125 | 70.4543 | 22.6336 | 538680.7113 | 44.8901 | 44.8901 | 100.8026 | 0.6 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 72.0208 | 24.2002 | 575964.0936 | 47.997 | 47.997 | 103.122 | 0.7 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 73.5873 | 25.7667 | 613247.4759 | 51.104 | 51.104 | 105.4415 | 0.8 | 72 | 17 | 642600 | 53.55 | 53.55 | 75.1539 | 27.3332 | 650530.8581 | 54.2109 | 54.2109 | 107.7609 | 0.9 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 76.7204 | 28.8998 | 687814.2404 | 57.3179 | 57.3179 | 110.0804 | 1 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 78.2869 | 30.4663 | 725097.6226 | 60.4248 | 60.4248 | 112.3998 | 70 | 70 | 29.3933 | 30 | 67.8
9/12/20XX 11:00:00 AM | 0.45833 | 1 | 73.8 | 63 | 74.8769 | 87.6104 | 12.7335 | 60 | 73.8 |  | 73.8 | 78.6969 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 64.2292 | 16.4085 | 390523.0017 | 32.5436 | 32.5436 | 92.3306 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 65.8367 | 18.0161 | 428782.2033 | 35.7319 | 35.7319 | 95.4559 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 67.4442 | 19.6236 | 467041.405 | 38.9201 | 38.9201 | 98.5811 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 69.0518 | 21.2311 | 505300.6066 | 42.1084 | 42.1084 | 101.7064 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 70.6593 | 22.8386 | 543559.8083 | 45.2967 | 45.2967 | 104.8317 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 72.2668 | 24.4462 | 581819.0099 | 48.4849 | 48.4849 | 107.9569 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 73.8743 | 26.0537 | 620078.2116 | 51.6732 | 51.6732 | 111.0822 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 75.4819 | 27.6612 | 658337.4132 | 54.8615 | 54.8615 | 114.2075 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 77.0894 | 29.2688 | 696596.6149 | 58.0497 | 58.0497 | 117.3327 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 78.6969 | 30.8763 | 734855.8166 | 61.238 | 61.238 | 120.458 | 75 | 65 | 30.0209 | 30 | 63
9/12/20XX 12:00:00 PM | 0.5 | 1 | 75.3 | 59.1 | 65.4753 | 78.8391 | 13.3637 | 50 | 75.3 |  | 75.3 | 77.6364 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 64.1231 | 16.3025 | 387998.8354 | 32.3332 | 32.3332 | 92.5927 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 65.6246 | 17.8039 | 423733.8708 | 35.3112 | 35.3112 | 95.9802 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 67.126 | 19.3054 | 459468.9062 | 38.2891 | 38.2891 | 99.3676 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 68.6275 | 20.8069 | 495203.9416 | 41.267 | 41.267 | 102.755 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 70.129 | 22.3084 | 530938.977 | 44.2449 | 44.2449 | 106.1424 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 71.6305 | 23.8098 | 566674.0124 | 47.2228 | 47.2228 | 109.5298 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 73.1319 | 25.3113 | 602409.0478 | 50.2008 | 50.2008 | 112.9173 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 74.6334 | 26.8128 | 638144.0832 | 53.1787 | 53.1787 | 116.3047 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 76.1349 | 28.3142 | 673879.1186 | 56.1566 | 56.1566 | 119.6921 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 77.6364 | 29.8157 | 709614.1541 | 59.1345 | 59.1345 | 123.0795 | 75 | 60 | 30.2224 | 30 | 59.1
9/12/20XX 1:00:00 PM | 0.54167 | 1 | 74.6 | 62.3 | 76.9684 | 90.0655 | 13.0971 | 60 | 74.6 |  | 74.6 | 79.9807 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 64.3575 | 16.5369 | 393578.4398 | 32.7982 | 32.7982 | 92.8372 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 66.0935 | 18.2728 | 434893.0795 | 36.2411 | 36.2411 | 96.4691 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 67.8294 | 20.0087 | 476207.7193 | 39.684 | 39.684 | 100.101 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 69.5653 | 21.7446 | 517522.359 | 43.1269 | 43.1269 | 103.7329 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 71.3012 | 23.4805 | 558836.9988 | 46.5697 | 46.5697 | 107.3647 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 73.0371 | 25.2165 | 600151.6386 | 50.0126 | 50.0126 | 110.9966 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 74.773 | 26.9524 | 641466.2783 | 53.4555 | 53.4555 | 114.6285 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 76.5089 | 28.6883 | 682780.9181 | 56.8984 | 56.8984 | 118.2604 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 78.2448 | 30.4242 | 724095.5578 | 60.3413 | 60.3413 | 121.8923 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 79.9807 | 32.1601 | 765410.1976 | 63.7842 | 63.7842 | 125.5242 | 75 | 60 | 30.4177 | 30 | 62.3
9/12/20XX 2:00:00 PM | 0.58333 | 1 | 74.4 | 64.9 | 76.4409 | 89.4463 | 13.0054 | 60 | 74.4 |  | 74.4 | 82.8135 | 0.1 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 64.6408 | 16.8202 | 400320.5395 | 33.36 | 33.36 | 93.336 | 0.2 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 66.66 | 18.8394 | 448377.2789 | 37.3648 | 37.3648 | 97.4668 | 0.3 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 68.6792 | 20.8586 | 496434.0184 | 41.3695 | 41.3695 | 101.5975 | 0.4 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 70.6984 | 22.8778 | 544490.7579 | 45.3742 | 45.3742 | 105.7282 | 0.5 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 72.7176 | 24.897 | 592547.4973 | 49.379 | 49.379 | 109.859 | 0.6 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 74.7368 | 26.9161 | 640604.2368 | 53.3837 | 53.3837 | 113.9897 | 0.7 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 76.756 | 28.9353 | 688660.9763 | 57.3884 | 57.3884 | 118.1204 | 0.8 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 78.7752 | 30.9545 | 736717.7157 | 61.3931 | 61.3931 | 122.2511 | 0.9 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 80.7943 | 32.9737 | 784774.4552 | 65.3979 | 65.3979 | 126.3819 | 1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 82.8135 | 34.9929 | 832831.1947 | 69.4026 | 69.4026 | 130.5126 | 75 | 65 | 30.8119 | 30 | 64.9
9/12/20XX 3:00:00 PM | 0.625 | 1 | 74.6 | 65.3 | 76.9684 | 90.0655 | 13.0971 | 60 | 74.6 |  | 74.6 | 83.9099 | 0.1 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 64.7505 | 16.9298 | 402929.7991 | 33.5775 | 33.5775 | 93.6165 | 0.2 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 66.8793 | 19.0586 | 453595.7982 | 37.7996 | 37.7996 | 98.0276 | 0.3 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 69.0081 | 21.1875 | 504261.7973 | 42.0218 | 42.0218 | 102.4388 | 0.4 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 71.1369 | 23.3163 | 554927.7964 | 46.244 | 46.244 | 106.85 | 0.5 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 73.2657 | 25.4451 | 605593.7955 | 50.4661 | 50.4661 | 111.2611 | 0.6 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 75.3946 | 27.5739 | 656259.7945 | 54.6883 | 54.6883 | 115.6723 | 0.7 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 77.5234 | 29.7028 | 706925.7936 | 58.9105 | 58.9105 | 120.0835 | 0.8 | 74.48 | 19.48 | 736344 | 61.362 | 61.362 | 79.6522 | 31.8316 | 757591.7927 | 63.1326 | 63.1326 | 124.4946 | 0.9 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 81.781 | 33.9604 | 808257.7918 | 67.3548 | 67.3548 | 128.9058 | 1 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 83.9099 | 36.0892 | 858923.7909 | 71.577 | 71.577 | 133.317 | 75 | 65 | 31.0325 | 32 | 65.3
9/12/20XX 4:00:00 PM | 0.66667 | 1 | 74.1 | 64.8 | 75.6554 | 88.5243 | 12.8688 | 60 | 74.1 |  | 74.1 | 81.8325 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 64.5427 | 16.7221 | 397985.6004 | 33.1655 | 33.1655 | 93.047 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 66.4638 | 18.6432 | 443707.4008 | 36.9756 | 36.9756 | 96.8886 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 68.3849 | 20.5643 | 489429.2012 | 40.7858 | 40.7858 | 100.7303 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 70.306 | 22.4853 | 535151.0016 | 44.5959 | 44.5959 | 104.5719 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 72.2271 | 24.4064 | 580872.8019 | 48.4061 | 48.4061 | 108.4136 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 74.1481 | 26.3275 | 626594.6023 | 52.2162 | 52.2162 | 112.2552 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 76.0692 | 28.2486 | 672316.4027 | 56.0264 | 56.0264 | 116.0969 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 77.9903 | 30.1697 | 718038.2031 | 59.8365 | 59.8365 | 119.9385 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 79.9114 | 32.0908 | 763760.0035 | 63.6467 | 63.6467 | 123.7802 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 81.8325 | 34.0118 | 809481.8039 | 67.4568 | 67.4568 | 127.6218 | 75 | 65 | 30.5849 | 30 | 64.8
9/12/20XX 5:00:00 PM | 0.70833 | 1 | 73 | 68.8 | 72.8342 | 85.2126 | 12.3784 | 60 | 73 |  | 73 | 83.7272 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.7322 | 16.9116 | 402495.1035 | 33.5413 | 33.5413 | 93.0763 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 66.8428 | 19.0221 | 452726.4069 | 37.7272 | 37.7272 | 96.9472 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 68.9533 | 21.1327 | 502957.7104 | 41.9131 | 41.9131 | 100.8181 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 71.0639 | 23.2432 | 553189.0139 | 46.0991 | 46.0991 | 104.6891 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 73.1744 | 25.3538 | 603420.3173 | 50.285 | 50.285 | 108.56 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 75.285 | 27.4644 | 653651.6208 | 54.471 | 54.471 | 112.431 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 77.3955 | 29.5749 | 703882.9243 | 58.6569 | 58.6569 | 116.3019 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 79.5061 | 31.6855 | 754114.2277 | 62.8429 | 62.8429 | 120.1729 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 81.6167 | 33.796 | 804345.5312 | 67.0288 | 67.0288 | 124.0438 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 83.7272 | 35.9066 | 854576.8347 | 71.2147 | 71.2147 | 127.9147 | 75 | 70 | 30.6114 | 30 | 68.8
9/12/20XX 6:00:00 PM | 0.75 | 1 | 71.4 | 72.9 | 80.586 | 92.3545 | 11.7685 | 70 | 71.4 |  | 71.4 | 83.9989 | 0.1 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 64.7594 | 16.9387 | 403141.7022 | 33.5951 | 33.5951 | 92.6261 | 0.2 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 66.8971 | 19.0765 | 454019.6044 | 37.835 | 37.835 | 96.047 | 0.3 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 69.0348 | 21.2142 | 504897.5065 | 42.0748 | 42.0748 | 99.4678 | 0.4 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 71.1725 | 23.3519 | 555775.4087 | 46.3146 | 46.3146 | 102.8886 | 0.5 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 73.3103 | 25.4896 | 606653.3109 | 50.5544 | 50.5544 | 106.3094 | 0.6 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 75.448 | 27.6274 | 657531.2131 | 54.7943 | 54.7943 | 109.7303 | 0.7 | 72.18 | 17.18 | 649404 | 54.117 | 54.117 | 77.5857 | 29.7651 | 708409.1153 | 59.0341 | 59.0341 | 113.1511 | 0.8 | 71.92 | 16.92 | 639576 | 53.298 | 53.298 | 79.7234 | 31.9028 | 759287.0175 | 63.2739 | 63.2739 | 116.5719 | 0.9 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 81.8612 | 34.0405 | 810164.9196 | 67.5137 | 67.5137 | 119.9927 | 1 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 83.9989 | 36.1783 | 861042.8218 | 71.7536 | 71.7536 | 123.4136 | 70 | 75 | 30.2614 | 30 | 72.9
9/12/20XX 7:00:00 PM | 0.79167 | 1 | 69.8 | 74.5 | 76.1788 | 87.2896 | 11.1108 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/12/20XX 8:00:00 PM | 0.83333 | 1 | 69 | 76.6 | 74.0553 | 84.8499 | 10.7946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/12/20XX 9:00:00 PM | 0.875 | 1 | 69 | 75.5 | 74.0553 | 84.8499 | 10.7946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/12/20XX 10:00:00 PM | 0.91667 | 1 | 68.3 | 77 | 72.24 | 82.7647 | 10.5247 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/12/20XX 11:00:00 PM | 0.95833 | 1 | 67.7 | 78.3 | 70.7155 | 81.0138 | 10.2983 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/12/20XX 12:00:00 AM | 0 | 2 | 67.8 | 78.1 | 70.9676 | 81.3033 | 10.3357 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/13/20XX 1:00:00 AM | 0.041667 | 2 | 67.2 | 79.3 | 69.467 | 79.58 | 10.113 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/13/20XX 2:00:00 AM | 0.083333 | 2 | 66.7 | 79.7 | 68.238 | 78.1688 | 9.9308 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/13/20XX 3:00:00 AM | 0.125 | 2 | 66.2 | 82.3 | 76.7802 | 86.5176 | 9.7374 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/13/20XX 4:00:00 AM | 0.16667 | 2 | 65.9 | 82.9 | 75.9577 | 85.5877 | 9.63 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/13/20XX 5:00:00 AM | 0.20833 | 2 | 65.4 | 82.3 | 74.6045 | 84.058 | 9.4535 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/13/20XX 6:00:00 AM | 0.25 | 2 | 65 | 83.5 | 73.5377 | 82.8522 | 9.3145 | 80 | 65 |  | 65 | 76.7978 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 76.7978 | 28.9771 | 689655.5422 | 57.4713 | 57.4713 | 88.9713 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 76.7978 | 28.9771 | 689655.5422 | 57.4713 | 57.4713 | 88.9713 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 76.7978 | 28.9771 | 689655.5422 | 57.4713 | 57.4713 | 88.9713 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 76.7978 | 28.9771 | 689655.5422 | 57.4713 | 57.4713 | 88.9713 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 76.7978 | 28.9771 | 689655.5422 | 57.4713 | 57.4713 | 88.9713 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 76.7978 | 28.9771 | 689655.5422 | 57.4713 | 57.4713 | 88.9713 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 76.7978 | 28.9771 | 689655.5422 | 57.4713 | 57.4713 | 88.9713 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 76.7978 | 28.9771 | 689655.5422 | 57.4713 | 57.4713 | 88.9713 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 76.7978 | 28.9771 | 689655.5422 | 57.4713 | 57.4713 | 88.9713 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 76.7978 | 28.9771 | 689655.5422 | 57.4713 | 57.4713 | 88.9713 | 65 | 85 | 27.5689 | 28 | 83.5
9/13/20XX 7:00:00 AM | 0.29167 | 2 | 66.3 | 80.4 | 77.0561 | 86.8295 | 9.7734 | 80 | 66.3 |  | 66.3 | 77.4471 | 0.1 | 73.23 | 18.23 | 689094 | 57.4245 | 57.4245 | 64.1042 | 16.2835 | 387548.3585 | 32.2957 | 32.2957 | 89.7202 | 0.2 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 65.5867 | 17.7661 | 422832.917 | 35.2361 | 35.2361 | 90.2351 | 0.3 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 67.0693 | 19.2486 | 458117.4755 | 38.1765 | 38.1765 | 90.75 | 0.4 | 70.92 | 15.92 | 601776 | 50.148 | 50.148 | 68.5518 | 20.7312 | 493402.034 | 41.1168 | 41.1168 | 91.2648 | 0.5 | 70.15 | 15.15 | 572670 | 47.7225 | 47.7225 | 70.0344 | 22.2137 | 528686.5925 | 44.0572 | 44.0572 | 91.7797 | 0.6 | 69.38 | 14.38 | 543564 | 45.297 | 45.297 | 71.5169 | 23.6963 | 563971.1511 | 46.9976 | 46.9976 | 92.2946 | 0.7 | 68.61 | 13.61 | 514458 | 42.8715 | 42.8715 | 72.9994 | 25.1788 | 599255.7096 | 49.938 | 49.938 | 92.8095 | 0.8 | 67.84 | 12.84 | 485352 | 40.446 | 40.446 | 74.482 | 26.6614 | 634540.2681 | 52.8784 | 52.8784 | 93.3244 | 0.9 | 67.07 | 12.07 | 456246 | 38.0205 | 38.0205 | 75.9645 | 28.1439 | 669824.8266 | 55.8187 | 55.8187 | 93.8392 | 1 | 66.3 | 11.3 | 427140 | 35.595 | 35.595 | 77.4471 | 29.6264 | 705109.3851 | 58.7591 | 58.7591 | 94.3541 | 65 | 80 | 27.9885 | 28 | 80.4
9/13/20XX 8:00:00 AM | 0.33333 | 2 | 67.5 | 77.9 | 70.2137 | 80.4375 | 10.2238 | 70 | 67.5 |  | 67.5 | 78.2905 | 0.1 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 64.1885 | 16.3679 | 389555.7554 | 32.463 | 32.463 | 90.2655 | 0.2 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 65.7554 | 17.9348 | 426847.7109 | 35.5706 | 35.5706 | 91.3256 | 0.3 | 72.05 | 17.05 | 644490 | 53.7075 | 53.7075 | 67.3223 | 19.5017 | 464139.6663 | 38.6783 | 38.6783 | 92.3858 | 0.4 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 68.8892 | 21.0686 | 501431.6217 | 41.786 | 41.786 | 93.446 | 0.5 | 70.75 | 15.75 | 595350 | 49.6125 | 49.6125 | 70.4561 | 22.6354 | 538723.5771 | 44.8936 | 44.8936 | 94.5061 | 0.6 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 72.023 | 24.2023 | 576015.5326 | 48.0013 | 48.0013 | 95.5663 | 0.7 | 69.45 | 14.45 | 546210 | 45.5175 | 45.5175 | 73.5899 | 25.7692 | 613307.488 | 51.109 | 51.109 | 96.6265 | 0.8 | 68.8 | 13.8 | 521640 | 43.47 | 43.47 | 75.1567 | 27.3361 | 650599.4434 | 54.2166 | 54.2166 | 97.6866 | 0.9 | 68.15 | 13.15 | 497070 | 41.4225 | 41.4225 | 76.7236 | 28.903 | 687891.3988 | 57.3243 | 57.3243 | 98.7468 | 1 | 67.5 | 12.5 | 472500 | 39.375 | 39.375 | 78.2905 | 30.4699 | 725183.3543 | 60.4319 | 60.4319 | 99.8069 | 65 | 80 | 28.414 | 28 | 77.9
9/13/20XX 9:00:00 AM | 0.375 | 2 | 69.6 | 71.6 | 75.643 | 86.674 | 11.031 | 70 | 69.6 |  | 69.6 | 77.4079 | 0.1 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 64.1003 | 16.2796 | 387455.1756 | 32.2879 | 32.2879 | 90.7519 | 0.2 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 65.5789 | 17.7583 | 422646.5513 | 35.2205 | 35.2205 | 92.2985 | 0.3 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 67.0575 | 19.2369 | 457837.9269 | 38.1532 | 38.1532 | 93.8452 | 0.4 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 68.5361 | 20.7155 | 493029.3025 | 41.0858 | 41.0858 | 95.3918 | 0.5 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 70.0148 | 22.1941 | 528220.6781 | 44.0184 | 44.0184 | 96.9384 | 0.6 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 71.4934 | 23.6728 | 563412.0538 | 46.951 | 46.951 | 98.485 | 0.7 | 70.92 | 15.92 | 601776 | 50.148 | 50.148 | 72.972 | 25.1514 | 598603.4294 | 49.8836 | 49.8836 | 100.0316 | 0.8 | 70.48 | 15.48 | 585144 | 48.762 | 48.762 | 74.4507 | 26.63 | 633794.805 | 52.8162 | 52.8162 | 101.5782 | 0.9 | 70.04 | 15.04 | 568512 | 47.376 | 47.376 | 75.9293 | 28.1087 | 668986.1806 | 55.7488 | 55.7488 | 103.1248 | 1 | 69.6 | 14.6 | 551880 | 45.99 | 45.99 | 77.4079 | 29.5873 | 704177.5563 | 58.6815 | 58.6815 | 104.6715 | 70 | 70 | 28.7906 | 28 | 71.6
9/13/20XX 10:00:00 AM | 0.41667 | 2 | 72 | 65.5 | 70.3485 | 82.2949 | 11.9464 | 60 | 72 |  | 72 | 76.919 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.0514 | 16.2307 | 386291.6021 | 32.191 | 32.191 | 91.411 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 65.4811 | 17.6605 | 420319.4043 | 35.0266 | 35.0266 | 93.6166 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 66.9109 | 19.0902 | 454347.2064 | 37.8623 | 37.8623 | 95.8223 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 68.3406 | 20.52 | 488375.0085 | 40.6979 | 40.6979 | 98.0279 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 69.7703 | 21.9497 | 522402.8107 | 43.5336 | 43.5336 | 100.2336 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 71.2001 | 23.3794 | 556430.6128 | 46.3692 | 46.3692 | 102.4392 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 72.6298 | 24.8092 | 590458.4149 | 49.2049 | 49.2049 | 104.6449 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 74.0595 | 26.2389 | 624486.2171 | 52.0405 | 52.0405 | 106.8505 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 75.4893 | 27.6687 | 658514.0192 | 54.8762 | 54.8762 | 109.0562 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 76.919 | 29.0984 | 692541.8213 | 57.7118 | 57.7118 | 111.2618 | 70 | 65 | 29.302 | 30 | 65.5
9/13/20XX 11:00:00 AM | 0.45833 | 2 | 73.8 | 60.6 | 74.8769 | 87.6104 | 12.7335 | 60 | 73.8 |  | 73.8 | 75.6409 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 63.9236 | 16.1029 | 383249.6443 | 31.9375 | 31.9375 | 91.7245 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 65.2255 | 17.4049 | 414235.4887 | 34.5196 | 34.5196 | 94.2436 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 66.5274 | 18.7068 | 445221.333 | 37.1018 | 37.1018 | 96.7628 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 67.8293 | 20.0087 | 476207.1774 | 39.6839 | 39.6839 | 99.2819 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 69.1313 | 21.3106 | 507193.0217 | 42.2661 | 42.2661 | 101.8011 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 70.4332 | 22.6126 | 538178.8661 | 44.8482 | 44.8482 | 104.3202 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 71.7351 | 23.9145 | 569164.7104 | 47.4304 | 47.4304 | 106.8394 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 73.037 | 25.2164 | 600150.5548 | 50.0125 | 50.0125 | 109.3585 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 74.339 | 26.5183 | 631136.3991 | 52.5947 | 52.5947 | 111.8777 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 75.6409 | 27.8203 | 662122.2435 | 55.1769 | 55.1769 | 114.3969 | 75 | 60 | 29.5429 | 30 | 60.6
9/13/20XX 12:00:00 PM | 0.5 | 2 | 75.5 | 57.5 | 65.924 | 79.3806 | 13.4566 | 50 | 75.5 |  | 75.5 | 76.0165 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 63.9611 | 16.1405 | 384143.5138 | 32.012 | 32.012 | 92.3345 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 65.3006 | 17.48 | 416023.2276 | 34.6686 | 34.6686 | 95.4636 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 66.6401 | 18.8195 | 447902.9414 | 37.3252 | 37.3252 | 98.5927 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 67.9796 | 20.1589 | 479782.6552 | 39.9819 | 39.9819 | 101.7219 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 69.3191 | 21.4984 | 511662.369 | 42.6385 | 42.6385 | 104.851 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 70.6585 | 22.8379 | 543542.0828 | 45.2952 | 45.2952 | 107.9802 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 71.998 | 24.1774 | 575421.7966 | 47.9518 | 47.9518 | 111.1093 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 73.3375 | 25.5169 | 607301.5103 | 50.6085 | 50.6085 | 114.2385 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 74.677 | 26.8564 | 639181.2241 | 53.2651 | 53.2651 | 117.3676 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 76.0165 | 28.1958 | 671060.9379 | 55.9217 | 55.9217 | 120.4967 | 75 | 55 | 30.0178 | 30 | 57.5
9/13/20XX 1:00:00 PM | 0.54167 | 2 | 77 | 55 | 69.3725 | 83.5433 | 14.1708 | 50 | 77 |  | 77 | 76.4579 | 0.1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 64.0053 | 16.1846 | 385194.1597 | 32.0995 | 32.0995 | 92.8945 | 0.2 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 65.3889 | 17.5683 | 418124.5195 | 34.8437 | 34.8437 | 96.5837 | 0.3 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 66.7725 | 18.9519 | 451054.8792 | 37.5879 | 37.5879 | 100.2729 | 0.4 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 68.1561 | 20.3355 | 483985.2389 | 40.3321 | 40.3321 | 103.9621 | 0.5 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 69.5398 | 21.7191 | 516915.5986 | 43.0763 | 43.0763 | 107.6513 | 0.6 | 75.8 | 20.8 | 786240 | 65.52 | 65.52 | 70.9234 | 23.1028 | 549845.9584 | 45.8205 | 45.8205 | 111.3405 | 0.7 | 76.1 | 21.1 | 797580 | 66.465 | 66.465 | 72.307 | 24.4864 | 582776.3181 | 48.5647 | 48.5647 | 115.0297 | 0.8 | 76.4 | 21.4 | 808920 | 67.41 | 67.41 | 73.6907 | 25.87 | 615706.6778 | 51.3089 | 51.3089 | 118.7189 | 0.9 | 76.7 | 21.7 | 820260 | 68.355 | 68.355 | 75.0743 | 27.2537 | 648637.0376 | 54.0531 | 54.0531 | 122.4081 | 1 | 77 | 22 | 831600 | 69.3 | 69.3 | 76.4579 | 28.6373 | 681567.3973 | 56.7973 | 56.7973 | 126.0973 | 75 | 55 | 30.4542 | 30 | 55
9/13/20XX 2:00:00 PM | 0.58333 | 2 | 76.8 | 54.2 | 68.9041 | 82.9779 | 14.0738 | 50 | 76.8 |  | 76.8 | 74.8151 | 0.1 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 63.841 | 16.0203 | 381284.2613 | 31.7737 | 31.7737 | 92.5057 | 0.2 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.0603 | 17.2397 | 410304.7225 | 34.1921 | 34.1921 | 95.8061 | 0.3 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 66.2797 | 18.459 | 439325.1838 | 36.6104 | 36.6104 | 99.1064 | 0.4 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 67.499 | 19.6784 | 468345.645 | 39.0288 | 39.0288 | 102.4068 | 0.5 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 68.7184 | 20.8977 | 497366.1063 | 41.4472 | 41.4472 | 105.7072 | 0.6 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 69.9377 | 22.1171 | 526386.5675 | 43.8655 | 43.8655 | 109.0075 | 0.7 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 71.1571 | 23.3364 | 555407.0288 | 46.2839 | 46.2839 | 112.3079 | 0.8 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 72.3764 | 24.5558 | 584427.49 | 48.7023 | 48.7023 | 115.6083 | 0.9 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 73.5958 | 25.7751 | 613447.9513 | 51.1207 | 51.1207 | 118.9087 | 1 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 74.8151 | 26.9945 | 642468.4125 | 53.539 | 53.539 | 122.209 | 75 | 55 | 30.148 | 30 | 54.2
9/13/20XX 3:00:00 PM | 0.625 | 2 | 75.3 | 58.7 | 65.4753 | 78.8391 | 13.3637 | 50 | 75.3 |  | 75.3 | 77.1018 | 0.1 | 74.13 | 19.13 | 723114 | 60.2595 | 60.2595 | 64.0696 | 16.249 | 386726.6072 | 32.2272 | 32.2272 | 92.4867 | 0.2 | 74.26 | 19.26 | 728028 | 60.669 | 60.669 | 65.5177 | 17.697 | 421189.4144 | 35.0991 | 35.0991 | 95.7681 | 0.3 | 74.39 | 19.39 | 732942 | 61.0785 | 61.0785 | 66.9657 | 19.1451 | 455652.2216 | 37.971 | 37.971 | 99.0495 | 0.4 | 74.52 | 19.52 | 737856 | 61.488 | 61.488 | 68.4137 | 20.5931 | 490115.0288 | 40.8429 | 40.8429 | 102.3309 | 0.5 | 74.65 | 19.65 | 742770 | 61.8975 | 61.8975 | 69.8617 | 22.0411 | 524577.836 | 43.7148 | 43.7148 | 105.6123 | 0.6 | 74.78 | 19.78 | 747684 | 62.307 | 62.307 | 71.3097 | 23.4891 | 559040.6432 | 46.5867 | 46.5867 | 108.8937 | 0.7 | 74.91 | 19.91 | 752598 | 62.7165 | 62.7165 | 72.7578 | 24.9371 | 593503.4503 | 49.4586 | 49.4586 | 112.1751 | 0.8 | 75.04 | 20.04 | 757512 | 63.126 | 63.126 | 74.2058 | 26.3851 | 627966.2575 | 52.3305 | 52.3305 | 115.4565 | 0.9 | 75.17 | 20.17 | 762426 | 63.5355 | 63.5355 | 75.6538 | 27.8332 | 662429.0647 | 55.2024 | 55.2024 | 118.7379 | 1 | 75.3 | 20.3 | 767340 | 63.945 | 63.945 | 77.1018 | 29.2812 | 696891.8719 | 58.0743 | 58.0743 | 122.0193 | 75 | 60 | 30.1387 | 30 | 58.7
9/13/20XX 4:00:00 PM | 0.66667 | 2 | 73.5 | 64.1 | 74.1052 | 86.7045 | 12.5993 | 60 | 73.5 |  | 73.5 | 79.2709 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 64.2866 | 16.4659 | 391889.122 | 32.6574 | 32.6574 | 92.3499 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 65.9515 | 18.1309 | 431514.4441 | 35.9595 | 35.9595 | 95.4945 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 67.6164 | 19.7958 | 471139.7661 | 39.2616 | 39.2616 | 98.6391 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 69.2814 | 21.4607 | 510765.0882 | 42.5638 | 42.5638 | 101.7838 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 70.9463 | 23.1256 | 550390.4102 | 45.8659 | 45.8659 | 104.9284 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 72.6112 | 24.7906 | 590015.7322 | 49.168 | 49.168 | 108.073 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 74.2761 | 26.4555 | 629641.0543 | 52.4701 | 52.4701 | 111.2176 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 75.9411 | 28.1204 | 669266.3763 | 55.7722 | 55.7722 | 114.3622 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 77.606 | 29.7854 | 708891.6984 | 59.0743 | 59.0743 | 117.5068 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 79.2709 | 31.4503 | 748517.0204 | 62.3764 | 62.3764 | 120.6514 | 75 | 65 | 30.0372 | 30 | 64.1
9/13/20XX 5:00:00 PM | 0.70833 | 2 | 72.4 | 66.2 | 71.3339 | 83.4515 | 12.1177 | 60 | 72.4 |  | 72.4 | 78.8468 | 0.1 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 64.2441 | 16.4235 | 390879.7028 | 32.5733 | 32.5733 | 91.9193 | 0.2 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 65.8667 | 18.046 | 429495.6055 | 35.7913 | 35.7913 | 94.6333 | 0.3 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 67.4892 | 19.6686 | 468111.5083 | 39.0093 | 39.0093 | 97.3473 | 0.4 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 69.1117 | 21.2911 | 506727.4111 | 42.2273 | 42.2273 | 100.0613 | 0.5 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 70.7342 | 22.9136 | 545343.3138 | 45.4453 | 45.4453 | 102.7753 | 0.6 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 72.3567 | 24.5361 | 583959.2166 | 48.6633 | 48.6633 | 105.4893 | 0.7 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 73.9793 | 26.1586 | 622575.1194 | 51.8813 | 51.8813 | 108.2033 | 0.8 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 75.6018 | 27.7811 | 661191.0222 | 55.0993 | 55.0993 | 110.9173 | 0.9 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 77.2243 | 29.4037 | 699806.9249 | 58.3172 | 58.3172 | 113.6312 | 1 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 78.8468 | 31.0262 | 738422.8277 | 61.5352 | 61.5352 | 116.3452 | 70 | 65 | 29.7013 | 30 | 66.2
9/13/20XX 6:00:00 PM | 0.75 | 2 | 71 | 70.9 | 79.4639 | 91.0648 | 11.6009 | 70 | 71 |  | 71 | 80.508 | 0.1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.4103 | 16.5896 | 394833.3783 | 32.9028 | 32.9028 | 91.8078 | 0.2 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 66.1989 | 18.3783 | 437402.9566 | 36.4502 | 36.4502 | 94.4102 | 0.3 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 67.9875 | 20.1669 | 479972.5349 | 39.9977 | 39.9977 | 97.0127 | 0.4 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 69.7762 | 21.9556 | 522542.1131 | 43.5452 | 43.5452 | 99.6152 | 0.5 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 71.5648 | 23.7442 | 565111.6914 | 47.0926 | 47.0926 | 102.2176 | 0.6 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 73.3535 | 25.5328 | 607681.2697 | 50.6401 | 50.6401 | 104.8201 | 0.7 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 75.1421 | 27.3215 | 650250.848 | 54.1876 | 54.1876 | 107.4226 | 0.8 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 76.9307 | 29.1101 | 692820.4263 | 57.735 | 57.735 | 110.025 | 0.9 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 78.7194 | 30.8987 | 735390.0046 | 61.2825 | 61.2825 | 112.6275 | 1 | 71 | 16 | 604800 | 50.4 | 50.4 | 80.508 | 32.6874 | 777959.5828 | 64.83 | 64.83 | 115.23 | 70 | 70 | 29.6178 | 30 | 70.9
9/13/20XX 7:00:00 PM | 0.79167 | 2 | 70.2 | 71.7 | 77.2604 | 88.5325 | 11.2721 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/13/20XX 8:00:00 PM | 0.83333 | 2 | 69.1 | 73.8 | 74.3178 | 85.1515 | 10.8337 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/13/20XX 9:00:00 PM | 0.875 | 2 | 68.5 | 73.3 | 72.7546 | 83.3558 | 10.6012 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/13/20XX 10:00:00 PM | 0.91667 | 2 | 67.6 | 74.5 | 70.4642 | 80.7252 | 10.261 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/13/20XX 11:00:00 PM | 0.95833 | 2 | 66.8 | 74.9 | 68.4823 | 78.4493 | 9.967 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/13/20XX 12:00:00 AM | 0 | 3 | 66 | 75.3 | 66.5501 | 76.231 | 9.6809 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/14/20XX 1:00:00 AM | 0.041667 | 3 | 65.3 | 76.3 | 64.8997 | 74.3365 | 9.4368 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/14/20XX 2:00:00 AM | 0.083333 | 3 | 64.8 | 77.3 | 63.7435 | 73.0095 | 9.266 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/14/20XX 3:00:00 AM | 0.125 | 3 | 64.1 | 79.3 | 62.156 | 71.1877 | 9.0317 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/14/20XX 4:00:00 AM | 0.16667 | 3 | 64 | 78.3 | 61.9322 | 70.9309 | 8.9987 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/14/20XX 5:00:00 AM | 0.20833 | 3 | 63.8 | 77.5 | 61.4867 | 70.4198 | 8.9331 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/14/20XX 6:00:00 AM | 0.25 | 3 | 63.2 | 80.3 | 68.9065 | 77.6187 | 8.7122 | 80 | 63.2 |  | 63.2 | 69.1678 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 69.1678 | 21.3472 | 508063.1956 | 42.3386 | 42.3386 | 68.1686 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 69.1678 | 21.3472 | 508063.1956 | 42.3386 | 42.3386 | 68.1686 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 69.1678 | 21.3472 | 508063.1956 | 42.3386 | 42.3386 | 68.1686 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 69.1678 | 21.3472 | 508063.1956 | 42.3386 | 42.3386 | 68.1686 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 69.1678 | 21.3472 | 508063.1956 | 42.3386 | 42.3386 | 68.1686 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 69.1678 | 21.3472 | 508063.1956 | 42.3386 | 42.3386 | 68.1686 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 69.1678 | 21.3472 | 508063.1956 | 42.3386 | 42.3386 | 68.1686 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 69.1678 | 21.3472 | 508063.1956 | 42.3386 | 42.3386 | 68.1686 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 69.1678 | 21.3472 | 508063.1956 | 42.3386 | 42.3386 | 68.1686 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 69.1678 | 21.3472 | 508063.1956 | 42.3386 | 42.3386 | 68.1686 | 65 | 80 | 25.9399 | 26 | 80.3
9/14/20XX 7:00:00 AM | 0.29167 | 3 | 64.5 | 77.6 | 63.0587 | 72.2236 | 9.1649 | 70 | 64.5 |  | 64.5 | 70.024 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 70.024 | 22.2034 | 528440.6922 | 44.0367 | 44.0367 | 73.9617 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 70.024 | 22.2034 | 528440.6922 | 44.0367 | 44.0367 | 73.9617 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 70.024 | 22.2034 | 528440.6922 | 44.0367 | 44.0367 | 73.9617 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 70.024 | 22.2034 | 528440.6922 | 44.0367 | 44.0367 | 73.9617 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 70.024 | 22.2034 | 528440.6922 | 44.0367 | 44.0367 | 73.9617 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 70.024 | 22.2034 | 528440.6922 | 44.0367 | 44.0367 | 73.9617 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 70.024 | 22.2034 | 528440.6922 | 44.0367 | 44.0367 | 73.9617 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 70.024 | 22.2034 | 528440.6922 | 44.0367 | 44.0367 | 73.9617 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 70.024 | 22.2034 | 528440.6922 | 44.0367 | 44.0367 | 73.9617 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 70.024 | 22.2034 | 528440.6922 | 44.0367 | 44.0367 | 73.9617 | 65 | 80 | 26.391 | 26 | 77.6
9/14/20XX 8:00:00 AM | 0.33333 | 3 | 65.8 | 73.5 | 66.0748 | 75.6853 | 9.6105 | 70 | 65.8 |  | 65.8 | 69.4385 | 0.1 | 73.18 | 18.18 | 687204 | 57.267 | 57.267 | 63.3033 | 15.4827 | 368487.8473 | 30.7073 | 30.7073 | 87.9743 | 0.2 | 72.36 | 17.36 | 656208 | 54.684 | 54.684 | 63.985 | 16.1644 | 384711.8947 | 32.0593 | 32.0593 | 86.7433 | 0.3 | 71.54 | 16.54 | 625212 | 52.101 | 52.101 | 64.6667 | 16.846 | 400935.942 | 33.4113 | 33.4113 | 85.5123 | 0.4 | 70.72 | 15.72 | 594216 | 49.518 | 49.518 | 65.3484 | 17.5277 | 417159.9893 | 34.7633 | 34.7633 | 84.2813 | 0.5 | 69.9 | 14.9 | 563220 | 46.935 | 46.935 | 66.03 | 18.2094 | 433384.0367 | 36.1153 | 36.1153 | 83.0503 | 0.6 | 69.08 | 14.08 | 532224 | 44.352 | 44.352 | 66.7117 | 18.8911 | 449608.084 | 37.4673 | 37.4673 | 81.8193 | 0.7 | 68.26 | 13.26 | 501228 | 41.769 | 41.769 | 67.3934 | 19.5728 | 465832.1313 | 38.8193 | 38.8193 | 80.5883 | 0.8 | 67.44 | 12.44 | 470232 | 39.186 | 39.186 | 68.0751 | 20.2545 | 482056.1787 | 40.1713 | 40.1713 | 79.3573 | 0.9 | 66.62 | 11.62 | 439236 | 36.603 | 36.603 | 68.7568 | 20.9361 | 498280.226 | 41.5234 | 41.5234 | 78.1264 | 1 | 65.8 | 10.8 | 408240 | 34.02 | 34.02 | 69.4385 | 21.6178 | 514504.2734 | 42.8754 | 42.8754 | 76.8954 | 65 | 75 | 26.6175 | 26 | 73.5
9/14/20XX 9:00:00 AM | 0.375 | 3 | 67.6 | 70.8 | 70.4642 | 80.7252 | 10.261 | 70 | 67.6 |  | 67.6 | 71.2851 | 0.1 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 63.488 | 15.6673 | 372882.8821 | 31.0736 | 31.0736 | 88.9076 | 0.2 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 64.3543 | 16.5337 | 393501.9642 | 32.7918 | 32.7918 | 88.6098 | 0.3 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 65.2207 | 17.4 | 414121.0463 | 34.5101 | 34.5101 | 88.3121 | 0.4 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 66.087 | 18.2664 | 434740.1284 | 36.2283 | 36.2283 | 88.0143 | 0.5 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 66.9534 | 19.1327 | 455359.2105 | 37.9466 | 37.9466 | 87.7166 | 0.6 | 70.16 | 15.16 | 573048 | 47.754 | 47.754 | 67.8197 | 19.9991 | 475978.2926 | 39.6649 | 39.6649 | 87.4189 | 0.7 | 69.52 | 14.52 | 548856 | 45.738 | 45.738 | 68.6861 | 20.8654 | 496597.3747 | 41.3831 | 41.3831 | 87.1211 | 0.8 | 68.88 | 13.88 | 524664 | 43.722 | 43.722 | 69.5524 | 21.7318 | 517216.4568 | 43.1014 | 43.1014 | 86.8234 | 0.9 | 68.24 | 13.24 | 500472 | 41.706 | 41.706 | 70.4188 | 22.5981 | 537835.5389 | 44.8196 | 44.8196 | 86.5256 | 1 | 67.6 | 12.6 | 476280 | 39.69 | 39.69 | 71.2851 | 23.4645 | 558454.621 | 46.5379 | 46.5379 | 86.2279 | 70 | 70 | 27.3456 | 28 | 70.8
9/14/20XX 10:00:00 AM | 0.41667 | 3 | 70.6 | 64.3 | 66.992 | 78.3554 | 11.3635 | 60 | 70.6 |  | 70.6 | 71.8782 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 63.5473 | 15.7267 | 374294.5485 | 31.1912 | 31.1912 | 89.9702 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 64.473 | 16.6523 | 396325.2971 | 33.0271 | 33.0271 | 90.7351 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 65.3986 | 17.578 | 418356.0456 | 34.863 | 34.863 | 91.5 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 66.3243 | 18.5036 | 440386.7942 | 36.6989 | 36.6989 | 92.2649 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 67.2499 | 19.4293 | 462417.5427 | 38.5348 | 38.5348 | 93.0298 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 68.1756 | 20.355 | 484448.2912 | 40.3707 | 40.3707 | 93.7947 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 69.1013 | 21.2806 | 506479.0398 | 42.2066 | 42.2066 | 94.5596 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 70.0269 | 22.2063 | 528509.7883 | 44.0425 | 44.0425 | 95.3245 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 70.9526 | 23.132 | 550540.5368 | 45.8784 | 45.8784 | 96.0894 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 71.8782 | 24.0576 | 572571.2854 | 47.7143 | 47.7143 | 96.8543 | 70 | 65 | 28.1718 | 28 | 64.3
9/14/20XX 11:00:00 AM | 0.45833 | 3 | 73.5 | 56.8 | 61.5526 | 74.1052 | 12.5526 | 50 | 73.5 |  | 73.5 | 70.0884 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 63.3683 | 15.5477 | 370034.6537 | 30.8362 | 30.8362 | 90.5287 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.115 | 16.2943 | 387805.5074 | 32.3171 | 32.3171 | 91.8521 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 64.8617 | 17.041 | 405576.3612 | 33.798 | 33.798 | 93.1755 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 65.6083 | 17.7877 | 423347.2149 | 35.2789 | 35.2789 | 94.4989 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 66.355 | 18.5344 | 441118.0686 | 36.7598 | 36.7598 | 95.8223 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 67.1017 | 19.281 | 458888.9223 | 38.2407 | 38.2407 | 97.1457 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 67.8484 | 20.0277 | 476659.776 | 39.7216 | 39.7216 | 98.4691 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 68.595 | 20.7744 | 494430.6298 | 41.2026 | 41.2026 | 99.7926 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 69.3417 | 21.5211 | 512201.4835 | 42.6835 | 42.6835 | 101.116 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 70.0884 | 22.2677 | 529972.3372 | 44.1644 | 44.1644 | 102.4394 | 75 | 55 | 28.6011 | 28 | 56.8
9/14/20XX 12:00:00 PM | 0.5 | 3 | 75.4 | 52.8 | 65.6994 | 79.1095 | 13.4101 | 50 | 75.4 |  | 75.4 | 69.4542 | 0.1 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 63.3049 | 15.4843 | 368525.2841 | 30.7104 | 30.7104 | 91.0014 | 0.2 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 63.9881 | 16.1675 | 384786.7682 | 32.0656 | 32.0656 | 92.7976 | 0.3 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 64.6714 | 16.8508 | 401048.2523 | 33.4207 | 33.4207 | 94.5937 | 0.4 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.3547 | 17.534 | 417309.7364 | 34.7758 | 34.7758 | 96.3898 | 0.5 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 66.0379 | 18.2173 | 433571.2205 | 36.1309 | 36.1309 | 98.1859 | 0.6 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 66.7212 | 18.9005 | 449832.7046 | 37.4861 | 37.4861 | 99.9821 | 0.7 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 67.4044 | 19.5838 | 466094.1887 | 38.8412 | 38.8412 | 101.7782 | 0.8 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 68.0877 | 20.267 | 482355.6728 | 40.1963 | 40.1963 | 103.5743 | 0.9 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 68.7709 | 20.9503 | 498617.1569 | 41.5514 | 41.5514 | 105.3704 | 1 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 69.4542 | 21.6336 | 514878.641 | 42.9066 | 42.9066 | 107.1666 | 75 | 55 | 28.9663 | 28 | 52.8
9/14/20XX 1:00:00 PM | 0.54167 | 3 | 76.8 | 47.7 | 54.949 | 68.9041 | 13.9552 | 40 | 76.8 |  | 76.8 | 65.6944 | 0.1 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 62.9289 | 15.1083 | 359577.0704 | 29.9648 | 29.9648 | 90.6968 | 0.2 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 63.2362 | 15.4156 | 366890.3409 | 30.5742 | 30.5742 | 92.1882 | 0.3 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 63.5435 | 15.7228 | 374203.6113 | 31.1836 | 31.1836 | 93.6796 | 0.4 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 63.8508 | 16.0301 | 381516.8817 | 31.7931 | 31.7931 | 95.1711 | 0.5 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 64.158 | 16.3374 | 388830.1522 | 32.4025 | 32.4025 | 96.6625 | 0.6 | 75.68 | 20.68 | 781704 | 65.142 | 65.142 | 64.4653 | 16.6447 | 396143.4226 | 33.012 | 33.012 | 98.154 | 0.7 | 75.96 | 20.96 | 792288 | 66.024 | 66.024 | 64.7726 | 16.952 | 403456.693 | 33.6214 | 33.6214 | 99.6454 | 0.8 | 76.24 | 21.24 | 802872 | 66.906 | 66.906 | 65.0799 | 17.2592 | 410769.9634 | 34.2308 | 34.2308 | 101.1368 | 0.9 | 76.52 | 21.52 | 813456 | 67.788 | 67.788 | 65.3872 | 17.5665 | 418083.2339 | 34.8403 | 34.8403 | 102.6283 | 1 | 76.8 | 21.8 | 824040 | 68.67 | 68.67 | 65.6944 | 17.8738 | 425396.5043 | 35.4497 | 35.4497 | 104.1197 | 75 | 50 | 28.7197 | 28 | 47.7
9/14/20XX 2:00:00 PM | 0.58333 | 3 | 76.2 | 48.2 | 53.8472 | 67.5149 | 13.6677 | 40 | 76.2 |  | 76.2 | 65.0547 | 0.1 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 62.8649 | 15.0443 | 358054.5108 | 29.8379 | 29.8379 | 90.3809 | 0.2 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 63.1082 | 15.2876 | 363845.2216 | 30.3204 | 30.3204 | 91.5564 | 0.3 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 63.3516 | 15.5309 | 369635.9324 | 30.803 | 30.803 | 92.732 | 0.4 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 63.5949 | 15.7742 | 375426.6433 | 31.2856 | 31.2856 | 93.9076 | 0.5 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 63.8382 | 16.0175 | 381217.3541 | 31.7681 | 31.7681 | 95.0831 | 0.6 | 75.32 | 20.32 | 768096 | 64.008 | 64.008 | 64.0815 | 16.2608 | 387008.0649 | 32.2507 | 32.2507 | 96.2587 | 0.7 | 75.54 | 20.54 | 776412 | 64.701 | 64.701 | 64.3248 | 16.5042 | 392798.7757 | 32.7332 | 32.7332 | 97.4342 | 0.8 | 75.76 | 20.76 | 784728 | 65.394 | 65.394 | 64.5681 | 16.7475 | 398589.4865 | 33.2158 | 33.2158 | 98.6098 | 0.9 | 75.98 | 20.98 | 793044 | 66.087 | 66.087 | 64.8114 | 16.9908 | 404380.1973 | 33.6983 | 33.6983 | 99.7853 | 1 | 76.2 | 21.2 | 801360 | 66.78 | 66.78 | 65.0547 | 17.2341 | 410170.9081 | 34.1809 | 34.1809 | 100.9609 | 75 | 50 | 28.473 | 28 | 48.2
9/14/20XX 3:00:00 PM | 0.625 | 3 | 75.9 | 49.9 | 53.3033 | 66.8292 | 13.5259 | 40 | 75.9 |  | 75.9 | 66.6939 | 0.1 | 74.19 | 19.19 | 725382 | 60.4485 | 60.4485 | 63.0289 | 15.2082 | 361955.8159 | 30.163 | 30.163 | 90.6115 | 0.2 | 74.38 | 19.38 | 732564 | 61.047 | 61.047 | 63.4361 | 15.6155 | 371647.8318 | 30.9707 | 30.9707 | 92.0177 | 0.3 | 74.57 | 19.57 | 739746 | 61.6455 | 61.6455 | 63.8433 | 16.0227 | 381339.8477 | 31.7783 | 31.7783 | 93.4238 | 0.4 | 74.76 | 19.76 | 746928 | 62.244 | 62.244 | 64.2505 | 16.4299 | 391031.8636 | 32.586 | 32.586 | 94.83 | 0.5 | 74.95 | 19.95 | 754110 | 62.8425 | 62.8425 | 64.6578 | 16.8371 | 400723.8795 | 33.3937 | 33.3937 | 96.2362 | 0.6 | 75.14 | 20.14 | 761292 | 63.441 | 63.441 | 65.065 | 17.2444 | 410415.8953 | 34.2013 | 34.2013 | 97.6423 | 0.7 | 75.33 | 20.33 | 768474 | 64.0395 | 64.0395 | 65.4722 | 17.6516 | 420107.9112 | 35.009 | 35.009 | 99.0485 | 0.8 | 75.52 | 20.52 | 775656 | 64.638 | 64.638 | 65.8795 | 18.0588 | 429799.9271 | 35.8167 | 35.8167 | 100.4547 | 0.9 | 75.71 | 20.71 | 782838 | 65.2365 | 65.2365 | 66.2867 | 18.466 | 439491.943 | 36.6243 | 36.6243 | 101.8608 | 1 | 75.9 | 20.9 | 790020 | 65.835 | 65.835 | 66.6939 | 18.8733 | 449183.9589 | 37.432 | 37.432 | 103.267 | 75 | 50 | 28.6564 | 28 | 49.9
9/14/20XX 4:00:00 PM | 0.66667 | 3 | 74.5 | 55.2 | 63.7064 | 76.7042 | 12.9978 | 50 | 74.5 |  | 74.5 | 70.4653 | 0.1 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 63.406 | 15.5854 | 370931.7323 | 30.911 | 30.911 | 90.9185 | 0.2 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 64.1904 | 16.3697 | 389599.6645 | 32.4666 | 32.4666 | 92.6316 | 0.3 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 64.9747 | 17.1541 | 408267.5968 | 34.0223 | 34.0223 | 94.3448 | 0.4 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 65.7591 | 17.9385 | 426935.529 | 35.578 | 35.578 | 96.058 | 0.5 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 66.5435 | 18.7228 | 445603.4613 | 37.1336 | 37.1336 | 97.7711 | 0.6 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 67.3278 | 19.5072 | 464271.3936 | 38.6893 | 38.6893 | 99.4843 | 0.7 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 68.1122 | 20.2916 | 482939.3258 | 40.2449 | 40.2449 | 101.1974 | 0.8 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 68.8966 | 21.0759 | 501607.2581 | 41.8006 | 41.8006 | 102.9106 | 0.9 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 69.6809 | 21.8603 | 520275.1904 | 43.3563 | 43.3563 | 104.6238 | 1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 70.4653 | 22.6447 | 538943.1226 | 44.9119 | 44.9119 | 106.3369 | 75 | 55 | 28.9045 | 28 | 55.2
9/14/20XX 5:00:00 PM | 0.70833 | 3 | 72.5 | 58.6 | 59.4614 | 71.5821 | 12.1207 | 50 | 72.5 |  | 72.5 | 69.8852 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 63.348 | 15.5274 | 369550.9863 | 30.7959 | 30.7959 | 90.1734 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.0743 | 16.2537 | 386838.1727 | 32.2365 | 32.2365 | 91.1415 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 64.8007 | 16.9801 | 404125.359 | 33.6771 | 33.6771 | 92.1096 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 65.527 | 17.7064 | 421412.5453 | 35.1177 | 35.1177 | 93.0777 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 66.2534 | 18.4328 | 438699.7317 | 36.5583 | 36.5583 | 94.0458 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 66.9797 | 19.1591 | 455986.918 | 37.9989 | 37.9989 | 95.0139 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 67.7061 | 19.8855 | 473274.1043 | 39.4395 | 39.4395 | 95.982 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 68.4325 | 20.6118 | 490561.2907 | 40.8801 | 40.8801 | 96.9501 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 69.1588 | 21.3382 | 507848.477 | 42.3207 | 42.3207 | 97.9182 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 69.8852 | 22.0645 | 525135.6633 | 43.7613 | 43.7613 | 98.8863 | 70 | 60 | 28.3249 | 28 | 58.6
9/14/20XX 6:00:00 PM | 0.75 | 3 | 71.5 | 60.2 | 69.1333 | 80.8687 | 11.7354 | 60 | 71.5 |  | 71.5 | 69.3681 | 0.1 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 63.2963 | 15.4756 | 368320.2751 | 30.6934 | 30.6934 | 89.7559 | 0.2 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 63.9709 | 16.1503 | 384376.7503 | 32.0314 | 32.0314 | 90.3064 | 0.3 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 64.6456 | 16.8249 | 400433.2254 | 33.3694 | 33.3694 | 90.8569 | 0.4 | 73 | 18 | 680400 | 56.7 | 56.7 | 65.3202 | 17.4996 | 416489.7006 | 34.7075 | 34.7075 | 91.4075 | 0.5 | 72.75 | 17.75 | 670950 | 55.9125 | 55.9125 | 65.9948 | 18.1742 | 432546.1757 | 36.0455 | 36.0455 | 91.958 | 0.6 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 66.6695 | 18.8489 | 448602.6509 | 37.3836 | 37.3836 | 92.5086 | 0.7 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 67.3441 | 19.5235 | 464659.126 | 38.7216 | 38.7216 | 93.0591 | 0.8 | 72 | 17 | 642600 | 53.55 | 53.55 | 68.0188 | 20.1981 | 480715.6012 | 40.0596 | 40.0596 | 93.6096 | 0.9 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 68.6934 | 20.8728 | 496772.0763 | 41.3977 | 41.3977 | 94.1602 | 1 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 69.3681 | 21.5474 | 512828.5515 | 42.7357 | 42.7357 | 94.7107 | 70 | 60 | 27.9996 | 28 | 60.2
9/14/20XX 7:00:00 PM | 0.79167 | 3 | 70.5 | 61.1 | 66.7576 | 78.0804 | 11.3228 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/14/20XX 8:00:00 PM | 0.83333 | 3 | 70.1 | 61.8 | 65.8275 | 76.9888 | 11.1613 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/14/20XX 9:00:00 PM | 0.875 | 3 | 69.3 | 62.7 | 64.0011 | 74.8454 | 10.8443 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/14/20XX 10:00:00 PM | 0.91667 | 3 | 68.4 | 64.4 | 61.9998 | 72.4969 | 10.4971 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/14/20XX 11:00:00 PM | 0.95833 | 3 | 67.3 | 65.2 | 59.6291 | 69.7151 | 10.086 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/14/20XX 12:00:00 AM | 0 | 4 | 66.3 | 66.2 | 57.5442 | 67.2689 | 9.7247 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/15/20XX 1:00:00 AM | 0.041667 | 4 | 65.7 | 67.4 | 56.3248 | 65.8382 | 9.5135 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/15/20XX 2:00:00 AM | 0.083333 | 4 | 64.8 | 70.3 | 63.7435 | 73.0095 | 9.266 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/15/20XX 3:00:00 AM | 0.125 | 4 | 64 | 70.4 | 61.9322 | 70.9309 | 8.9987 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/15/20XX 4:00:00 AM | 0.16667 | 4 | 63.1 | 71.6 | 59.9503 | 68.6572 | 8.7068 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/15/20XX 5:00:00 AM | 0.20833 | 4 | 62.6 | 72.2 | 58.8745 | 67.423 | 8.5486 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/15/20XX 6:00:00 AM | 0.25 | 4 | 62.1 | 72 | 57.8163 | 66.2093 | 8.393 | 70 | 62.1 |  | 62.1 | 59.4949 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 59.4949 | 11.6743 | 277847.6316 | 23.154 | 23.154 | 45.519 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 59.4949 | 11.6743 | 277847.6316 | 23.154 | 23.154 | 45.519 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 59.4949 | 11.6743 | 277847.6316 | 23.154 | 23.154 | 45.519 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 59.4949 | 11.6743 | 277847.6316 | 23.154 | 23.154 | 45.519 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 59.4949 | 11.6743 | 277847.6316 | 23.154 | 23.154 | 45.519 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 59.4949 | 11.6743 | 277847.6316 | 23.154 | 23.154 | 45.519 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 59.4949 | 11.6743 | 277847.6316 | 23.154 | 23.154 | 45.519 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 59.4949 | 11.6743 | 277847.6316 | 23.154 | 23.154 | 45.519 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 59.4949 | 11.6743 | 277847.6316 | 23.154 | 23.154 | 45.519 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 59.4949 | 11.6743 | 277847.6316 | 23.154 | 23.154 | 45.519 | 60 | 70 | 24.1653 | 24 | 72
9/15/20XX 7:00:00 AM | 0.29167 | 4 | 62.5 | 71.1 | 58.6614 | 67.1787 | 8.5172 | 70 | 62.5 |  | 62.5 | 59.5983 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 59.5983 | 11.7777 | 280309.0752 | 23.3591 | 23.3591 | 46.9841 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 59.5983 | 11.7777 | 280309.0752 | 23.3591 | 23.3591 | 46.9841 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 59.5983 | 11.7777 | 280309.0752 | 23.3591 | 23.3591 | 46.9841 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 59.5983 | 11.7777 | 280309.0752 | 23.3591 | 23.3591 | 46.9841 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 59.5983 | 11.7777 | 280309.0752 | 23.3591 | 23.3591 | 46.9841 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 59.5983 | 11.7777 | 280309.0752 | 23.3591 | 23.3591 | 46.9841 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 59.5983 | 11.7777 | 280309.0752 | 23.3591 | 23.3591 | 46.9841 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 59.5983 | 11.7777 | 280309.0752 | 23.3591 | 23.3591 | 46.9841 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 59.5983 | 11.7777 | 280309.0752 | 23.3591 | 23.3591 | 46.9841 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 59.5983 | 11.7777 | 280309.0752 | 23.3591 | 23.3591 | 46.9841 | 60 | 70 | 24.2789 | 24 | 71.1
9/15/20XX 8:00:00 AM | 0.33333 | 4 | 64.8 | 66.1 | 54.5392 | 63.7435 | 9.2043 | 60 | 64.8 |  | 64.8 | 60.1538 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 60.1538 | 12.3332 | 293529.5888 | 24.4608 | 24.4608 | 55.3308 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 60.1538 | 12.3332 | 293529.5888 | 24.4608 | 24.4608 | 55.3308 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 60.1538 | 12.3332 | 293529.5888 | 24.4608 | 24.4608 | 55.3308 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 60.1538 | 12.3332 | 293529.5888 | 24.4608 | 24.4608 | 55.3308 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 60.1538 | 12.3332 | 293529.5888 | 24.4608 | 24.4608 | 55.3308 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 60.1538 | 12.3332 | 293529.5888 | 24.4608 | 24.4608 | 55.3308 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 60.1538 | 12.3332 | 293529.5888 | 24.4608 | 24.4608 | 55.3308 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 60.1538 | 12.3332 | 293529.5888 | 24.4608 | 24.4608 | 55.3308 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 60.1538 | 12.3332 | 293529.5888 | 24.4608 | 24.4608 | 55.3308 | 1 | 64.8 | 9.8 | 370440 | 30.87 | 30.87 | 60.1538 | 12.3332 | 293529.5888 | 24.4608 | 24.4608 | 55.3308 | 65 | 65 | 24.9262 | 24 | 66.1
9/15/20XX 9:00:00 AM | 0.375 | 4 | 67.1 | 59.6 | 49.1993 | 59.2068 | 10.0075 | 50 | 67.1 |  | 67.1 | 58.8065 | 0.1 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 62.2401 | 14.4195 | 343183.7625 | 28.5986 | 28.5986 | 86.2751 | 0.2 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 61.8586 | 14.038 | 334103.7249 | 27.842 | 27.842 | 83.345 | 0.3 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 61.4771 | 13.6565 | 325023.6874 | 27.0853 | 27.0853 | 80.4148 | 0.4 | 71.24 | 16.24 | 613872 | 51.156 | 51.156 | 61.0956 | 13.2749 | 315943.6499 | 26.3286 | 26.3286 | 77.4846 | 0.5 | 70.55 | 15.55 | 587790 | 48.9825 | 48.9825 | 60.7141 | 12.8934 | 306863.6123 | 25.572 | 25.572 | 74.5545 | 0.6 | 69.86 | 14.86 | 561708 | 46.809 | 46.809 | 60.3325 | 12.5119 | 297783.5748 | 24.8153 | 24.8153 | 71.6243 | 0.7 | 69.17 | 14.17 | 535626 | 44.6355 | 44.6355 | 59.951 | 12.1304 | 288703.5372 | 24.0586 | 24.0586 | 68.6941 | 0.8 | 68.48 | 13.48 | 509544 | 42.462 | 42.462 | 59.5695 | 11.7489 | 279623.4997 | 23.302 | 23.302 | 65.764 | 0.9 | 67.79 | 12.79 | 483462 | 40.2885 | 40.2885 | 59.188 | 11.3674 | 270543.4622 | 22.5453 | 22.5453 | 62.8338 | 1 | 67.1 | 12.1 | 457380 | 38.115 | 38.115 | 58.8065 | 10.9859 | 261463.4246 | 21.7886 | 21.7886 | 59.9036 | 65 | 60 | 25.2768 | 26 | 59.6
9/15/20XX 10:00:00 AM | 0.41667 | 4 | 69.3 | 54.7 | 53.176 | 64.0011 | 10.8251 | 50 | 69.3 |  | 69.3 | 58.2638 | 0.1 | 73.53 | 18.53 | 700434 | 58.3695 | 58.3695 | 62.1858 | 14.3652 | 341892.1478 | 28.491 | 28.491 | 86.8605 | 0.2 | 73.06 | 18.06 | 682668 | 56.889 | 56.889 | 61.7501 | 13.9294 | 331520.4955 | 27.6267 | 27.6267 | 84.5157 | 0.3 | 72.59 | 17.59 | 664902 | 55.4085 | 55.4085 | 61.3143 | 13.4936 | 321148.8433 | 26.7624 | 26.7624 | 82.1709 | 0.4 | 72.12 | 17.12 | 647136 | 53.928 | 53.928 | 60.8785 | 13.0579 | 310777.1911 | 25.8981 | 25.8981 | 79.8261 | 0.5 | 71.65 | 16.65 | 629370 | 52.4475 | 52.4475 | 60.4427 | 12.6221 | 300405.5389 | 25.0338 | 25.0338 | 77.4813 | 0.6 | 71.18 | 16.18 | 611604 | 50.967 | 50.967 | 60.0069 | 12.1863 | 290033.8866 | 24.1695 | 24.1695 | 75.1365 | 0.7 | 70.71 | 15.71 | 593838 | 49.4865 | 49.4865 | 59.5711 | 11.7505 | 279662.2344 | 23.3052 | 23.3052 | 72.7917 | 0.8 | 70.24 | 15.24 | 576072 | 48.006 | 48.006 | 59.1354 | 11.3147 | 269290.5822 | 22.4409 | 22.4409 | 70.4469 | 0.9 | 69.77 | 14.77 | 558306 | 46.5255 | 46.5255 | 58.6996 | 10.8789 | 258918.9299 | 21.5766 | 21.5766 | 68.1021 | 1 | 69.3 | 14.3 | 540540 | 45.045 | 45.045 | 58.2638 | 10.4432 | 248547.2777 | 20.7123 | 20.7123 | 65.7573 | 70 | 55 | 25.7283 | 26 | 54.7
9/15/20XX 11:00:00 AM | 0.45833 | 4 | 71.9 | 49.5 | 46.4833 | 58.2361 | 11.7528 | 40 | 71.9 |  | 71.9 | 57.6485 | 0.1 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 62.1243 | 14.3037 | 340427.7275 | 28.369 | 28.369 | 87.5575 | 0.2 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 61.627 | 13.8064 | 328591.6551 | 27.3826 | 27.3826 | 85.9096 | 0.3 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 61.1297 | 13.3091 | 316755.5826 | 26.3963 | 26.3963 | 84.2618 | 0.4 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 60.6324 | 12.8117 | 304919.5101 | 25.41 | 25.41 | 82.614 | 0.5 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 60.1351 | 12.3144 | 293083.4376 | 24.4236 | 24.4236 | 80.9661 | 0.6 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 59.6377 | 11.8171 | 281247.3652 | 23.4373 | 23.4373 | 79.3183 | 0.7 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 59.1404 | 11.3198 | 269411.2927 | 22.4509 | 22.4509 | 77.6704 | 0.8 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 58.6431 | 10.8225 | 257575.2202 | 21.4646 | 21.4646 | 76.0226 | 0.9 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 58.1458 | 10.3252 | 245739.1477 | 20.4783 | 20.4783 | 74.3748 | 1 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 57.6485 | 9.8279 | 233903.0753 | 19.4919 | 19.4919 | 72.7269 | 70 | 50 | 26.2658 | 26 | 49.5
9/15/20XX 12:00:00 PM | 0.5 | 4 | 73.1 | 49.4 | 48.4465 | 60.7087 | 12.2622 | 40 | 73.1 |  | 73.1 | 59.9729 | 0.1 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 62.3568 | 14.5361 | 345959.9027 | 28.83 | 28.83 | 88.3965 | 0.2 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 62.0919 | 14.2713 | 339656.0054 | 28.3047 | 28.3047 | 87.5877 | 0.3 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 61.827 | 14.0064 | 333352.1081 | 27.7793 | 27.7793 | 86.7788 | 0.4 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 61.5622 | 13.7415 | 327048.2109 | 27.254 | 27.254 | 85.97 | 0.5 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 61.2973 | 13.4767 | 320744.3136 | 26.7287 | 26.7287 | 85.1612 | 0.6 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 61.0324 | 13.2118 | 314440.4163 | 26.2034 | 26.2034 | 84.3524 | 0.7 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 60.7675 | 12.9469 | 308136.519 | 25.678 | 25.678 | 83.5435 | 0.8 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 60.5027 | 12.682 | 301832.6217 | 25.1527 | 25.1527 | 82.7347 | 0.9 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 60.2378 | 12.4172 | 295528.7244 | 24.6274 | 24.6274 | 81.9259 | 1 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 59.9729 | 12.1523 | 289224.8272 | 24.1021 | 24.1021 | 81.1171 | 75 | 50 | 26.9216 | 26 | 49.4
9/15/20XX 1:00:00 PM | 0.54167 | 4 | 73.5 | 49.6 | 49.1164 | 61.5526 | 12.4362 | 40 | 73.5 |  | 73.5 | 61.0552 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 62.465 | 14.6444 | 348535.6089 | 29.0446 | 29.0446 | 88.7371 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 62.3083 | 14.4877 | 344807.4177 | 28.734 | 28.734 | 88.269 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 62.1517 | 14.3311 | 341079.2266 | 28.4233 | 28.4233 | 87.8008 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 61.995 | 14.1744 | 337351.0354 | 28.1126 | 28.1126 | 87.3326 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 61.8384 | 14.0178 | 333622.8443 | 27.8019 | 27.8019 | 86.8644 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 61.6818 | 13.8611 | 329894.6531 | 27.4912 | 27.4912 | 86.3962 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 61.5251 | 13.7045 | 326166.462 | 27.1805 | 27.1805 | 85.928 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 61.3685 | 13.5478 | 322438.2708 | 26.8699 | 26.8699 | 85.4599 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 61.2118 | 13.3912 | 318710.0797 | 26.5592 | 26.5592 | 84.9917 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 61.0552 | 13.2345 | 314981.8885 | 26.2485 | 26.2485 | 84.5235 | 75 | 50 | 27.1884 | 28 | 49.6
9/15/20XX 2:00:00 PM | 0.58333 | 4 | 74.2 | 47.1 | 50.3078 | 63.0537 | 12.7459 | 40 | 74.2 |  | 74.2 | 59.3574 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 62.2952 | 14.4746 | 344494.8126 | 28.7079 | 28.7079 | 88.6209 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 61.9688 | 14.1481 | 336725.8253 | 28.0605 | 28.0605 | 88.0365 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 61.6423 | 13.8217 | 328956.8379 | 27.4131 | 27.4131 | 87.4521 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 61.3159 | 13.4953 | 321187.8506 | 26.7657 | 26.7657 | 86.8677 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 60.9895 | 13.1689 | 313418.8632 | 26.1182 | 26.1182 | 86.2832 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 60.6631 | 12.8424 | 305649.8758 | 25.4708 | 25.4708 | 85.6988 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 60.3366 | 12.516 | 297880.8885 | 24.8234 | 24.8234 | 85.1144 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 60.0102 | 12.1896 | 290111.9011 | 24.176 | 24.176 | 84.53 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 59.6838 | 11.8631 | 282342.9138 | 23.5286 | 23.5286 | 83.9456 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 59.3574 | 11.5367 | 274573.9264 | 22.8812 | 22.8812 | 83.3612 | 75 | 45 | 27.0935 | 28 | 47.1
9/15/20XX 3:00:00 PM | 0.625 | 4 | 73.9 | 48.3 | 49.7942 | 62.4066 | 12.6123 | 40 | 73.9 |  | 73.9 | 60.2625 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 62.3857 | 14.5651 | 346649.0022 | 28.8874 | 28.8874 | 88.7059 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 62.1498 | 14.3292 | 341034.2045 | 28.4195 | 28.4195 | 88.2065 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 61.9139 | 14.0933 | 335419.4067 | 27.9516 | 27.9516 | 87.7071 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 61.678 | 13.8573 | 329804.609 | 27.4837 | 27.4837 | 87.2077 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 61.4421 | 13.6214 | 324189.8112 | 27.0158 | 27.0158 | 86.7083 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 61.2061 | 13.3855 | 318575.0134 | 26.5479 | 26.5479 | 86.2089 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 60.9702 | 13.1496 | 312960.2157 | 26.08 | 26.08 | 85.7095 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 60.7343 | 12.9137 | 307345.4179 | 25.6121 | 25.6121 | 85.2101 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 60.4984 | 12.6778 | 301730.6201 | 25.1442 | 25.1442 | 84.7107 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 60.2625 | 12.4418 | 296115.8224 | 24.6763 | 24.6763 | 84.2113 | 75 | 50 | 27.162 | 28 | 48.3
9/15/20XX 4:00:00 PM | 0.66667 | 4 | 73 | 49.6 | 48.2802 | 60.4992 | 12.219 | 40 | 73 |  | 73 | 60.0105 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 62.3605 | 14.5399 | 346049.2448 | 28.8374 | 28.8374 | 88.3724 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 62.0994 | 14.2788 | 339834.6897 | 28.3196 | 28.3196 | 87.5396 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 61.8383 | 14.0177 | 333620.1345 | 27.8017 | 27.8017 | 86.7067 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 61.5772 | 13.7565 | 327405.5793 | 27.2838 | 27.2838 | 85.8738 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 61.3161 | 13.4954 | 321191.0242 | 26.7659 | 26.7659 | 85.0409 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 61.0549 | 13.2343 | 314976.469 | 26.248 | 26.248 | 84.208 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 60.7938 | 12.9732 | 308761.9139 | 25.7302 | 25.7302 | 83.3752 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 60.5327 | 12.7121 | 302547.3587 | 25.2123 | 25.2123 | 82.5423 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 60.2716 | 12.451 | 296332.8035 | 24.6944 | 24.6944 | 81.7094 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 60.0105 | 12.1898 | 290118.2484 | 24.1765 | 24.1765 | 80.8765 | 75 | 50 | 26.9031 | 26 | 49.6
9/15/20XX 5:00:00 PM | 0.70833 | 4 | 71.4 | 51.1 | 57.2318 | 68.8925 | 11.6607 | 50 | 71.4 |  | 71.4 | 58.5145 | 0.1 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 62.2109 | 14.3903 | 342488.8092 | 28.5407 | 28.5407 | 87.5717 | 0.2 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 61.8002 | 13.9796 | 332713.8184 | 27.7262 | 27.7262 | 85.9382 | 0.3 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 61.3895 | 13.5689 | 322938.8276 | 26.9116 | 26.9116 | 84.3046 | 0.4 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 60.9788 | 13.1581 | 313163.8367 | 26.097 | 26.097 | 82.671 | 0.5 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 60.5681 | 12.7474 | 303388.8459 | 25.2824 | 25.2824 | 81.0374 | 0.6 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 60.1573 | 12.3367 | 293613.8551 | 24.4678 | 24.4678 | 79.4038 | 0.7 | 72.18 | 17.18 | 649404 | 54.117 | 54.117 | 59.7466 | 11.926 | 283838.8643 | 23.6532 | 23.6532 | 77.7702 | 0.8 | 71.92 | 16.92 | 639576 | 53.298 | 53.298 | 59.3359 | 11.5153 | 274063.8735 | 22.8387 | 22.8387 | 76.1367 | 0.9 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 58.9252 | 11.1046 | 264288.8827 | 22.0241 | 22.0241 | 74.5031 | 1 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 58.5145 | 10.6939 | 254513.8919 | 21.2095 | 21.2095 | 72.8695 | 70 | 50 | 26.2793 | 26 | 51.1
9/15/20XX 6:00:00 PM | 0.75 | 4 | 69.7 | 54.2 | 53.9286 | 64.9086 | 10.98 | 50 | 69.7 |  | 69.7 | 58.5402 | 0.1 | 73.57 | 18.57 | 701946 | 58.4955 | 58.4955 | 62.2135 | 14.3929 | 342550.0594 | 28.5458 | 28.5458 | 87.0413 | 0.2 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 61.8054 | 13.9847 | 332836.3189 | 27.7364 | 27.7364 | 84.8774 | 0.3 | 72.71 | 17.71 | 669438 | 55.7865 | 55.7865 | 61.3972 | 13.5766 | 323122.5783 | 26.9269 | 26.9269 | 82.7134 | 0.4 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 60.9891 | 13.1684 | 313408.8378 | 26.1174 | 26.1174 | 80.5494 | 0.5 | 71.85 | 16.85 | 636930 | 53.0775 | 53.0775 | 60.5809 | 12.7603 | 303695.0972 | 25.3079 | 25.3079 | 78.3854 | 0.6 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 60.1728 | 12.3522 | 293981.3567 | 24.4984 | 24.4984 | 76.2214 | 0.7 | 70.99 | 15.99 | 604422 | 50.3685 | 50.3685 | 59.7646 | 11.944 | 284267.6161 | 23.689 | 23.689 | 74.0575 | 0.8 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 59.3565 | 11.5359 | 274553.8756 | 22.8795 | 22.8795 | 71.8935 | 0.9 | 70.13 | 15.13 | 571914 | 47.6595 | 47.6595 | 58.9484 | 11.1277 | 264840.135 | 22.07 | 22.07 | 69.7295 | 1 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 58.5402 | 10.7196 | 255126.3944 | 21.2605 | 21.2605 | 67.5655 | 70 | 55 | 25.869 | 26 | 54.2
9/15/20XX 7:00:00 PM | 0.79167 | 4 | 68.3 | 58.5 | 51.3346 | 61.7809 | 10.4463 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/15/20XX 8:00:00 PM | 0.83333 | 4 | 67.6 | 58.8 | 50.0793 | 60.2675 | 10.1882 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/15/20XX 9:00:00 PM | 0.875 | 4 | 67.2 | 59.8 | 49.3742 | 59.4176 | 10.0434 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/15/20XX 10:00:00 PM | 0.91667 | 4 | 66.4 | 61 | 57.7497 | 67.51 | 9.7603 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/15/20XX 11:00:00 PM | 0.95833 | 4 | 65.2 | 65.6 | 55.3264 | 64.667 | 9.3406 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/15/20XX 12:00:00 AM | 0 | 5 | 64.9 | 66 | 54.735 | 63.9732 | 9.2382 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/16/20XX 1:00:00 AM | 0.041667 | 5 | 64.3 | 67.1 | 53.5694 | 62.6059 | 9.0365 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/16/20XX 2:00:00 AM | 0.083333 | 5 | 63.3 | 69.8 | 51.6767 | 60.3857 | 8.709 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/16/20XX 3:00:00 AM | 0.125 | 5 | 62.9 | 71.3 | 59.5179 | 68.161 | 8.6432 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/16/20XX 4:00:00 AM | 0.16667 | 5 | 62.4 | 72.6 | 58.4491 | 66.9351 | 8.486 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/16/20XX 5:00:00 AM | 0.20833 | 5 | 62 | 73.8 | 57.6068 | 65.969 | 8.3623 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/16/20XX 6:00:00 AM | 0.25 | 5 | 62.1 | 75 | 57.8163 | 66.2093 | 8.393 | 70 | 62.1 |  | 62.1 | 62.0128 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 62.0128 | 14.1922 | 337773.9362 | 28.1478 | 28.1478 | 50.5128 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 62.0128 | 14.1922 | 337773.9362 | 28.1478 | 28.1478 | 50.5128 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 62.0128 | 14.1922 | 337773.9362 | 28.1478 | 28.1478 | 50.5128 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 62.0128 | 14.1922 | 337773.9362 | 28.1478 | 28.1478 | 50.5128 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 62.0128 | 14.1922 | 337773.9362 | 28.1478 | 28.1478 | 50.5128 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 62.0128 | 14.1922 | 337773.9362 | 28.1478 | 28.1478 | 50.5128 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 62.0128 | 14.1922 | 337773.9362 | 28.1478 | 28.1478 | 50.5128 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 62.0128 | 14.1922 | 337773.9362 | 28.1478 | 28.1478 | 50.5128 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 62.0128 | 14.1922 | 337773.9362 | 28.1478 | 28.1478 | 50.5128 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 62.0128 | 14.1922 | 337773.9362 | 28.1478 | 28.1478 | 50.5128 | 60 | 75 | 24.5573 | 24 | 75
9/16/20XX 7:00:00 AM | 0.29167 | 5 | 63.2 | 75 | 60.1677 | 68.9065 | 8.7388 | 70 | 63.2 |  | 63.2 | 64.5371 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 64.5371 | 16.7164 | 397850.9513 | 33.1542 | 33.1542 | 58.9842 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 64.5371 | 16.7164 | 397850.9513 | 33.1542 | 33.1542 | 58.9842 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 64.5371 | 16.7164 | 397850.9513 | 33.1542 | 33.1542 | 58.9842 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 64.5371 | 16.7164 | 397850.9513 | 33.1542 | 33.1542 | 58.9842 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 64.5371 | 16.7164 | 397850.9513 | 33.1542 | 33.1542 | 58.9842 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 64.5371 | 16.7164 | 397850.9513 | 33.1542 | 33.1542 | 58.9842 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 64.5371 | 16.7164 | 397850.9513 | 33.1542 | 33.1542 | 58.9842 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 64.5371 | 16.7164 | 397850.9513 | 33.1542 | 33.1542 | 58.9842 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 64.5371 | 16.7164 | 397850.9513 | 33.1542 | 33.1542 | 58.9842 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 64.5371 | 16.7164 | 397850.9513 | 33.1542 | 33.1542 | 58.9842 | 65 | 75 | 25.2187 | 26 | 75
9/16/20XX 8:00:00 AM | 0.33333 | 5 | 64.4 | 71.3 | 62.8319 | 71.9634 | 9.1314 | 70 | 64.4 |  | 64.4 | 64.019 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 64.019 | 16.1984 | 385521.3117 | 32.1268 | 32.1268 | 61.7368 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 64.019 | 16.1984 | 385521.3117 | 32.1268 | 32.1268 | 61.7368 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 64.019 | 16.1984 | 385521.3117 | 32.1268 | 32.1268 | 61.7368 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 64.019 | 16.1984 | 385521.3117 | 32.1268 | 32.1268 | 61.7368 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 64.019 | 16.1984 | 385521.3117 | 32.1268 | 32.1268 | 61.7368 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 64.019 | 16.1984 | 385521.3117 | 32.1268 | 32.1268 | 61.7368 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 64.019 | 16.1984 | 385521.3117 | 32.1268 | 32.1268 | 61.7368 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 64.019 | 16.1984 | 385521.3117 | 32.1268 | 32.1268 | 61.7368 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 64.019 | 16.1984 | 385521.3117 | 32.1268 | 32.1268 | 61.7368 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 64.019 | 16.1984 | 385521.3117 | 32.1268 | 32.1268 | 61.7368 | 65 | 70 | 25.4309 | 26 | 71.3
9/16/20XX 9:00:00 AM | 0.375 | 5 | 66.3 | 67.2 | 57.5442 | 67.2689 | 9.7247 | 60 | 66.3 |  | 66.3 | 64.546 | 0.1 | 73.23 | 18.23 | 689094 | 57.4245 | 57.4245 | 62.8141 | 14.9934 | 356843.7214 | 29.737 | 29.737 | 87.1615 | 0.2 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 63.0065 | 15.1859 | 361423.6427 | 30.1186 | 30.1186 | 85.1176 | 0.3 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 63.1989 | 15.3783 | 366003.5641 | 30.5003 | 30.5003 | 83.0738 | 0.4 | 70.92 | 15.92 | 601776 | 50.148 | 50.148 | 63.3914 | 15.5707 | 370583.4854 | 30.882 | 30.882 | 81.03 | 0.5 | 70.15 | 15.15 | 572670 | 47.7225 | 47.7225 | 63.5838 | 15.7632 | 375163.4068 | 31.2636 | 31.2636 | 78.9861 | 0.6 | 69.38 | 14.38 | 543564 | 45.297 | 45.297 | 63.7762 | 15.9556 | 379743.3281 | 31.6453 | 31.6453 | 76.9423 | 0.7 | 68.61 | 13.61 | 514458 | 42.8715 | 42.8715 | 63.9687 | 16.148 | 384323.2495 | 32.0269 | 32.0269 | 74.8984 | 0.8 | 67.84 | 12.84 | 485352 | 40.446 | 40.446 | 64.1611 | 16.3405 | 388903.1708 | 32.4086 | 32.4086 | 72.8546 | 0.9 | 67.07 | 12.07 | 456246 | 38.0205 | 38.0205 | 64.3535 | 16.5329 | 393483.0922 | 32.7903 | 32.7903 | 70.8108 | 1 | 66.3 | 11.3 | 427140 | 35.595 | 35.595 | 64.546 | 16.7253 | 398063.0135 | 33.1719 | 33.1719 | 68.7669 | 65 | 65 | 25.9768 | 26 | 67.2
9/16/20XX 10:00:00 AM | 0.41667 | 5 | 67.8 | 64.7 | 60.6965 | 70.9676 | 10.2711 | 60 | 67.8 |  | 67.8 | 65.5239 | 0.1 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 62.9119 | 15.0912 | 359171.2993 | 29.9309 | 29.9309 | 87.8279 | 0.2 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 63.2021 | 15.3815 | 366078.7987 | 30.5066 | 30.5066 | 86.4506 | 0.3 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 63.4923 | 15.6717 | 372986.298 | 31.0822 | 31.0822 | 85.0732 | 0.4 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 63.7826 | 15.9619 | 379893.7973 | 31.6578 | 31.6578 | 83.6958 | 0.5 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 64.0728 | 16.2522 | 386801.2966 | 32.2334 | 32.2334 | 82.3184 | 0.6 | 70.28 | 15.28 | 577584 | 48.132 | 48.132 | 64.363 | 16.5424 | 393708.796 | 32.8091 | 32.8091 | 80.9411 | 0.7 | 69.66 | 14.66 | 554148 | 46.179 | 46.179 | 64.6532 | 16.8326 | 400616.2953 | 33.3847 | 33.3847 | 79.5637 | 0.8 | 69.04 | 14.04 | 530712 | 44.226 | 44.226 | 64.9435 | 17.1228 | 407523.7946 | 33.9603 | 33.9603 | 78.1863 | 0.9 | 68.42 | 13.42 | 507276 | 42.273 | 42.273 | 65.2337 | 17.4131 | 414431.2939 | 34.5359 | 34.5359 | 76.8089 | 1 | 67.8 | 12.8 | 483840 | 40.32 | 40.32 | 65.5239 | 17.7033 | 421338.7933 | 35.1116 | 35.1116 | 75.4316 | 70 | 65 | 26.4956 | 26 | 64.7
9/16/20XX 11:00:00 AM | 0.45833 | 5 | 70.3 | 60.2 | 66.2911 | 77.5329 | 11.2418 | 60 | 70.3 |  | 70.3 | 66.516 | 0.1 | 73.63 | 18.63 | 704214 | 58.6845 | 58.6845 | 63.0111 | 15.1904 | 361532.2914 | 30.1277 | 30.1277 | 88.8122 | 0.2 | 73.26 | 18.26 | 690228 | 57.519 | 57.519 | 63.4005 | 15.5799 | 370800.7827 | 30.9001 | 30.9001 | 88.4191 | 0.3 | 72.89 | 17.89 | 676242 | 56.3535 | 56.3535 | 63.7899 | 15.9693 | 380069.2741 | 31.6724 | 31.6724 | 88.0259 | 0.4 | 72.52 | 17.52 | 662256 | 55.188 | 55.188 | 64.1794 | 16.3587 | 389337.7654 | 32.4448 | 32.4448 | 87.6328 | 0.5 | 72.15 | 17.15 | 648270 | 54.0225 | 54.0225 | 64.5688 | 16.7482 | 398606.2568 | 33.2172 | 33.2172 | 87.2397 | 0.6 | 71.78 | 16.78 | 634284 | 52.857 | 52.857 | 64.9582 | 17.1376 | 407874.7481 | 33.9896 | 33.9896 | 86.8466 | 0.7 | 71.41 | 16.41 | 620298 | 51.6915 | 51.6915 | 65.3477 | 17.527 | 417143.2395 | 34.7619 | 34.7619 | 86.4534 | 0.8 | 71.04 | 16.04 | 606312 | 50.526 | 50.526 | 65.7371 | 17.9165 | 426411.7308 | 35.5343 | 35.5343 | 86.0603 | 0.9 | 70.67 | 15.67 | 592326 | 49.3605 | 49.3605 | 66.1265 | 18.3059 | 435680.2222 | 36.3067 | 36.3067 | 85.6672 | 1 | 70.3 | 15.3 | 578340 | 48.195 | 48.195 | 66.516 | 18.6953 | 444948.7135 | 37.0791 | 37.0791 | 85.2741 | 70 | 60 | 27.2609 | 28 | 60.2
9/16/20XX 12:00:00 PM | 0.5 | 5 | 71.8 | 57.7 | 58.0341 | 69.8602 | 11.8262 | 50 | 71.8 |  | 71.8 | 67.1402 | 0.1 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 63.0735 | 15.2529 | 363018.011 | 30.2515 | 30.2515 | 89.4085 | 0.2 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 63.5253 | 15.7047 | 373772.2221 | 31.1477 | 31.1477 | 89.6117 | 0.3 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 63.9772 | 16.1566 | 384526.4331 | 32.0439 | 32.0439 | 89.8149 | 0.4 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 64.4291 | 16.6084 | 395280.6441 | 32.9401 | 32.9401 | 90.0181 | 0.5 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 64.8809 | 17.0603 | 406034.8552 | 33.8362 | 33.8362 | 90.2212 | 0.6 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 65.3328 | 17.5121 | 416789.0662 | 34.7324 | 34.7324 | 90.4244 | 0.7 | 72.46 | 17.46 | 659988 | 54.999 | 54.999 | 65.7846 | 17.964 | 427543.2772 | 35.6286 | 35.6286 | 90.6276 | 0.8 | 72.24 | 17.24 | 651672 | 54.306 | 54.306 | 66.2365 | 18.4159 | 438297.4882 | 36.5248 | 36.5248 | 90.8308 | 0.9 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 66.6884 | 18.8677 | 449051.6993 | 37.421 | 37.421 | 91.034 | 1 | 71.8 | 16.8 | 635040 | 52.92 | 52.92 | 67.1402 | 19.3196 | 459805.9103 | 38.3172 | 38.3172 | 91.2372 | 70 | 60 | 27.7248 | 28 | 57.7
9/16/20XX 1:00:00 PM | 0.54167 | 5 | 73.3 | 54.2 | 61.1294 | 73.5946 | 12.4652 | 50 | 73.3 |  | 73.3 | 66.3648 | 0.1 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 62.9959 | 15.1753 | 361172.4434 | 30.0977 | 30.0977 | 89.7272 | 0.2 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 63.3703 | 15.5496 | 370081.0868 | 30.8401 | 30.8401 | 90.2491 | 0.3 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 63.7446 | 15.9239 | 378989.7303 | 31.5825 | 31.5825 | 90.771 | 0.4 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 64.1189 | 16.2983 | 387898.3737 | 32.3249 | 32.3249 | 91.2929 | 0.5 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 64.4932 | 16.6726 | 396807.0171 | 33.0673 | 33.0673 | 91.8148 | 0.6 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 64.8675 | 17.0469 | 405715.6605 | 33.8096 | 33.8096 | 92.3366 | 0.7 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 65.2418 | 17.4212 | 414624.304 | 34.552 | 34.552 | 92.8585 | 0.8 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 65.6161 | 17.7955 | 423532.9474 | 35.2944 | 35.2944 | 93.3804 | 0.9 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 65.9904 | 18.1698 | 432441.5908 | 36.0368 | 36.0368 | 93.9023 | 1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 66.3648 | 18.5441 | 441350.2342 | 36.7792 | 36.7792 | 94.4242 | 75 | 55 | 27.9699 | 28 | 54.2
9/16/20XX 2:00:00 PM | 0.58333 | 5 | 73.7 | 51.7 | 61.9783 | 74.6189 | 12.6406 | 50 | 73.7 |  | 73.7 | 64.1272 | 0.1 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 62.7722 | 14.9516 | 355847.1248 | 29.6539 | 29.6539 | 89.4094 | 0.2 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 62.9228 | 15.1021 | 359430.4497 | 29.9525 | 29.9525 | 89.6135 | 0.3 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 63.0733 | 15.2527 | 363013.7745 | 30.2511 | 30.2511 | 89.8176 | 0.4 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 63.2239 | 15.4032 | 366597.0993 | 30.5498 | 30.5498 | 90.0218 | 0.5 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 63.3744 | 15.5538 | 370180.4242 | 30.8484 | 30.8484 | 90.2259 | 0.6 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 63.525 | 15.7044 | 373763.749 | 31.147 | 31.147 | 90.43 | 0.7 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 63.6756 | 15.8549 | 377347.0738 | 31.4456 | 31.4456 | 90.6341 | 0.8 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 63.8261 | 16.0055 | 380930.3987 | 31.7442 | 31.7442 | 90.8382 | 0.9 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 63.9767 | 16.156 | 384513.7235 | 32.0428 | 32.0428 | 91.0423 | 1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.1272 | 16.3066 | 388097.0483 | 32.3414 | 32.3414 | 91.2464 | 75 | 50 | 27.7177 | 28 | 51.7
9/16/20XX 3:00:00 PM | 0.625 | 5 | 73 | 53.9 | 60.4992 | 72.8342 | 12.335 | 50 | 73 |  | 73 | 65.3099 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 62.8905 | 15.0698 | 358661.8413 | 29.8885 | 29.8885 | 89.4235 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 63.1593 | 15.3387 | 365059.8826 | 30.4217 | 30.4217 | 89.6417 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 63.4281 | 15.6075 | 371457.9239 | 30.9548 | 30.9548 | 89.8598 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 63.6969 | 15.8763 | 377855.9652 | 31.488 | 31.488 | 90.078 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 63.9658 | 16.1451 | 384254.0065 | 32.0212 | 32.0212 | 90.2962 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 64.2346 | 16.414 | 390652.0478 | 32.5543 | 32.5543 | 90.5143 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 64.5034 | 16.6828 | 397050.0891 | 33.0875 | 33.0875 | 90.7325 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 64.7722 | 16.9516 | 403448.1304 | 33.6207 | 33.6207 | 90.9507 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 65.0411 | 17.2204 | 409846.1717 | 34.1538 | 34.1538 | 91.1688 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 65.3099 | 17.4893 | 416244.213 | 34.687 | 34.687 | 91.387 | 75 | 55 | 27.7317 | 28 | 53.9
9/16/20XX 4:00:00 PM | 0.66667 | 5 | 72.1 | 57 | 58.6421 | 70.5937 | 11.9516 | 50 | 72.1 |  | 72.1 | 67.0082 | 0.1 | 73.81 | 18.81 | 711018 | 59.2515 | 59.2515 | 63.0603 | 15.2397 | 362703.9083 | 30.2253 | 30.2253 | 89.4768 | 0.2 | 73.62 | 18.62 | 703836 | 58.653 | 58.653 | 63.499 | 15.6783 | 373144.0166 | 31.0953 | 31.0953 | 89.7483 | 0.3 | 73.43 | 18.43 | 696654 | 58.0545 | 58.0545 | 63.9376 | 16.117 | 383584.1249 | 31.9653 | 31.9653 | 90.0198 | 0.4 | 73.24 | 18.24 | 689472 | 57.456 | 57.456 | 64.3763 | 16.5556 | 394024.2332 | 32.8354 | 32.8354 | 90.2914 | 0.5 | 73.05 | 18.05 | 682290 | 56.8575 | 56.8575 | 64.8149 | 16.9943 | 404464.3415 | 33.7054 | 33.7054 | 90.5629 | 0.6 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 65.2536 | 17.433 | 414904.4499 | 34.5754 | 34.5754 | 90.8344 | 0.7 | 72.67 | 17.67 | 667926 | 55.6605 | 55.6605 | 65.6923 | 17.8716 | 425344.5582 | 35.4454 | 35.4454 | 91.1059 | 0.8 | 72.48 | 17.48 | 660744 | 55.062 | 55.062 | 66.1309 | 18.3103 | 435784.6665 | 36.3154 | 36.3154 | 91.3774 | 0.9 | 72.29 | 17.29 | 653562 | 54.4635 | 54.4635 | 66.5696 | 18.7489 | 446224.7748 | 37.1854 | 37.1854 | 91.6489 | 1 | 72.1 | 17.1 | 646380 | 53.865 | 53.865 | 67.0082 | 19.1876 | 456664.8831 | 38.0554 | 38.0554 | 91.9204 | 70 | 55 | 27.7774 | 28 | 57
9/16/20XX 5:00:00 PM | 0.70833 | 5 | 70.7 | 59.9 | 55.851 | 67.227 | 11.376 | 50 | 70.7 |  | 70.7 | 67.1132 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 63.0708 | 15.2502 | 362953.8317 | 30.2462 | 30.2462 | 89.0567 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 63.52 | 15.6993 | 373643.8634 | 31.137 | 31.137 | 88.908 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 63.9691 | 16.1485 | 384333.8951 | 32.0278 | 32.0278 | 88.7593 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 64.4183 | 16.5976 | 395023.9268 | 32.9187 | 32.9187 | 88.6107 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 64.8674 | 17.0468 | 405713.9584 | 33.8095 | 33.8095 | 88.462 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 65.3166 | 17.496 | 416403.9901 | 34.7003 | 34.7003 | 88.3133 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 65.7658 | 17.9451 | 427094.0218 | 35.5912 | 35.5912 | 88.1647 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 66.2149 | 18.3943 | 437784.0535 | 36.482 | 36.482 | 88.016 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 66.6641 | 18.8434 | 448474.0852 | 37.3728 | 37.3728 | 87.8673 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 67.1132 | 19.2926 | 459164.1169 | 38.2637 | 38.2637 | 87.7187 | 70 | 60 | 27.4519 | 28 | 59.9
9/16/20XX 6:00:00 PM | 0.75 | 5 | 69.7 | 61.4 | 64.9086 | 75.9105 | 11.0018 | 60 | 69.7 |  | 69.7 | 66.4489 | 0.1 | 73.57 | 18.57 | 701946 | 58.4955 | 58.4955 | 63.0044 | 15.1837 | 361372.7026 | 30.1144 | 30.1144 | 88.6099 | 0.2 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 63.3871 | 15.5665 | 370481.6053 | 30.8735 | 30.8735 | 88.0145 | 0.3 | 72.71 | 17.71 | 669438 | 55.7865 | 55.7865 | 63.7698 | 15.9492 | 379590.5079 | 31.6325 | 31.6325 | 87.419 | 0.4 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 64.1525 | 16.3319 | 388699.4105 | 32.3916 | 32.3916 | 86.8236 | 0.5 | 71.85 | 16.85 | 636930 | 53.0775 | 53.0775 | 64.5353 | 16.7146 | 397808.3131 | 33.1507 | 33.1507 | 86.2282 | 0.6 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 64.918 | 17.0974 | 406917.2158 | 33.9098 | 33.9098 | 85.6328 | 0.7 | 70.99 | 15.99 | 604422 | 50.3685 | 50.3685 | 65.3007 | 17.4801 | 416026.1184 | 34.6688 | 34.6688 | 85.0373 | 0.8 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 65.6834 | 17.8628 | 425135.021 | 35.4279 | 35.4279 | 84.4419 | 0.9 | 70.13 | 15.13 | 571914 | 47.6595 | 47.6595 | 66.0662 | 18.2455 | 434243.9236 | 36.187 | 36.187 | 83.8465 | 1 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 66.4489 | 18.6283 | 443352.8263 | 36.9461 | 36.9461 | 83.2511 | 70 | 60 | 27.1039 | 28 | 61.4
9/16/20XX 7:00:00 PM | 0.79167 | 5 | 68.3 | 63 | 61.7809 | 72.24 | 10.4591 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/16/20XX 8:00:00 PM | 0.83333 | 5 | 67.6 | 64.3 | 60.2675 | 70.4642 | 10.1967 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/16/20XX 9:00:00 PM | 0.875 | 5 | 67.1 | 66.5 | 59.2068 | 69.2196 | 10.0128 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/16/20XX 10:00:00 PM | 0.91667 | 5 | 65.7 | 69.7 | 56.3248 | 65.8382 | 9.5135 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/16/20XX 11:00:00 PM | 0.95833 | 5 | 65.2 | 68.8 | 55.3264 | 64.667 | 9.3406 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/16/20XX 12:00:00 AM | 0 | 6 | 64.3 | 69.5 | 53.5694 | 62.6059 | 9.0365 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/17/20XX 1:00:00 AM | 0.041667 | 6 | 63.5 | 70.7 | 60.8239 | 69.6593 | 8.8354 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/17/20XX 2:00:00 AM | 0.083333 | 6 | 62.4 | 73.8 | 58.4491 | 66.9351 | 8.486 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/17/20XX 3:00:00 AM | 0.125 | 6 | 61.7 | 74.1 | 56.9823 | 65.2529 | 8.2706 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/17/20XX 4:00:00 AM | 0.16667 | 6 | 61.4 | 75.5 | 56.3642 | 64.544 | 8.1799 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/17/20XX 5:00:00 AM | 0.20833 | 6 | 61 | 76.4 | 55.5495 | 63.61 | 8.0604 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/17/20XX 6:00:00 AM | 0.25 | 6 | 60.8 | 76.8 | 55.1463 | 63.1476 | 8.0013 | 70 | 60.8 |  | 60.8 | 60.5872 | 1 | 60.8 | 5.8 | 219240 | 18.27 | 18.27 | 60.5872 | 12.7666 | 303844.6057 | 25.3204 | 25.3204 | 43.5904 | 1 | 60.8 | 5.8 | 219240 | 18.27 | 18.27 | 60.5872 | 12.7666 | 303844.6057 | 25.3204 | 25.3204 | 43.5904 | 1 | 60.8 | 5.8 | 219240 | 18.27 | 18.27 | 60.5872 | 12.7666 | 303844.6057 | 25.3204 | 25.3204 | 43.5904 | 1 | 60.8 | 5.8 | 219240 | 18.27 | 18.27 | 60.5872 | 12.7666 | 303844.6057 | 25.3204 | 25.3204 | 43.5904 | 1 | 60.8 | 5.8 | 219240 | 18.27 | 18.27 | 60.5872 | 12.7666 | 303844.6057 | 25.3204 | 25.3204 | 43.5904 | 1 | 60.8 | 5.8 | 219240 | 18.27 | 18.27 | 60.5872 | 12.7666 | 303844.6057 | 25.3204 | 25.3204 | 43.5904 | 1 | 60.8 | 5.8 | 219240 | 18.27 | 18.27 | 60.5872 | 12.7666 | 303844.6057 | 25.3204 | 25.3204 | 43.5904 | 1 | 60.8 | 5.8 | 219240 | 18.27 | 18.27 | 60.5872 | 12.7666 | 303844.6057 | 25.3204 | 25.3204 | 43.5904 | 1 | 60.8 | 5.8 | 219240 | 18.27 | 18.27 | 60.5872 | 12.7666 | 303844.6057 | 25.3204 | 25.3204 | 43.5904 | 1 | 60.8 | 5.8 | 219240 | 18.27 | 18.27 | 60.5872 | 12.7666 | 303844.6057 | 25.3204 | 25.3204 | 43.5904 | 60 | 75 | 24.0184 | 24 | 76.8
9/17/20XX 7:00:00 AM | 0.29167 | 6 | 61.9 | 74.3 | 57.3979 | 65.7295 | 8.3316 | 70 | 61.9 |  | 61.9 | 60.9805 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.9805 | 13.1599 | 313205.2385 | 26.1004 | 26.1004 | 47.8354 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.9805 | 13.1599 | 313205.2385 | 26.1004 | 26.1004 | 47.8354 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.9805 | 13.1599 | 313205.2385 | 26.1004 | 26.1004 | 47.8354 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.9805 | 13.1599 | 313205.2385 | 26.1004 | 26.1004 | 47.8354 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.9805 | 13.1599 | 313205.2385 | 26.1004 | 26.1004 | 47.8354 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.9805 | 13.1599 | 313205.2385 | 26.1004 | 26.1004 | 47.8354 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.9805 | 13.1599 | 313205.2385 | 26.1004 | 26.1004 | 47.8354 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.9805 | 13.1599 | 313205.2385 | 26.1004 | 26.1004 | 47.8354 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.9805 | 13.1599 | 313205.2385 | 26.1004 | 26.1004 | 47.8354 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.9805 | 13.1599 | 313205.2385 | 26.1004 | 26.1004 | 47.8354 | 60 | 75 | 24.3478 | 24 | 74.3
9/17/20XX 8:00:00 AM | 0.33333 | 6 | 63.7 | 70.8 | 61.265 | 70.1655 | 8.9004 | 70 | 63.7 |  | 63.7 | 61.9771 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.9771 | 14.1564 | 336923.2424 | 28.0769 | 28.0769 | 55.4819 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.9771 | 14.1564 | 336923.2424 | 28.0769 | 28.0769 | 55.4819 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.9771 | 14.1564 | 336923.2424 | 28.0769 | 28.0769 | 55.4819 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.9771 | 14.1564 | 336923.2424 | 28.0769 | 28.0769 | 55.4819 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.9771 | 14.1564 | 336923.2424 | 28.0769 | 28.0769 | 55.4819 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.9771 | 14.1564 | 336923.2424 | 28.0769 | 28.0769 | 55.4819 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.9771 | 14.1564 | 336923.2424 | 28.0769 | 28.0769 | 55.4819 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.9771 | 14.1564 | 336923.2424 | 28.0769 | 28.0769 | 55.4819 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.9771 | 14.1564 | 336923.2424 | 28.0769 | 28.0769 | 55.4819 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.9771 | 14.1564 | 336923.2424 | 28.0769 | 28.0769 | 55.4819 | 65 | 70 | 24.942 | 24 | 70.8
9/17/20XX 9:00:00 AM | 0.375 | 6 | 65.7 | 65.1 | 56.3248 | 65.8382 | 9.5135 | 60 | 65.7 |  | 65.7 | 61.1766 | 0.1 | 73.17 | 18.17 | 686826 | 57.2355 | 57.2355 | 62.4771 | 14.6565 | 348824.7321 | 29.0687 | 29.0687 | 86.3042 | 0.2 | 72.34 | 17.34 | 655452 | 54.621 | 54.621 | 62.3326 | 14.512 | 345385.6642 | 28.7821 | 28.7821 | 83.4031 | 0.3 | 71.51 | 16.51 | 624078 | 52.0065 | 52.0065 | 62.1881 | 14.3675 | 341946.5964 | 28.4955 | 28.4955 | 80.502 | 0.4 | 70.68 | 15.68 | 592704 | 49.392 | 49.392 | 62.0436 | 14.223 | 338507.5285 | 28.209 | 28.209 | 77.601 | 0.5 | 69.85 | 14.85 | 561330 | 46.7775 | 46.7775 | 61.8991 | 14.0785 | 335068.4606 | 27.9224 | 27.9224 | 74.6999 | 0.6 | 69.02 | 14.02 | 529956 | 44.163 | 44.163 | 61.7546 | 13.934 | 331629.3927 | 27.6358 | 27.6358 | 71.7988 | 0.7 | 68.19 | 13.19 | 498582 | 41.5485 | 41.5485 | 61.6101 | 13.7895 | 328190.3248 | 27.3492 | 27.3492 | 68.8977 | 0.8 | 67.36 | 12.36 | 467208 | 38.934 | 38.934 | 61.4656 | 13.645 | 324751.257 | 27.0626 | 27.0626 | 65.9966 | 0.9 | 66.53 | 11.53 | 435834 | 36.3195 | 36.3195 | 61.3211 | 13.5005 | 321312.1891 | 26.776 | 26.776 | 63.0955 | 1 | 65.7 | 10.7 | 404460 | 33.705 | 33.705 | 61.1766 | 13.356 | 317873.1212 | 26.4894 | 26.4894 | 60.1944 | 65 | 65 | 25.3051 | 26 | 65.1
9/17/20XX 10:00:00 AM | 0.41667 | 6 | 67.3 | 60 | 59.6291 | 69.7151 | 10.086 | 60 | 67.3 |  | 67.3 | 59.6291 | 0.1 | 73.33 | 18.33 | 692874 | 57.7395 | 57.7395 | 62.3224 | 14.5017 | 345141.5156 | 28.7618 | 28.7618 | 86.5013 | 0.2 | 72.66 | 17.66 | 667548 | 55.629 | 55.629 | 62.0231 | 14.2025 | 338019.2312 | 28.1683 | 28.1683 | 83.7973 | 0.3 | 71.99 | 16.99 | 642222 | 53.5185 | 53.5185 | 61.7239 | 13.9032 | 330896.9467 | 27.5747 | 27.5747 | 81.0932 | 0.4 | 71.32 | 16.32 | 616896 | 51.408 | 51.408 | 61.4246 | 13.604 | 323774.6623 | 26.9812 | 26.9812 | 78.3892 | 0.5 | 70.65 | 15.65 | 591570 | 49.2975 | 49.2975 | 61.1254 | 13.3047 | 316652.3779 | 26.3877 | 26.3877 | 75.6852 | 0.6 | 69.98 | 14.98 | 566244 | 47.187 | 47.187 | 60.8261 | 13.0055 | 309530.0935 | 25.7942 | 25.7942 | 72.9812 | 0.7 | 69.31 | 14.31 | 540918 | 45.0765 | 45.0765 | 60.5268 | 12.7062 | 302407.8091 | 25.2007 | 25.2007 | 70.2772 | 0.8 | 68.64 | 13.64 | 515592 | 42.966 | 42.966 | 60.2276 | 12.407 | 295285.5247 | 24.6071 | 24.6071 | 67.5731 | 0.9 | 67.97 | 12.97 | 490266 | 40.8555 | 40.8555 | 59.9283 | 12.1077 | 288163.2402 | 24.0136 | 24.0136 | 64.8691 | 1 | 67.3 | 12.3 | 464940 | 38.745 | 38.745 | 59.6291 | 11.8084 | 281040.9558 | 23.4201 | 23.4201 | 62.1651 | 65 | 60 | 25.4539 | 26 | 60
9/17/20XX 11:00:00 AM | 0.45833 | 6 | 70.1 | 55.5 | 54.6905 | 65.8275 | 11.1369 | 50 | 70.1 |  | 70.1 | 60.8158 | 0.1 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 62.4411 | 14.6204 | 347966.0129 | 28.9972 | 28.9972 | 87.6187 | 0.2 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 62.2605 | 14.4398 | 343668.2259 | 28.639 | 28.639 | 86.032 | 0.3 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 62.0799 | 14.2593 | 339370.4388 | 28.2809 | 28.2809 | 84.4454 | 0.4 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 61.8993 | 14.0787 | 335072.6517 | 27.9227 | 27.9227 | 82.8587 | 0.5 | 72.05 | 17.05 | 644490 | 53.7075 | 53.7075 | 61.7187 | 13.8981 | 330774.8646 | 27.5646 | 27.5646 | 81.2721 | 0.6 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 61.5382 | 13.7175 | 326477.0776 | 27.2064 | 27.2064 | 79.6854 | 0.7 | 71.27 | 16.27 | 615006 | 51.2505 | 51.2505 | 61.3576 | 13.5369 | 322179.2905 | 26.8483 | 26.8483 | 78.0988 | 0.8 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 61.177 | 13.3564 | 317881.5034 | 26.4901 | 26.4901 | 76.5121 | 0.9 | 70.49 | 15.49 | 585522 | 48.7935 | 48.7935 | 60.9964 | 13.1758 | 313583.7164 | 26.132 | 26.132 | 74.9255 | 1 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 60.8158 | 12.9952 | 309285.9293 | 25.7738 | 25.7738 | 73.3388 | 70 | 55 | 26.3218 | 26 | 55.5
9/17/20XX 12:00:00 PM | 0.5 | 6 | 71.3 | 53.2 | 57.0328 | 68.6524 | 11.6196 | 50 | 71.3 |  | 71.3 | 60.751 | 0.1 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 62.4346 | 14.6139 | 347811.8086 | 28.9843 | 28.9843 | 87.9838 | 0.2 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 62.2475 | 14.4269 | 343359.8171 | 28.6133 | 28.6133 | 86.7623 | 0.3 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 62.0605 | 14.2398 | 338907.8257 | 28.2423 | 28.2423 | 85.5408 | 0.4 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 61.8734 | 14.0528 | 334455.8342 | 27.8713 | 27.8713 | 84.3193 | 0.5 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 61.6863 | 13.8657 | 330003.8428 | 27.5003 | 27.5003 | 83.0978 | 0.6 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 61.4993 | 13.6786 | 325551.8513 | 27.1293 | 27.1293 | 81.8763 | 0.7 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 61.3122 | 13.4916 | 321099.8599 | 26.7583 | 26.7583 | 80.6548 | 0.8 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 61.1252 | 13.3045 | 316647.8685 | 26.3873 | 26.3873 | 79.4333 | 0.9 | 71.57 | 16.57 | 626346 | 52.1955 | 52.1955 | 60.9381 | 13.1175 | 312195.877 | 26.0163 | 26.0163 | 78.2118 | 1 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 60.751 | 12.9304 | 307743.8856 | 25.6453 | 25.6453 | 76.9903 | 70 | 55 | 26.6043 | 26 | 53.2
9/17/20XX 1:00:00 PM | 0.54167 | 6 | 72.4 | 51.8 | 59.2556 | 71.3339 | 12.0782 | 50 | 72.4 |  | 72.4 | 61.4297 | 0.1 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 62.5024 | 14.6818 | 349427.0076 | 29.1189 | 29.1189 | 88.4649 | 0.2 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 62.3832 | 14.5626 | 346590.2151 | 28.8825 | 28.8825 | 87.7245 | 0.3 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 62.2641 | 14.4434 | 343753.4227 | 28.6461 | 28.6461 | 86.9841 | 0.4 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 62.1449 | 14.3242 | 340916.6302 | 28.4097 | 28.4097 | 86.2437 | 0.5 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 62.0257 | 14.205 | 338079.8378 | 28.1733 | 28.1733 | 85.5033 | 0.6 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 61.9065 | 14.0858 | 335243.0454 | 27.9369 | 27.9369 | 84.7629 | 0.7 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 61.7873 | 13.9666 | 332406.2529 | 27.7005 | 27.7005 | 84.0225 | 0.8 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 61.6681 | 13.8475 | 329569.4605 | 27.4641 | 27.4641 | 83.2821 | 0.9 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 61.5489 | 13.7283 | 326732.6681 | 27.2277 | 27.2277 | 82.5417 | 1 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 61.4297 | 13.6091 | 323895.8756 | 26.9913 | 26.9913 | 81.8013 | 70 | 50 | 26.9787 | 26 | 51.8
9/17/20XX 2:00:00 PM | 0.58333 | 6 | 72.8 | 51.7 | 60.0822 | 72.3311 | 12.2489 | 50 | 72.8 |  | 72.8 | 62.1645 | 0.1 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 62.5759 | 14.7553 | 351175.9224 | 29.2647 | 29.2647 | 88.7367 | 0.2 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 62.5302 | 14.7096 | 350088.0449 | 29.174 | 29.174 | 88.268 | 0.3 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 62.4845 | 14.6639 | 349000.1673 | 29.0833 | 29.0833 | 87.7993 | 0.4 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 62.4388 | 14.6182 | 347912.2897 | 28.9927 | 28.9927 | 87.3307 | 0.5 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 62.3931 | 14.5725 | 346824.4121 | 28.902 | 28.902 | 86.862 | 0.6 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 62.3474 | 14.5267 | 345736.5346 | 28.8114 | 28.8114 | 86.3934 | 0.7 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 62.3017 | 14.481 | 344648.657 | 28.7207 | 28.7207 | 85.9247 | 0.8 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 62.256 | 14.4353 | 343560.7794 | 28.6301 | 28.6301 | 85.4561 | 0.9 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 62.2103 | 14.3896 | 342472.9019 | 28.5394 | 28.5394 | 84.9874 | 1 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 62.1645 | 14.3439 | 341385.0243 | 28.4488 | 28.4488 | 84.5188 | 75 | 50 | 27.1911 | 28 | 51.7
9/17/20XX 3:00:00 PM | 0.625 | 6 | 72.6 | 50.8 | 59.6677 | 71.831 | 12.1633 | 50 | 72.6 |  | 72.6 | 60.6408 | 0.1 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 62.4235 | 14.6029 | 347549.3214 | 28.9624 | 28.9624 | 88.3714 | 0.2 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 62.2255 | 14.4048 | 342834.8428 | 28.5696 | 28.5696 | 87.5376 | 0.3 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 62.0274 | 14.2067 | 338120.3641 | 28.1767 | 28.1767 | 86.7037 | 0.4 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 61.8293 | 14.0087 | 333405.8855 | 27.7838 | 27.7838 | 85.8698 | 0.5 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 61.6312 | 13.8106 | 328691.4069 | 27.391 | 27.391 | 85.036 | 0.6 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 61.4331 | 13.6125 | 323976.9283 | 26.9981 | 26.9981 | 84.2021 | 0.7 | 73.02 | 18.02 | 681156 | 56.763 | 56.763 | 61.235 | 13.4144 | 319262.4497 | 26.6052 | 26.6052 | 83.3682 | 0.8 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 61.0369 | 13.2163 | 314547.9711 | 26.2123 | 26.2123 | 82.5343 | 0.9 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 60.8388 | 13.0182 | 309833.4924 | 25.8195 | 25.8195 | 81.7005 | 1 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 60.6408 | 12.8201 | 305119.0138 | 25.4266 | 25.4266 | 80.8666 | 75 | 50 | 26.9041 | 26 | 50.8
9/17/20XX 4:00:00 PM | 0.66667 | 6 | 71.1 | 55 | 56.6364 | 68.1744 | 11.5379 | 50 | 71.1 |  | 71.1 | 62.4054 | 0.1 | 73.71 | 18.71 | 707238 | 58.9365 | 58.9365 | 62.6 | 14.7794 | 351749.1978 | 29.3124 | 29.3124 | 88.2489 | 0.2 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 62.5784 | 14.7578 | 351234.5955 | 29.2695 | 29.2695 | 87.2925 | 0.3 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 62.5568 | 14.7361 | 350719.9933 | 29.2267 | 29.2267 | 86.3362 | 0.4 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 62.5351 | 14.7145 | 350205.391 | 29.1838 | 29.1838 | 85.3798 | 0.5 | 72.55 | 17.55 | 663390 | 55.2825 | 55.2825 | 62.5135 | 14.6929 | 349690.7888 | 29.1409 | 29.1409 | 84.4234 | 0.6 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 62.4919 | 14.6713 | 349176.1865 | 29.098 | 29.098 | 83.467 | 0.7 | 71.97 | 16.97 | 641466 | 53.4555 | 53.4555 | 62.4703 | 14.6496 | 348661.5843 | 29.0551 | 29.0551 | 82.5106 | 0.8 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 62.4487 | 14.628 | 348146.9821 | 29.0122 | 29.0122 | 81.5542 | 0.9 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 62.427 | 14.6064 | 347632.3798 | 28.9694 | 28.9694 | 80.5979 | 1 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 62.4054 | 14.5848 | 347117.7776 | 28.9265 | 28.9265 | 79.6415 | 70 | 55 | 26.8141 | 26 | 55
9/17/20XX 5:00:00 PM | 0.70833 | 6 | 69.8 | 57.4 | 54.1182 | 65.1373 | 11.0191 | 50 | 69.8 |  | 69.8 | 62.2723 | 0.1 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 62.5867 | 14.7661 | 351432.467 | 29.286 | 29.286 | 87.813 | 0.2 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 62.5518 | 14.7311 | 350601.1341 | 29.2168 | 29.2168 | 86.4208 | 0.3 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 62.5168 | 14.6962 | 349769.8011 | 29.1475 | 29.1475 | 85.0285 | 0.4 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 62.4819 | 14.6613 | 348938.4681 | 29.0782 | 29.0782 | 83.6362 | 0.5 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 62.447 | 14.6264 | 348107.1352 | 29.0089 | 29.0089 | 82.2439 | 0.6 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 62.4121 | 14.5914 | 347275.8022 | 28.9397 | 28.9397 | 80.8517 | 0.7 | 71.06 | 16.06 | 607068 | 50.589 | 50.589 | 62.3771 | 14.5565 | 346444.4692 | 28.8704 | 28.8704 | 79.4594 | 0.8 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 62.3422 | 14.5216 | 345613.1363 | 28.8011 | 28.8011 | 78.0671 | 0.9 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 62.3073 | 14.4866 | 344781.8033 | 28.7318 | 28.7318 | 76.6748 | 1 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 62.2723 | 14.4517 | 343950.4703 | 28.6625 | 28.6625 | 75.2825 | 70 | 55 | 26.4761 | 26 | 57.4
9/17/20XX 6:00:00 PM | 0.75 | 6 | 68.1 | 60.3 | 61.3451 | 71.7287 | 10.3836 | 60 | 68.1 |  | 68.1 | 61.6566 | 0.1 | 73.41 | 18.41 | 695898 | 57.9915 | 57.9915 | 62.5251 | 14.7045 | 349967.0645 | 29.1639 | 29.1639 | 87.1554 | 0.2 | 72.82 | 17.82 | 673596 | 56.133 | 56.133 | 62.4286 | 14.608 | 347670.329 | 28.9725 | 28.9725 | 85.1055 | 0.3 | 72.23 | 17.23 | 651294 | 54.2745 | 54.2745 | 62.3321 | 14.5115 | 345373.5935 | 28.7811 | 28.7811 | 83.0556 | 0.4 | 71.64 | 16.64 | 628992 | 52.416 | 52.416 | 62.2356 | 14.415 | 343076.858 | 28.5897 | 28.5897 | 81.0057 | 0.5 | 71.05 | 16.05 | 606690 | 50.5575 | 50.5575 | 62.1391 | 14.3185 | 340780.1225 | 28.3983 | 28.3983 | 78.9558 | 0.6 | 70.46 | 15.46 | 584388 | 48.699 | 48.699 | 62.0426 | 14.222 | 338483.387 | 28.2069 | 28.2069 | 76.9059 | 0.7 | 69.87 | 14.87 | 562086 | 46.8405 | 46.8405 | 61.9461 | 14.1255 | 336186.6515 | 28.0156 | 28.0156 | 74.8561 | 0.8 | 69.28 | 14.28 | 539784 | 44.982 | 44.982 | 61.8496 | 14.029 | 333889.916 | 27.8242 | 27.8242 | 72.8062 | 0.9 | 68.69 | 13.69 | 517482 | 43.1235 | 43.1235 | 61.7531 | 13.9325 | 331593.1805 | 27.6328 | 27.6328 | 70.7563 | 1 | 68.1 | 13.1 | 495180 | 41.265 | 41.265 | 61.6566 | 13.836 | 329296.445 | 27.4414 | 27.4414 | 68.7064 | 70 | 60 | 25.9653 | 26 | 60.3
9/17/20XX 7:00:00 PM | 0.79167 | 6 | 67 | 62.6 | 58.9966 | 68.973 | 9.9764 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/17/20XX 8:00:00 PM | 0.83333 | 6 | 66.2 | 63.6 | 57.3393 | 67.0285 | 9.6892 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/17/20XX 9:00:00 PM | 0.875 | 6 | 65.1 | 67.6 | 55.1286 | 64.435 | 9.3063 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/17/20XX 10:00:00 PM | 0.91667 | 6 | 65 | 69.4 | 54.9315 | 64.2037 | 9.2722 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/17/20XX 11:00:00 PM | 0.95833 | 6 | 64.8 | 71.7 | 63.7435 | 73.0095 | 9.266 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/17/20XX 12:00:00 AM | 0 | 7 | 64.5 | 73.5 | 63.0587 | 72.2236 | 9.1649 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/18/20XX 1:00:00 AM | 0.041667 | 7 | 64.1 | 74.6 | 62.156 | 71.1877 | 9.0317 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/18/20XX 2:00:00 AM | 0.083333 | 7 | 64.3 | 75.3 | 62.6059 | 71.704 | 9.0981 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/18/20XX 3:00:00 AM | 0.125 | 7 | 64.2 | 76.1 | 62.3806 | 71.4454 | 9.0649 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/18/20XX 4:00:00 AM | 0.16667 | 7 | 64.1 | 76.5 | 62.156 | 71.1877 | 9.0317 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/18/20XX 5:00:00 AM | 0.20833 | 7 | 63.7 | 78.6 | 61.265 | 70.1655 | 8.9004 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/18/20XX 6:00:00 AM | 0.25 | 7 | 63.6 | 78.7 | 61.0441 | 69.912 | 8.8679 | 70 | 63.6 |  | 63.6 | 68.7592 | 1 | 63.6 | 8.6 | 325080 | 27.09 | 27.09 | 68.7592 | 20.9385 | 498336.9323 | 41.5281 | 41.5281 | 68.6181 | 1 | 63.6 | 8.6 | 325080 | 27.09 | 27.09 | 68.7592 | 20.9385 | 498336.9323 | 41.5281 | 41.5281 | 68.6181 | 1 | 63.6 | 8.6 | 325080 | 27.09 | 27.09 | 68.7592 | 20.9385 | 498336.9323 | 41.5281 | 41.5281 | 68.6181 | 1 | 63.6 | 8.6 | 325080 | 27.09 | 27.09 | 68.7592 | 20.9385 | 498336.9323 | 41.5281 | 41.5281 | 68.6181 | 1 | 63.6 | 8.6 | 325080 | 27.09 | 27.09 | 68.7592 | 20.9385 | 498336.9323 | 41.5281 | 41.5281 | 68.6181 | 1 | 63.6 | 8.6 | 325080 | 27.09 | 27.09 | 68.7592 | 20.9385 | 498336.9323 | 41.5281 | 41.5281 | 68.6181 | 1 | 63.6 | 8.6 | 325080 | 27.09 | 27.09 | 68.7592 | 20.9385 | 498336.9323 | 41.5281 | 41.5281 | 68.6181 | 1 | 63.6 | 8.6 | 325080 | 27.09 | 27.09 | 68.7592 | 20.9385 | 498336.9323 | 41.5281 | 41.5281 | 68.6181 | 1 | 63.6 | 8.6 | 325080 | 27.09 | 27.09 | 68.7592 | 20.9385 | 498336.9323 | 41.5281 | 41.5281 | 68.6181 | 1 | 63.6 | 8.6 | 325080 | 27.09 | 27.09 | 68.7592 | 20.9385 | 498336.9323 | 41.5281 | 41.5281 | 68.6181 | 65 | 80 | 25.974 | 26 | 78.7
9/18/20XX 7:00:00 AM | 0.29167 | 7 | 64.4 | 77.3 | 62.8319 | 71.9634 | 9.1314 | 70 | 64.4 |  | 64.4 | 69.4979 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 69.4979 | 21.6772 | 515918.2334 | 42.9932 | 42.9932 | 72.6032 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 69.4979 | 21.6772 | 515918.2334 | 42.9932 | 42.9932 | 72.6032 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 69.4979 | 21.6772 | 515918.2334 | 42.9932 | 42.9932 | 72.6032 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 69.4979 | 21.6772 | 515918.2334 | 42.9932 | 42.9932 | 72.6032 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 69.4979 | 21.6772 | 515918.2334 | 42.9932 | 42.9932 | 72.6032 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 69.4979 | 21.6772 | 515918.2334 | 42.9932 | 42.9932 | 72.6032 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 69.4979 | 21.6772 | 515918.2334 | 42.9932 | 42.9932 | 72.6032 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 69.4979 | 21.6772 | 515918.2334 | 42.9932 | 42.9932 | 72.6032 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 69.4979 | 21.6772 | 515918.2334 | 42.9932 | 42.9932 | 72.6032 | 1 | 64.4 | 9.4 | 355320 | 29.61 | 29.61 | 69.4979 | 21.6772 | 515918.2334 | 42.9932 | 42.9932 | 72.6032 | 65 | 75 | 26.2846 | 26 | 77.3
9/18/20XX 8:00:00 AM | 0.33333 | 7 | 65.9 | 74.7 | 66.3121 | 75.9577 | 9.6456 | 70 | 65.9 |  | 65.9 | 70.8455 | 0.1 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 63.444 | 15.6234 | 371836.6374 | 30.9864 | 30.9864 | 88.2849 | 0.2 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 64.2664 | 16.4458 | 391409.4749 | 32.6175 | 32.6175 | 87.3645 | 0.3 | 71.57 | 16.57 | 626346 | 52.1955 | 52.1955 | 65.0888 | 17.2682 | 410982.3123 | 34.2485 | 34.2485 | 86.444 | 0.4 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 65.9112 | 18.0906 | 430555.1498 | 35.8796 | 35.8796 | 85.5236 | 0.5 | 69.95 | 14.95 | 565110 | 47.0925 | 47.0925 | 66.7336 | 18.9129 | 450127.9872 | 37.5107 | 37.5107 | 84.6032 | 0.6 | 69.14 | 14.14 | 534492 | 44.541 | 44.541 | 67.556 | 19.7353 | 469700.8247 | 39.1417 | 39.1417 | 83.6827 | 0.7 | 68.33 | 13.33 | 503874 | 41.9895 | 41.9895 | 68.3783 | 20.5577 | 489273.6621 | 40.7728 | 40.7728 | 82.7623 | 0.8 | 67.52 | 12.52 | 473256 | 39.438 | 39.438 | 69.2007 | 21.3801 | 508846.4995 | 42.4039 | 42.4039 | 81.8419 | 0.9 | 66.71 | 11.71 | 442638 | 36.8865 | 36.8865 | 70.0231 | 22.2025 | 528419.337 | 44.0349 | 44.0349 | 80.9214 | 1 | 65.9 | 10.9 | 412020 | 34.335 | 34.335 | 70.8455 | 23.0249 | 547992.1744 | 45.666 | 45.666 | 80.001 | 65 | 75 | 26.8613 | 26 | 74.7
9/18/20XX 9:00:00 AM | 0.375 | 7 | 67.9 | 72.2 | 71.2205 | 81.5937 | 10.3732 | 70 | 67.9 |  | 67.9 | 73.5026 | 0.1 | 73.39 | 18.39 | 695142 | 57.9285 | 57.9285 | 63.7097 | 15.8891 | 378160.5487 | 31.5134 | 31.5134 | 89.4419 | 0.2 | 72.78 | 17.78 | 672084 | 56.007 | 56.007 | 64.7978 | 16.9772 | 404057.2974 | 33.6714 | 33.6714 | 89.6784 | 0.3 | 72.17 | 17.17 | 649026 | 54.0855 | 54.0855 | 65.8859 | 18.0653 | 429954.0461 | 35.8295 | 35.8295 | 89.915 | 0.4 | 71.56 | 16.56 | 625968 | 52.164 | 52.164 | 66.974 | 19.1534 | 455850.7948 | 37.9876 | 37.9876 | 90.1516 | 0.5 | 70.95 | 15.95 | 602910 | 50.2425 | 50.2425 | 68.0621 | 20.2415 | 481747.5434 | 40.1456 | 40.1456 | 90.3881 | 0.6 | 70.34 | 15.34 | 579852 | 48.321 | 48.321 | 69.1502 | 21.3296 | 507644.2921 | 42.3037 | 42.3037 | 90.6247 | 0.7 | 69.73 | 14.73 | 556794 | 46.3995 | 46.3995 | 70.2383 | 22.4177 | 533541.0408 | 44.4618 | 44.4618 | 90.8613 | 0.8 | 69.12 | 14.12 | 533736 | 44.478 | 44.478 | 71.3264 | 23.5058 | 559437.7895 | 46.6198 | 46.6198 | 91.0978 | 0.9 | 68.51 | 13.51 | 510678 | 42.5565 | 42.5565 | 72.4145 | 24.5939 | 585334.5382 | 48.7779 | 48.7779 | 91.3344 | 1 | 67.9 | 12.9 | 487620 | 40.635 | 40.635 | 73.5026 | 25.682 | 611231.2869 | 50.9359 | 50.9359 | 91.5709 | 70 | 70 | 27.7649 | 28 | 72.2
9/18/20XX 10:00:00 AM | 0.41667 | 7 | 69.8 | 67.7 | 65.1373 | 76.1788 | 11.0415 | 60 | 69.8 |  | 69.8 | 73.6392 | 0.1 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 63.7234 | 15.9028 | 378485.7188 | 31.5405 | 31.5405 | 90.0675 | 0.2 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 64.8252 | 17.0045 | 404707.6376 | 33.7256 | 33.7256 | 90.9296 | 0.3 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 65.9269 | 18.1063 | 430929.5565 | 35.9108 | 35.9108 | 91.7918 | 0.4 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 67.0287 | 19.208 | 457151.4753 | 38.096 | 38.096 | 92.654 | 0.5 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 68.1304 | 20.3098 | 483373.3941 | 40.2811 | 40.2811 | 93.5161 | 0.6 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 69.2322 | 21.4116 | 509595.3129 | 42.4663 | 42.4663 | 94.3783 | 0.7 | 71.06 | 16.06 | 607068 | 50.589 | 50.589 | 70.334 | 22.5133 | 535817.2317 | 44.6514 | 44.6514 | 95.2404 | 0.8 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 71.4357 | 23.6151 | 562039.1506 | 46.8366 | 46.8366 | 96.1026 | 0.9 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 72.5375 | 24.7169 | 588261.0694 | 49.0218 | 49.0218 | 96.9648 | 1 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 73.6392 | 25.8186 | 614482.9882 | 51.2069 | 51.2069 | 97.8269 | 70 | 70 | 28.2511 | 28 | 67.7
9/18/20XX 11:00:00 AM | 0.45833 | 7 | 72 | 63.4 | 70.3485 | 82.2949 | 11.9464 | 60 | 72 |  | 72 | 74.4103 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 63.8005 | 15.9799 | 380320.7694 | 31.6934 | 31.6934 | 90.9134 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 64.9794 | 17.1587 | 408377.7387 | 34.0315 | 34.0315 | 92.6215 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 66.1582 | 18.3376 | 436434.7081 | 36.3696 | 36.3696 | 94.3296 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 67.3371 | 19.5165 | 464491.6775 | 38.7076 | 38.7076 | 96.0376 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 68.516 | 20.6953 | 492548.6469 | 41.0457 | 41.0457 | 97.7457 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 69.6948 | 21.8742 | 520605.6162 | 43.3838 | 43.3838 | 99.4538 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 70.8737 | 23.053 | 548662.5856 | 45.7219 | 45.7219 | 101.1619 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 72.0525 | 24.2319 | 576719.555 | 48.06 | 48.06 | 102.87 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 73.2314 | 25.4108 | 604776.5244 | 50.398 | 50.398 | 104.578 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 74.4103 | 26.5896 | 632833.4937 | 52.7361 | 52.7361 | 106.2861 | 70 | 65 | 28.9099 | 28 | 63.4
9/18/20XX 12:00:00 PM | 0.5 | 7 | 73 | 61.2 | 72.8342 | 85.2126 | 12.3784 | 60 | 73 |  | 73 | 74.3196 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 63.7914 | 15.9708 | 380105.0655 | 31.6754 | 31.6754 | 91.2104 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.9612 | 17.1406 | 407946.331 | 33.9955 | 33.9955 | 93.2155 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 66.131 | 18.3104 | 435787.5965 | 36.3156 | 36.3156 | 95.2206 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 67.3008 | 19.4802 | 463628.8619 | 38.6357 | 38.6357 | 97.2257 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 68.4706 | 20.65 | 491470.1274 | 40.9558 | 40.9558 | 99.2308 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 69.6404 | 21.8198 | 519311.3929 | 43.2759 | 43.2759 | 101.2359 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 70.8102 | 22.9896 | 547152.6584 | 45.5961 | 45.5961 | 103.2411 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 71.98 | 24.1594 | 574993.9239 | 47.9162 | 47.9162 | 105.2462 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 73.1498 | 25.3292 | 602835.1894 | 50.2363 | 50.2363 | 107.2513 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 74.3196 | 26.499 | 630676.4549 | 52.5564 | 52.5564 | 109.2564 | 75 | 60 | 29.1405 | 30 | 61.2
9/18/20XX 1:00:00 PM | 0.54167 | 7 | 73.6 | 61.7 | 74.3617 | 87.0056 | 12.6439 | 60 | 73.6 |  | 73.6 | 76.5111 | 0.1 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 64.0106 | 16.19 | 385320.8196 | 32.1101 | 32.1101 | 91.8341 | 0.2 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 65.3995 | 17.5789 | 418377.8391 | 34.8648 | 34.8648 | 94.4628 | 0.3 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 66.7885 | 18.9679 | 451434.8587 | 37.6196 | 37.6196 | 97.0916 | 0.4 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 68.1774 | 20.3568 | 484491.8783 | 40.3743 | 40.3743 | 99.7203 | 0.5 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 69.5664 | 21.7458 | 517548.8978 | 43.1291 | 43.1291 | 102.3491 | 0.6 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 70.9553 | 23.1347 | 550605.9174 | 45.8838 | 45.8838 | 104.9778 | 0.7 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 72.3443 | 24.5237 | 583662.937 | 48.6386 | 48.6386 | 107.6066 | 0.8 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 73.7332 | 25.9126 | 616719.9565 | 51.3933 | 51.3933 | 110.2353 | 0.9 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 75.1222 | 27.3016 | 649776.9761 | 54.1481 | 54.1481 | 112.8641 | 1 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 76.5111 | 28.6905 | 682833.9957 | 56.9028 | 56.9028 | 115.4928 | 75 | 60 | 29.63 | 30 | 61.7
9/18/20XX 2:00:00 PM | 0.58333 | 7 | 73.5 | 60 | 74.1052 | 86.7045 | 12.5993 | 60 | 73.5 |  | 73.5 | 74.1052 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 63.77 | 15.9494 | 379594.7107 | 31.6329 | 31.6329 | 91.3254 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.9183 | 17.0977 | 406925.6213 | 33.9105 | 33.9105 | 93.4455 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 66.0667 | 18.2461 | 434256.532 | 36.188 | 36.188 | 95.5655 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 67.2151 | 19.3944 | 461587.4427 | 38.4656 | 38.4656 | 97.6856 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 68.3634 | 20.5428 | 488918.3534 | 40.7432 | 40.7432 | 99.8057 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 69.5118 | 21.6911 | 516249.264 | 43.0208 | 43.0208 | 101.9258 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 70.6601 | 22.8395 | 543580.1747 | 45.2983 | 45.2983 | 104.0458 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 71.8085 | 23.9879 | 570911.0854 | 47.5759 | 47.5759 | 106.1659 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 72.9569 | 25.1362 | 598241.996 | 49.8535 | 49.8535 | 108.286 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 74.1052 | 26.2846 | 625572.9067 | 52.1311 | 52.1311 | 110.4061 | 75 | 60 | 29.2293 | 30 | 60
9/18/20XX 3:00:00 PM | 0.625 | 7 | 73.3 | 60.5 | 73.5946 | 86.1051 | 12.5105 | 60 | 73.3 |  | 73.3 | 74.2201 | 0.1 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 63.7815 | 15.9608 | 379868.1058 | 31.6557 | 31.6557 | 91.2852 | 0.2 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 64.9413 | 17.1207 | 407472.4116 | 33.956 | 33.956 | 93.365 | 0.3 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 66.1012 | 18.2805 | 435076.7174 | 36.2564 | 36.2564 | 95.4449 | 0.4 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 67.261 | 19.4404 | 462681.0232 | 38.5568 | 38.5568 | 97.5248 | 0.5 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 68.4209 | 20.6002 | 490285.329 | 40.8571 | 40.8571 | 99.6046 | 0.6 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 69.5807 | 21.7601 | 517889.6348 | 43.1575 | 43.1575 | 101.6845 | 0.7 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 70.7405 | 22.9199 | 545493.9406 | 45.4578 | 45.4578 | 103.7643 | 0.8 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 71.9004 | 24.0798 | 573098.2464 | 47.7582 | 47.7582 | 105.8442 | 0.9 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 73.0602 | 25.2396 | 600702.5522 | 50.0585 | 50.0585 | 107.924 | 1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 74.2201 | 26.3994 | 628306.858 | 52.3589 | 52.3589 | 110.0039 | 75 | 60 | 29.1983 | 30 | 60.5
9/18/20XX 4:00:00 PM | 0.66667 | 7 | 73 | 60.5 | 72.8342 | 85.2126 | 12.3784 | 60 | 73 |  | 73 | 73.4532 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 63.7048 | 15.8842 | 378042.8251 | 31.5036 | 31.5036 | 91.0386 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.7879 | 16.9673 | 403821.8503 | 33.6518 | 33.6518 | 92.8718 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 65.8711 | 18.0505 | 429600.8754 | 35.8001 | 35.8001 | 94.7051 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 66.9542 | 19.1336 | 455379.9006 | 37.9483 | 37.9483 | 96.5383 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 68.0374 | 20.2168 | 481158.9257 | 40.0966 | 40.0966 | 98.3716 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 69.1205 | 21.2999 | 506937.9509 | 42.2448 | 42.2448 | 100.2048 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 70.2037 | 22.3831 | 532716.976 | 44.3931 | 44.3931 | 102.0381 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 71.2869 | 23.4662 | 558496.0012 | 46.5413 | 46.5413 | 103.8713 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 72.37 | 24.5494 | 584275.0263 | 48.6896 | 48.6896 | 105.7046 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 73.4532 | 25.6325 | 610054.0514 | 50.8378 | 50.8378 | 107.5378 | 75 | 60 | 29.005 | 30 | 60.5
9/18/20XX 5:00:00 PM | 0.70833 | 7 | 72 | 62.7 | 70.3485 | 82.2949 | 11.9464 | 60 | 72 |  | 72 | 73.574 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 63.7169 | 15.8962 | 378330.4918 | 31.5275 | 31.5275 | 90.7475 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 64.8121 | 16.9915 | 404397.1836 | 33.6998 | 33.6998 | 92.2898 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 65.9073 | 18.0867 | 430463.8754 | 35.872 | 35.872 | 93.832 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 67.0026 | 19.182 | 456530.5671 | 38.0442 | 38.0442 | 95.3742 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 68.0978 | 20.2772 | 482597.2589 | 40.2164 | 40.2164 | 96.9164 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 69.1931 | 21.3724 | 508663.9507 | 42.3887 | 42.3887 | 98.4587 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 70.2883 | 22.4677 | 534730.6425 | 44.5609 | 44.5609 | 100.0009 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 71.3835 | 23.5629 | 560797.3343 | 46.7331 | 46.7331 | 101.5431 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 72.4788 | 24.6582 | 586864.0261 | 48.9053 | 48.9053 | 103.0853 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 73.574 | 25.7534 | 612930.7179 | 51.0776 | 51.0776 | 104.6276 | 70 | 65 | 28.7792 | 28 | 62.7
9/18/20XX 6:00:00 PM | 0.75 | 7 | 70.5 | 66.2 | 66.7576 | 78.0804 | 11.3228 | 60 | 70.5 |  | 70.5 | 73.7778 | 0.1 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 63.7372 | 15.9166 | 378815.3735 | 31.5679 | 31.5679 | 90.3154 | 0.2 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 64.8529 | 17.0322 | 405366.947 | 33.7806 | 33.7806 | 91.4256 | 0.3 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 65.9685 | 18.1478 | 431918.5205 | 35.9932 | 35.9932 | 92.5357 | 0.4 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 67.0841 | 19.2634 | 458470.094 | 38.2058 | 38.2058 | 93.6458 | 0.5 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 68.1997 | 20.3791 | 485021.6674 | 40.4185 | 40.4185 | 94.756 | 0.6 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 69.3153 | 21.4947 | 511573.2409 | 42.6311 | 42.6311 | 95.8661 | 0.7 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 70.4309 | 22.6103 | 538124.8144 | 44.8437 | 44.8437 | 96.9762 | 0.8 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 71.5465 | 23.7259 | 564676.3879 | 47.0564 | 47.0564 | 98.0864 | 0.9 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 72.6621 | 24.8415 | 591227.9614 | 49.269 | 49.269 | 99.1965 | 1 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 73.7778 | 25.9571 | 617779.5349 | 51.4816 | 51.4816 | 100.3066 | 70 | 65 | 28.444 | 28 | 66.2
9/18/20XX 7:00:00 PM | 0.79167 | 7 | 69.2 | 69 | 63.776 | 74.5812 | 10.8052 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/18/20XX 8:00:00 PM | 0.83333 | 7 | 68.6 | 71.8 | 73.0131 | 83.6528 | 10.6396 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/18/20XX 9:00:00 PM | 0.875 | 7 | 68.3 | 72.2 | 72.24 | 82.7647 | 10.5247 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/18/20XX 10:00:00 PM | 0.91667 | 7 | 68.1 | 72.7 | 71.7287 | 82.1774 | 10.4487 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/18/20XX 11:00:00 PM | 0.95833 | 7 | 67.5 | 74.6 | 70.2137 | 80.4375 | 10.2238 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/18/20XX 12:00:00 AM | 0 | 1 | 66.7 | 74.9 | 68.238 | 78.1688 | 9.9308 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/19/20XX 1:00:00 AM | 0.041667 | 1 | 65.5 | 77 | 65.3675 | 74.8734 | 9.5059 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/19/20XX 2:00:00 AM | 0.083333 | 1 | 64.8 | 76.6 | 63.7435 | 73.0095 | 9.266 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/19/20XX 3:00:00 AM | 0.125 | 1 | 64.1 | 75.8 | 62.156 | 71.1877 | 9.0317 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/19/20XX 4:00:00 AM | 0.16667 | 1 | 63.5 | 75.7 | 60.8239 | 69.6593 | 8.8354 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/19/20XX 5:00:00 AM | 0.20833 | 1 | 62.7 | 77.5 | 59.0882 | 67.6682 | 8.58 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/19/20XX 6:00:00 AM | 0.25 | 1 | 62.1 | 76.6 | 57.8163 | 66.2093 | 8.393 | 70 | 62.1 |  | 62.1 | 63.3557 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 63.3557 | 15.5351 | 369734.6319 | 30.8112 | 30.8112 | 53.1762 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 63.3557 | 15.5351 | 369734.6319 | 30.8112 | 30.8112 | 53.1762 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 63.3557 | 15.5351 | 369734.6319 | 30.8112 | 30.8112 | 53.1762 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 63.3557 | 15.5351 | 369734.6319 | 30.8112 | 30.8112 | 53.1762 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 63.3557 | 15.5351 | 369734.6319 | 30.8112 | 30.8112 | 53.1762 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 63.3557 | 15.5351 | 369734.6319 | 30.8112 | 30.8112 | 53.1762 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 63.3557 | 15.5351 | 369734.6319 | 30.8112 | 30.8112 | 53.1762 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 63.3557 | 15.5351 | 369734.6319 | 30.8112 | 30.8112 | 53.1762 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 63.3557 | 15.5351 | 369734.6319 | 30.8112 | 30.8112 | 53.1762 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 63.3557 | 15.5351 | 369734.6319 | 30.8112 | 30.8112 | 53.1762 | 60 | 75 | 24.7663 | 24 | 76.6
9/19/20XX 7:00:00 AM | 0.29167 | 1 | 62.4 | 74.8 | 58.4491 | 66.9351 | 8.486 | 70 | 62.4 |  | 62.4 | 62.5224 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 62.5224 | 14.7017 | 349901.5824 | 29.1585 | 29.1585 | 52.4685 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 62.5224 | 14.7017 | 349901.5824 | 29.1585 | 29.1585 | 52.4685 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 62.5224 | 14.7017 | 349901.5824 | 29.1585 | 29.1585 | 52.4685 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 62.5224 | 14.7017 | 349901.5824 | 29.1585 | 29.1585 | 52.4685 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 62.5224 | 14.7017 | 349901.5824 | 29.1585 | 29.1585 | 52.4685 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 62.5224 | 14.7017 | 349901.5824 | 29.1585 | 29.1585 | 52.4685 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 62.5224 | 14.7017 | 349901.5824 | 29.1585 | 29.1585 | 52.4685 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 62.5224 | 14.7017 | 349901.5824 | 29.1585 | 29.1585 | 52.4685 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 62.5224 | 14.7017 | 349901.5824 | 29.1585 | 29.1585 | 52.4685 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 62.5224 | 14.7017 | 349901.5824 | 29.1585 | 29.1585 | 52.4685 | 60 | 75 | 24.7098 | 24 | 74.8
9/19/20XX 8:00:00 AM | 0.33333 | 1 | 63.7 | 70.3 | 61.265 | 70.1655 | 8.9004 | 70 | 63.7 |  | 63.7 | 61.5321 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.5321 | 13.7114 | 326331.751 | 27.1943 | 27.1943 | 54.5993 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.5321 | 13.7114 | 326331.751 | 27.1943 | 27.1943 | 54.5993 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.5321 | 13.7114 | 326331.751 | 27.1943 | 27.1943 | 54.5993 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.5321 | 13.7114 | 326331.751 | 27.1943 | 27.1943 | 54.5993 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.5321 | 13.7114 | 326331.751 | 27.1943 | 27.1943 | 54.5993 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.5321 | 13.7114 | 326331.751 | 27.1943 | 27.1943 | 54.5993 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.5321 | 13.7114 | 326331.751 | 27.1943 | 27.1943 | 54.5993 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.5321 | 13.7114 | 326331.751 | 27.1943 | 27.1943 | 54.5993 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.5321 | 13.7114 | 326331.751 | 27.1943 | 27.1943 | 54.5993 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 61.5321 | 13.7114 | 326331.751 | 27.1943 | 27.1943 | 54.5993 | 65 | 70 | 24.8727 | 24 | 70.3
9/19/20XX 9:00:00 AM | 0.375 | 1 | 65.6 | 66.3 | 56.1238 | 65.6025 | 9.4787 | 60 | 65.6 |  | 65.6 | 62.0954 | 0.1 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 62.569 | 14.7484 | 351011.2963 | 29.2509 | 29.2509 | 86.4549 | 0.2 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 62.5164 | 14.6957 | 349758.7926 | 29.1466 | 29.1466 | 83.7046 | 0.3 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 62.4638 | 14.6431 | 348506.2889 | 29.0422 | 29.0422 | 80.9542 | 0.4 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 62.4111 | 14.5905 | 347253.7853 | 28.9378 | 28.9378 | 78.2038 | 0.5 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 62.3585 | 14.5379 | 346001.2816 | 28.8334 | 28.8334 | 75.4534 | 0.6 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 62.3059 | 14.4852 | 344748.7779 | 28.7291 | 28.7291 | 72.7031 | 0.7 | 68.12 | 13.12 | 495936 | 41.328 | 41.328 | 62.2532 | 14.4326 | 343496.2742 | 28.6247 | 28.6247 | 69.9527 | 0.8 | 67.28 | 12.28 | 464184 | 38.682 | 38.682 | 62.2006 | 14.38 | 342243.7705 | 28.5203 | 28.5203 | 67.2023 | 0.9 | 66.44 | 11.44 | 432432 | 36.036 | 36.036 | 62.148 | 14.3274 | 340991.2668 | 28.4159 | 28.4159 | 64.4519 | 1 | 65.6 | 10.6 | 400680 | 33.39 | 33.39 | 62.0954 | 14.2747 | 339738.7631 | 28.3116 | 28.3116 | 61.7016 | 65 | 65 | 25.4239 | 26 | 66.3
9/19/20XX 10:00:00 AM | 0.41667 | 1 | 67.9 | 62.5 | 60.912 | 71.2205 | 10.3085 | 60 | 67.9 |  | 67.9 | 63.4892 | 0.1 | 73.39 | 18.39 | 695142 | 57.9285 | 57.9285 | 62.7084 | 14.8878 | 354328.5175 | 29.5274 | 29.5274 | 87.4559 | 0.2 | 72.78 | 17.78 | 672084 | 56.007 | 56.007 | 62.7951 | 14.9745 | 356393.2349 | 29.6994 | 29.6994 | 85.7064 | 0.3 | 72.17 | 17.17 | 649026 | 54.0855 | 54.0855 | 62.8819 | 15.0613 | 358457.9524 | 29.8715 | 29.8715 | 83.957 | 0.4 | 71.56 | 16.56 | 625968 | 52.164 | 52.164 | 62.9686 | 15.148 | 360522.6699 | 30.0436 | 30.0436 | 82.2076 | 0.5 | 70.95 | 15.95 | 602910 | 50.2425 | 50.2425 | 63.0554 | 15.2348 | 362587.3874 | 30.2156 | 30.2156 | 80.4581 | 0.6 | 70.34 | 15.34 | 579852 | 48.321 | 48.321 | 63.1421 | 15.3215 | 364652.1048 | 30.3877 | 30.3877 | 78.7087 | 0.7 | 69.73 | 14.73 | 556794 | 46.3995 | 46.3995 | 63.2289 | 15.4083 | 366716.8223 | 30.5597 | 30.5597 | 76.9592 | 0.8 | 69.12 | 14.12 | 533736 | 44.478 | 44.478 | 63.3157 | 15.495 | 368781.5398 | 30.7318 | 30.7318 | 75.2098 | 0.9 | 68.51 | 13.51 | 510678 | 42.5565 | 42.5565 | 63.4024 | 15.5818 | 370846.2572 | 30.9039 | 30.9039 | 73.4604 | 1 | 67.9 | 12.9 | 487620 | 40.635 | 40.635 | 63.4892 | 15.6685 | 372910.9747 | 31.0759 | 31.0759 | 71.7109 | 70 | 60 | 26.2025 | 26 | 62.5
9/19/20XX 11:00:00 AM | 0.45833 | 1 | 70.9 | 57.4 | 56.2425 | 67.6992 | 11.4567 | 50 | 70.9 |  | 70.9 | 64.7205 | 0.1 | 73.69 | 18.69 | 706482 | 58.8735 | 58.8735 | 62.8315 | 15.0109 | 357259.1033 | 29.7716 | 29.7716 | 88.6451 | 0.2 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 63.0414 | 15.2208 | 362254.4067 | 30.1879 | 30.1879 | 88.0849 | 0.3 | 73.07 | 18.07 | 683046 | 56.9205 | 56.9205 | 63.2513 | 15.4307 | 367249.71 | 30.6041 | 30.6041 | 87.5246 | 0.4 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 63.4612 | 15.6405 | 372245.0134 | 31.0204 | 31.0204 | 86.9644 | 0.5 | 72.45 | 17.45 | 659610 | 54.9675 | 54.9675 | 63.6711 | 15.8504 | 377240.3167 | 31.4367 | 31.4367 | 86.4042 | 0.6 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 63.881 | 16.0603 | 382235.6201 | 31.853 | 31.853 | 85.844 | 0.7 | 71.83 | 16.83 | 636174 | 53.0145 | 53.0145 | 64.0908 | 16.2702 | 387230.9234 | 32.2692 | 32.2692 | 85.2837 | 0.8 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 64.3007 | 16.4801 | 392226.2268 | 32.6855 | 32.6855 | 84.7235 | 0.9 | 71.21 | 16.21 | 612738 | 51.0615 | 51.0615 | 64.5106 | 16.69 | 397221.5301 | 33.1018 | 33.1018 | 84.1633 | 1 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 64.7205 | 16.8999 | 402216.8334 | 33.5181 | 33.5181 | 83.6031 | 70 | 55 | 27.1269 | 28 | 57.4
9/19/20XX 12:00:00 PM | 0.5 | 1 | 72.5 | 52.3 | 59.4614 | 71.5821 | 12.1207 | 50 | 72.5 |  | 72.5 | 62.2491 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 62.5844 | 14.7637 | 351377.2027 | 29.2814 | 29.2814 | 88.6589 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 62.5471 | 14.7265 | 350490.6053 | 29.2076 | 29.2076 | 88.1126 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 62.5099 | 14.6892 | 349604.008 | 29.1337 | 29.1337 | 87.5662 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 62.4726 | 14.652 | 348717.4106 | 29.0598 | 29.0598 | 87.0198 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 62.4354 | 14.6147 | 347830.8133 | 28.9859 | 28.9859 | 86.4734 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 62.3981 | 14.5775 | 346944.216 | 28.912 | 28.912 | 85.927 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 62.3609 | 14.5402 | 346057.6186 | 28.8381 | 28.8381 | 85.3806 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 62.3236 | 14.503 | 345171.0213 | 28.7643 | 28.7643 | 84.8343 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 62.2864 | 14.4657 | 344284.4239 | 28.6904 | 28.6904 | 84.2879 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 62.2491 | 14.4285 | 343397.8266 | 28.6165 | 28.6165 | 83.7415 | 70 | 50 | 27.1312 | 28 | 52.3
9/19/20XX 1:00:00 PM | 0.54167 | 1 | 73.1 | 51.9 | 60.7087 | 73.0869 | 12.3783 | 50 | 73.1 |  | 73.1 | 63.0605 | 0.1 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 62.6655 | 14.8449 | 353308.3867 | 29.4424 | 29.4424 | 89.0089 | 0.2 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 62.7094 | 14.8888 | 354352.9735 | 29.5294 | 29.5294 | 88.8124 | 0.3 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 62.7533 | 14.9327 | 355397.5602 | 29.6165 | 29.6165 | 88.616 | 0.4 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 62.7972 | 14.9766 | 356442.1469 | 29.7035 | 29.7035 | 88.4195 | 0.5 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 62.8411 | 15.0205 | 357486.7336 | 29.7906 | 29.7906 | 88.2231 | 0.6 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 62.885 | 15.0643 | 358531.3204 | 29.8776 | 29.8776 | 88.0266 | 0.7 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 62.9289 | 15.1082 | 359575.9071 | 29.9647 | 29.9647 | 87.8302 | 0.8 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 62.9728 | 15.1521 | 360620.4938 | 30.0517 | 30.0517 | 87.6337 | 0.9 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 63.0166 | 15.196 | 361665.0806 | 30.1388 | 30.1388 | 87.4373 | 1 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 63.0605 | 15.2399 | 362709.6673 | 30.2258 | 30.2258 | 87.2408 | 75 | 50 | 27.4044 | 28 | 51.9
9/19/20XX 2:00:00 PM | 0.58333 | 1 | 73.7 | 50.3 | 61.9783 | 74.6189 | 12.6406 | 50 | 73.7 |  | 73.7 | 62.3576 | 0.1 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 62.5952 | 14.7746 | 351635.2889 | 29.3029 | 29.3029 | 89.0584 | 0.2 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 62.5688 | 14.7482 | 351006.7778 | 29.2506 | 29.2506 | 88.9116 | 0.3 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 62.5424 | 14.7218 | 350378.2667 | 29.1982 | 29.1982 | 88.7647 | 0.4 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 62.516 | 14.6954 | 349749.7556 | 29.1458 | 29.1458 | 88.6178 | 0.5 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 62.4896 | 14.669 | 349121.2444 | 29.0934 | 29.0934 | 88.4709 | 0.6 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 62.4632 | 14.6426 | 348492.7333 | 29.0411 | 29.0411 | 88.3241 | 0.7 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 62.4368 | 14.6161 | 347864.2222 | 28.9887 | 28.9887 | 88.1772 | 0.8 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 62.4104 | 14.5897 | 347235.7111 | 28.9363 | 28.9363 | 88.0303 | 0.9 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 62.384 | 14.5633 | 346607.2 | 28.8839 | 28.8839 | 87.8834 | 1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 62.3576 | 14.5369 | 345978.6889 | 28.8316 | 28.8316 | 87.7366 | 75 | 50 | 27.4409 | 28 | 50.3
9/19/20XX 3:00:00 PM | 0.625 | 1 | 72.3 | 54.8 | 59.0505 | 71.0864 | 12.0359 | 50 | 72.3 |  | 72.3 | 64.8277 | 0.1 | 73.83 | 18.83 | 711774 | 59.3145 | 59.3145 | 62.8422 | 15.0216 | 357514.3235 | 29.7929 | 29.7929 | 89.1074 | 0.2 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 63.0629 | 15.2422 | 362764.847 | 30.2304 | 30.2304 | 89.0094 | 0.3 | 73.49 | 18.49 | 698922 | 58.2435 | 58.2435 | 63.2835 | 15.4628 | 368015.3705 | 30.6679 | 30.6679 | 88.9114 | 0.4 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 63.5041 | 15.6834 | 373265.8941 | 31.1055 | 31.1055 | 88.8135 | 0.5 | 73.15 | 18.15 | 686070 | 57.1725 | 57.1725 | 63.7247 | 15.9041 | 378516.4176 | 31.543 | 31.543 | 88.7155 | 0.6 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 63.9453 | 16.1247 | 383766.9411 | 31.9806 | 31.9806 | 88.6176 | 0.7 | 72.81 | 17.81 | 673218 | 56.1015 | 56.1015 | 64.1659 | 16.3453 | 389017.4646 | 32.4181 | 32.4181 | 88.5196 | 0.8 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 64.3865 | 16.5659 | 394267.9881 | 32.8557 | 32.8557 | 88.4217 | 0.9 | 72.47 | 17.47 | 660366 | 55.0305 | 55.0305 | 64.6071 | 16.7865 | 399518.5116 | 33.2932 | 33.2932 | 88.3237 | 1 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 64.8277 | 17.0071 | 404769.0352 | 33.7308 | 33.7308 | 88.2258 | 70 | 55 | 27.4854 | 28 | 54.8
9/19/20XX 4:00:00 PM | 0.66667 | 1 | 71.5 | 56 | 57.4315 | 69.1333 | 11.7019 | 50 | 71.5 |  | 71.5 | 64.4526 | 0.1 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 62.8047 | 14.9841 | 356621.4926 | 29.7185 | 29.7185 | 88.781 | 0.2 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 62.9878 | 15.1672 | 360979.1852 | 30.0816 | 30.0816 | 88.3566 | 0.3 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 63.1709 | 15.3503 | 365336.8779 | 30.4447 | 30.4447 | 87.9322 | 0.4 | 73 | 18 | 680400 | 56.7 | 56.7 | 63.354 | 15.5334 | 369694.5705 | 30.8079 | 30.8079 | 87.5079 | 0.5 | 72.75 | 17.75 | 670950 | 55.9125 | 55.9125 | 63.5371 | 15.7165 | 374052.2631 | 31.171 | 31.171 | 87.0835 | 0.6 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 63.7202 | 15.8996 | 378409.9557 | 31.5342 | 31.5342 | 86.6592 | 0.7 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 63.9033 | 16.0827 | 382767.6484 | 31.8973 | 31.8973 | 86.2348 | 0.8 | 72 | 17 | 642600 | 53.55 | 53.55 | 64.0864 | 16.2658 | 387125.341 | 32.2604 | 32.2604 | 85.8104 | 0.9 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 64.2695 | 16.4489 | 391483.0336 | 32.6236 | 32.6236 | 85.3861 | 1 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 64.4526 | 16.632 | 395840.7262 | 32.9867 | 32.9867 | 84.9617 | 70 | 55 | 27.2315 | 28 | 56
9/19/20XX 5:00:00 PM | 0.70833 | 1 | 69.7 | 60.1 | 64.9086 | 75.9105 | 11.0018 | 60 | 69.7 |  | 69.7 | 65.0187 | 0.1 | 73.57 | 18.57 | 701946 | 58.4955 | 58.4955 | 62.8613 | 15.0407 | 357968.7416 | 29.8307 | 29.8307 | 88.3262 | 0.2 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 63.101 | 15.2804 | 363673.6832 | 30.3061 | 30.3061 | 87.4471 | 0.3 | 72.71 | 17.71 | 669438 | 55.7865 | 55.7865 | 63.3407 | 15.5201 | 369378.6249 | 30.7816 | 30.7816 | 86.5681 | 0.4 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 63.5804 | 15.7598 | 375083.5665 | 31.257 | 31.257 | 85.689 | 0.5 | 71.85 | 16.85 | 636930 | 53.0775 | 53.0775 | 63.8201 | 15.9995 | 380788.5081 | 31.7324 | 31.7324 | 84.8099 | 0.6 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 64.0599 | 16.2392 | 386493.4497 | 32.2078 | 32.2078 | 83.9308 | 0.7 | 70.99 | 15.99 | 604422 | 50.3685 | 50.3685 | 64.2996 | 16.4789 | 392198.3913 | 32.6832 | 32.6832 | 83.0517 | 0.8 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 64.5393 | 16.7186 | 397903.3329 | 33.1586 | 33.1586 | 82.1726 | 0.9 | 70.13 | 15.13 | 571914 | 47.6595 | 47.6595 | 64.779 | 16.9583 | 403608.2746 | 33.634 | 33.634 | 81.2935 | 1 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 65.0187 | 17.198 | 409313.2162 | 34.1094 | 34.1094 | 80.4144 | 70 | 60 | 26.8806 | 26 | 60.1
9/19/20XX 6:00:00 PM | 0.75 | 1 | 68.2 | 66.4 | 61.5627 | 71.984 | 10.4213 | 60 | 68.2 |  | 68.2 | 68.2323 | 0.1 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 63.1827 | 15.3621 | 365617.165 | 30.4681 | 30.4681 | 88.4911 | 0.2 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 63.7438 | 15.9231 | 378970.5299 | 31.5809 | 31.5809 | 87.7769 | 0.3 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 64.3048 | 16.4842 | 392323.8949 | 32.6937 | 32.6937 | 87.0627 | 0.4 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 64.8659 | 17.0453 | 405677.2599 | 33.8064 | 33.8064 | 86.3484 | 0.5 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 65.427 | 17.6063 | 419030.6248 | 34.9192 | 34.9192 | 85.6342 | 0.6 | 70.52 | 15.52 | 586656 | 48.888 | 48.888 | 65.988 | 18.1674 | 432383.9898 | 36.032 | 36.032 | 84.92 | 0.7 | 69.94 | 14.94 | 564732 | 47.061 | 47.061 | 66.5491 | 18.7285 | 445737.3547 | 37.1448 | 37.1448 | 84.2058 | 0.8 | 69.36 | 14.36 | 542808 | 45.234 | 45.234 | 67.1102 | 19.2895 | 459090.7197 | 38.2576 | 38.2576 | 83.4916 | 0.9 | 68.78 | 13.78 | 520884 | 43.407 | 43.407 | 67.6712 | 19.8506 | 472444.0847 | 39.3703 | 39.3703 | 82.7773 | 1 | 68.2 | 13.2 | 498960 | 41.58 | 41.58 | 68.2323 | 20.4117 | 485797.4496 | 40.4831 | 40.4831 | 82.0631 | 70 | 65 | 27.0159 | 28 | 66.4
9/19/20XX 7:00:00 PM | 0.79167 | 1 | 67.1 | 70.5 | 69.2196 | 79.2959 | 10.0763 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/19/20XX 8:00:00 PM | 0.83333 | 1 | 66.7 | 71.3 | 68.238 | 78.1688 | 9.9308 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/19/20XX 9:00:00 PM | 0.875 | 1 | 66.4 | 71.9 | 67.51 | 77.333 | 9.823 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/19/20XX 10:00:00 PM | 0.91667 | 1 | 66.5 | 70.4 | 67.7519 | 77.6107 | 9.8588 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/19/20XX 11:00:00 PM | 0.95833 | 1 | 66.1 | 69.9 | 57.1351 | 66.7889 | 9.6538 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/19/20XX 12:00:00 AM | 0 | 2 | 65.3 | 73.5 | 64.8997 | 74.3365 | 9.4368 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/20/20XX 1:00:00 AM | 0.041667 | 2 | 64.9 | 74.5 | 63.9732 | 73.2731 | 9.2999 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/20/20XX 2:00:00 AM | 0.083333 | 2 | 64.5 | 75 | 63.0587 | 72.2236 | 9.1649 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/20/20XX 3:00:00 AM | 0.125 | 2 | 63.6 | 76.4 | 61.0441 | 69.912 | 8.8679 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/20/20XX 4:00:00 AM | 0.16667 | 2 | 63.5 | 76.5 | 60.8239 | 69.6593 | 8.8354 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/20/20XX 5:00:00 AM | 0.20833 | 2 | 63 | 76.3 | 59.7337 | 68.4087 | 8.6749 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/20/20XX 6:00:00 AM | 0.25 | 2 | 63.1 | 75.3 | 59.9503 | 68.6572 | 8.7068 | 70 | 63.1 |  | 63.1 | 64.565 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 64.565 | 16.7443 | 398514.8711 | 33.2096 | 33.2096 | 58.7246 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 64.565 | 16.7443 | 398514.8711 | 33.2096 | 33.2096 | 58.7246 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 64.565 | 16.7443 | 398514.8711 | 33.2096 | 33.2096 | 58.7246 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 64.565 | 16.7443 | 398514.8711 | 33.2096 | 33.2096 | 58.7246 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 64.565 | 16.7443 | 398514.8711 | 33.2096 | 33.2096 | 58.7246 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 64.565 | 16.7443 | 398514.8711 | 33.2096 | 33.2096 | 58.7246 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 64.565 | 16.7443 | 398514.8711 | 33.2096 | 33.2096 | 58.7246 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 64.565 | 16.7443 | 398514.8711 | 33.2096 | 33.2096 | 58.7246 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 64.565 | 16.7443 | 398514.8711 | 33.2096 | 33.2096 | 58.7246 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 64.565 | 16.7443 | 398514.8711 | 33.2096 | 33.2096 | 58.7246 | 65 | 75 | 25.1987 | 26 | 75.3
9/20/20XX 7:00:00 AM | 0.29167 | 2 | 63.7 | 74.9 | 61.265 | 70.1655 | 8.9004 | 70 | 63.7 |  | 63.7 | 65.6262 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 65.6262 | 17.8056 | 423773.4719 | 35.3145 | 35.3145 | 62.7195 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 65.6262 | 17.8056 | 423773.4719 | 35.3145 | 35.3145 | 62.7195 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 65.6262 | 17.8056 | 423773.4719 | 35.3145 | 35.3145 | 62.7195 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 65.6262 | 17.8056 | 423773.4719 | 35.3145 | 35.3145 | 62.7195 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 65.6262 | 17.8056 | 423773.4719 | 35.3145 | 35.3145 | 62.7195 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 65.6262 | 17.8056 | 423773.4719 | 35.3145 | 35.3145 | 62.7195 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 65.6262 | 17.8056 | 423773.4719 | 35.3145 | 35.3145 | 62.7195 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 65.6262 | 17.8056 | 423773.4719 | 35.3145 | 35.3145 | 62.7195 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 65.6262 | 17.8056 | 423773.4719 | 35.3145 | 35.3145 | 62.7195 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 65.6262 | 17.8056 | 423773.4719 | 35.3145 | 35.3145 | 62.7195 | 65 | 75 | 25.5104 | 26 | 74.9
9/20/20XX 8:00:00 AM | 0.33333 | 2 | 65.4 | 69.2 | 55.7238 | 65.1332 | 9.4094 | 60 | 65.4 |  | 65.4 | 64.3805 | 0.1 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 62.7975 | 14.9769 | 356449.8067 | 29.7042 | 29.7042 | 86.8452 | 0.2 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 62.9734 | 15.1528 | 360635.8133 | 30.053 | 30.053 | 84.485 | 0.3 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 63.1493 | 15.3286 | 364821.82 | 30.4018 | 30.4018 | 82.1248 | 0.4 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 63.3252 | 15.5045 | 369007.8266 | 30.7507 | 30.7507 | 79.7647 | 0.5 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 63.501 | 15.6804 | 373193.8333 | 31.0995 | 31.0995 | 77.4045 | 0.6 | 68.84 | 13.84 | 523152 | 43.596 | 43.596 | 63.6769 | 15.8563 | 377379.84 | 31.4483 | 31.4483 | 75.0443 | 0.7 | 67.98 | 12.98 | 490644 | 40.887 | 40.887 | 63.8528 | 16.0322 | 381565.8466 | 31.7972 | 31.7972 | 72.6842 | 0.8 | 67.12 | 12.12 | 458136 | 38.178 | 38.178 | 64.0287 | 16.2081 | 385751.8533 | 32.146 | 32.146 | 70.324 | 0.9 | 66.26 | 11.26 | 425628 | 35.469 | 35.469 | 64.2046 | 16.3839 | 389937.86 | 32.4948 | 32.4948 | 67.9638 | 1 | 65.4 | 10.4 | 393120 | 32.76 | 32.76 | 64.3805 | 16.5598 | 394123.8666 | 32.8437 | 32.8437 | 65.6037 | 65 | 70 | 25.7313 | 26 | 69.2
9/20/20XX 9:00:00 AM | 0.375 | 2 | 66.7 | 67.2 | 58.3702 | 68.238 | 9.8678 | 60 | 66.7 |  | 66.7 | 65.475 | 0.1 | 73.27 | 18.27 | 690606 | 57.5505 | 57.5505 | 62.907 | 15.0863 | 359054.9059 | 29.9212 | 29.9212 | 87.4717 | 0.2 | 72.54 | 17.54 | 663012 | 55.251 | 55.251 | 63.1923 | 15.3717 | 365846.0118 | 30.4872 | 30.4872 | 85.7382 | 0.3 | 71.81 | 16.81 | 635418 | 52.9515 | 52.9515 | 63.4777 | 15.657 | 372637.1177 | 31.0531 | 31.0531 | 84.0046 | 0.4 | 71.08 | 16.08 | 607824 | 50.652 | 50.652 | 63.763 | 15.9424 | 379428.2236 | 31.619 | 31.619 | 82.271 | 0.5 | 70.35 | 15.35 | 580230 | 48.3525 | 48.3525 | 64.0483 | 16.2277 | 386219.3296 | 32.1849 | 32.1849 | 80.5374 | 0.6 | 69.62 | 14.62 | 552636 | 46.053 | 46.053 | 64.3337 | 16.513 | 393010.4355 | 32.7509 | 32.7509 | 78.8039 | 0.7 | 68.89 | 13.89 | 525042 | 43.7535 | 43.7535 | 64.619 | 16.7984 | 399801.5414 | 33.3168 | 33.3168 | 77.0703 | 0.8 | 68.16 | 13.16 | 497448 | 41.454 | 41.454 | 64.9044 | 17.0837 | 406592.6473 | 33.8827 | 33.8827 | 75.3367 | 0.9 | 67.43 | 12.43 | 469854 | 39.1545 | 39.1545 | 65.1897 | 17.3691 | 413383.7532 | 34.4486 | 34.4486 | 73.6031 | 1 | 66.7 | 11.7 | 442260 | 36.855 | 36.855 | 65.475 | 17.6544 | 420174.8591 | 35.0146 | 35.0146 | 71.8696 | 65 | 65 | 26.2194 | 26 | 67.2
9/20/20XX 10:00:00 AM | 0.41667 | 2 | 68.6 | 65.3 | 62.4397 | 73.0131 | 10.5734 | 60 | 68.6 |  | 68.6 | 68.0436 | 0.1 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 63.1638 | 15.3432 | 365168.1412 | 30.4307 | 30.4307 | 88.5797 | 0.2 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 63.706 | 15.8854 | 378072.4824 | 31.506 | 31.506 | 87.954 | 0.3 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 64.2482 | 16.4276 | 390976.8236 | 32.5814 | 32.5814 | 87.3284 | 0.4 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 64.7904 | 16.9698 | 403881.1648 | 33.6568 | 33.6568 | 86.7028 | 0.5 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 65.3326 | 17.512 | 416785.506 | 34.7321 | 34.7321 | 86.0771 | 0.6 | 70.76 | 15.76 | 595728 | 49.644 | 49.644 | 65.8748 | 18.0542 | 429689.8472 | 35.8075 | 35.8075 | 85.4515 | 0.7 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 66.417 | 18.5964 | 442594.1884 | 36.8828 | 36.8828 | 84.8258 | 0.8 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 66.9592 | 19.1386 | 455498.5296 | 37.9582 | 37.9582 | 84.2002 | 0.9 | 69.14 | 14.14 | 534492 | 44.541 | 44.541 | 67.5014 | 19.6808 | 468402.8708 | 39.0336 | 39.0336 | 83.5746 | 1 | 68.6 | 13.6 | 514080 | 42.84 | 42.84 | 68.0436 | 20.223 | 481307.212 | 40.1089 | 40.1089 | 82.9489 | 70 | 65 | 27.0842 | 28 | 65.3
9/20/20XX 11:00:00 AM | 0.45833 | 2 | 70.8 | 60.8 | 67.4628 | 78.908 | 11.4452 | 60 | 70.8 |  | 70.8 | 68.3784 | 0.1 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 63.1973 | 15.3767 | 365964.8666 | 30.4971 | 30.4971 | 89.3391 | 0.2 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 63.773 | 15.9524 | 379665.9332 | 31.6388 | 31.6388 | 89.4728 | 0.3 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 64.3487 | 16.528 | 393366.9997 | 32.7806 | 32.7806 | 89.6066 | 0.4 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 64.9243 | 17.1037 | 407068.0663 | 33.9223 | 33.9223 | 89.7403 | 0.5 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 65.5 | 17.6794 | 420769.1329 | 35.0641 | 35.0641 | 89.8741 | 0.6 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 66.0757 | 18.2551 | 434470.1995 | 36.2058 | 36.2058 | 90.0078 | 0.7 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 66.6514 | 18.8307 | 448171.266 | 37.3476 | 37.3476 | 90.1416 | 0.8 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 67.227 | 19.4064 | 461872.3326 | 38.4894 | 38.4894 | 90.2754 | 0.9 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 67.8027 | 19.9821 | 475573.3992 | 39.6311 | 39.6311 | 90.4091 | 1 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 68.3784 | 20.5578 | 489274.4658 | 40.7729 | 40.7729 | 90.5429 | 70 | 60 | 27.674 | 28 | 60.8
9/20/20XX 12:00:00 PM | 0.5 | 2 | 72.9 | 57.6 | 60.2904 | 72.5823 | 12.2919 | 50 | 72.9 |  | 72.9 | 69.6323 | 0.1 | 73.89 | 18.89 | 714042 | 59.5035 | 59.5035 | 63.3227 | 15.5021 | 368949.0726 | 30.7458 | 30.7458 | 90.2493 | 0.2 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 64.0238 | 16.2031 | 385634.3451 | 32.1362 | 32.1362 | 91.2932 | 0.3 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 64.7248 | 16.9042 | 402319.6177 | 33.5266 | 33.5266 | 92.3371 | 0.4 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 65.4259 | 17.6052 | 419004.8902 | 34.9171 | 34.9171 | 93.3811 | 0.5 | 73.45 | 18.45 | 697410 | 58.1175 | 58.1175 | 66.1269 | 18.3063 | 435690.1628 | 36.3075 | 36.3075 | 94.425 | 0.6 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 66.828 | 19.0074 | 452375.4353 | 37.698 | 37.698 | 95.469 | 0.7 | 73.23 | 18.23 | 689094 | 57.4245 | 57.4245 | 67.5291 | 19.7084 | 469060.7079 | 39.0884 | 39.0884 | 96.5129 | 0.8 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 68.2301 | 20.4095 | 485745.9804 | 40.4788 | 40.4788 | 97.5568 | 0.9 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 68.9312 | 21.1106 | 502431.253 | 41.8693 | 41.8693 | 98.6008 | 1 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 69.6323 | 21.8116 | 519116.5255 | 43.2597 | 43.2597 | 99.6447 | 75 | 60 | 28.3831 | 28 | 57.6
9/20/20XX 1:00:00 PM | 0.54167 | 2 | 73.3 | 56 | 61.1294 | 73.5946 | 12.4652 | 50 | 73.3 |  | 73.3 | 68.6085 | 0.1 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 63.2203 | 15.3997 | 366512.5181 | 30.5427 | 30.5427 | 90.1722 | 0.2 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 63.819 | 15.9984 | 380761.2362 | 31.7301 | 31.7301 | 91.1391 | 0.3 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 64.4177 | 16.5971 | 395009.9543 | 32.9175 | 32.9175 | 92.106 | 0.4 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 65.0164 | 17.1957 | 409258.6724 | 34.1049 | 34.1049 | 93.0729 | 0.5 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 65.6151 | 17.7944 | 423507.3905 | 35.2923 | 35.2923 | 94.0398 | 0.6 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 66.2137 | 18.3931 | 437756.1085 | 36.4797 | 36.4797 | 95.0067 | 0.7 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 66.8124 | 18.9918 | 452004.8266 | 37.6671 | 37.6671 | 95.9736 | 0.8 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 67.4111 | 19.5905 | 466253.5447 | 38.8545 | 38.8545 | 96.9405 | 0.9 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 68.0098 | 20.1892 | 480502.2628 | 40.0419 | 40.0419 | 97.9074 | 1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 68.6085 | 20.7879 | 494750.9809 | 41.2292 | 41.2292 | 98.8742 | 75 | 55 | 28.3208 | 28 | 56
9/20/20XX 2:00:00 PM | 0.58333 | 2 | 73.8 | 55.3 | 62.1921 | 74.8769 | 12.6847 | 50 | 73.8 |  | 73.8 | 68.9151 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 63.251 | 15.4303 | 367242.1452 | 30.6035 | 30.6035 | 90.3905 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 63.8803 | 16.0597 | 382220.4904 | 31.8517 | 31.8517 | 91.5757 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 64.5097 | 16.689 | 397198.8356 | 33.0999 | 33.0999 | 92.7609 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 65.139 | 17.3184 | 412177.1808 | 34.3481 | 34.3481 | 93.9461 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 65.7683 | 17.9477 | 427155.526 | 35.5963 | 35.5963 | 95.1313 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 66.3977 | 18.5771 | 442133.8712 | 36.8445 | 36.8445 | 96.3165 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 67.027 | 19.2064 | 457112.2164 | 38.0927 | 38.0927 | 97.5017 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 67.6564 | 19.8357 | 472090.5616 | 39.3409 | 39.3409 | 98.6869 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 68.2857 | 20.4651 | 487068.9067 | 40.5891 | 40.5891 | 99.8721 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 68.9151 | 21.0944 | 502047.2519 | 41.8373 | 41.8373 | 101.0573 | 75 | 55 | 28.4909 | 28 | 55.3
9/20/20XX 3:00:00 PM | 0.625 | 2 | 73.2 | 56.8 | 60.9187 | 73.3404 | 12.4216 | 50 | 73.2 |  | 73.2 | 69.3654 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 63.296 | 15.4754 | 368314.049 | 30.6928 | 30.6928 | 90.2908 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 63.9704 | 16.1498 | 384364.2979 | 32.0304 | 32.0304 | 91.3764 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 64.6448 | 16.8241 | 400414.5469 | 33.3679 | 33.3679 | 92.4619 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 65.3192 | 17.4985 | 416464.7958 | 34.7054 | 34.7054 | 93.5474 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 65.9935 | 18.1729 | 432515.0448 | 36.0429 | 36.0429 | 94.6329 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 66.6679 | 18.8473 | 448565.2937 | 37.3804 | 37.3804 | 95.7184 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 67.3423 | 19.5217 | 464615.5427 | 38.718 | 38.718 | 96.804 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 68.0167 | 20.196 | 480665.7916 | 40.0555 | 40.0555 | 97.8895 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 68.6911 | 20.8704 | 496716.0406 | 41.393 | 41.393 | 98.975 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 69.3654 | 21.5448 | 512766.2896 | 42.7305 | 42.7305 | 100.0605 | 75 | 55 | 28.4147 | 28 | 56.8
9/20/20XX 4:00:00 PM | 0.66667 | 2 | 71.9 | 58.4 | 58.2361 | 70.104 | 11.8679 | 50 | 71.9 |  | 71.9 | 68.2051 | 0.1 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 63.18 | 15.3593 | 365552.5261 | 30.4627 | 30.4627 | 89.6512 | 0.2 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 63.7383 | 15.9177 | 378841.2521 | 31.5701 | 31.5701 | 90.0971 | 0.3 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 64.2967 | 16.476 | 392129.9782 | 32.6775 | 32.6775 | 90.543 | 0.4 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 64.855 | 17.0344 | 405418.7043 | 33.7849 | 33.7849 | 90.9889 | 0.5 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 65.4134 | 17.5927 | 418707.4303 | 34.8923 | 34.8923 | 91.4348 | 0.6 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 65.9717 | 18.1511 | 431996.1564 | 35.9997 | 35.9997 | 91.8807 | 0.7 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 66.5301 | 18.7094 | 445284.8825 | 37.1071 | 37.1071 | 92.3266 | 0.8 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 67.0884 | 19.2678 | 458573.6085 | 38.2145 | 38.2145 | 92.7725 | 0.9 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 67.6468 | 19.8261 | 471862.3346 | 39.3219 | 39.3219 | 93.2184 | 1 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 68.2051 | 20.3845 | 485151.0607 | 40.4293 | 40.4293 | 93.6643 | 70 | 60 | 27.9156 | 28 | 58.4
9/20/20XX 5:00:00 PM | 0.70833 | 2 | 71 | 59.4 | 56.4392 | 67.9365 | 11.4973 | 50 | 71 |  | 71 | 67.2466 | 0.1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 63.0841 | 15.2635 | 363271.2622 | 30.2726 | 30.2726 | 89.1776 | 0.2 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 63.5466 | 15.726 | 374278.7243 | 31.1899 | 31.1899 | 89.1499 | 0.3 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 64.0091 | 16.1885 | 385286.1865 | 32.1072 | 32.1072 | 89.1222 | 0.4 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 64.4716 | 16.651 | 396293.6487 | 33.0245 | 33.0245 | 89.0945 | 0.5 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 64.9341 | 17.1135 | 407301.1108 | 33.9418 | 33.9418 | 89.0668 | 0.6 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 65.3966 | 17.576 | 418308.573 | 34.859 | 34.859 | 89.039 | 0.7 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 65.8591 | 18.0385 | 429316.0352 | 35.7763 | 35.7763 | 89.0113 | 0.8 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 66.3216 | 18.501 | 440323.4973 | 36.6936 | 36.6936 | 88.9836 | 0.9 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 66.7841 | 18.9635 | 451330.9595 | 37.6109 | 37.6109 | 88.9559 | 1 | 71 | 16 | 604800 | 50.4 | 50.4 | 67.2466 | 19.426 | 462338.4217 | 38.5282 | 38.5282 | 88.9282 | 70 | 60 | 27.546 | 28 | 59.4
9/20/20XX 6:00:00 PM | 0.75 | 2 | 69.4 | 64 | 64.2269 | 75.1104 | 10.8835 | 60 | 69.4 |  | 69.4 | 68.5803 | 0.1 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 63.2175 | 15.3969 | 366445.5172 | 30.5371 | 30.5371 | 88.9381 | 0.2 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 63.8134 | 15.9927 | 380627.2344 | 31.7189 | 31.7189 | 88.6709 | 0.3 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 64.4092 | 16.5886 | 394808.9516 | 32.9007 | 32.9007 | 88.4037 | 0.4 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 65.0051 | 17.1845 | 408990.6688 | 34.0826 | 34.0826 | 88.1366 | 0.5 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 65.601 | 17.7804 | 423172.386 | 35.2644 | 35.2644 | 87.8694 | 0.6 | 71.24 | 16.24 | 613872 | 51.156 | 51.156 | 66.1969 | 18.3762 | 437354.1032 | 36.4462 | 36.4462 | 87.6022 | 0.7 | 70.78 | 15.78 | 596484 | 49.707 | 49.707 | 66.7927 | 18.9721 | 451535.8204 | 37.628 | 37.628 | 87.335 | 0.8 | 70.32 | 15.32 | 579096 | 48.258 | 48.258 | 67.3886 | 19.568 | 465717.5377 | 38.8098 | 38.8098 | 87.0678 | 0.9 | 69.86 | 14.86 | 561708 | 46.809 | 46.809 | 67.9845 | 20.1638 | 479899.2549 | 39.9916 | 39.9916 | 86.8006 | 1 | 69.4 | 14.4 | 544320 | 45.36 | 45.36 | 68.5803 | 20.7597 | 494080.9721 | 41.1734 | 41.1734 | 86.5334 | 70 | 65 | 27.3634 | 28 | 64
9/20/20XX 7:00:00 PM | 0.79167 | 2 | 68.4 | 67.1 | 61.9998 | 72.4969 | 10.4971 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/20/20XX 8:00:00 PM | 0.83333 | 2 | 68 | 67.3 | 61.1282 | 71.4742 | 10.346 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/20/20XX 9:00:00 PM | 0.875 | 2 | 67.6 | 68.1 | 60.2675 | 70.4642 | 10.1967 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/20/20XX 10:00:00 PM | 0.91667 | 2 | 66.8 | 70.9 | 68.4823 | 78.4493 | 9.967 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/20/20XX 11:00:00 PM | 0.95833 | 2 | 66.5 | 71 | 67.7519 | 77.6107 | 9.8588 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/20/20XX 12:00:00 AM | 0 | 3 | 66 | 71.8 | 66.5501 | 76.231 | 9.6809 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/21/20XX 1:00:00 AM | 0.041667 | 3 | 65.6 | 73.5 | 65.6025 | 75.1431 | 9.5407 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/21/20XX 2:00:00 AM | 0.083333 | 3 | 65 | 74.7 | 64.2037 | 73.5377 | 9.3339 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/21/20XX 3:00:00 AM | 0.125 | 3 | 64.7 | 75.3 | 63.5145 | 72.7466 | 9.2322 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/21/20XX 4:00:00 AM | 0.16667 | 3 | 63.6 | 78.1 | 61.0441 | 69.912 | 8.8679 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/21/20XX 5:00:00 AM | 0.20833 | 3 | 63.4 | 78.9 | 60.6044 | 69.4076 | 8.8031 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/21/20XX 6:00:00 AM | 0.25 | 3 | 63.5 | 79.1 | 60.8239 | 69.6593 | 8.8354 | 70 | 63.5 |  | 63.5 | 68.8642 | 1 | 63.5 | 8.5 | 321300 | 26.775 | 26.775 | 68.8642 | 21.0435 | 500835.9715 | 41.7363 | 41.7363 | 68.5113 | 1 | 63.5 | 8.5 | 321300 | 26.775 | 26.775 | 68.8642 | 21.0435 | 500835.9715 | 41.7363 | 41.7363 | 68.5113 | 1 | 63.5 | 8.5 | 321300 | 26.775 | 26.775 | 68.8642 | 21.0435 | 500835.9715 | 41.7363 | 41.7363 | 68.5113 | 1 | 63.5 | 8.5 | 321300 | 26.775 | 26.775 | 68.8642 | 21.0435 | 500835.9715 | 41.7363 | 41.7363 | 68.5113 | 1 | 63.5 | 8.5 | 321300 | 26.775 | 26.775 | 68.8642 | 21.0435 | 500835.9715 | 41.7363 | 41.7363 | 68.5113 | 1 | 63.5 | 8.5 | 321300 | 26.775 | 26.775 | 68.8642 | 21.0435 | 500835.9715 | 41.7363 | 41.7363 | 68.5113 | 1 | 63.5 | 8.5 | 321300 | 26.775 | 26.775 | 68.8642 | 21.0435 | 500835.9715 | 41.7363 | 41.7363 | 68.5113 | 1 | 63.5 | 8.5 | 321300 | 26.775 | 26.775 | 68.8642 | 21.0435 | 500835.9715 | 41.7363 | 41.7363 | 68.5113 | 1 | 63.5 | 8.5 | 321300 | 26.775 | 26.775 | 68.8642 | 21.0435 | 500835.9715 | 41.7363 | 41.7363 | 68.5113 | 1 | 63.5 | 8.5 | 321300 | 26.775 | 26.775 | 68.8642 | 21.0435 | 500835.9715 | 41.7363 | 41.7363 | 68.5113 | 65 | 80 | 25.9659 | 26 | 79.1
9/21/20XX 7:00:00 AM | 0.29167 | 3 | 64.6 | 76.7 | 63.2862 | 72.4847 | 9.1985 | 70 | 64.6 |  | 64.6 | 69.4492 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 69.4492 | 21.6286 | 514759.8655 | 42.8967 | 42.8967 | 73.1367 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 69.4492 | 21.6286 | 514759.8655 | 42.8967 | 42.8967 | 73.1367 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 69.4492 | 21.6286 | 514759.8655 | 42.8967 | 42.8967 | 73.1367 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 69.4492 | 21.6286 | 514759.8655 | 42.8967 | 42.8967 | 73.1367 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 69.4492 | 21.6286 | 514759.8655 | 42.8967 | 42.8967 | 73.1367 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 69.4492 | 21.6286 | 514759.8655 | 42.8967 | 42.8967 | 73.1367 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 69.4492 | 21.6286 | 514759.8655 | 42.8967 | 42.8967 | 73.1367 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 69.4492 | 21.6286 | 514759.8655 | 42.8967 | 42.8967 | 73.1367 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 69.4492 | 21.6286 | 514759.8655 | 42.8967 | 42.8967 | 73.1367 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 69.4492 | 21.6286 | 514759.8655 | 42.8967 | 42.8967 | 73.1367 | 65 | 75 | 26.3259 | 26 | 76.7
9/21/20XX 8:00:00 AM | 0.33333 | 3 | 66.1 | 73.3 | 66.7889 | 76.5051 | 9.7162 | 70 | 66.1 |  | 66.1 | 69.9953 | 0.1 | 73.21 | 18.21 | 688338 | 57.3615 | 57.3615 | 63.359 | 15.5384 | 369813.1027 | 30.8178 | 30.8178 | 88.1793 | 0.2 | 72.42 | 17.42 | 658476 | 54.873 | 54.873 | 64.0964 | 16.2757 | 387362.4053 | 32.2802 | 32.2802 | 87.1532 | 0.3 | 71.63 | 16.63 | 628614 | 52.3845 | 52.3845 | 64.8337 | 17.0131 | 404911.708 | 33.7426 | 33.7426 | 86.1271 | 0.4 | 70.84 | 15.84 | 598752 | 49.896 | 49.896 | 65.5711 | 17.7505 | 422461.0107 | 35.2051 | 35.2051 | 85.1011 | 0.5 | 70.05 | 15.05 | 568890 | 47.4075 | 47.4075 | 66.3085 | 18.4878 | 440010.3133 | 36.6675 | 36.6675 | 84.075 | 0.6 | 69.26 | 14.26 | 539028 | 44.919 | 44.919 | 67.0458 | 19.2252 | 457559.616 | 38.13 | 38.13 | 83.049 | 0.7 | 68.47 | 13.47 | 509166 | 42.4305 | 42.4305 | 67.7832 | 19.9626 | 475108.9186 | 39.5924 | 39.5924 | 82.0229 | 0.8 | 67.68 | 12.68 | 479304 | 39.942 | 39.942 | 68.5206 | 20.6999 | 492658.2213 | 41.0549 | 41.0549 | 80.9969 | 0.9 | 66.89 | 11.89 | 449442 | 37.4535 | 37.4535 | 69.2579 | 21.4373 | 510207.524 | 42.5173 | 42.5173 | 79.9708 | 1 | 66.1 | 11.1 | 419580 | 34.965 | 34.965 | 69.9953 | 22.1747 | 527756.8266 | 43.9797 | 43.9797 | 78.9447 | 65 | 75 | 26.7777 | 26 | 73.3
9/21/20XX 9:00:00 AM | 0.375 | 3 | 67.7 | 69 | 60.4817 | 70.7155 | 10.2338 | 60 | 67.7 |  | 67.7 | 69.6921 | 0.1 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 63.3287 | 15.5081 | 369091.6251 | 30.7576 | 30.7576 | 88.6231 | 0.2 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 64.0357 | 16.2151 | 385919.4502 | 32.16 | 32.16 | 88.041 | 0.3 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 64.7428 | 16.9222 | 402747.2754 | 33.5623 | 33.5623 | 87.4588 | 0.4 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 65.4498 | 17.6292 | 419575.1005 | 34.9646 | 34.9646 | 86.8766 | 0.5 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 66.1569 | 18.3363 | 436402.9256 | 36.3669 | 36.3669 | 86.2944 | 0.6 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 66.8639 | 19.0433 | 453230.7507 | 37.7692 | 37.7692 | 85.7122 | 0.7 | 69.59 | 14.59 | 551502 | 45.9585 | 45.9585 | 67.571 | 19.7504 | 470058.5758 | 39.1715 | 39.1715 | 85.13 | 0.8 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 68.278 | 20.4574 | 486886.401 | 40.5739 | 40.5739 | 84.5479 | 0.9 | 68.33 | 13.33 | 503874 | 41.9895 | 41.9895 | 68.9851 | 21.1645 | 503714.2261 | 41.9762 | 41.9762 | 83.9657 | 1 | 67.7 | 12.7 | 480060 | 40.005 | 40.005 | 69.6921 | 21.8715 | 520542.0512 | 43.3785 | 43.3785 | 83.3835 | 70 | 70 | 27.1215 | 28 | 69
9/21/20XX 10:00:00 AM | 0.41667 | 3 | 69.7 | 64.9 | 64.9086 | 75.9105 | 11.0018 | 60 | 69.7 |  | 69.7 | 70.2995 | 0.1 | 73.57 | 18.57 | 701946 | 58.4955 | 58.4955 | 63.3894 | 15.5688 | 370537.213 | 30.8781 | 30.8781 | 89.3736 | 0.2 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 64.1572 | 16.3366 | 388810.6261 | 32.4009 | 32.4009 | 89.5419 | 0.3 | 72.71 | 17.71 | 669438 | 55.7865 | 55.7865 | 64.925 | 17.1044 | 407084.0391 | 33.9237 | 33.9237 | 89.7102 | 0.4 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 65.6928 | 17.8722 | 425357.4521 | 35.4465 | 35.4465 | 89.8785 | 0.5 | 71.85 | 16.85 | 636930 | 53.0775 | 53.0775 | 66.4606 | 18.64 | 443630.8652 | 36.9692 | 36.9692 | 90.0467 | 0.6 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 67.2284 | 19.4077 | 461904.2782 | 38.492 | 38.492 | 90.215 | 0.7 | 70.99 | 15.99 | 604422 | 50.3685 | 50.3685 | 67.9962 | 20.1755 | 480177.6912 | 40.0148 | 40.0148 | 90.3833 | 0.8 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 68.764 | 20.9433 | 498451.1043 | 41.5376 | 41.5376 | 90.5516 | 0.9 | 70.13 | 15.13 | 571914 | 47.6595 | 47.6595 | 69.5317 | 21.7111 | 516724.5173 | 43.0604 | 43.0604 | 90.7199 | 1 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 70.2995 | 22.4789 | 534997.9303 | 44.5832 | 44.5832 | 90.8882 | 70 | 65 | 27.7052 | 28 | 64.9
9/21/20XX 11:00:00 AM | 0.45833 | 3 | 72.2 | 60.3 | 70.8397 | 82.8715 | 12.0318 | 60 | 72.2 |  | 72.2 | 71.2006 | 0.1 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 63.4795 | 15.6589 | 372681.848 | 31.0568 | 31.0568 | 90.3398 | 0.2 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 64.3374 | 16.5168 | 393099.896 | 32.7583 | 32.7583 | 91.4743 | 0.3 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 65.1953 | 17.3747 | 413517.9439 | 34.4598 | 34.4598 | 92.6088 | 0.4 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 66.0532 | 18.2326 | 433935.9919 | 36.1613 | 36.1613 | 93.7433 | 0.5 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 66.9111 | 19.0905 | 454354.0399 | 37.8628 | 37.8628 | 94.8778 | 0.6 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 67.769 | 19.9484 | 474772.0879 | 39.5643 | 39.5643 | 96.0123 | 0.7 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 68.6269 | 20.8063 | 495190.1358 | 41.2658 | 41.2658 | 97.1468 | 0.8 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 69.4848 | 21.6642 | 515608.1838 | 42.9673 | 42.9673 | 98.2813 | 0.9 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 70.3427 | 22.5221 | 536026.2318 | 44.6689 | 44.6689 | 99.4159 | 1 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 71.2006 | 23.38 | 556444.2798 | 46.3704 | 46.3704 | 100.5504 | 70 | 60 | 28.4572 | 28 | 60.3
9/21/20XX 12:00:00 PM | 0.5 | 3 | 73.2 | 58 | 60.9187 | 73.3404 | 12.4216 | 50 | 73.2 |  | 73.2 | 70.856 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 63.4451 | 15.6244 | 371861.6698 | 30.9885 | 30.9885 | 90.5865 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 64.2685 | 16.4479 | 391459.5396 | 32.6216 | 32.6216 | 91.9676 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 65.092 | 17.2713 | 411057.4095 | 34.2548 | 34.2548 | 93.3488 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 65.9154 | 18.0948 | 430655.2793 | 35.8879 | 35.8879 | 94.7299 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 66.7388 | 18.9182 | 450253.1491 | 37.5211 | 37.5211 | 96.1111 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 67.5623 | 19.7416 | 469851.0189 | 39.1543 | 39.1543 | 97.4923 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 68.3857 | 20.5651 | 489448.8887 | 40.7874 | 40.7874 | 98.8734 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 69.2092 | 21.3885 | 509046.7585 | 42.4206 | 42.4206 | 100.2546 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 70.0326 | 22.212 | 528644.6284 | 44.0537 | 44.0537 | 101.6357 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 70.856 | 23.0354 | 548242.4982 | 45.6869 | 45.6869 | 103.0169 | 75 | 60 | 28.6478 | 28 | 58
9/21/20XX 1:00:00 PM | 0.54167 | 3 | 74.1 | 55.9 | 62.8373 | 75.6554 | 12.8181 | 50 | 74.1 |  | 74.1 | 70.4 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 63.3995 | 15.5788 | 370776.338 | 30.898 | 30.898 | 90.7795 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 64.1773 | 16.3567 | 389288.876 | 32.4407 | 32.4407 | 92.3537 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 64.9551 | 17.1345 | 407801.414 | 33.9835 | 33.9835 | 93.928 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 65.733 | 17.9124 | 426313.952 | 35.5262 | 35.5262 | 95.5022 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 66.5108 | 18.6902 | 444826.49 | 37.0689 | 37.0689 | 97.0764 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 67.2887 | 19.468 | 463339.028 | 38.6116 | 38.6116 | 98.6506 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 68.0665 | 20.2459 | 481851.566 | 40.1543 | 40.1543 | 100.2248 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 68.8443 | 21.0237 | 500364.104 | 41.697 | 41.697 | 101.799 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 69.6222 | 21.8015 | 518876.642 | 43.2397 | 43.2397 | 103.3732 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 70.4 | 22.5794 | 537389.18 | 44.7824 | 44.7824 | 104.9474 | 75 | 55 | 28.7965 | 28 | 55.9
9/21/20XX 2:00:00 PM | 0.58333 | 3 | 74.4 | 56.4 | 63.4882 | 76.4409 | 12.9527 | 50 | 74.4 |  | 74.4 | 71.7779 | 0.1 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 63.5373 | 15.7166 | 374055.7745 | 31.1713 | 31.1713 | 91.1473 | 0.2 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 64.4529 | 16.6323 | 395847.7489 | 32.9873 | 32.9873 | 93.0893 | 0.3 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.3685 | 17.5479 | 417639.7234 | 34.8033 | 34.8033 | 95.0313 | 0.4 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 66.2841 | 18.4635 | 439431.6979 | 36.6193 | 36.6193 | 96.9733 | 0.5 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 67.1998 | 19.3791 | 461223.6724 | 38.4353 | 38.4353 | 98.9153 | 0.6 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 68.1154 | 20.2948 | 483015.6468 | 40.2513 | 40.2513 | 100.8573 | 0.7 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 69.031 | 21.2104 | 504807.6213 | 42.0673 | 42.0673 | 102.7993 | 0.8 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 69.9467 | 22.126 | 526599.5958 | 43.8833 | 43.8833 | 104.7413 | 0.9 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 70.8623 | 23.0417 | 548391.5703 | 45.6993 | 45.6993 | 106.6833 | 1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 71.7779 | 23.9573 | 570183.5447 | 47.5153 | 47.5153 | 108.6253 | 75 | 55 | 29.0854 | 30 | 56.4
9/21/20XX 3:00:00 PM | 0.625 | 3 | 73.8 | 57.6 | 62.1921 | 74.8769 | 12.6847 | 50 | 73.8 |  | 73.8 | 71.8325 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 63.5427 | 15.7221 | 374185.7766 | 31.1821 | 31.1821 | 90.9691 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 64.4638 | 16.6432 | 396107.7532 | 33.009 | 33.009 | 92.733 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 65.3849 | 17.5643 | 418029.7298 | 34.8358 | 34.8358 | 94.4968 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 66.306 | 18.4854 | 439951.7064 | 36.6626 | 36.6626 | 96.2606 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 67.2271 | 19.4065 | 461873.683 | 38.4895 | 38.4895 | 98.0245 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 68.1482 | 20.3275 | 483795.6596 | 40.3163 | 40.3163 | 99.7883 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 69.0693 | 21.2486 | 505717.6362 | 42.1431 | 42.1431 | 101.5521 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 69.9904 | 22.1697 | 527639.6128 | 43.97 | 43.97 | 103.316 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 70.9115 | 23.0908 | 549561.5894 | 45.7968 | 45.7968 | 105.0798 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 71.8325 | 24.0119 | 571483.566 | 47.6236 | 47.6236 | 106.8436 | 75 | 60 | 28.9472 | 28 | 57.6
9/21/20XX 4:00:00 PM | 0.66667 | 3 | 73.3 | 57.7 | 61.1294 | 73.5946 | 12.4652 | 50 | 73.3 |  | 73.3 | 70.7276 | 0.1 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 63.4322 | 15.6116 | 371555.9219 | 30.963 | 30.963 | 90.5925 | 0.2 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 64.2428 | 16.4222 | 390848.0439 | 32.5707 | 32.5707 | 91.9797 | 0.3 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 65.0534 | 17.2328 | 410140.1658 | 34.1783 | 34.1783 | 93.3668 | 0.4 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 65.864 | 18.0434 | 429432.2878 | 35.786 | 35.786 | 94.754 | 0.5 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 66.6746 | 18.854 | 448724.4097 | 37.3937 | 37.3937 | 96.1412 | 0.6 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 67.4852 | 19.6646 | 468016.5317 | 39.0014 | 39.0014 | 97.5284 | 0.7 | 73.51 | 18.51 | 699678 | 58.3065 | 58.3065 | 68.2958 | 20.4752 | 487308.6536 | 40.6091 | 40.6091 | 98.9156 | 0.8 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 69.1064 | 21.2857 | 506600.7755 | 42.2167 | 42.2167 | 100.3027 | 0.9 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 69.917 | 22.0963 | 525892.8975 | 43.8244 | 43.8244 | 101.6899 | 1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 70.7276 | 22.9069 | 545185.0194 | 45.4321 | 45.4321 | 103.0771 | 75 | 60 | 28.6522 | 28 | 57.7
9/21/20XX 5:00:00 PM | 0.70833 | 3 | 72.3 | 61.1 | 71.0864 | 83.1611 | 12.0747 | 60 | 72.3 |  | 72.3 | 72.4146 | 0.1 | 73.83 | 18.83 | 711774 | 59.3145 | 59.3145 | 63.6009 | 15.7803 | 375571.0991 | 31.2976 | 31.2976 | 90.6121 | 0.2 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 64.5802 | 16.7596 | 398878.3981 | 33.2399 | 33.2399 | 92.0189 | 0.3 | 73.49 | 18.49 | 698922 | 58.2435 | 58.2435 | 65.5595 | 17.7389 | 422185.6972 | 35.1821 | 35.1821 | 93.4256 | 0.4 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 66.5388 | 18.7182 | 445492.9962 | 37.1244 | 37.1244 | 94.8324 | 0.5 | 73.15 | 18.15 | 686070 | 57.1725 | 57.1725 | 67.5181 | 19.6975 | 468800.2953 | 39.0667 | 39.0667 | 96.2392 | 0.6 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 68.4974 | 20.6768 | 492107.5943 | 41.009 | 41.009 | 97.646 | 0.7 | 72.81 | 17.81 | 673218 | 56.1015 | 56.1015 | 69.4767 | 21.6561 | 515414.8934 | 42.9512 | 42.9512 | 99.0527 | 0.8 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 70.456 | 22.6354 | 538722.1925 | 44.8935 | 44.8935 | 100.4595 | 0.9 | 72.47 | 17.47 | 660366 | 55.0305 | 55.0305 | 71.4353 | 23.6147 | 562029.4915 | 46.8358 | 46.8358 | 101.8663 | 1 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 72.4146 | 24.594 | 585336.7906 | 48.7781 | 48.7781 | 103.2731 | 70 | 60 | 28.6714 | 28 | 61.1
9/21/20XX 6:00:00 PM | 0.75 | 3 | 70.7 | 65.9 | 67.227 | 78.6313 | 11.4043 | 60 | 70.7 |  | 70.7 | 73.9555 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 63.755 | 15.9344 | 379238.4714 | 31.6032 | 31.6032 | 90.4137 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 64.8884 | 17.0678 | 406213.1428 | 33.8511 | 33.8511 | 91.6221 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 66.0218 | 18.2012 | 433187.8142 | 36.099 | 36.099 | 92.8305 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 67.1552 | 19.3346 | 460162.4856 | 38.3469 | 38.3469 | 94.0389 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 68.2886 | 20.4679 | 487137.157 | 40.5948 | 40.5948 | 95.2473 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 69.422 | 21.6013 | 514111.8284 | 42.8427 | 42.8427 | 96.4557 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 70.5554 | 22.7347 | 541086.4998 | 45.0905 | 45.0905 | 97.664 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 71.6887 | 23.8681 | 568061.1712 | 47.3384 | 47.3384 | 98.8724 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 72.8221 | 25.0015 | 595035.8426 | 49.5863 | 49.5863 | 100.0808 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 73.9555 | 26.1349 | 622010.514 | 51.8342 | 51.8342 | 101.2892 | 70 | 65 | 28.5207 | 28 | 65.9
9/21/20XX 7:00:00 PM | 0.79167 | 3 | 70 | 69.7 | 65.5967 | 76.7179 | 11.1212 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/21/20XX 8:00:00 PM | 0.83333 | 3 | 69.6 | 71.9 | 75.643 | 86.674 | 11.031 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/21/20XX 9:00:00 PM | 0.875 | 3 | 69 | 73.3 | 74.0553 | 84.8499 | 10.7946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/21/20XX 10:00:00 PM | 0.91667 | 3 | 68.7 | 74.3 | 73.2724 | 83.9506 | 10.6782 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/21/20XX 11:00:00 PM | 0.95833 | 3 | 68.4 | 75.3 | 72.4969 | 83.0598 | 10.5629 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/21/20XX 12:00:00 AM | 0 | 4 | 67.7 | 76.6 | 70.7155 | 81.0138 | 10.2983 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/22/20XX 1:00:00 AM | 0.041667 | 4 | 67.2 | 74.7 | 69.467 | 79.58 | 10.113 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/22/20XX 2:00:00 AM | 0.083333 | 4 | 67 | 73.9 | 68.973 | 79.0128 | 10.0398 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/22/20XX 3:00:00 AM | 0.125 | 4 | 66.2 | 74.9 | 67.0285 | 76.7802 | 9.7517 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/22/20XX 4:00:00 AM | 0.16667 | 4 | 65.9 | 76.4 | 66.3121 | 75.9577 | 9.6456 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/22/20XX 5:00:00 AM | 0.20833 | 4 | 65.6 | 76 | 65.6025 | 75.1431 | 9.5407 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/22/20XX 6:00:00 AM | 0.25 | 4 | 65.3 | 77.6 | 64.8997 | 74.3365 | 9.4368 | 70 | 65.3 |  | 65.3 | 72.0717 | 0.1 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 63.5666 | 15.746 | 374754.8767 | 31.2296 | 31.2296 | 88.3391 | 0.2 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 64.5116 | 16.691 | 397245.9534 | 33.1038 | 33.1038 | 87.4728 | 0.3 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 65.4566 | 17.636 | 419737.0301 | 34.9781 | 34.9781 | 86.6066 | 0.4 | 70.52 | 15.52 | 586656 | 48.888 | 48.888 | 66.4016 | 18.581 | 442228.1068 | 36.8523 | 36.8523 | 85.7403 | 0.5 | 69.65 | 14.65 | 553770 | 46.1475 | 46.1475 | 67.3466 | 19.526 | 464719.1835 | 38.7266 | 38.7266 | 84.8741 | 0.6 | 68.78 | 13.78 | 520884 | 43.407 | 43.407 | 68.2917 | 20.471 | 487210.2602 | 40.6009 | 40.6009 | 84.0079 | 0.7 | 67.91 | 12.91 | 487998 | 40.6665 | 40.6665 | 69.2367 | 21.416 | 509701.3369 | 42.4751 | 42.4751 | 83.1416 | 0.8 | 67.04 | 12.04 | 455112 | 37.926 | 37.926 | 70.1817 | 22.361 | 532192.4136 | 44.3494 | 44.3494 | 82.2754 | 0.9 | 66.17 | 11.17 | 422226 | 35.1855 | 35.1855 | 71.1267 | 23.306 | 554683.4903 | 46.2236 | 46.2236 | 81.4091 | 1 | 65.3 | 10.3 | 389340 | 32.445 | 32.445 | 72.0717 | 24.251 | 577174.567 | 48.0979 | 48.0979 | 80.5429 | 65 | 80 | 26.9057 | 26 | 77.6
9/22/20XX 7:00:00 AM | 0.29167 | 4 | 65.7 | 73.5 | 65.8382 | 75.4138 | 9.5755 | 70 | 65.7 |  | 65.7 | 69.1897 | 0.1 | 73.17 | 18.17 | 686826 | 57.2355 | 57.2355 | 63.2784 | 15.4578 | 367895.7628 | 30.658 | 30.658 | 87.8935 | 0.2 | 72.34 | 17.34 | 655452 | 54.621 | 54.621 | 63.9352 | 16.1146 | 383527.7256 | 31.9606 | 31.9606 | 86.5816 | 0.3 | 71.51 | 16.51 | 624078 | 52.0065 | 52.0065 | 64.592 | 16.7714 | 399159.6884 | 33.2633 | 33.2633 | 85.2698 | 0.4 | 70.68 | 15.68 | 592704 | 49.392 | 49.392 | 65.2489 | 17.4282 | 414791.6512 | 34.566 | 34.566 | 83.958 | 0.5 | 69.85 | 14.85 | 561330 | 46.7775 | 46.7775 | 65.9057 | 18.085 | 430423.614 | 35.8686 | 35.8686 | 82.6461 | 0.6 | 69.02 | 14.02 | 529956 | 44.163 | 44.163 | 66.5625 | 18.7418 | 446055.5768 | 37.1713 | 37.1713 | 81.3343 | 0.7 | 68.19 | 13.19 | 498582 | 41.5485 | 41.5485 | 67.2193 | 19.3986 | 461687.5397 | 38.474 | 38.474 | 80.0225 | 0.8 | 67.36 | 12.36 | 467208 | 38.934 | 38.934 | 67.8761 | 20.0554 | 477319.5025 | 39.7766 | 39.7766 | 78.7106 | 0.9 | 66.53 | 11.53 | 435834 | 36.3195 | 36.3195 | 68.5329 | 20.7122 | 492951.4653 | 41.0793 | 41.0793 | 77.3988 | 1 | 65.7 | 10.7 | 404460 | 33.705 | 33.705 | 69.1897 | 21.3691 | 508583.4281 | 42.382 | 42.382 | 76.087 | 65 | 75 | 26.5543 | 26 | 73.5
9/22/20XX 8:00:00 AM | 0.33333 | 4 | 66.8 | 69.6 | 58.5784 | 68.4823 | 9.9039 | 60 | 66.8 |  | 66.8 | 68.0861 | 0.1 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 63.1681 | 15.3474 | 365269.2305 | 30.4391 | 30.4391 | 88.0211 | 0.2 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 63.7145 | 15.8939 | 378274.661 | 31.5229 | 31.5229 | 86.8369 | 0.3 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 64.261 | 16.4403 | 391280.0915 | 32.6067 | 32.6067 | 85.6527 | 0.4 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 64.8074 | 16.9868 | 404285.522 | 33.6905 | 33.6905 | 84.4685 | 0.5 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 65.3539 | 17.5332 | 417290.9525 | 34.7742 | 34.7742 | 83.2842 | 0.6 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 65.9003 | 18.0797 | 430296.3829 | 35.858 | 35.858 | 82.1 | 0.7 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 66.4468 | 18.6261 | 443301.8134 | 36.9418 | 36.9418 | 80.9158 | 0.8 | 68.24 | 13.24 | 500472 | 41.706 | 41.706 | 66.9932 | 19.1726 | 456307.2439 | 38.0256 | 38.0256 | 79.7316 | 0.9 | 67.52 | 12.52 | 473256 | 39.438 | 39.438 | 67.5397 | 19.719 | 469312.6744 | 39.1094 | 39.1094 | 78.5474 | 1 | 66.8 | 11.8 | 446040 | 37.17 | 37.17 | 68.0861 | 20.2655 | 482318.1049 | 40.1932 | 40.1932 | 77.3632 | 65 | 70 | 26.651 | 26 | 69.6
9/22/20XX 9:00:00 AM | 0.375 | 4 | 68.8 | 63.8 | 62.8824 | 73.5326 | 10.6502 | 60 | 68.8 |  | 68.8 | 66.9294 | 0.1 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 63.0524 | 15.2318 | 362516.382 | 30.2097 | 30.2097 | 88.4217 | 0.2 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 63.4832 | 15.6626 | 372768.9639 | 31.0641 | 31.0641 | 87.6381 | 0.3 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 63.914 | 16.0933 | 383021.5459 | 31.9185 | 31.9185 | 86.8545 | 0.4 | 71.92 | 16.92 | 639576 | 53.298 | 53.298 | 64.3448 | 16.5241 | 393274.1278 | 32.7728 | 32.7728 | 86.0708 | 0.5 | 71.4 | 16.4 | 619920 | 51.66 | 51.66 | 64.7755 | 16.9549 | 403526.7098 | 33.6272 | 33.6272 | 85.2872 | 0.6 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 65.2063 | 17.3857 | 413779.2917 | 34.4816 | 34.4816 | 84.5036 | 0.7 | 70.36 | 15.36 | 580608 | 48.384 | 48.384 | 65.6371 | 17.8165 | 424031.8737 | 35.336 | 35.336 | 83.72 | 0.8 | 69.84 | 14.84 | 560952 | 46.746 | 46.746 | 66.0679 | 18.2472 | 434284.4556 | 36.1904 | 36.1904 | 82.9364 | 0.9 | 69.32 | 14.32 | 541296 | 45.108 | 45.108 | 66.4987 | 18.678 | 444537.0376 | 37.0448 | 37.0448 | 82.1528 | 1 | 68.8 | 13.8 | 521640 | 43.47 | 43.47 | 66.9294 | 19.1088 | 454789.6195 | 37.8991 | 37.8991 | 81.3691 | 70 | 65 | 26.9591 | 26 | 63.8
9/22/20XX 10:00:00 AM | 0.41667 | 4 | 70.7 | 59.4 | 55.851 | 67.227 | 11.376 | 50 | 70.7 |  | 70.7 | 66.5444 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 63.0139 | 15.1933 | 361600.0845 | 30.1333 | 30.1333 | 88.9438 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 63.4062 | 15.5856 | 370936.369 | 30.9114 | 30.9114 | 88.6824 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 63.7985 | 15.9778 | 380272.6536 | 31.6894 | 31.6894 | 88.4209 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 64.1908 | 16.3701 | 389608.9381 | 32.4674 | 32.4674 | 88.1594 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 64.583 | 16.7624 | 398945.2226 | 33.2454 | 33.2454 | 87.8979 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 64.9753 | 17.1547 | 408281.5071 | 34.0235 | 34.0235 | 87.6365 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 65.3676 | 17.547 | 417617.7916 | 34.8015 | 34.8015 | 87.375 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 65.7599 | 17.9392 | 426954.0761 | 35.5795 | 35.5795 | 87.1135 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 66.1522 | 18.3315 | 436290.3607 | 36.3575 | 36.3575 | 86.852 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 66.5444 | 18.7238 | 445626.6452 | 37.1356 | 37.1356 | 86.5906 | 70 | 60 | 27.363 | 28 | 59.4
9/22/20XX 11:00:00 AM | 0.45833 | 4 | 73.2 | 56.2 | 60.9187 | 73.3404 | 12.4216 | 50 | 73.2 |  | 73.2 | 68.6201 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 63.2215 | 15.4009 | 366540.2385 | 30.545 | 30.545 | 90.143 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 63.8213 | 16.0007 | 380816.677 | 31.7347 | 31.7347 | 91.0807 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 64.4212 | 16.6006 | 395093.1156 | 32.9244 | 32.9244 | 92.0184 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 65.021 | 17.2004 | 409369.5541 | 34.1141 | 34.1141 | 92.9561 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 65.6209 | 17.8003 | 423645.9926 | 35.3038 | 35.3038 | 93.8938 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 66.2207 | 18.4001 | 437922.4311 | 36.4935 | 36.4935 | 94.8315 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 66.8206 | 19 | 452198.8697 | 37.6832 | 37.6832 | 95.7692 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 67.4204 | 19.5998 | 466475.3082 | 38.8729 | 38.8729 | 96.7069 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 68.0203 | 20.1997 | 480751.7467 | 40.0626 | 40.0626 | 97.6446 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 68.6201 | 20.7995 | 495028.1852 | 41.2523 | 41.2523 | 98.5823 | 75 | 55 | 28.2982 | 28 | 56.2
9/22/20XX 12:00:00 PM | 0.5 | 4 | 73.7 | 56.8 | 61.9783 | 74.6189 | 12.6406 | 50 | 73.7 |  | 73.7 | 70.5739 | 0.1 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 63.4169 | 15.5962 | 371190.2415 | 30.9325 | 30.9325 | 90.688 | 0.2 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 64.2121 | 16.3915 | 390116.683 | 32.5097 | 32.5097 | 92.1707 | 0.3 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 65.0073 | 17.1867 | 409043.1245 | 34.0869 | 34.0869 | 93.6534 | 0.4 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 65.8025 | 17.9819 | 427969.5659 | 35.6641 | 35.6641 | 95.1361 | 0.5 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 66.5978 | 18.7771 | 446896.0074 | 37.2413 | 37.2413 | 96.6188 | 0.6 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 67.393 | 19.5724 | 465822.4489 | 38.8185 | 38.8185 | 98.1015 | 0.7 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 68.1882 | 20.3676 | 484748.8904 | 40.3957 | 40.3957 | 99.5842 | 0.8 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 68.9835 | 21.1628 | 503675.3319 | 41.9729 | 41.9729 | 101.0669 | 0.9 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 69.7787 | 21.9581 | 522601.7734 | 43.5501 | 43.5501 | 102.5496 | 1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 70.5739 | 22.7533 | 541528.2149 | 45.1274 | 45.1274 | 104.0324 | 75 | 55 | 28.7259 | 28 | 56.8
9/22/20XX 1:00:00 PM | 0.54167 | 4 | 75.4 | 52.4 | 65.6994 | 79.1095 | 13.4101 | 50 | 75.4 |  | 75.4 | 68.9178 | 0.1 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 63.2512 | 15.4306 | 367248.6424 | 30.6041 | 30.6041 | 90.8951 | 0.2 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 63.8809 | 16.0602 | 382233.4849 | 31.8528 | 31.8528 | 92.5848 | 0.3 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 64.5105 | 16.6898 | 397218.3273 | 33.1015 | 33.1015 | 94.2745 | 0.4 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 65.1401 | 17.3195 | 412203.1698 | 34.3503 | 34.3503 | 95.9643 | 0.5 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 65.7697 | 17.9491 | 427188.0122 | 35.599 | 35.599 | 97.654 | 0.6 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 66.3993 | 18.5787 | 442172.8547 | 36.8477 | 36.8477 | 99.3437 | 0.7 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 67.0289 | 19.2083 | 457157.6971 | 38.0965 | 38.0965 | 101.0335 | 0.8 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 67.6586 | 19.8379 | 472142.5395 | 39.3452 | 39.3452 | 102.7232 | 0.9 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 68.2882 | 20.4675 | 487127.382 | 40.5939 | 40.5939 | 104.4129 | 1 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 68.9178 | 21.0972 | 502112.2244 | 41.8427 | 41.8427 | 106.1027 | 75 | 50 | 28.8823 | 28 | 52.4
9/22/20XX 2:00:00 PM | 0.58333 | 4 | 75.5 | 52.6 | 65.924 | 79.3806 | 13.4566 | 50 | 75.5 |  | 75.5 | 69.4227 | 0.1 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 63.3017 | 15.4811 | 368450.4276 | 30.7042 | 30.7042 | 91.0267 | 0.2 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 63.9819 | 16.1612 | 384637.0553 | 32.0531 | 32.0531 | 92.8481 | 0.3 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 64.662 | 16.8413 | 400823.6829 | 33.402 | 33.402 | 94.6695 | 0.4 | 74.6 | 19.6 | 740880 | 61.74 | 61.74 | 65.3421 | 17.5214 | 417010.3106 | 34.7509 | 34.7509 | 96.4909 | 0.5 | 74.75 | 19.75 | 746550 | 62.2125 | 62.2125 | 66.0222 | 18.2016 | 433196.9382 | 36.0997 | 36.0997 | 98.3122 | 0.6 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 66.7023 | 18.8817 | 449383.5659 | 37.4486 | 37.4486 | 100.1336 | 0.7 | 75.05 | 20.05 | 757890 | 63.1575 | 63.1575 | 67.3824 | 19.5618 | 465570.1935 | 38.7975 | 38.7975 | 101.955 | 0.8 | 75.2 | 20.2 | 763560 | 63.63 | 63.63 | 68.0625 | 20.2419 | 481756.8212 | 40.1464 | 40.1464 | 103.7764 | 0.9 | 75.35 | 20.35 | 769230 | 64.1025 | 64.1025 | 68.7426 | 20.922 | 497943.4488 | 41.4953 | 41.4953 | 105.5978 | 1 | 75.5 | 20.5 | 774900 | 64.575 | 64.575 | 69.4227 | 21.6021 | 514130.0765 | 42.8442 | 42.8442 | 107.4192 | 75 | 55 | 28.9858 | 28 | 52.6
9/22/20XX 3:00:00 PM | 0.625 | 4 | 74.3 | 54.6 | 63.2706 | 76.1783 | 12.9077 | 50 | 74.3 |  | 74.3 | 69.2081 | 0.1 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 63.2803 | 15.4597 | 367939.7111 | 30.6616 | 30.6616 | 90.6061 | 0.2 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 63.9389 | 16.1183 | 383615.6221 | 31.968 | 31.968 | 92.007 | 0.3 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 64.5976 | 16.777 | 399291.5332 | 33.2743 | 33.2743 | 93.4078 | 0.4 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 65.2562 | 17.4356 | 414967.4443 | 34.5806 | 34.5806 | 94.8086 | 0.5 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 65.9149 | 18.0943 | 430643.3554 | 35.8869 | 35.8869 | 96.2094 | 0.6 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 66.5735 | 18.7529 | 446319.2664 | 37.1933 | 37.1933 | 97.6103 | 0.7 | 74.21 | 19.21 | 726138 | 60.5115 | 60.5115 | 67.2322 | 19.4116 | 461995.1775 | 38.4996 | 38.4996 | 99.0111 | 0.8 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 67.8908 | 20.0702 | 477671.0886 | 39.8059 | 39.8059 | 100.4119 | 0.9 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 68.5495 | 20.7289 | 493346.9996 | 41.1122 | 41.1122 | 101.8127 | 1 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 69.2081 | 21.3875 | 509022.9107 | 42.4186 | 42.4186 | 103.2136 | 75 | 55 | 28.659 | 28 | 54.6
9/22/20XX 4:00:00 PM | 0.66667 | 4 | 73.4 | 54.8 | 61.3407 | 73.8495 | 12.5088 | 50 | 73.4 |  | 73.4 | 67.3449 | 0.1 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 63.094 | 15.2733 | 363505.2241 | 30.2921 | 30.2921 | 89.9531 | 0.2 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 63.5663 | 15.7457 | 374746.6483 | 31.2289 | 31.2289 | 90.7009 | 0.3 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 64.0386 | 16.218 | 385988.0724 | 32.1657 | 32.1657 | 91.4487 | 0.4 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 64.5109 | 16.6903 | 397229.4966 | 33.1025 | 33.1025 | 92.1965 | 0.5 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.9833 | 17.1626 | 408470.9207 | 34.0392 | 34.0392 | 92.9442 | 0.6 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 65.4556 | 17.635 | 419712.3449 | 34.976 | 34.976 | 93.692 | 0.7 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 65.9279 | 18.1073 | 430953.769 | 35.9128 | 35.9128 | 94.4398 | 0.8 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 66.4003 | 18.5796 | 442195.1931 | 36.8496 | 36.8496 | 95.1876 | 0.9 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 66.8726 | 19.052 | 453436.6173 | 37.7864 | 37.7864 | 95.9354 | 1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 67.3449 | 19.5243 | 464678.0414 | 38.7232 | 38.7232 | 96.6832 | 75 | 55 | 28.1476 | 28 | 54.8
9/22/20XX 5:00:00 PM | 0.70833 | 4 | 72.1 | 56.2 | 58.6421 | 70.5937 | 11.9516 | 50 | 72.1 |  | 72.1 | 66.0521 | 0.1 | 73.81 | 18.81 | 711018 | 59.2515 | 59.2515 | 62.9647 | 15.144 | 360428.3202 | 30.0357 | 30.0357 | 89.2872 | 0.2 | 73.62 | 18.62 | 703836 | 58.653 | 58.653 | 63.3077 | 15.4871 | 368592.8405 | 30.7161 | 30.7161 | 89.3691 | 0.3 | 73.43 | 18.43 | 696654 | 58.0545 | 58.0545 | 63.6508 | 15.8301 | 376757.3607 | 31.3964 | 31.3964 | 89.4509 | 0.4 | 73.24 | 18.24 | 689472 | 57.456 | 57.456 | 63.9938 | 16.1732 | 384921.8809 | 32.0768 | 32.0768 | 89.5328 | 0.5 | 73.05 | 18.05 | 682290 | 56.8575 | 56.8575 | 64.3369 | 16.5162 | 393086.4012 | 32.7572 | 32.7572 | 89.6147 | 0.6 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 64.6799 | 16.8593 | 401250.9214 | 33.4376 | 33.4376 | 89.6966 | 0.7 | 72.67 | 17.67 | 667926 | 55.6605 | 55.6605 | 65.023 | 17.2023 | 409415.4416 | 34.118 | 34.118 | 89.7785 | 0.8 | 72.48 | 17.48 | 660744 | 55.062 | 55.062 | 65.366 | 17.5454 | 417579.9619 | 34.7983 | 34.7983 | 89.8603 | 0.9 | 72.29 | 17.29 | 653562 | 54.4635 | 54.4635 | 65.7091 | 17.8884 | 425744.4821 | 35.4787 | 35.4787 | 89.9422 | 1 | 72.1 | 17.1 | 646380 | 53.865 | 53.865 | 66.0521 | 18.2315 | 433909.0023 | 36.1591 | 36.1591 | 90.0241 | 70 | 55 | 27.628 | 28 | 56.2
9/22/20XX 6:00:00 PM | 0.75 | 4 | 70.8 | 57.1 | 56.0465 | 67.4628 | 11.4163 | 50 | 70.8 |  | 70.8 | 64.152 | 0.1 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 62.7747 | 14.954 | 355906.1572 | 29.6588 | 29.6588 | 88.5008 | 0.2 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 62.9277 | 15.1071 | 359548.5143 | 29.9624 | 29.9624 | 87.7964 | 0.3 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 63.0808 | 15.2601 | 363190.8715 | 30.2659 | 30.2659 | 87.0919 | 0.4 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 63.2338 | 15.4132 | 366833.2286 | 30.5694 | 30.5694 | 86.3874 | 0.5 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 63.3868 | 15.5662 | 370475.5858 | 30.873 | 30.873 | 85.683 | 0.6 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 63.5399 | 15.7192 | 374117.9429 | 31.1765 | 31.1765 | 84.9785 | 0.7 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 63.6929 | 15.8723 | 377760.3001 | 31.48 | 31.48 | 84.274 | 0.8 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 63.846 | 16.0253 | 381402.6572 | 31.7836 | 31.7836 | 83.5696 | 0.9 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 63.999 | 16.1784 | 385045.0144 | 32.0871 | 32.0871 | 82.8651 | 1 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 64.152 | 16.3314 | 388687.3716 | 32.3906 | 32.3906 | 82.1606 | 70 | 55 | 27.0137 | 28 | 57.1
9/22/20XX 7:00:00 PM | 0.79167 | 4 | 70.2 | 58.7 | 54.8825 | 66.0589 | 11.1765 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/22/20XX 8:00:00 PM | 0.83333 | 4 | 68.7 | 61.2 | 62.6607 | 73.2724 | 10.6117 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/22/20XX 9:00:00 PM | 0.875 | 4 | 67.1 | 65.3 | 59.2068 | 69.2196 | 10.0128 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/22/20XX 10:00:00 PM | 0.91667 | 4 | 66.3 | 67 | 57.5442 | 67.2689 | 9.7247 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/22/20XX 11:00:00 PM | 0.95833 | 4 | 65.9 | 69 | 56.7286 | 66.3121 | 9.5834 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/22/20XX 12:00:00 AM | 0 | 5 | 65.3 | 70.6 | 64.8997 | 74.3365 | 9.4368 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/23/20XX 1:00:00 AM | 0.041667 | 5 | 64.9 | 70.8 | 63.9732 | 73.2731 | 9.2999 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/23/20XX 2:00:00 AM | 0.083333 | 5 | 64.4 | 71.9 | 62.8319 | 71.9634 | 9.1314 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/23/20XX 3:00:00 AM | 0.125 | 5 | 63.6 | 71.7 | 61.0441 | 69.912 | 8.8679 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/23/20XX 4:00:00 AM | 0.16667 | 5 | 63.5 | 71.8 | 60.8239 | 69.6593 | 8.8354 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/23/20XX 5:00:00 AM | 0.20833 | 5 | 62.7 | 72.7 | 59.0882 | 67.6682 | 8.58 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/23/20XX 6:00:00 AM | 0.25 | 5 | 61.9 | 73.8 | 57.3979 | 65.7295 | 8.3316 | 70 | 61.9 |  | 61.9 | 60.5639 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.5639 | 12.7433 | 303290.6362 | 25.2742 | 25.2742 | 47.0092 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.5639 | 12.7433 | 303290.6362 | 25.2742 | 25.2742 | 47.0092 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.5639 | 12.7433 | 303290.6362 | 25.2742 | 25.2742 | 47.0092 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.5639 | 12.7433 | 303290.6362 | 25.2742 | 25.2742 | 47.0092 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.5639 | 12.7433 | 303290.6362 | 25.2742 | 25.2742 | 47.0092 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.5639 | 12.7433 | 303290.6362 | 25.2742 | 25.2742 | 47.0092 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.5639 | 12.7433 | 303290.6362 | 25.2742 | 25.2742 | 47.0092 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.5639 | 12.7433 | 303290.6362 | 25.2742 | 25.2742 | 47.0092 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.5639 | 12.7433 | 303290.6362 | 25.2742 | 25.2742 | 47.0092 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 60.5639 | 12.7433 | 303290.6362 | 25.2742 | 25.2742 | 47.0092 | 60 | 75 | 24.283 | 24 | 73.8
9/23/20XX 7:00:00 AM | 0.29167 | 5 | 62.7 | 72.7 | 59.0882 | 67.6682 | 8.58 | 70 | 62.7 |  | 62.7 | 61.4048 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 61.4048 | 13.5842 | 323303.6806 | 26.942 | 26.942 | 51.197 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 61.4048 | 13.5842 | 323303.6806 | 26.942 | 26.942 | 51.197 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 61.4048 | 13.5842 | 323303.6806 | 26.942 | 26.942 | 51.197 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 61.4048 | 13.5842 | 323303.6806 | 26.942 | 26.942 | 51.197 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 61.4048 | 13.5842 | 323303.6806 | 26.942 | 26.942 | 51.197 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 61.4048 | 13.5842 | 323303.6806 | 26.942 | 26.942 | 51.197 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 61.4048 | 13.5842 | 323303.6806 | 26.942 | 26.942 | 51.197 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 61.4048 | 13.5842 | 323303.6806 | 26.942 | 26.942 | 51.197 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 61.4048 | 13.5842 | 323303.6806 | 26.942 | 26.942 | 51.197 | 1 | 62.7 | 7.7 | 291060 | 24.255 | 24.255 | 61.4048 | 13.5842 | 323303.6806 | 26.942 | 26.942 | 51.197 | 65 | 75 | 24.609 | 24 | 72.7
9/23/20XX 8:00:00 AM | 0.33333 | 5 | 64.1 | 69 | 53.1859 | 62.156 | 8.9701 | 60 | 64.1 |  | 64.1 | 61.259 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 61.259 | 13.4384 | 319833.0282 | 26.6528 | 26.6528 | 55.3178 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 61.259 | 13.4384 | 319833.0282 | 26.6528 | 26.6528 | 55.3178 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 61.259 | 13.4384 | 319833.0282 | 26.6528 | 26.6528 | 55.3178 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 61.259 | 13.4384 | 319833.0282 | 26.6528 | 26.6528 | 55.3178 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 61.259 | 13.4384 | 319833.0282 | 26.6528 | 26.6528 | 55.3178 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 61.259 | 13.4384 | 319833.0282 | 26.6528 | 26.6528 | 55.3178 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 61.259 | 13.4384 | 319833.0282 | 26.6528 | 26.6528 | 55.3178 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 61.259 | 13.4384 | 319833.0282 | 26.6528 | 26.6528 | 55.3178 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 61.259 | 13.4384 | 319833.0282 | 26.6528 | 26.6528 | 55.3178 | 1 | 64.1 | 9.1 | 343980 | 28.665 | 28.665 | 61.259 | 13.4384 | 319833.0282 | 26.6528 | 26.6528 | 55.3178 | 65 | 70 | 24.9277 | 24 | 69
9/23/20XX 9:00:00 AM | 0.375 | 5 | 66.1 | 63.9 | 57.1351 | 66.7889 | 9.6538 | 60 | 66.1 |  | 66.1 | 60.9001 | 0.1 | 73.21 | 18.21 | 688338 | 57.3615 | 57.3615 | 62.4495 | 14.6288 | 348166.5659 | 29.0139 | 29.0139 | 86.3754 | 0.2 | 72.42 | 17.42 | 658476 | 54.873 | 54.873 | 62.2773 | 14.4567 | 344069.3319 | 28.6724 | 28.6724 | 83.5454 | 0.3 | 71.63 | 16.63 | 628614 | 52.3845 | 52.3845 | 62.1052 | 14.2845 | 339972.0978 | 28.331 | 28.331 | 80.7155 | 0.4 | 70.84 | 15.84 | 598752 | 49.896 | 49.896 | 61.933 | 14.1124 | 335874.8637 | 27.9896 | 27.9896 | 77.8856 | 0.5 | 70.05 | 15.05 | 568890 | 47.4075 | 47.4075 | 61.7609 | 13.9402 | 331777.6297 | 27.6481 | 27.6481 | 75.0556 | 0.6 | 69.26 | 14.26 | 539028 | 44.919 | 44.919 | 61.5887 | 13.7681 | 327680.3956 | 27.3067 | 27.3067 | 72.2257 | 0.7 | 68.47 | 13.47 | 509166 | 42.4305 | 42.4305 | 61.4166 | 13.5959 | 323583.1615 | 26.9653 | 26.9653 | 69.3958 | 0.8 | 67.68 | 12.68 | 479304 | 39.942 | 39.942 | 61.2444 | 13.4238 | 319485.9274 | 26.6238 | 26.6238 | 66.5658 | 0.9 | 66.89 | 11.89 | 449442 | 37.4535 | 37.4535 | 61.0723 | 13.2516 | 315388.6934 | 26.2824 | 26.2824 | 63.7359 | 1 | 66.1 | 11.1 | 419580 | 34.965 | 34.965 | 60.9001 | 13.0795 | 311291.4593 | 25.941 | 25.941 | 60.906 | 65 | 65 | 25.3595 | 26 | 63.9
9/23/20XX 10:00:00 AM | 0.41667 | 5 | 68 | 57.5 | 50.7933 | 61.1282 | 10.335 | 50 | 68 |  | 68 | 58.5445 | 0.1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 62.2139 | 14.3933 | 342560.2048 | 28.5467 | 28.5467 | 86.5067 | 0.2 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 61.8062 | 13.9856 | 332856.6096 | 27.7381 | 27.7381 | 83.8081 | 0.3 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 61.3985 | 13.5779 | 323153.0143 | 26.9294 | 26.9294 | 81.1094 | 0.4 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 60.9908 | 13.1701 | 313449.4191 | 26.1208 | 26.1208 | 78.4108 | 0.5 | 71 | 16 | 604800 | 50.4 | 50.4 | 60.5831 | 12.7624 | 303745.8239 | 25.3122 | 25.3122 | 75.7122 | 0.6 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 60.1753 | 12.3547 | 294042.2287 | 24.5035 | 24.5035 | 73.0135 | 0.7 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 59.7676 | 11.947 | 284338.6334 | 23.6949 | 23.6949 | 70.3149 | 0.8 | 69.2 | 14.2 | 536760 | 44.73 | 44.73 | 59.3599 | 11.5393 | 274635.0382 | 22.8863 | 22.8863 | 67.6163 | 0.9 | 68.6 | 13.6 | 514080 | 42.84 | 42.84 | 58.9522 | 11.1316 | 264931.443 | 22.0776 | 22.0776 | 64.9176 | 1 | 68 | 13 | 491400 | 40.95 | 40.95 | 58.5445 | 10.7239 | 255227.8478 | 21.269 | 21.269 | 62.219 | 70 | 55 | 25.4553 | 26 | 57.5
9/23/20XX 11:00:00 AM | 0.45833 | 5 | 70.5 | 53.3 | 55.4618 | 66.7576 | 11.2958 | 50 | 70.5 |  | 70.5 | 59.1894 | 0.1 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 62.2784 | 14.4578 | 344095.1456 | 28.6746 | 28.6746 | 87.4221 | 0.2 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 61.9352 | 14.1146 | 335926.4913 | 27.9939 | 27.9939 | 85.6389 | 0.3 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 61.592 | 13.7713 | 327757.8369 | 27.3132 | 27.3132 | 83.8557 | 0.4 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 61.2487 | 13.4281 | 319589.1825 | 26.6324 | 26.6324 | 82.0724 | 0.5 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 60.9055 | 13.0849 | 311420.5281 | 25.9517 | 25.9517 | 80.2892 | 0.6 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 60.5623 | 12.7417 | 303251.8738 | 25.271 | 25.271 | 78.506 | 0.7 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 60.2191 | 12.3985 | 295083.2194 | 24.5903 | 24.5903 | 76.7228 | 0.8 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 59.8759 | 12.0552 | 286914.565 | 23.9095 | 23.9095 | 74.9395 | 0.9 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 59.5326 | 11.712 | 278745.9106 | 23.2288 | 23.2288 | 73.1563 | 1 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 59.1894 | 11.3688 | 270577.2563 | 22.5481 | 22.5481 | 71.3731 | 70 | 55 | 26.1653 | 26 | 53.3
9/23/20XX 12:00:00 PM | 0.5 | 5 | 72.7 | 51.8 | 59.8747 | 72.0807 | 12.206 | 50 | 72.7 |  | 72.7 | 62.0717 | 0.1 | 73.87 | 18.87 | 713286 | 59.4405 | 59.4405 | 62.5666 | 14.746 | 350955.0552 | 29.2463 | 29.2463 | 88.6868 | 0.2 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 62.5117 | 14.691 | 349646.3103 | 29.1372 | 29.1372 | 88.1682 | 0.3 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 62.4567 | 14.636 | 348337.5655 | 29.0281 | 29.0281 | 87.6496 | 0.4 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 62.4017 | 14.581 | 347028.8206 | 28.9191 | 28.9191 | 87.1311 | 0.5 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 62.3467 | 14.5261 | 345720.0758 | 28.81 | 28.81 | 86.6125 | 0.6 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 62.2917 | 14.4711 | 344411.331 | 28.7009 | 28.7009 | 86.0939 | 0.7 | 73.09 | 18.09 | 683802 | 56.9835 | 56.9835 | 62.2367 | 14.4161 | 343102.5861 | 28.5919 | 28.5919 | 85.5754 | 0.8 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 62.1817 | 14.3611 | 341793.8413 | 28.4828 | 28.4828 | 85.0568 | 0.9 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 62.1267 | 14.3061 | 340485.0964 | 28.3738 | 28.3738 | 84.5383 | 1 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 62.0717 | 14.2511 | 339176.3516 | 28.2647 | 28.2647 | 84.0197 | 75 | 50 | 27.1522 | 28 | 51.8
9/23/20XX 1:00:00 PM | 0.54167 | 5 | 74.5 | 49.1 | 50.8258 | 63.7064 | 12.8806 | 40 | 74.5 |  | 74.5 | 62.5472 | 0.1 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 62.6142 | 14.7936 | 352086.6169 | 29.3406 | 29.3406 | 89.3481 | 0.2 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 62.6067 | 14.7861 | 351909.4338 | 29.3258 | 29.3258 | 89.4908 | 0.3 | 74.15 | 19.15 | 723870 | 60.3225 | 60.3225 | 62.5993 | 14.7787 | 351732.2507 | 29.311 | 29.311 | 89.6335 | 0.4 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 62.5919 | 14.7712 | 351555.0676 | 29.2963 | 29.2963 | 89.7763 | 0.5 | 74.25 | 19.25 | 727650 | 60.6375 | 60.6375 | 62.5844 | 14.7638 | 351377.8845 | 29.2815 | 29.2815 | 89.919 | 0.6 | 74.3 | 19.3 | 729540 | 60.795 | 60.795 | 62.577 | 14.7563 | 351200.7014 | 29.2667 | 29.2667 | 90.0617 | 0.7 | 74.35 | 19.35 | 731430 | 60.9525 | 60.9525 | 62.5695 | 14.7489 | 351023.5183 | 29.252 | 29.252 | 90.2045 | 0.8 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 62.5621 | 14.7414 | 350846.3352 | 29.2372 | 29.2372 | 90.3472 | 0.9 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 62.5546 | 14.734 | 350669.1521 | 29.2224 | 29.2224 | 90.4899 | 1 | 74.5 | 19.5 | 737100 | 61.425 | 61.425 | 62.5472 | 14.7266 | 350491.969 | 29.2077 | 29.2077 | 90.6327 | 75 | 50 | 27.6657 | 28 | 49.1
9/23/20XX 2:00:00 PM | 0.58333 | 5 | 74.2 | 50.2 | 63.0537 | 75.9165 | 12.8628 | 50 | 74.2 |  | 74.2 | 63.3109 | 0.1 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 62.6906 | 14.8699 | 353904.2801 | 29.492 | 29.492 | 89.405 | 0.2 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 62.7595 | 14.9389 | 355544.7602 | 29.6287 | 29.6287 | 89.6047 | 0.3 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 62.8284 | 15.0078 | 357185.2403 | 29.7654 | 29.7654 | 89.8044 | 0.4 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 62.8973 | 15.0767 | 358825.7204 | 29.9021 | 29.9021 | 90.0041 | 0.5 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 62.9663 | 15.1456 | 360466.2005 | 30.0389 | 30.0389 | 90.2039 | 0.6 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 63.0352 | 15.2146 | 362106.6806 | 30.1756 | 30.1756 | 90.4036 | 0.7 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 63.1041 | 15.2835 | 363747.1607 | 30.3123 | 30.3123 | 90.6033 | 0.8 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 63.1731 | 15.3524 | 365387.6408 | 30.449 | 30.449 | 90.803 | 0.9 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 63.242 | 15.4213 | 367028.1209 | 30.5857 | 30.5857 | 91.0027 | 1 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 63.3109 | 15.4903 | 368668.601 | 30.7224 | 30.7224 | 91.2024 | 75 | 50 | 27.712 | 28 | 50.2
9/23/20XX 3:00:00 PM | 0.625 | 5 | 74.4 | 50.4 | 63.4882 | 76.4409 | 12.9527 | 50 | 74.4 |  | 74.4 | 64.0063 | 0.1 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 62.7601 | 14.9395 | 355559.349 | 29.6299 | 29.6299 | 89.6059 | 0.2 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 62.8986 | 15.0779 | 358854.8981 | 29.9046 | 29.9046 | 90.0066 | 0.3 | 74.12 | 19.12 | 722736 | 60.228 | 60.228 | 63.037 | 15.2164 | 362150.4471 | 30.1792 | 30.1792 | 90.4072 | 0.4 | 74.16 | 19.16 | 724248 | 60.354 | 60.354 | 63.1755 | 15.3549 | 365445.9962 | 30.4538 | 30.4538 | 90.8078 | 0.5 | 74.2 | 19.2 | 725760 | 60.48 | 60.48 | 63.314 | 15.4933 | 368741.5452 | 30.7285 | 30.7285 | 91.2085 | 0.6 | 74.24 | 19.24 | 727272 | 60.606 | 60.606 | 63.4524 | 15.6318 | 372037.0943 | 31.0031 | 31.0031 | 91.6091 | 0.7 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 63.5909 | 15.7703 | 375332.6433 | 31.2777 | 31.2777 | 92.0097 | 0.8 | 74.32 | 19.32 | 730296 | 60.858 | 60.858 | 63.7294 | 15.9087 | 378628.1924 | 31.5523 | 31.5523 | 92.4103 | 0.9 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 63.8678 | 16.0472 | 381923.7414 | 31.827 | 31.827 | 92.811 | 1 | 74.4 | 19.4 | 733320 | 61.11 | 61.11 | 64.0063 | 16.1857 | 385219.2905 | 32.1016 | 32.1016 | 93.2116 | 75 | 50 | 27.8696 | 28 | 50.4
9/23/20XX 4:00:00 PM | 0.66667 | 5 | 73.8 | 52 | 62.1921 | 74.8769 | 12.6847 | 50 | 73.8 |  | 73.8 | 64.7291 | 0.1 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 62.8324 | 15.0117 | 357279.5436 | 29.7733 | 29.7733 | 89.5603 | 0.2 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 63.0431 | 15.2225 | 362295.2872 | 30.1913 | 30.1913 | 89.9153 | 0.3 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 63.2539 | 15.4332 | 367311.0308 | 30.6093 | 30.6093 | 90.2703 | 0.4 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 63.4646 | 15.644 | 372326.7745 | 31.0272 | 31.0272 | 90.6252 | 0.5 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 63.6754 | 15.8547 | 377342.5181 | 31.4452 | 31.4452 | 90.9802 | 0.6 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 63.8861 | 16.0655 | 382358.2617 | 31.8632 | 31.8632 | 91.3352 | 0.7 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 64.0969 | 16.2762 | 387374.0053 | 32.2812 | 32.2812 | 91.6902 | 0.8 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 64.3076 | 16.487 | 392389.7489 | 32.6991 | 32.6991 | 92.0451 | 0.9 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 64.5183 | 16.6977 | 397405.4925 | 33.1171 | 33.1171 | 92.4001 | 1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.7291 | 16.9085 | 402421.2361 | 33.5351 | 33.5351 | 92.7551 | 75 | 50 | 27.8362 | 28 | 52
9/23/20XX 5:00:00 PM | 0.70833 | 5 | 72.6 | 54 | 59.6677 | 71.831 | 12.1633 | 50 | 72.6 |  | 72.6 | 64.533 | 0.1 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 62.8128 | 14.9921 | 356812.8917 | 29.7344 | 29.7344 | 89.1434 | 0.2 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 63.0039 | 15.1833 | 361361.9834 | 30.1135 | 30.1135 | 89.0815 | 0.3 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 63.195 | 15.3744 | 365911.075 | 30.4926 | 30.4926 | 89.0196 | 0.4 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 63.3862 | 15.5656 | 370460.1667 | 30.8717 | 30.8717 | 88.9577 | 0.5 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 63.5773 | 15.7567 | 375009.2584 | 31.2508 | 31.2508 | 88.8958 | 0.6 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 63.7685 | 15.9478 | 379558.3501 | 31.6299 | 31.6299 | 88.8339 | 0.7 | 73.02 | 18.02 | 681156 | 56.763 | 56.763 | 63.9596 | 16.139 | 384107.4418 | 32.009 | 32.009 | 88.772 | 0.8 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 64.1507 | 16.3301 | 388656.5335 | 32.388 | 32.388 | 88.71 | 0.9 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 64.3419 | 16.5212 | 393205.6251 | 32.7671 | 32.7671 | 88.6481 | 1 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 64.533 | 16.7124 | 397754.7168 | 33.1462 | 33.1462 | 88.5862 | 75 | 55 | 27.5126 | 28 | 54
9/23/20XX 6:00:00 PM | 0.75 | 5 | 70.8 | 57.8 | 56.0465 | 67.4628 | 11.4163 | 50 | 70.8 |  | 70.8 | 64.9512 | 0.1 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 62.8546 | 15.034 | 357808.115 | 29.8173 | 29.8173 | 88.6593 | 0.2 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 63.0875 | 15.2669 | 363352.4301 | 30.2794 | 30.2794 | 88.1134 | 0.3 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 63.3205 | 15.4999 | 368896.7451 | 30.7414 | 30.7414 | 87.5674 | 0.4 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 63.5535 | 15.7328 | 374441.0601 | 31.2034 | 31.2034 | 87.0214 | 0.5 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 63.7864 | 15.9658 | 379985.3751 | 31.6654 | 31.6654 | 86.4754 | 0.6 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 64.0194 | 16.1987 | 385529.6902 | 32.1275 | 32.1275 | 85.9295 | 0.7 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 64.2523 | 16.4317 | 391074.0052 | 32.5895 | 32.5895 | 85.3835 | 0.8 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 64.4853 | 16.6646 | 396618.3202 | 33.0515 | 33.0515 | 84.8375 | 0.9 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 64.7182 | 16.8976 | 402162.6353 | 33.5136 | 33.5136 | 84.2916 | 1 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 64.9512 | 17.1305 | 407706.9503 | 33.9756 | 33.9756 | 83.7456 | 70 | 60 | 27.1386 | 28 | 57.8
9/23/20XX 7:00:00 PM | 0.79167 | 5 | 69.6 | 61.4 | 64.6807 | 75.643 | 10.9623 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/23/20XX 8:00:00 PM | 0.83333 | 5 | 68.4 | 64.5 | 61.9998 | 72.4969 | 10.4971 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/23/20XX 9:00:00 PM | 0.875 | 5 | 67.8 | 67.2 | 60.6965 | 70.9676 | 10.2711 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/23/20XX 10:00:00 PM | 0.91667 | 5 | 67 | 70.6 | 68.973 | 79.0128 | 10.0398 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/23/20XX 11:00:00 PM | 0.95833 | 5 | 66.5 | 70.9 | 67.7519 | 77.6107 | 9.8588 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/23/20XX 12:00:00 AM | 0 | 6 | 64.9 | 76 | 63.9732 | 73.2731 | 9.2999 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/24/20XX 1:00:00 AM | 0.041667 | 6 | 64.1 | 77.6 | 62.156 | 71.1877 | 9.0317 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/24/20XX 2:00:00 AM | 0.083333 | 6 | 63.5 | 78.5 | 60.8239 | 69.6593 | 8.8354 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/24/20XX 3:00:00 AM | 0.125 | 6 | 62.7 | 80.5 | 67.6682 | 76.2198 | 8.5516 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/24/20XX 4:00:00 AM | 0.16667 | 6 | 62.3 | 80.4 | 66.6924 | 75.1174 | 8.425 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/24/20XX 5:00:00 AM | 0.20833 | 6 | 61.7 | 81 | 65.2529 | 73.4915 | 8.2386 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/24/20XX 6:00:00 AM | 0.25 | 6 | 61.4 | 81.3 | 64.544 | 72.6909 | 8.1469 | 80 | 61.4 |  | 61.4 | 65.6031 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 65.6031 | 17.7825 | 423223.6134 | 35.2686 | 35.2686 | 55.4286 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 65.6031 | 17.7825 | 423223.6134 | 35.2686 | 35.2686 | 55.4286 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 65.6031 | 17.7825 | 423223.6134 | 35.2686 | 35.2686 | 55.4286 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 65.6031 | 17.7825 | 423223.6134 | 35.2686 | 35.2686 | 55.4286 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 65.6031 | 17.7825 | 423223.6134 | 35.2686 | 35.2686 | 55.4286 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 65.6031 | 17.7825 | 423223.6134 | 35.2686 | 35.2686 | 55.4286 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 65.6031 | 17.7825 | 423223.6134 | 35.2686 | 35.2686 | 55.4286 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 65.6031 | 17.7825 | 423223.6134 | 35.2686 | 35.2686 | 55.4286 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 65.6031 | 17.7825 | 423223.6134 | 35.2686 | 35.2686 | 55.4286 | 1 | 61.4 | 6.4 | 241920 | 20.16 | 20.16 | 65.6031 | 17.7825 | 423223.6134 | 35.2686 | 35.2686 | 55.4286 | 60 | 80 | 24.9453 | 24 | 81.3
9/24/20XX 7:00:00 AM | 0.29167 | 6 | 62.4 | 78.1 | 58.4491 | 66.9351 | 8.486 | 70 | 62.4 |  | 62.4 | 65.3228 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 65.3228 | 17.5021 | 416550.7651 | 34.7126 | 34.7126 | 58.0226 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 65.3228 | 17.5021 | 416550.7651 | 34.7126 | 34.7126 | 58.0226 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 65.3228 | 17.5021 | 416550.7651 | 34.7126 | 34.7126 | 58.0226 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 65.3228 | 17.5021 | 416550.7651 | 34.7126 | 34.7126 | 58.0226 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 65.3228 | 17.5021 | 416550.7651 | 34.7126 | 34.7126 | 58.0226 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 65.3228 | 17.5021 | 416550.7651 | 34.7126 | 34.7126 | 58.0226 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 65.3228 | 17.5021 | 416550.7651 | 34.7126 | 34.7126 | 58.0226 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 65.3228 | 17.5021 | 416550.7651 | 34.7126 | 34.7126 | 58.0226 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 65.3228 | 17.5021 | 416550.7651 | 34.7126 | 34.7126 | 58.0226 | 1 | 62.4 | 7.4 | 279720 | 23.31 | 23.31 | 65.3228 | 17.5021 | 416550.7651 | 34.7126 | 34.7126 | 58.0226 | 60 | 80 | 25.1458 | 26 | 78.1
9/24/20XX 8:00:00 AM | 0.33333 | 6 | 64.6 | 72.8 | 63.2862 | 72.4847 | 9.1985 | 70 | 64.6 |  | 64.6 | 65.8618 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 65.8618 | 18.0412 | 429379.6013 | 35.7816 | 35.7816 | 66.0216 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 65.8618 | 18.0412 | 429379.6013 | 35.7816 | 35.7816 | 66.0216 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 65.8618 | 18.0412 | 429379.6013 | 35.7816 | 35.7816 | 66.0216 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 65.8618 | 18.0412 | 429379.6013 | 35.7816 | 35.7816 | 66.0216 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 65.8618 | 18.0412 | 429379.6013 | 35.7816 | 35.7816 | 66.0216 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 65.8618 | 18.0412 | 429379.6013 | 35.7816 | 35.7816 | 66.0216 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 65.8618 | 18.0412 | 429379.6013 | 35.7816 | 35.7816 | 66.0216 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 65.8618 | 18.0412 | 429379.6013 | 35.7816 | 35.7816 | 66.0216 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 65.8618 | 18.0412 | 429379.6013 | 35.7816 | 35.7816 | 66.0216 | 1 | 64.6 | 9.6 | 362880 | 30.24 | 30.24 | 65.8618 | 18.0412 | 429379.6013 | 35.7816 | 35.7816 | 66.0216 | 65 | 75 | 25.7669 | 26 | 72.8
9/24/20XX 9:00:00 AM | 0.375 | 6 | 66.2 | 68.3 | 57.3393 | 67.0285 | 9.6892 | 60 | 66.2 |  | 66.2 | 65.3814 | 0.1 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 62.8976 | 15.077 | 358831.9606 | 29.9027 | 29.9027 | 87.2957 | 0.2 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 63.1736 | 15.3529 | 365400.1212 | 30.45 | 30.45 | 85.386 | 0.3 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 63.4496 | 15.6289 | 371968.2818 | 30.9974 | 30.9974 | 83.4764 | 0.4 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 63.7255 | 15.9049 | 378536.4424 | 31.5447 | 31.5447 | 81.5667 | 0.5 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 64.0015 | 16.1809 | 385104.603 | 32.0921 | 32.0921 | 79.6571 | 0.6 | 69.32 | 14.32 | 541296 | 45.108 | 45.108 | 64.2775 | 16.4568 | 391672.7637 | 32.6394 | 32.6394 | 77.7474 | 0.7 | 68.54 | 13.54 | 511812 | 42.651 | 42.651 | 64.5534 | 16.7328 | 398240.9243 | 33.1867 | 33.1867 | 75.8377 | 0.8 | 67.76 | 12.76 | 482328 | 40.194 | 40.194 | 64.8294 | 17.0088 | 404809.0849 | 33.7341 | 33.7341 | 73.9281 | 0.9 | 66.98 | 11.98 | 452844 | 37.737 | 37.737 | 65.1054 | 17.2848 | 411377.2455 | 34.2814 | 34.2814 | 72.0184 | 1 | 66.2 | 11.2 | 423360 | 35.28 | 35.28 | 65.3814 | 17.5607 | 417945.4061 | 34.8288 | 34.8288 | 70.1088 | 65 | 70 | 26.0827 | 26 | 68.3
9/24/20XX 10:00:00 AM | 0.41667 | 6 | 68.1 | 64.5 | 61.3451 | 71.7287 | 10.3836 | 60 | 68.1 |  | 68.1 | 66.0177 | 0.1 | 73.41 | 18.41 | 695898 | 57.9915 | 57.9915 | 62.9612 | 15.1406 | 360346.472 | 30.0289 | 30.0289 | 88.0204 | 0.2 | 72.82 | 17.82 | 673596 | 56.133 | 56.133 | 63.3008 | 15.4802 | 368429.1439 | 30.7024 | 30.7024 | 86.8354 | 0.3 | 72.23 | 17.23 | 651294 | 54.2745 | 54.2745 | 63.6405 | 15.8198 | 376511.8159 | 31.376 | 31.376 | 85.6505 | 0.4 | 71.64 | 16.64 | 628992 | 52.416 | 52.416 | 63.9801 | 16.1594 | 384594.4878 | 32.0495 | 32.0495 | 84.4655 | 0.5 | 71.05 | 16.05 | 606690 | 50.5575 | 50.5575 | 64.3197 | 16.499 | 392677.1598 | 32.7231 | 32.7231 | 83.2806 | 0.6 | 70.46 | 15.46 | 584388 | 48.699 | 48.699 | 64.6593 | 16.8386 | 400759.8317 | 33.3967 | 33.3967 | 82.0957 | 0.7 | 69.87 | 14.87 | 562086 | 46.8405 | 46.8405 | 64.9989 | 17.1783 | 408842.5037 | 34.0702 | 34.0702 | 80.9107 | 0.8 | 69.28 | 14.28 | 539784 | 44.982 | 44.982 | 65.3385 | 17.5179 | 416925.1756 | 34.7438 | 34.7438 | 79.7258 | 0.9 | 68.69 | 13.69 | 517482 | 43.1235 | 43.1235 | 65.6781 | 17.8575 | 425007.8476 | 35.4173 | 35.4173 | 78.5408 | 1 | 68.1 | 13.1 | 495180 | 41.265 | 41.265 | 66.0177 | 18.1971 | 433090.5195 | 36.0909 | 36.0909 | 77.3559 | 70 | 65 | 26.6459 | 26 | 64.5
9/24/20XX 11:00:00 AM | 0.45833 | 6 | 70.9 | 59.2 | 56.2425 | 67.6992 | 11.4567 | 50 | 70.9 |  | 70.9 | 66.7827 | 0.1 | 73.69 | 18.69 | 706482 | 58.8735 | 58.8735 | 63.0377 | 15.2171 | 362167.1652 | 30.1806 | 30.1806 | 89.0541 | 0.2 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 63.4538 | 15.6332 | 372070.5304 | 31.0059 | 31.0059 | 88.9029 | 0.3 | 73.07 | 18.07 | 683046 | 56.9205 | 56.9205 | 63.87 | 16.0493 | 381973.8956 | 31.8312 | 31.8312 | 88.7517 | 0.4 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 64.2861 | 16.4654 | 391877.2608 | 32.6564 | 32.6564 | 88.6004 | 0.5 | 72.45 | 17.45 | 659610 | 54.9675 | 54.9675 | 64.7022 | 16.8815 | 401780.6259 | 33.4817 | 33.4817 | 88.4492 | 0.6 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 65.1183 | 17.2976 | 411683.9911 | 34.307 | 34.307 | 88.298 | 0.7 | 71.83 | 16.83 | 636174 | 53.0145 | 53.0145 | 65.5344 | 17.7138 | 421587.3563 | 35.1323 | 35.1323 | 88.1468 | 0.8 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 65.9505 | 18.1299 | 431490.7215 | 35.9576 | 35.9576 | 87.9956 | 0.9 | 71.21 | 16.21 | 612738 | 51.0615 | 51.0615 | 66.3666 | 18.546 | 441394.0867 | 36.7828 | 36.7828 | 87.8443 | 1 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 66.7827 | 18.9621 | 451297.4519 | 37.6081 | 37.6081 | 87.6931 | 70 | 60 | 27.4491 | 28 | 59.2
9/24/20XX 12:00:00 PM | 0.5 | 6 | 73.5 | 53.5 | 61.5526 | 74.1052 | 12.5526 | 50 | 73.5 |  | 73.5 | 65.946 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 62.9541 | 15.1334 | 360175.845 | 30.0147 | 30.0147 | 89.7072 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 63.2865 | 15.4659 | 368087.89 | 30.674 | 30.674 | 90.209 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 63.6189 | 15.7983 | 375999.935 | 31.3333 | 31.3333 | 90.7108 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 63.9514 | 16.1308 | 383911.98 | 31.9927 | 31.9927 | 91.2127 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 64.2838 | 16.4632 | 391824.0249 | 32.652 | 32.652 | 91.7145 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.6163 | 16.7956 | 399736.0699 | 33.3113 | 33.3113 | 92.2163 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 64.9487 | 17.1281 | 407648.1149 | 33.9707 | 33.9707 | 92.7182 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 65.2811 | 17.4605 | 415560.1599 | 34.63 | 34.63 | 93.22 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 65.6136 | 17.7929 | 423472.2049 | 35.2894 | 35.2894 | 93.7219 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 65.946 | 18.1254 | 431384.2499 | 35.9487 | 35.9487 | 94.2237 | 75 | 55 | 27.9533 | 28 | 53.5
9/24/20XX 1:00:00 PM | 0.54167 | 6 | 74.9 | 49.6 | 51.5235 | 64.5858 | 13.0622 | 40 | 74.9 |  | 74.9 | 64.0633 | 0.1 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 62.7658 | 14.9452 | 355694.8942 | 29.6412 | 29.6412 | 89.7747 | 0.2 | 74.18 | 19.18 | 725004 | 60.417 | 60.417 | 62.91 | 15.0893 | 359125.9884 | 29.9272 | 29.9272 | 90.3442 | 0.3 | 74.27 | 19.27 | 728406 | 60.7005 | 60.7005 | 63.0541 | 15.2335 | 362557.0826 | 30.2131 | 30.2131 | 90.9136 | 0.4 | 74.36 | 19.36 | 731808 | 60.984 | 60.984 | 63.1983 | 15.3777 | 365988.1768 | 30.499 | 30.499 | 91.483 | 0.5 | 74.45 | 19.45 | 735210 | 61.2675 | 61.2675 | 63.3425 | 15.5218 | 369419.271 | 30.7849 | 30.7849 | 92.0524 | 0.6 | 74.54 | 19.54 | 738612 | 61.551 | 61.551 | 63.4866 | 15.666 | 372850.3652 | 31.0709 | 31.0709 | 92.6219 | 0.7 | 74.63 | 19.63 | 742014 | 61.8345 | 61.8345 | 63.6308 | 15.8101 | 376281.4594 | 31.3568 | 31.3568 | 93.1913 | 0.8 | 74.72 | 19.72 | 745416 | 62.118 | 62.118 | 63.7749 | 15.9543 | 379712.5537 | 31.6427 | 31.6427 | 93.7607 | 0.9 | 74.81 | 19.81 | 748818 | 62.4015 | 62.4015 | 63.9191 | 16.0985 | 383143.6479 | 31.9286 | 31.9286 | 94.3301 | 1 | 74.9 | 19.9 | 752220 | 62.685 | 62.685 | 64.0633 | 16.2426 | 386574.7421 | 32.2146 | 32.2146 | 94.8996 | 75 | 50 | 28.0005 | 28 | 49.6
9/24/20XX 2:00:00 PM | 0.58333 | 6 | 75.4 | 48.9 | 52.4071 | 65.6994 | 13.2923 | 40 | 75.4 |  | 75.4 | 64.2372 | 0.1 | 74.14 | 19.14 | 723492 | 60.291 | 60.291 | 62.7832 | 14.9626 | 356108.8666 | 29.6757 | 29.6757 | 89.9667 | 0.2 | 74.28 | 19.28 | 728784 | 60.732 | 60.732 | 62.9447 | 15.1241 | 359953.9332 | 29.9962 | 29.9962 | 90.7282 | 0.3 | 74.42 | 19.42 | 734076 | 61.173 | 61.173 | 63.1063 | 15.2857 | 363798.9998 | 30.3166 | 30.3166 | 91.4896 | 0.4 | 74.56 | 19.56 | 739368 | 61.614 | 61.614 | 63.2679 | 15.4472 | 367644.0664 | 30.637 | 30.637 | 92.251 | 0.5 | 74.7 | 19.7 | 744660 | 62.055 | 62.055 | 63.4294 | 15.6088 | 371489.1329 | 30.9574 | 30.9574 | 93.0124 | 0.6 | 74.84 | 19.84 | 749952 | 62.496 | 62.496 | 63.591 | 15.7703 | 375334.1995 | 31.2778 | 31.2778 | 93.7738 | 0.7 | 74.98 | 19.98 | 755244 | 62.937 | 62.937 | 63.7525 | 15.9319 | 379179.2661 | 31.5983 | 31.5983 | 94.5353 | 0.8 | 75.12 | 20.12 | 760536 | 63.378 | 63.378 | 63.9141 | 16.0935 | 383024.3327 | 31.9187 | 31.9187 | 95.2967 | 0.9 | 75.26 | 20.26 | 765828 | 63.819 | 63.819 | 64.0756 | 16.255 | 386869.3993 | 32.2391 | 32.2391 | 96.0581 | 1 | 75.4 | 20.4 | 771120 | 64.26 | 64.26 | 64.2372 | 16.4166 | 390714.4659 | 32.5595 | 32.5595 | 96.8195 | 75 | 50 | 28.1498 | 28 | 48.9
9/24/20XX 3:00:00 PM | 0.625 | 6 | 75.1 | 49.6 | 51.8754 | 65.0293 | 13.1538 | 40 | 75.1 |  | 75.1 | 64.5031 | 0.1 | 74.11 | 19.11 | 722358 | 60.1965 | 60.1965 | 62.8098 | 14.9891 | 356741.7168 | 29.7285 | 29.7285 | 89.925 | 0.2 | 74.22 | 19.22 | 726516 | 60.543 | 60.543 | 62.9979 | 15.1773 | 361219.6337 | 30.1016 | 30.1016 | 90.6446 | 0.3 | 74.33 | 19.33 | 730674 | 60.8895 | 60.8895 | 63.1861 | 15.3654 | 365697.5505 | 30.4748 | 30.4748 | 91.3643 | 0.4 | 74.44 | 19.44 | 734832 | 61.236 | 61.236 | 63.3742 | 15.5536 | 370175.4674 | 30.848 | 30.848 | 92.084 | 0.5 | 74.55 | 19.55 | 738990 | 61.5825 | 61.5825 | 63.5624 | 15.7417 | 374653.3842 | 31.2211 | 31.2211 | 92.8036 | 0.6 | 74.66 | 19.66 | 743148 | 61.929 | 61.929 | 63.7505 | 15.9299 | 379131.301 | 31.5943 | 31.5943 | 93.5233 | 0.7 | 74.77 | 19.77 | 747306 | 62.2755 | 62.2755 | 63.9387 | 16.118 | 383609.2179 | 31.9674 | 31.9674 | 94.2429 | 0.8 | 74.88 | 19.88 | 751464 | 62.622 | 62.622 | 64.1268 | 16.3062 | 388087.1347 | 32.3406 | 32.3406 | 94.9626 | 0.9 | 74.99 | 19.99 | 755622 | 62.9685 | 62.9685 | 64.315 | 16.4943 | 392565.0515 | 32.7138 | 32.7138 | 95.6823 | 1 | 75.1 | 20.1 | 759780 | 63.315 | 63.315 | 64.5031 | 16.6825 | 397042.9684 | 33.0869 | 33.0869 | 96.4019 | 75 | 50 | 28.1182 | 28 | 49.6
9/24/20XX 4:00:00 PM | 0.66667 | 6 | 74.1 | 50.1 | 62.8373 | 75.6554 | 12.8181 | 50 | 74.1 |  | 74.1 | 62.9655 | 0.1 | 74.01 | 19.01 | 718578 | 59.8815 | 59.8815 | 62.656 | 14.8354 | 353082.2227 | 29.4235 | 29.4235 | 89.305 | 0.2 | 74.02 | 19.02 | 718956 | 59.913 | 59.913 | 62.6904 | 14.8698 | 353900.6453 | 29.4917 | 29.4917 | 89.4047 | 0.3 | 74.03 | 19.03 | 719334 | 59.9445 | 59.9445 | 62.7248 | 14.9042 | 354719.068 | 29.5599 | 29.5599 | 89.5044 | 0.4 | 74.04 | 19.04 | 719712 | 59.976 | 59.976 | 62.7592 | 14.9386 | 355537.4907 | 29.6281 | 29.6281 | 89.6041 | 0.5 | 74.05 | 19.05 | 720090 | 60.0075 | 60.0075 | 62.7936 | 14.9729 | 356355.9134 | 29.6963 | 29.6963 | 89.7038 | 0.6 | 74.06 | 19.06 | 720468 | 60.039 | 60.039 | 62.828 | 15.0073 | 357174.336 | 29.7645 | 29.7645 | 89.8035 | 0.7 | 74.07 | 19.07 | 720846 | 60.0705 | 60.0705 | 62.8623 | 15.0417 | 357992.7587 | 29.8327 | 29.8327 | 89.9032 | 0.8 | 74.08 | 19.08 | 721224 | 60.102 | 60.102 | 62.8967 | 15.0761 | 358811.1814 | 29.9009 | 29.9009 | 90.0029 | 0.9 | 74.09 | 19.09 | 721602 | 60.1335 | 60.1335 | 62.9311 | 15.1105 | 359629.604 | 29.9691 | 29.9691 | 90.1026 | 1 | 74.1 | 19.1 | 721980 | 60.165 | 60.165 | 62.9655 | 15.1449 | 360448.0267 | 30.0373 | 30.0373 | 90.2023 | 75 | 50 | 27.6336 | 28 | 50.1
9/24/20XX 5:00:00 PM | 0.70833 | 6 | 72.7 | 53 | 59.8747 | 72.0807 | 12.206 | 50 | 72.7 |  | 72.7 | 63.5365 | 0.1 | 73.87 | 18.87 | 713286 | 59.4405 | 59.4405 | 62.7131 | 14.8925 | 354441.0972 | 29.5368 | 29.5368 | 88.9773 | 0.2 | 73.74 | 18.74 | 708372 | 59.031 | 59.031 | 62.8046 | 14.984 | 356618.3943 | 29.7182 | 29.7182 | 88.7492 | 0.3 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 62.8961 | 15.0754 | 358795.6915 | 29.8996 | 29.8996 | 88.5211 | 0.4 | 73.48 | 18.48 | 698544 | 58.212 | 58.212 | 62.9876 | 15.1669 | 360972.9887 | 30.0811 | 30.0811 | 88.2931 | 0.5 | 73.35 | 18.35 | 693630 | 57.8025 | 57.8025 | 63.079 | 15.2584 | 363150.2859 | 30.2625 | 30.2625 | 88.065 | 0.6 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 63.1705 | 15.3499 | 365327.583 | 30.444 | 30.444 | 87.837 | 0.7 | 73.09 | 18.09 | 683802 | 56.9835 | 56.9835 | 63.262 | 15.4414 | 367504.8802 | 30.6254 | 30.6254 | 87.6089 | 0.8 | 72.96 | 17.96 | 678888 | 56.574 | 56.574 | 63.3535 | 15.5329 | 369682.1774 | 30.8068 | 30.8068 | 87.3808 | 0.9 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 63.445 | 15.6243 | 371859.4745 | 30.9883 | 30.9883 | 87.1528 | 1 | 72.7 | 17.7 | 669060 | 55.755 | 55.755 | 63.5365 | 15.7158 | 374036.7717 | 31.1697 | 31.1697 | 86.9247 | 75 | 55 | 27.3812 | 28 | 53
9/24/20XX 6:00:00 PM | 0.75 | 6 | 70.6 | 57 | 55.6561 | 66.992 | 11.3359 | 50 | 70.6 |  | 70.6 | 63.5912 | 0.1 | 73.66 | 18.66 | 705348 | 58.779 | 58.779 | 62.7186 | 14.898 | 354571.3673 | 29.5476 | 29.5476 | 88.3266 | 0.2 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 62.8155 | 14.9949 | 356878.9346 | 29.7399 | 29.7399 | 87.4479 | 0.3 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 62.9125 | 15.0919 | 359186.5019 | 29.9322 | 29.9322 | 86.5692 | 0.4 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 63.0095 | 15.1888 | 361494.0692 | 30.1245 | 30.1245 | 85.6905 | 0.5 | 72.3 | 17.3 | 653940 | 54.495 | 54.495 | 63.1064 | 15.2858 | 363801.6365 | 30.3168 | 30.3168 | 84.8118 | 0.6 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 63.2034 | 15.3827 | 366109.2038 | 30.5091 | 30.5091 | 83.9331 | 0.7 | 71.62 | 16.62 | 628236 | 52.353 | 52.353 | 63.3003 | 15.4797 | 368416.7711 | 30.7014 | 30.7014 | 83.0544 | 0.8 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 63.3973 | 15.5767 | 370724.3384 | 30.8937 | 30.8937 | 82.1757 | 0.9 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 63.4942 | 15.6736 | 373031.9058 | 31.086 | 31.086 | 81.297 | 1 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 63.5912 | 15.7706 | 375339.4731 | 31.2783 | 31.2783 | 80.4183 | 70 | 55 | 26.8773 | 26 | 57
9/24/20XX 7:00:00 PM | 0.79167 | 6 | 69.1 | 60.2 | 63.5515 | 74.3178 | 10.7663 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/24/20XX 8:00:00 PM | 0.83333 | 6 | 68.5 | 60.2 | 62.2194 | 72.7546 | 10.5352 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/24/20XX 9:00:00 PM | 0.875 | 6 | 68.4 | 60.1 | 61.9998 | 72.4969 | 10.4971 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/24/20XX 10:00:00 PM | 0.91667 | 6 | 67.8 | 60.7 | 60.6965 | 70.9676 | 10.2711 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/24/20XX 11:00:00 PM | 0.95833 | 6 | 67.3 | 60.9 | 59.6291 | 69.7151 | 10.086 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/24/20XX 12:00:00 AM | 0 | 7 | 66.7 | 61.3 | 58.3702 | 68.238 | 9.8678 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/25/20XX 1:00:00 AM | 0.041667 | 7 | 65.6 | 64.2 | 56.1238 | 65.6025 | 9.4787 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/25/20XX 2:00:00 AM | 0.083333 | 7 | 65 | 65.3 | 54.9315 | 64.2037 | 9.2722 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/25/20XX 3:00:00 AM | 0.125 | 7 | 64.2 | 67.9 | 53.3774 | 62.3806 | 9.0032 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/25/20XX 4:00:00 AM | 0.16667 | 7 | 63.4 | 72.5 | 60.6044 | 69.4076 | 8.8031 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/25/20XX 5:00:00 AM | 0.20833 | 7 | 62.9 | 73 | 59.5179 | 68.161 | 8.6432 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/25/20XX 6:00:00 AM | 0.25 | 7 | 62.5 | 74.8 | 58.6614 | 67.1787 | 8.5172 | 70 | 62.5 |  | 62.5 | 62.7497 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 62.7497 | 14.9291 | 355311.7935 | 29.6093 | 29.6093 | 53.2343 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 62.7497 | 14.9291 | 355311.7935 | 29.6093 | 29.6093 | 53.2343 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 62.7497 | 14.9291 | 355311.7935 | 29.6093 | 29.6093 | 53.2343 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 62.7497 | 14.9291 | 355311.7935 | 29.6093 | 29.6093 | 53.2343 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 62.7497 | 14.9291 | 355311.7935 | 29.6093 | 29.6093 | 53.2343 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 62.7497 | 14.9291 | 355311.7935 | 29.6093 | 29.6093 | 53.2343 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 62.7497 | 14.9291 | 355311.7935 | 29.6093 | 29.6093 | 53.2343 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 62.7497 | 14.9291 | 355311.7935 | 29.6093 | 29.6093 | 53.2343 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 62.7497 | 14.9291 | 355311.7935 | 29.6093 | 29.6093 | 53.2343 | 1 | 62.5 | 7.5 | 283500 | 23.625 | 23.625 | 62.7497 | 14.9291 | 355311.7935 | 29.6093 | 29.6093 | 53.2343 | 60 | 75 | 24.7696 | 24 | 74.8
9/25/20XX 7:00:00 AM | 0.29167 | 7 | 63.2 | 73.9 | 60.1677 | 68.9065 | 8.7388 | 70 | 63.2 |  | 63.2 | 63.5758 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 63.5758 | 15.7552 | 374972.7749 | 31.2477 | 31.2477 | 57.0777 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 63.5758 | 15.7552 | 374972.7749 | 31.2477 | 31.2477 | 57.0777 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 63.5758 | 15.7552 | 374972.7749 | 31.2477 | 31.2477 | 57.0777 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 63.5758 | 15.7552 | 374972.7749 | 31.2477 | 31.2477 | 57.0777 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 63.5758 | 15.7552 | 374972.7749 | 31.2477 | 31.2477 | 57.0777 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 63.5758 | 15.7552 | 374972.7749 | 31.2477 | 31.2477 | 57.0777 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 63.5758 | 15.7552 | 374972.7749 | 31.2477 | 31.2477 | 57.0777 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 63.5758 | 15.7552 | 374972.7749 | 31.2477 | 31.2477 | 57.0777 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 63.5758 | 15.7552 | 374972.7749 | 31.2477 | 31.2477 | 57.0777 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 63.5758 | 15.7552 | 374972.7749 | 31.2477 | 31.2477 | 57.0777 | 65 | 75 | 25.069 | 26 | 73.9
9/25/20XX 8:00:00 AM | 0.33333 | 7 | 64.3 | 71.5 | 62.6059 | 71.704 | 9.0981 | 70 | 64.3 |  | 64.3 | 63.9706 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 63.9706 | 16.15 | 384369.0471 | 32.0308 | 32.0308 | 61.3258 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 63.9706 | 16.15 | 384369.0471 | 32.0308 | 32.0308 | 61.3258 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 63.9706 | 16.15 | 384369.0471 | 32.0308 | 32.0308 | 61.3258 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 63.9706 | 16.15 | 384369.0471 | 32.0308 | 32.0308 | 61.3258 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 63.9706 | 16.15 | 384369.0471 | 32.0308 | 32.0308 | 61.3258 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 63.9706 | 16.15 | 384369.0471 | 32.0308 | 32.0308 | 61.3258 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 63.9706 | 16.15 | 384369.0471 | 32.0308 | 32.0308 | 61.3258 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 63.9706 | 16.15 | 384369.0471 | 32.0308 | 32.0308 | 61.3258 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 63.9706 | 16.15 | 384369.0471 | 32.0308 | 32.0308 | 61.3258 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 63.9706 | 16.15 | 384369.0471 | 32.0308 | 32.0308 | 61.3258 | 65 | 70 | 25.399 | 26 | 71.5
9/25/20XX 9:00:00 AM | 0.375 | 7 | 65.8 | 66.9 | 56.5264 | 66.0748 | 9.5484 | 60 | 65.8 |  | 65.8 | 63.1148 | 0.1 | 73.18 | 18.18 | 687204 | 57.267 | 57.267 | 62.6709 | 14.8503 | 353437.4787 | 29.4531 | 29.4531 | 86.7201 | 0.2 | 72.36 | 17.36 | 656208 | 54.684 | 54.684 | 62.7203 | 14.8996 | 354611.1574 | 29.5509 | 29.5509 | 84.2349 | 0.3 | 71.54 | 16.54 | 625212 | 52.101 | 52.101 | 62.7696 | 14.9489 | 355784.8361 | 29.6487 | 29.6487 | 81.7497 | 0.4 | 70.72 | 15.72 | 594216 | 49.518 | 49.518 | 62.8189 | 14.9983 | 356958.5148 | 29.7465 | 29.7465 | 79.2645 | 0.5 | 69.9 | 14.9 | 563220 | 46.935 | 46.935 | 62.8682 | 15.0476 | 358132.1935 | 29.8443 | 29.8443 | 76.7793 | 0.6 | 69.08 | 14.08 | 532224 | 44.352 | 44.352 | 62.9175 | 15.0969 | 359305.8723 | 29.9422 | 29.9422 | 74.2942 | 0.7 | 68.26 | 13.26 | 501228 | 41.769 | 41.769 | 62.9668 | 15.1462 | 360479.551 | 30.04 | 30.04 | 71.809 | 0.8 | 67.44 | 12.44 | 470232 | 39.186 | 39.186 | 63.0161 | 15.1955 | 361653.2297 | 30.1378 | 30.1378 | 69.3238 | 0.9 | 66.62 | 11.62 | 439236 | 36.603 | 36.603 | 63.0655 | 15.2448 | 362826.9084 | 30.2356 | 30.2356 | 66.8386 | 1 | 65.8 | 10.8 | 408240 | 34.02 | 34.02 | 63.1148 | 15.2941 | 364000.5871 | 30.3334 | 30.3334 | 64.3534 | 65 | 65 | 25.6316 | 26 | 66.9
9/25/20XX 10:00:00 AM | 0.41667 | 7 | 68 | 63.8 | 61.1282 | 71.4742 | 10.346 | 60 | 68 |  | 68 | 65.0597 | 0.1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 62.8654 | 15.0448 | 358066.4003 | 29.8389 | 29.8389 | 87.7989 | 0.2 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 63.1092 | 15.2886 | 363869.0005 | 30.3224 | 30.3224 | 86.3924 | 0.3 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 63.3531 | 15.5324 | 369671.6008 | 30.806 | 30.806 | 84.986 | 0.4 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 63.5969 | 15.7762 | 375474.2011 | 31.2895 | 31.2895 | 83.5795 | 0.5 | 71 | 16 | 604800 | 50.4 | 50.4 | 63.8407 | 16.02 | 381276.8014 | 31.7731 | 31.7731 | 82.1731 | 0.6 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 64.0845 | 16.2638 | 387079.4016 | 32.2566 | 32.2566 | 80.7666 | 0.7 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 64.3283 | 16.5076 | 392882.0019 | 32.7402 | 32.7402 | 79.3602 | 0.8 | 69.2 | 14.2 | 536760 | 44.73 | 44.73 | 64.5721 | 16.7515 | 398684.6022 | 33.2237 | 33.2237 | 77.9537 | 0.9 | 68.6 | 13.6 | 514080 | 42.84 | 42.84 | 64.8159 | 16.9953 | 404487.2025 | 33.7073 | 33.7073 | 76.5473 | 1 | 68 | 13 | 491400 | 40.95 | 40.95 | 65.0597 | 17.2391 | 410289.8027 | 34.1908 | 34.1908 | 75.1408 | 70 | 65 | 26.4719 | 26 | 63.8
9/25/20XX 11:00:00 AM | 0.45833 | 7 | 70.7 | 56.9 | 55.851 | 67.227 | 11.376 | 50 | 70.7 |  | 70.7 | 63.7004 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 62.7295 | 14.9089 | 354831.3487 | 29.5693 | 29.5693 | 88.3798 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 62.8374 | 15.0168 | 357398.8973 | 29.7832 | 29.7832 | 87.5542 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 62.9453 | 15.1246 | 359966.446 | 29.9972 | 29.9972 | 86.7287 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 63.0532 | 15.2325 | 362533.9946 | 30.2112 | 30.2112 | 85.9032 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 63.161 | 15.3404 | 365101.5433 | 30.4251 | 30.4251 | 85.0776 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 63.2689 | 15.4483 | 367669.092 | 30.6391 | 30.6391 | 84.2521 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 63.3768 | 15.5562 | 370236.6406 | 30.8531 | 30.8531 | 83.4266 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 63.4847 | 15.664 | 372804.1893 | 31.067 | 31.067 | 82.601 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 63.5926 | 15.7719 | 375371.7379 | 31.281 | 31.281 | 81.7755 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 63.7004 | 15.8798 | 377939.2866 | 31.4949 | 31.4949 | 80.9499 | 70 | 55 | 26.9188 | 26 | 56.9
9/25/20XX 12:00:00 PM | 0.5 | 7 | 71.5 | 56.3 | 57.4315 | 69.1333 | 11.7019 | 50 | 71.5 |  | 71.5 | 64.8037 | 0.1 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 62.8398 | 15.0192 | 357457.0061 | 29.7881 | 29.7881 | 88.8506 | 0.2 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 63.058 | 15.2374 | 362650.2122 | 30.2209 | 30.2209 | 88.4959 | 0.3 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 63.2762 | 15.4556 | 367843.4183 | 30.6536 | 30.6536 | 88.1411 | 0.4 | 73 | 18 | 680400 | 56.7 | 56.7 | 63.4944 | 15.6738 | 373036.6244 | 31.0864 | 31.0864 | 87.7864 | 0.5 | 72.75 | 17.75 | 670950 | 55.9125 | 55.9125 | 63.7126 | 15.892 | 378229.8305 | 31.5192 | 31.5192 | 87.4317 | 0.6 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 63.9308 | 16.1102 | 383423.0366 | 31.9519 | 31.9519 | 87.0769 | 0.7 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 64.149 | 16.3284 | 388616.2427 | 32.3847 | 32.3847 | 86.7222 | 0.8 | 72 | 17 | 642600 | 53.55 | 53.55 | 64.3672 | 16.5466 | 393809.4488 | 32.8175 | 32.8175 | 86.3675 | 0.9 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 64.5854 | 16.7648 | 399002.6549 | 33.2502 | 33.2502 | 86.0127 | 1 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 64.8037 | 16.983 | 404195.861 | 33.683 | 33.683 | 85.658 | 70 | 55 | 27.2864 | 28 | 56.3
9/25/20XX 1:00:00 PM | 0.54167 | 7 | 73.5 | 53 | 61.5526 | 74.1052 | 12.5526 | 50 | 73.5 |  | 73.5 | 65.3184 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 62.8913 | 15.0707 | 358682.0861 | 29.8902 | 29.8902 | 89.5827 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 63.161 | 15.3404 | 365100.3722 | 30.425 | 30.425 | 89.96 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 63.4307 | 15.61 | 371518.6583 | 30.9599 | 30.9599 | 90.3374 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 63.7003 | 15.8797 | 377936.9444 | 31.4947 | 31.4947 | 90.7147 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 63.97 | 16.1494 | 384355.2304 | 32.0296 | 32.0296 | 91.0921 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.2397 | 16.4191 | 390773.5165 | 32.5645 | 32.5645 | 91.4695 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 64.5094 | 16.6887 | 397191.8026 | 33.0993 | 33.0993 | 91.8468 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 64.779 | 16.9584 | 403610.0887 | 33.6342 | 33.6342 | 92.2242 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 65.0487 | 17.2281 | 410028.3748 | 34.169 | 34.169 | 92.6015 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 65.3184 | 17.4978 | 416446.6609 | 34.7039 | 34.7039 | 92.9789 | 75 | 55 | 27.8551 | 28 | 53
9/25/20XX 2:00:00 PM | 0.58333 | 7 | 73.9 | 53.1 | 62.4066 | 75.1356 | 12.7291 | 50 | 73.9 |  | 73.9 | 66.3526 | 0.1 | 73.99 | 18.99 | 717822 | 59.8185 | 59.8185 | 62.9947 | 15.1741 | 361143.4572 | 30.0953 | 30.0953 | 89.9138 | 0.2 | 73.98 | 18.98 | 717444 | 59.787 | 59.787 | 63.3678 | 15.5472 | 370023.1145 | 30.8353 | 30.8353 | 90.6223 | 0.3 | 73.97 | 18.97 | 717066 | 59.7555 | 59.7555 | 63.7409 | 15.9203 | 378902.7717 | 31.5752 | 31.5752 | 91.3307 | 0.4 | 73.96 | 18.96 | 716688 | 59.724 | 59.724 | 64.114 | 16.2934 | 387782.4289 | 32.3152 | 32.3152 | 92.0392 | 0.5 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 64.4871 | 16.6665 | 396662.0862 | 33.0552 | 33.0552 | 92.7477 | 0.6 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 64.8602 | 17.0396 | 405541.7434 | 33.7951 | 33.7951 | 93.4561 | 0.7 | 73.93 | 18.93 | 715554 | 59.6295 | 59.6295 | 65.2333 | 17.4127 | 414421.4006 | 34.5351 | 34.5351 | 94.1646 | 0.8 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 65.6064 | 17.7858 | 423301.0578 | 35.2751 | 35.2751 | 94.8731 | 0.9 | 73.91 | 18.91 | 714798 | 59.5665 | 59.5665 | 65.9795 | 18.1589 | 432180.7151 | 36.0151 | 36.0151 | 95.5816 | 1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 66.3526 | 18.5319 | 441060.3723 | 36.755 | 36.755 | 96.29 | 75 | 55 | 28.1145 | 28 | 53.1
9/25/20XX 3:00:00 PM | 0.625 | 7 | 73.4 | 53.5 | 61.3407 | 73.8495 | 12.5088 | 50 | 73.4 |  | 73.4 | 65.7188 | 0.1 | 73.94 | 18.94 | 715932 | 59.661 | 59.661 | 62.9313 | 15.1107 | 359634.9978 | 29.9696 | 29.9696 | 89.6306 | 0.2 | 73.88 | 18.88 | 713664 | 59.472 | 59.472 | 63.2411 | 15.4204 | 367006.1957 | 30.5838 | 30.5838 | 90.0558 | 0.3 | 73.82 | 18.82 | 711396 | 59.283 | 59.283 | 63.5508 | 15.7301 | 374377.3935 | 31.1981 | 31.1981 | 90.4811 | 0.4 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 63.8605 | 16.0399 | 381748.5914 | 31.8124 | 31.8124 | 90.9064 | 0.5 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.1702 | 16.3496 | 389119.7892 | 32.4266 | 32.4266 | 91.3316 | 0.6 | 73.64 | 18.64 | 704592 | 58.716 | 58.716 | 64.4799 | 16.6593 | 396490.9871 | 33.0409 | 33.0409 | 91.7569 | 0.7 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 64.7896 | 16.969 | 403862.1849 | 33.6552 | 33.6552 | 92.1822 | 0.8 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 65.0993 | 17.2787 | 411233.3827 | 34.2694 | 34.2694 | 92.6074 | 0.9 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 65.4091 | 17.5884 | 418604.5806 | 34.8837 | 34.8837 | 93.0327 | 1 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 65.7188 | 17.8981 | 425975.7784 | 35.498 | 35.498 | 93.458 | 75 | 55 | 27.8933 | 28 | 53.5
9/25/20XX 4:00:00 PM | 0.66667 | 7 | 72.5 | 53.6 | 59.4614 | 71.5821 | 12.1207 | 50 | 72.5 |  | 72.5 | 63.8248 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 62.7419 | 14.9213 | 355127.3485 | 29.5939 | 29.5939 | 88.9714 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 62.8623 | 15.0416 | 357990.897 | 29.8326 | 29.8326 | 88.7376 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 62.9826 | 15.162 | 360854.4455 | 30.0712 | 30.0712 | 88.5037 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 63.1029 | 15.2823 | 363717.994 | 30.3098 | 30.3098 | 88.2698 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 63.2232 | 15.4026 | 366581.5425 | 30.5485 | 30.5485 | 88.036 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 63.3435 | 15.5229 | 369445.091 | 30.7871 | 30.7871 | 87.8021 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 63.4639 | 15.6432 | 372308.6395 | 31.0257 | 31.0257 | 87.5682 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 63.5842 | 15.7635 | 375172.188 | 31.2643 | 31.2643 | 87.3343 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 63.7045 | 15.8839 | 378035.7365 | 31.503 | 31.503 | 87.1005 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 63.8248 | 16.0042 | 380899.285 | 31.7416 | 31.7416 | 86.8666 | 70 | 55 | 27.3775 | 28 | 53.6
9/25/20XX 5:00:00 PM | 0.70833 | 7 | 71.3 | 55.1 | 57.0328 | 68.6524 | 11.6196 | 50 | 71.3 |  | 71.3 | 62.9588 | 0.1 | 73.73 | 18.73 | 707994 | 58.9995 | 58.9995 | 62.6553 | 14.8347 | 353066.2126 | 29.4222 | 29.4222 | 88.4217 | 0.2 | 73.46 | 18.46 | 697788 | 58.149 | 58.149 | 62.6891 | 14.8684 | 353868.6252 | 29.4891 | 29.4891 | 87.6381 | 0.3 | 73.19 | 18.19 | 687582 | 57.2985 | 57.2985 | 62.7228 | 14.9021 | 354671.0378 | 29.5559 | 29.5559 | 86.8544 | 0.4 | 72.92 | 17.92 | 677376 | 56.448 | 56.448 | 62.7565 | 14.9359 | 355473.4504 | 29.6228 | 29.6228 | 86.0708 | 0.5 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 62.7902 | 14.9696 | 356275.863 | 29.6897 | 29.6897 | 85.2872 | 0.6 | 72.38 | 17.38 | 656964 | 54.747 | 54.747 | 62.8239 | 15.0033 | 357078.2757 | 29.7565 | 29.7565 | 84.5035 | 0.7 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 62.8576 | 15.037 | 357880.6883 | 29.8234 | 29.8234 | 83.7199 | 0.8 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 62.8914 | 15.0707 | 358683.1009 | 29.8903 | 29.8903 | 82.9363 | 0.9 | 71.57 | 16.57 | 626346 | 52.1955 | 52.1955 | 62.9251 | 15.1044 | 359485.5135 | 29.9571 | 29.9571 | 82.1526 | 1 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 62.9588 | 15.1381 | 360287.9261 | 30.024 | 30.024 | 81.369 | 70 | 55 | 26.9493 | 26 | 55.1
9/25/20XX 6:00:00 PM | 0.75 | 7 | 69.7 | 57.2 | 53.9286 | 64.9086 | 10.98 | 50 | 69.7 |  | 69.7 | 61.8342 | 0.1 | 73.57 | 18.57 | 701946 | 58.4955 | 58.4955 | 62.5429 | 14.7223 | 350389.8038 | 29.1992 | 29.1992 | 87.6947 | 0.2 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 62.4642 | 14.6435 | 348515.8075 | 29.043 | 29.043 | 86.184 | 0.3 | 72.71 | 17.71 | 669438 | 55.7865 | 55.7865 | 62.3854 | 14.5648 | 346641.8113 | 28.8868 | 28.8868 | 84.6733 | 0.4 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 62.3067 | 14.486 | 344767.8151 | 28.7307 | 28.7307 | 83.1627 | 0.5 | 71.85 | 16.85 | 636930 | 53.0775 | 53.0775 | 62.2279 | 14.4073 | 342893.8188 | 28.5745 | 28.5745 | 81.652 | 0.6 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 62.1492 | 14.3286 | 341019.8226 | 28.4183 | 28.4183 | 80.1413 | 0.7 | 70.99 | 15.99 | 604422 | 50.3685 | 50.3685 | 62.0705 | 14.2498 | 339145.8264 | 28.2622 | 28.2622 | 78.6307 | 0.8 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 61.9917 | 14.1711 | 337271.8301 | 28.106 | 28.106 | 77.12 | 0.9 | 70.13 | 15.13 | 571914 | 47.6595 | 47.6595 | 61.913 | 14.0923 | 335397.8339 | 27.9498 | 27.9498 | 75.6093 | 1 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 61.8342 | 14.0136 | 333523.8376 | 27.7937 | 27.7937 | 74.0987 | 70 | 55 | 26.3833 | 26 | 57.2
9/25/20XX 7:00:00 PM | 0.79167 | 7 | 68.2 | 58.3 | 51.1536 | 61.5627 | 10.4091 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/25/20XX 8:00:00 PM | 0.83333 | 7 | 67.9 | 60.9 | 60.912 | 71.2205 | 10.3085 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/25/20XX 9:00:00 PM | 0.875 | 7 | 67 | 63.6 | 58.9966 | 68.973 | 9.9764 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/25/20XX 10:00:00 PM | 0.91667 | 7 | 66.1 | 65.8 | 57.1351 | 66.7889 | 9.6538 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/25/20XX 11:00:00 PM | 0.95833 | 7 | 65.3 | 69.3 | 55.5248 | 64.8997 | 9.3749 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/25/20XX 12:00:00 AM | 0 | 1 | 64.9 | 70.4 | 63.9732 | 73.2731 | 9.2999 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/26/20XX 1:00:00 AM | 0.041667 | 1 | 64.6 | 71.1 | 63.2862 | 72.4847 | 9.1985 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/26/20XX 2:00:00 AM | 0.083333 | 1 | 63.6 | 73.6 | 61.0441 | 69.912 | 8.8679 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/26/20XX 3:00:00 AM | 0.125 | 1 | 63.8 | 73 | 61.4867 | 70.4198 | 8.9331 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/26/20XX 4:00:00 AM | 0.16667 | 1 | 63.5 | 73.8 | 60.8239 | 69.6593 | 8.8354 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/26/20XX 5:00:00 AM | 0.20833 | 1 | 63.2 | 74.5 | 60.1677 | 68.9065 | 8.7388 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/26/20XX 6:00:00 AM | 0.25 | 1 | 63.1 | 76.7 | 59.9503 | 68.6572 | 8.7068 | 70 | 63.1 |  | 63.1 | 65.7839 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 65.7839 | 17.9633 | 427525.9725 | 35.6272 | 35.6272 | 61.1422 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 65.7839 | 17.9633 | 427525.9725 | 35.6272 | 35.6272 | 61.1422 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 65.7839 | 17.9633 | 427525.9725 | 35.6272 | 35.6272 | 61.1422 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 65.7839 | 17.9633 | 427525.9725 | 35.6272 | 35.6272 | 61.1422 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 65.7839 | 17.9633 | 427525.9725 | 35.6272 | 35.6272 | 61.1422 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 65.7839 | 17.9633 | 427525.9725 | 35.6272 | 35.6272 | 61.1422 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 65.7839 | 17.9633 | 427525.9725 | 35.6272 | 35.6272 | 61.1422 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 65.7839 | 17.9633 | 427525.9725 | 35.6272 | 35.6272 | 61.1422 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 65.7839 | 17.9633 | 427525.9725 | 35.6272 | 35.6272 | 61.1422 | 1 | 63.1 | 8.1 | 306180 | 25.515 | 25.515 | 65.7839 | 17.9633 | 427525.9725 | 35.6272 | 35.6272 | 61.1422 | 65 | 75 | 25.3885 | 26 | 76.7
9/26/20XX 7:00:00 AM | 0.29167 | 1 | 63.8 | 74.3 | 61.4867 | 70.4198 | 8.9331 | 70 | 63.8 |  | 63.8 | 65.3279 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 65.3279 | 17.5073 | 416673.1575 | 34.7228 | 34.7228 | 62.4428 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 65.3279 | 17.5073 | 416673.1575 | 34.7228 | 34.7228 | 62.4428 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 65.3279 | 17.5073 | 416673.1575 | 34.7228 | 34.7228 | 62.4428 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 65.3279 | 17.5073 | 416673.1575 | 34.7228 | 34.7228 | 62.4428 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 65.3279 | 17.5073 | 416673.1575 | 34.7228 | 34.7228 | 62.4428 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 65.3279 | 17.5073 | 416673.1575 | 34.7228 | 34.7228 | 62.4428 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 65.3279 | 17.5073 | 416673.1575 | 34.7228 | 34.7228 | 62.4428 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 65.3279 | 17.5073 | 416673.1575 | 34.7228 | 34.7228 | 62.4428 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 65.3279 | 17.5073 | 416673.1575 | 34.7228 | 34.7228 | 62.4428 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 65.3279 | 17.5073 | 416673.1575 | 34.7228 | 34.7228 | 62.4428 | 65 | 75 | 25.4884 | 26 | 74.3
9/26/20XX 8:00:00 AM | 0.33333 | 1 | 65.3 | 71.2 | 64.8997 | 74.3365 | 9.4368 | 70 | 65.3 |  | 65.3 | 66.0321 | 0.1 | 73.13 | 18.13 | 685314 | 57.1095 | 57.1095 | 62.9627 | 15.142 | 360380.772 | 30.0317 | 30.0317 | 87.1412 | 0.2 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 63.3037 | 15.4831 | 368497.7439 | 30.7081 | 30.7081 | 85.0771 | 0.3 | 71.39 | 16.39 | 619542 | 51.6285 | 51.6285 | 63.6448 | 15.8241 | 376614.7159 | 31.3846 | 31.3846 | 83.0131 | 0.4 | 70.52 | 15.52 | 586656 | 48.888 | 48.888 | 63.9858 | 16.1652 | 384731.6878 | 32.061 | 32.061 | 80.949 | 0.5 | 69.65 | 14.65 | 553770 | 46.1475 | 46.1475 | 64.3269 | 16.5062 | 392848.6598 | 32.7374 | 32.7374 | 78.8849 | 0.6 | 68.78 | 13.78 | 520884 | 43.407 | 43.407 | 64.6679 | 16.8473 | 400965.6317 | 33.4138 | 33.4138 | 76.8208 | 0.7 | 67.91 | 12.91 | 487998 | 40.6665 | 40.6665 | 65.009 | 17.1883 | 409082.6037 | 34.0902 | 34.0902 | 74.7567 | 0.8 | 67.04 | 12.04 | 455112 | 37.926 | 37.926 | 65.35 | 17.5294 | 417199.5757 | 34.7666 | 34.7666 | 72.6926 | 0.9 | 66.17 | 11.17 | 422226 | 35.1855 | 35.1855 | 65.6911 | 17.8704 | 425316.5476 | 35.443 | 35.443 | 70.6285 | 1 | 65.3 | 10.3 | 389340 | 32.445 | 32.445 | 66.0321 | 18.2115 | 433433.5196 | 36.1195 | 36.1195 | 68.5645 | 65 | 70 | 25.9644 | 26 | 71.2
9/26/20XX 9:00:00 AM | 0.375 | 1 | 67.3 | 68.3 | 59.6291 | 69.7151 | 10.086 | 60 | 67.3 |  | 67.3 | 68.0005 | 0.1 | 73.33 | 18.33 | 692874 | 57.7395 | 57.7395 | 63.1595 | 15.3389 | 365065.4402 | 30.4221 | 30.4221 | 88.1616 | 0.2 | 72.66 | 17.66 | 667548 | 55.629 | 55.629 | 63.6974 | 15.8768 | 377867.0804 | 31.4889 | 31.4889 | 87.1179 | 0.3 | 71.99 | 16.99 | 642222 | 53.5185 | 53.5185 | 64.2353 | 16.4147 | 390668.7205 | 32.5557 | 32.5557 | 86.0742 | 0.4 | 71.32 | 16.32 | 616896 | 51.408 | 51.408 | 64.7732 | 16.9525 | 403470.3607 | 33.6225 | 33.6225 | 85.0305 | 0.5 | 70.65 | 15.65 | 591570 | 49.2975 | 49.2975 | 65.3111 | 17.4904 | 416272.0009 | 34.6893 | 34.6893 | 83.9868 | 0.6 | 69.98 | 14.98 | 566244 | 47.187 | 47.187 | 65.8489 | 18.0283 | 429073.6411 | 35.7561 | 35.7561 | 82.9431 | 0.7 | 69.31 | 14.31 | 540918 | 45.0765 | 45.0765 | 66.3868 | 18.5662 | 441875.2812 | 36.8229 | 36.8229 | 81.8994 | 0.8 | 68.64 | 13.64 | 515592 | 42.966 | 42.966 | 66.9247 | 19.1041 | 454676.9214 | 37.8897 | 37.8897 | 80.8557 | 0.9 | 67.97 | 12.97 | 490266 | 40.8555 | 40.8555 | 67.4626 | 19.642 | 467478.5616 | 38.9565 | 38.9565 | 79.812 | 1 | 67.3 | 12.3 | 464940 | 38.745 | 38.745 | 68.0005 | 20.1798 | 480280.2018 | 40.0234 | 40.0234 | 78.7684 | 65 | 70 | 26.7598 | 26 | 68.3
9/26/20XX 10:00:00 AM | 0.41667 | 1 | 68.9 | 66.4 | 63.1047 | 73.7935 | 10.6888 | 60 | 68.9 |  | 68.9 | 69.9455 | 0.1 | 73.49 | 18.49 | 698922 | 58.2435 | 58.2435 | 63.354 | 15.5334 | 369694.7057 | 30.8079 | 30.8079 | 89.0514 | 0.2 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 64.0864 | 16.2658 | 387125.6115 | 32.2605 | 32.2605 | 88.8975 | 0.3 | 72.47 | 17.47 | 660366 | 55.0305 | 55.0305 | 64.8188 | 16.9982 | 404556.5172 | 33.713 | 33.713 | 88.7435 | 0.4 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 65.5512 | 17.7306 | 421987.4229 | 35.1656 | 35.1656 | 88.5896 | 0.5 | 71.45 | 16.45 | 621810 | 51.8175 | 51.8175 | 66.2836 | 18.463 | 439418.3287 | 36.6182 | 36.6182 | 88.4357 | 0.6 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 67.016 | 19.1953 | 456849.2344 | 38.0708 | 38.0708 | 88.2818 | 0.7 | 70.43 | 15.43 | 583254 | 48.6045 | 48.6045 | 67.7484 | 19.9277 | 474280.1401 | 39.5233 | 39.5233 | 88.1278 | 0.8 | 69.92 | 14.92 | 563976 | 46.998 | 46.998 | 68.4808 | 20.6601 | 491711.0459 | 40.9759 | 40.9759 | 87.9739 | 0.9 | 69.41 | 14.41 | 544698 | 45.3915 | 45.3915 | 69.2132 | 21.3925 | 509141.9516 | 42.4285 | 42.4285 | 87.82 | 1 | 68.9 | 13.9 | 525420 | 43.785 | 43.785 | 69.9455 | 22.1249 | 526572.8573 | 43.8811 | 43.8811 | 87.6661 | 70 | 65 | 27.4543 | 28 | 66.4
9/26/20XX 11:00:00 AM | 0.45833 | 1 | 70.9 | 61.3 | 67.6992 | 79.1855 | 11.4863 | 60 | 70.9 |  | 70.9 | 69.1925 | 0.1 | 73.69 | 18.69 | 706482 | 58.8735 | 58.8735 | 63.2787 | 15.4581 | 367902.3823 | 30.6585 | 30.6585 | 89.532 | 0.2 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 63.9358 | 16.1152 | 383540.9647 | 31.9617 | 31.9617 | 89.8587 | 0.3 | 73.07 | 18.07 | 683046 | 56.9205 | 56.9205 | 64.5929 | 16.7722 | 399179.547 | 33.265 | 33.265 | 90.1855 | 0.4 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 65.25 | 17.4293 | 414818.1293 | 34.5682 | 34.5682 | 90.5122 | 0.5 | 72.45 | 17.45 | 659610 | 54.9675 | 54.9675 | 65.907 | 18.0864 | 430456.7117 | 35.8714 | 35.8714 | 90.8389 | 0.6 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 66.5641 | 18.7435 | 446095.294 | 37.1746 | 37.1746 | 91.1656 | 0.7 | 71.83 | 16.83 | 636174 | 53.0145 | 53.0145 | 67.2212 | 19.4006 | 461733.8763 | 38.4778 | 38.4778 | 91.4923 | 0.8 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 67.8783 | 20.0577 | 477372.4587 | 39.781 | 39.781 | 91.819 | 0.9 | 71.21 | 16.21 | 612738 | 51.0615 | 51.0615 | 68.5354 | 20.7147 | 493011.041 | 41.0843 | 41.0843 | 92.1458 | 1 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 69.1925 | 21.3718 | 508649.6233 | 42.3875 | 42.3875 | 92.4725 | 70 | 60 | 27.8256 | 28 | 61.3
9/26/20XX 12:00:00 PM | 0.5 | 1 | 72.4 | 58.9 | 59.2556 | 71.3339 | 12.0782 | 50 | 72.4 |  | 72.4 | 70.0053 | 0.1 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 63.36 | 15.5394 | 369836.813 | 30.8197 | 30.8197 | 90.1657 | 0.2 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 64.0984 | 16.2777 | 387409.8261 | 32.2842 | 32.2842 | 91.1262 | 0.3 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 64.8367 | 17.0161 | 404982.8391 | 33.7486 | 33.7486 | 92.0866 | 0.4 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 65.5751 | 17.7544 | 422555.8522 | 35.213 | 35.213 | 93.047 | 0.5 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 66.3134 | 18.4928 | 440128.8652 | 36.6774 | 36.6774 | 94.0074 | 0.6 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 67.0518 | 19.2312 | 457701.8783 | 38.1418 | 38.1418 | 94.9678 | 0.7 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 67.7902 | 19.9695 | 475274.8913 | 39.6062 | 39.6062 | 95.9282 | 0.8 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 68.5285 | 20.7079 | 492847.9044 | 41.0707 | 41.0707 | 96.8887 | 0.9 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 69.2669 | 21.4463 | 510420.9174 | 42.5351 | 42.5351 | 97.8491 | 1 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 70.0053 | 22.1846 | 527993.9305 | 43.9995 | 43.9995 | 98.8095 | 70 | 60 | 28.3192 | 28 | 58.9
9/26/20XX 1:00:00 PM | 0.54167 | 1 | 73 | 58.5 | 60.4992 | 72.8342 | 12.335 | 50 | 73 |  | 73 | 70.984 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 63.4579 | 15.6372 | 372166.2008 | 31.0139 | 31.0139 | 90.5489 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.2941 | 16.4735 | 392068.6017 | 32.6724 | 32.6724 | 91.8924 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 65.1303 | 17.3097 | 411971.0025 | 34.3309 | 34.3309 | 93.2359 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 65.9666 | 18.1459 | 431873.4033 | 35.9895 | 35.9895 | 94.5795 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 66.8028 | 18.9822 | 451775.8042 | 37.648 | 37.648 | 95.923 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 67.639 | 19.8184 | 471678.205 | 39.3065 | 39.3065 | 97.2665 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 68.4753 | 20.6546 | 491580.6058 | 40.9651 | 40.9651 | 98.6101 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 69.3115 | 21.4909 | 511483.0066 | 42.6236 | 42.6236 | 99.9536 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 70.1478 | 22.3271 | 531385.4075 | 44.2821 | 44.2821 | 101.2971 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 70.984 | 23.1634 | 551287.8083 | 45.9407 | 45.9407 | 102.6407 | 75 | 60 | 28.6189 | 28 | 58.5
9/26/20XX 2:00:00 PM | 0.58333 | 1 | 73.5 | 56.8 | 61.5526 | 74.1052 | 12.5526 | 50 | 73.5 |  | 73.5 | 70.0884 | 0.1 | 73.95 | 18.95 | 716310 | 59.6925 | 59.6925 | 63.3683 | 15.5477 | 370034.6537 | 30.8362 | 30.8362 | 90.5287 | 0.2 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.115 | 16.2943 | 387805.5074 | 32.3171 | 32.3171 | 91.8521 | 0.3 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 64.8617 | 17.041 | 405576.3612 | 33.798 | 33.798 | 93.1755 | 0.4 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 65.6083 | 17.7877 | 423347.2149 | 35.2789 | 35.2789 | 94.4989 | 0.5 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 66.355 | 18.5344 | 441118.0686 | 36.7598 | 36.7598 | 95.8223 | 0.6 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 67.1017 | 19.281 | 458888.9223 | 38.2407 | 38.2407 | 97.1457 | 0.7 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 67.8484 | 20.0277 | 476659.776 | 39.7216 | 39.7216 | 98.4691 | 0.8 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 68.595 | 20.7744 | 494430.6298 | 41.2026 | 41.2026 | 99.7926 | 0.9 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 69.3417 | 21.5211 | 512201.4835 | 42.6835 | 42.6835 | 101.116 | 1 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 70.0884 | 22.2677 | 529972.3372 | 44.1644 | 44.1644 | 102.4394 | 75 | 55 | 28.6011 | 28 | 56.8
9/26/20XX 3:00:00 PM | 0.625 | 1 | 73.2 | 58.1 | 60.9187 | 73.3404 | 12.4216 | 50 | 73.2 |  | 73.2 | 70.9802 | 0.1 | 73.92 | 18.92 | 715176 | 59.598 | 59.598 | 63.4575 | 15.6369 | 372157.3049 | 31.0131 | 31.0131 | 90.6111 | 0.2 | 73.84 | 18.84 | 712152 | 59.346 | 59.346 | 64.2934 | 16.4727 | 392050.8098 | 32.6709 | 32.6709 | 92.0169 | 0.3 | 73.76 | 18.76 | 709128 | 59.094 | 59.094 | 65.1292 | 17.3086 | 411944.3147 | 34.3287 | 34.3287 | 93.4227 | 0.4 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 65.9651 | 18.1444 | 431837.8196 | 35.9865 | 35.9865 | 94.8285 | 0.5 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 66.8009 | 18.9803 | 451731.3244 | 37.6443 | 37.6443 | 96.2343 | 0.6 | 73.52 | 18.52 | 700056 | 58.338 | 58.338 | 67.6368 | 19.8162 | 471624.8293 | 39.3021 | 39.3021 | 97.6401 | 0.7 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 68.4727 | 20.652 | 491518.3342 | 40.9599 | 40.9599 | 99.0459 | 0.8 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 69.3085 | 21.4879 | 511411.8391 | 42.6177 | 42.6177 | 100.4517 | 0.9 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 70.1444 | 22.3238 | 531305.344 | 44.2754 | 44.2754 | 101.8574 | 1 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 70.9802 | 23.1596 | 551198.8489 | 45.9332 | 45.9332 | 103.2632 | 75 | 60 | 28.6672 | 28 | 58.1
9/26/20XX 4:00:00 PM | 0.66667 | 1 | 72.6 | 58.8 | 59.6677 | 71.831 | 12.1633 | 50 | 72.6 |  | 72.6 | 70.3714 | 0.1 | 73.86 | 18.86 | 712908 | 59.409 | 59.409 | 63.3966 | 15.576 | 370708.2471 | 30.8924 | 30.8924 | 90.3014 | 0.2 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 64.1716 | 16.351 | 389152.6943 | 32.4294 | 32.4294 | 91.3974 | 0.3 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 64.9466 | 17.1259 | 407597.1414 | 33.9664 | 33.9664 | 92.4934 | 0.4 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 65.7215 | 17.9009 | 426041.5885 | 35.5035 | 35.5035 | 93.5895 | 0.5 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 66.4965 | 18.6759 | 444486.0357 | 37.0405 | 37.0405 | 94.6855 | 0.6 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 67.2715 | 19.4509 | 462930.4828 | 38.5775 | 38.5775 | 95.7815 | 0.7 | 73.02 | 18.02 | 681156 | 56.763 | 56.763 | 68.0465 | 20.2258 | 481374.9299 | 40.1146 | 40.1146 | 96.8776 | 0.8 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 68.8214 | 21.0008 | 499819.3771 | 41.6516 | 41.6516 | 97.9736 | 0.9 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 69.5964 | 21.7758 | 518263.8242 | 43.1887 | 43.1887 | 99.0697 | 1 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 70.3714 | 22.5508 | 536708.2713 | 44.7257 | 44.7257 | 100.1657 | 75 | 60 | 28.4253 | 28 | 58.8
9/26/20XX 5:00:00 PM | 0.70833 | 1 | 71.2 | 60 | 68.413 | 80.0233 | 11.6102 | 60 | 71.2 |  | 71.2 | 68.413 | 0.1 | 73.72 | 18.72 | 707616 | 58.968 | 58.968 | 63.2008 | 15.3801 | 366047.3275 | 30.5039 | 30.5039 | 89.4719 | 0.2 | 73.44 | 18.44 | 697032 | 58.086 | 58.086 | 63.7799 | 15.9593 | 379830.8549 | 31.6526 | 31.6526 | 89.7386 | 0.3 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 64.3591 | 16.5384 | 393614.3824 | 32.8012 | 32.8012 | 90.0052 | 0.4 | 72.88 | 17.88 | 675864 | 56.322 | 56.322 | 64.9382 | 17.1176 | 407397.9098 | 33.9498 | 33.9498 | 90.2718 | 0.5 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 65.5173 | 17.6967 | 421181.4373 | 35.0985 | 35.0985 | 90.5385 | 0.6 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 66.0965 | 18.2758 | 434964.9647 | 36.2471 | 36.2471 | 90.8051 | 0.7 | 72.04 | 17.04 | 644112 | 53.676 | 53.676 | 66.6756 | 18.855 | 448748.4922 | 37.3957 | 37.3957 | 91.0717 | 0.8 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 67.2548 | 19.4341 | 462532.0196 | 38.5443 | 38.5443 | 91.3383 | 0.9 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 67.8339 | 20.0133 | 476315.5471 | 39.693 | 39.693 | 91.605 | 1 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 68.413 | 20.5924 | 490099.0745 | 40.8416 | 40.8416 | 91.8716 | 70 | 60 | 27.7771 | 28 | 60
9/26/20XX 6:00:00 PM | 0.75 | 1 | 69.9 | 63.3 | 65.3666 | 76.4479 | 11.0813 | 60 | 69.9 |  | 69.9 | 69.0235 | 0.1 | 73.59 | 18.59 | 702702 | 58.5585 | 58.5585 | 63.2618 | 15.4412 | 367500.179 | 30.625 | 30.625 | 89.1835 | 0.2 | 73.18 | 18.18 | 687204 | 57.267 | 57.267 | 63.902 | 16.0814 | 382736.5581 | 31.8947 | 31.8947 | 89.1617 | 0.3 | 72.77 | 17.77 | 671706 | 55.9755 | 55.9755 | 64.5422 | 16.7216 | 397972.9371 | 33.1644 | 33.1644 | 89.1399 | 0.4 | 72.36 | 17.36 | 656208 | 54.684 | 54.684 | 65.1824 | 17.3617 | 413209.3162 | 34.4341 | 34.4341 | 89.1181 | 0.5 | 71.95 | 16.95 | 640710 | 53.3925 | 53.3925 | 65.8226 | 18.0019 | 428445.6952 | 35.7038 | 35.7038 | 89.0963 | 0.6 | 71.54 | 16.54 | 625212 | 52.101 | 52.101 | 66.4627 | 18.6421 | 443682.0742 | 36.9735 | 36.9735 | 89.0745 | 0.7 | 71.13 | 16.13 | 609714 | 50.8095 | 50.8095 | 67.1029 | 19.2823 | 458918.4533 | 38.2432 | 38.2432 | 89.0527 | 0.8 | 70.72 | 15.72 | 594216 | 49.518 | 49.518 | 67.7431 | 19.9225 | 474154.8323 | 39.5129 | 39.5129 | 89.0309 | 0.9 | 70.31 | 15.31 | 578718 | 48.2265 | 48.2265 | 68.3833 | 20.5627 | 489391.2114 | 40.7826 | 40.7826 | 89.0091 | 1 | 69.9 | 14.9 | 563220 | 46.935 | 46.935 | 69.0235 | 21.2028 | 504627.5904 | 42.0523 | 42.0523 | 88.9873 | 70 | 65 | 27.5548 | 28 | 63.3
9/26/20XX 7:00:00 PM | 0.79167 | 1 | 69.2 | 66 | 63.776 | 74.5812 | 10.8052 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/26/20XX 8:00:00 PM | 0.83333 | 1 | 68.6 | 69.8 | 62.4397 | 73.0131 | 10.5734 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/26/20XX 9:00:00 PM | 0.875 | 1 | 67.5 | 73.3 | 70.2137 | 80.4375 | 10.2238 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/26/20XX 10:00:00 PM | 0.91667 | 1 | 66.7 | 75.7 | 68.238 | 78.1688 | 9.9308 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/26/20XX 11:00:00 PM | 0.95833 | 1 | 65.9 | 79.5 | 66.3121 | 75.9577 | 9.6456 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/26/20XX 12:00:00 AM | 0 | 2 | 65.6 | 79.2 | 65.6025 | 75.1431 | 9.5407 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/27/20XX 1:00:00 AM | 0.041667 | 2 | 65.5 | 79.8 | 65.3675 | 74.8734 | 9.5059 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/27/20XX 2:00:00 AM | 0.083333 | 2 | 64.5 | 81.3 | 72.2236 | 81.367 | 9.1434 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/27/20XX 3:00:00 AM | 0.125 | 2 | 64.1 | 83 | 71.1877 | 80.1964 | 9.0087 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/27/20XX 4:00:00 AM | 0.16667 | 2 | 64 | 83.4 | 70.9309 | 79.9062 | 8.9753 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/27/20XX 5:00:00 AM | 0.20833 | 2 | 63.4 | 83.7 | 69.4076 | 78.1848 | 8.7773 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/27/20XX 6:00:00 AM | 0.25 | 2 | 63.2 | 84.5 | 68.9065 | 77.6187 | 8.7122 | 80 | 63.2 |  | 63.2 | 72.827 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 72.827 | 25.0063 | 595150.6589 | 49.5959 | 49.5959 | 75.4259 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 72.827 | 25.0063 | 595150.6589 | 49.5959 | 49.5959 | 75.4259 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 72.827 | 25.0063 | 595150.6589 | 49.5959 | 49.5959 | 75.4259 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 72.827 | 25.0063 | 595150.6589 | 49.5959 | 49.5959 | 75.4259 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 72.827 | 25.0063 | 595150.6589 | 49.5959 | 49.5959 | 75.4259 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 72.827 | 25.0063 | 595150.6589 | 49.5959 | 49.5959 | 75.4259 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 72.827 | 25.0063 | 595150.6589 | 49.5959 | 49.5959 | 75.4259 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 72.827 | 25.0063 | 595150.6589 | 49.5959 | 49.5959 | 75.4259 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 72.827 | 25.0063 | 595150.6589 | 49.5959 | 49.5959 | 75.4259 | 1 | 63.2 | 8.2 | 309960 | 25.83 | 25.83 | 72.827 | 25.0063 | 595150.6589 | 49.5959 | 49.5959 | 75.4259 | 65 | 85 | 26.5098 | 26 | 84.5
9/27/20XX 7:00:00 AM | 0.29167 | 2 | 63.8 | 82.3 | 70.4198 | 79.3286 | 8.9088 | 80 | 63.8 |  | 63.8 | 72.4688 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 72.4688 | 24.6482 | 586626.043 | 48.8855 | 48.8855 | 76.6055 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 72.4688 | 24.6482 | 586626.043 | 48.8855 | 48.8855 | 76.6055 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 72.4688 | 24.6482 | 586626.043 | 48.8855 | 48.8855 | 76.6055 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 72.4688 | 24.6482 | 586626.043 | 48.8855 | 48.8855 | 76.6055 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 72.4688 | 24.6482 | 586626.043 | 48.8855 | 48.8855 | 76.6055 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 72.4688 | 24.6482 | 586626.043 | 48.8855 | 48.8855 | 76.6055 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 72.4688 | 24.6482 | 586626.043 | 48.8855 | 48.8855 | 76.6055 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 72.4688 | 24.6482 | 586626.043 | 48.8855 | 48.8855 | 76.6055 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 72.4688 | 24.6482 | 586626.043 | 48.8855 | 48.8855 | 76.6055 | 1 | 63.8 | 8.8 | 332640 | 27.72 | 27.72 | 72.4688 | 24.6482 | 586626.043 | 48.8855 | 48.8855 | 76.6055 | 65 | 80 | 26.6007 | 26 | 82.3
9/27/20XX 8:00:00 AM | 0.33333 | 2 | 64.7 | 81.5 | 72.7466 | 81.9581 | 9.2115 | 80 | 64.7 |  | 64.7 | 74.1284 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 74.1284 | 26.3077 | 626124.2563 | 52.177 | 52.177 | 82.732 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 74.1284 | 26.3077 | 626124.2563 | 52.177 | 52.177 | 82.732 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 74.1284 | 26.3077 | 626124.2563 | 52.177 | 52.177 | 82.732 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 74.1284 | 26.3077 | 626124.2563 | 52.177 | 52.177 | 82.732 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 74.1284 | 26.3077 | 626124.2563 | 52.177 | 52.177 | 82.732 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 74.1284 | 26.3077 | 626124.2563 | 52.177 | 52.177 | 82.732 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 74.1284 | 26.3077 | 626124.2563 | 52.177 | 52.177 | 82.732 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 74.1284 | 26.3077 | 626124.2563 | 52.177 | 52.177 | 82.732 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 74.1284 | 26.3077 | 626124.2563 | 52.177 | 52.177 | 82.732 | 1 | 64.7 | 9.7 | 366660 | 30.555 | 30.555 | 74.1284 | 26.3077 | 626124.2563 | 52.177 | 52.177 | 82.732 | 65 | 80 | 27.0795 | 28 | 81.5
9/27/20XX 9:00:00 AM | 0.375 | 2 | 66.2 | 78.6 | 67.0285 | 76.7802 | 9.7517 | 70 | 66.2 |  | 66.2 | 75.415 | 0.1 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 63.901 | 16.0803 | 382711.9317 | 31.8927 | 31.8927 | 89.2857 | 0.2 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 65.1803 | 17.3597 | 413160.0635 | 34.43 | 34.43 | 89.366 | 0.3 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 66.4596 | 18.639 | 443608.1952 | 36.9673 | 36.9673 | 89.4463 | 0.4 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 67.739 | 19.9183 | 474056.3269 | 39.5047 | 39.5047 | 89.5267 | 0.5 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 69.0183 | 21.1977 | 504504.4586 | 42.042 | 42.042 | 89.607 | 0.6 | 69.32 | 14.32 | 541296 | 45.108 | 45.108 | 70.2976 | 22.477 | 534952.5904 | 44.5794 | 44.5794 | 89.6874 | 0.7 | 68.54 | 13.54 | 511812 | 42.651 | 42.651 | 71.577 | 23.7563 | 565400.7221 | 47.1167 | 47.1167 | 89.7677 | 0.8 | 67.76 | 12.76 | 482328 | 40.194 | 40.194 | 72.8563 | 25.0357 | 595848.8538 | 49.6541 | 49.6541 | 89.8481 | 0.9 | 66.98 | 11.98 | 452844 | 37.737 | 37.737 | 74.1356 | 26.315 | 626296.9855 | 52.1914 | 52.1914 | 89.9284 | 1 | 66.2 | 11.2 | 423360 | 35.28 | 35.28 | 75.415 | 27.5943 | 656745.1173 | 54.7288 | 54.7288 | 90.0088 | 65 | 80 | 27.6472 | 28 | 78.6
9/27/20XX 10:00:00 AM | 0.41667 | 2 | 67.8 | 74.5 | 70.9676 | 81.3033 | 10.3357 | 70 | 67.8 |  | 67.8 | 75.6187 | 0.1 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 63.9213 | 16.1007 | 383196.7755 | 31.9331 | 31.9331 | 89.8301 | 0.2 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 65.221 | 17.4004 | 414129.7509 | 34.5108 | 34.5108 | 90.4548 | 0.3 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 66.5207 | 18.7001 | 445062.7264 | 37.0886 | 37.0886 | 91.0796 | 0.4 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 67.8205 | 19.9998 | 475995.7019 | 39.6663 | 39.6663 | 91.7043 | 0.5 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 69.1202 | 21.2995 | 506928.6774 | 42.2441 | 42.2441 | 92.3291 | 0.6 | 70.28 | 15.28 | 577584 | 48.132 | 48.132 | 70.4199 | 22.5992 | 537861.6528 | 44.8218 | 44.8218 | 92.9538 | 0.7 | 69.66 | 14.66 | 554148 | 46.179 | 46.179 | 71.7196 | 23.8989 | 568794.6283 | 47.3996 | 47.3996 | 93.5786 | 0.8 | 69.04 | 14.04 | 530712 | 44.226 | 44.226 | 73.0193 | 25.1986 | 599727.6038 | 49.9773 | 49.9773 | 94.2033 | 0.9 | 68.42 | 13.42 | 507276 | 42.273 | 42.273 | 74.319 | 26.4983 | 630660.5792 | 52.555 | 52.555 | 94.828 | 1 | 67.8 | 12.8 | 483840 | 40.32 | 40.32 | 75.6187 | 27.798 | 661593.5547 | 55.1328 | 55.1328 | 95.4528 | 70 | 75 | 28.0706 | 28 | 74.5
9/27/20XX 11:00:00 AM | 0.45833 | 2 | 70.7 | 70.6 | 78.6313 | 90.1079 | 11.4766 | 70 | 70.7 |  | 70.7 | 79.3199 | 0.1 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 64.2915 | 16.4708 | 392005.6256 | 32.6671 | 32.6671 | 91.4776 | 0.2 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 65.9613 | 18.1406 | 431747.4511 | 35.979 | 35.979 | 93.75 | 0.3 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 67.6311 | 19.8105 | 471489.2767 | 39.2908 | 39.2908 | 96.0223 | 0.4 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 69.3009 | 21.4803 | 511231.1023 | 42.6026 | 42.6026 | 98.2946 | 0.5 | 72.35 | 17.35 | 655830 | 54.6525 | 54.6525 | 70.9708 | 23.1501 | 550972.9278 | 45.9144 | 45.9144 | 100.5669 | 0.6 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 72.6406 | 24.8199 | 590714.7534 | 49.2262 | 49.2262 | 102.8392 | 0.7 | 71.69 | 16.69 | 630882 | 52.5735 | 52.5735 | 74.3104 | 26.4898 | 630456.579 | 52.538 | 52.538 | 105.1115 | 0.8 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 75.9802 | 28.1596 | 670198.4045 | 55.8499 | 55.8499 | 107.3839 | 0.9 | 71.03 | 16.03 | 605934 | 50.4945 | 50.4945 | 77.6501 | 29.8294 | 709940.2301 | 59.1617 | 59.1617 | 109.6562 | 1 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 79.3199 | 31.4992 | 749682.0557 | 62.4735 | 62.4735 | 111.9285 | 70 | 70 | 29.3587 | 30 | 70.6
9/27/20XX 12:00:00 PM | 0.5 | 2 | 72.1 | 67 | 70.5937 | 82.5828 | 11.9891 | 60 | 72.1 |  | 72.1 | 78.9861 | 0.1 | 73.81 | 18.81 | 711018 | 59.2515 | 59.2515 | 64.2581 | 16.4374 | 391211.1221 | 32.6009 | 32.6009 | 91.8524 | 0.2 | 73.62 | 18.62 | 703836 | 58.653 | 58.653 | 65.8945 | 18.0739 | 430158.4441 | 35.8465 | 35.8465 | 94.4995 | 0.3 | 73.43 | 18.43 | 696654 | 58.0545 | 58.0545 | 67.531 | 19.7103 | 469105.7662 | 39.0921 | 39.0921 | 97.1466 | 0.4 | 73.24 | 18.24 | 689472 | 57.456 | 57.456 | 69.1674 | 21.3468 | 508053.0882 | 42.3378 | 42.3378 | 99.7938 | 0.5 | 73.05 | 18.05 | 682290 | 56.8575 | 56.8575 | 70.8038 | 22.9832 | 547000.4103 | 45.5834 | 45.5834 | 102.4409 | 0.6 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 72.4403 | 24.6197 | 585947.7324 | 48.829 | 48.829 | 105.088 | 0.7 | 72.67 | 17.67 | 667926 | 55.6605 | 55.6605 | 74.0767 | 26.2561 | 624895.0544 | 52.0746 | 52.0746 | 107.7351 | 0.8 | 72.48 | 17.48 | 660744 | 55.062 | 55.062 | 75.7132 | 27.8925 | 663842.3765 | 55.3202 | 55.3202 | 110.3822 | 0.9 | 72.29 | 17.29 | 653562 | 54.4635 | 54.4635 | 77.3496 | 29.529 | 702789.6985 | 58.5658 | 58.5658 | 113.0293 | 1 | 72.1 | 17.1 | 646380 | 53.865 | 53.865 | 78.9861 | 31.1654 | 741737.0206 | 61.8114 | 61.8114 | 115.6764 | 70 | 65 | 29.6496 | 30 | 67
9/27/20XX 1:00:00 PM | 0.54167 | 2 | 71.7 | 67.6 | 69.6172 | 81.4366 | 11.8194 | 60 | 71.7 |  | 71.7 | 78.5999 | 0.1 | 73.77 | 18.77 | 709506 | 59.1255 | 59.1255 | 64.2195 | 16.3988 | 390292.1847 | 32.5243 | 32.5243 | 91.6498 | 0.2 | 73.54 | 18.54 | 700812 | 58.401 | 58.401 | 65.8173 | 17.9967 | 428320.5694 | 35.6934 | 35.6934 | 94.0944 | 0.3 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 67.4151 | 19.5945 | 466348.954 | 38.8624 | 38.8624 | 96.5389 | 0.4 | 73.08 | 18.08 | 683424 | 56.952 | 56.952 | 69.013 | 21.1923 | 504377.3387 | 42.0314 | 42.0314 | 98.9834 | 0.5 | 72.85 | 17.85 | 674730 | 56.2275 | 56.2275 | 70.6108 | 22.7902 | 542405.7234 | 45.2005 | 45.2005 | 101.428 | 0.6 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 72.2086 | 24.388 | 580434.1081 | 48.3695 | 48.3695 | 103.8725 | 0.7 | 72.39 | 17.39 | 657342 | 54.7785 | 54.7785 | 73.8065 | 25.9858 | 618462.4928 | 51.5385 | 51.5385 | 106.317 | 0.8 | 72.16 | 17.16 | 648648 | 54.054 | 54.054 | 75.4043 | 27.5837 | 656490.8774 | 54.7076 | 54.7076 | 108.7616 | 0.9 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 77.0021 | 29.1815 | 694519.2621 | 57.8766 | 57.8766 | 111.2061 | 1 | 71.7 | 16.7 | 631260 | 52.605 | 52.605 | 78.5999 | 30.7793 | 732547.6468 | 61.0456 | 61.0456 | 113.6506 | 70 | 70 | 29.4912 | 30 | 67.6
9/27/20XX 2:00:00 PM | 0.58333 | 2 | 72.9 | 64.7 | 72.5823 | 84.9169 | 12.3346 | 60 | 72.9 |  | 72.9 | 78.3796 | 0.1 | 73.89 | 18.89 | 714042 | 59.5035 | 59.5035 | 64.1974 | 16.3768 | 389767.6855 | 32.4806 | 32.4806 | 91.9841 | 0.2 | 73.78 | 18.78 | 709884 | 59.157 | 59.157 | 65.7732 | 17.9526 | 427271.571 | 35.606 | 35.606 | 94.763 | 0.3 | 73.67 | 18.67 | 705726 | 58.8105 | 58.8105 | 67.349 | 19.5284 | 464775.4565 | 38.7313 | 38.7313 | 97.5418 | 0.4 | 73.56 | 18.56 | 701568 | 58.464 | 58.464 | 68.9248 | 21.1042 | 502279.342 | 41.8566 | 41.8566 | 100.3206 | 0.5 | 73.45 | 18.45 | 697410 | 58.1175 | 58.1175 | 70.5006 | 22.68 | 539783.2275 | 44.9819 | 44.9819 | 103.0994 | 0.6 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 72.0764 | 24.2558 | 577287.113 | 48.1073 | 48.1073 | 105.8783 | 0.7 | 73.23 | 18.23 | 689094 | 57.4245 | 57.4245 | 73.6522 | 25.8316 | 614790.9984 | 51.2326 | 51.2326 | 108.6571 | 0.8 | 73.12 | 18.12 | 684936 | 57.078 | 57.078 | 75.228 | 27.4073 | 652294.8839 | 54.3579 | 54.3579 | 111.4359 | 0.9 | 73.01 | 18.01 | 680778 | 56.7315 | 56.7315 | 76.8038 | 28.9831 | 689798.7694 | 57.4832 | 57.4832 | 114.2147 | 1 | 72.9 | 17.9 | 676620 | 56.385 | 56.385 | 78.3796 | 30.5589 | 727302.6549 | 60.6086 | 60.6086 | 116.9936 | 75 | 65 | 29.7508 | 30 | 64.7
9/27/20XX 3:00:00 PM | 0.625 | 2 | 73 | 65.2 | 72.8342 | 85.2126 | 12.3784 | 60 | 73 |  | 73 | 79.271 | 0.1 | 73.9 | 18.9 | 714420 | 59.535 | 59.535 | 64.2866 | 16.4659 | 391889.296 | 32.6574 | 32.6574 | 92.1924 | 0.2 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 65.9515 | 18.1309 | 431514.792 | 35.9596 | 35.9596 | 95.1796 | 0.3 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 67.6164 | 19.7958 | 471140.288 | 39.2617 | 39.2617 | 98.1667 | 0.4 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 69.2814 | 21.4607 | 510765.784 | 42.5638 | 42.5638 | 101.1538 | 0.5 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 70.9463 | 23.1257 | 550391.28 | 45.8659 | 45.8659 | 104.1409 | 0.6 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 72.6113 | 24.7906 | 590016.776 | 49.1681 | 49.1681 | 107.1281 | 0.7 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 74.2762 | 26.4556 | 629642.272 | 52.4702 | 52.4702 | 110.1152 | 0.8 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 75.9411 | 28.1205 | 669267.768 | 55.7723 | 55.7723 | 113.1023 | 0.9 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 77.6061 | 29.7854 | 708893.264 | 59.0744 | 59.0744 | 116.0894 | 1 | 73 | 18 | 680400 | 56.7 | 56.7 | 79.271 | 31.4504 | 748518.76 | 62.3766 | 62.3766 | 119.0766 | 75 | 65 | 29.9146 | 30 | 65.2
9/27/20XX 4:00:00 PM | 0.66667 | 2 | 72.5 | 67.7 | 71.5821 | 83.7428 | 12.1608 | 60 | 72.5 |  | 72.5 | 80.9459 | 0.1 | 73.85 | 18.85 | 712530 | 59.3775 | 59.3775 | 64.4541 | 16.6334 | 395875.4509 | 32.9896 | 32.9896 | 92.3671 | 0.2 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 66.2865 | 18.4658 | 439487.1019 | 36.6239 | 36.6239 | 95.5289 | 0.3 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 68.1189 | 20.2983 | 483098.7528 | 40.2582 | 40.2582 | 98.6907 | 0.4 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 69.9513 | 22.1307 | 526710.4037 | 43.8925 | 43.8925 | 101.8525 | 0.5 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 71.7837 | 23.9631 | 570322.0546 | 47.5268 | 47.5268 | 105.0143 | 0.6 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 73.6162 | 25.7955 | 613933.7056 | 51.1611 | 51.1611 | 108.1761 | 0.7 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 75.4486 | 27.628 | 657545.3565 | 54.7954 | 54.7954 | 111.3379 | 0.8 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 77.281 | 29.4604 | 701157.0074 | 58.4298 | 58.4298 | 114.4998 | 0.9 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 79.1134 | 31.2928 | 744768.6583 | 62.0641 | 62.0641 | 117.6616 | 1 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 80.9459 | 33.1252 | 788380.3093 | 65.6984 | 65.6984 | 120.8234 | 70 | 70 | 30.054 | 30 | 67.7
9/27/20XX 5:00:00 PM | 0.70833 | 2 | 71.5 | 69.2 | 69.1333 | 80.8687 | 11.7354 | 60 | 71.5 |  | 71.5 | 79.9299 | 0.1 | 73.75 | 18.75 | 708750 | 59.0625 | 59.0625 | 64.3525 | 16.5318 | 393457.402 | 32.7881 | 32.7881 | 91.8506 | 0.2 | 73.5 | 18.5 | 699300 | 58.275 | 58.275 | 66.0833 | 18.2626 | 434651.004 | 36.2209 | 36.2209 | 94.4959 | 0.3 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 67.8141 | 19.9935 | 475844.606 | 39.6537 | 39.6537 | 97.1412 | 0.4 | 73 | 18 | 680400 | 56.7 | 56.7 | 69.5449 | 21.7243 | 517038.208 | 43.0865 | 43.0865 | 99.7865 | 0.5 | 72.75 | 17.75 | 670950 | 55.9125 | 55.9125 | 71.2758 | 23.4551 | 558231.81 | 46.5193 | 46.5193 | 102.4318 | 0.6 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 73.0066 | 25.1859 | 599425.412 | 49.9521 | 49.9521 | 105.0771 | 0.7 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 74.7374 | 26.9168 | 640619.014 | 53.3849 | 53.3849 | 107.7224 | 0.8 | 72 | 17 | 642600 | 53.55 | 53.55 | 76.4682 | 28.6476 | 681812.616 | 56.8177 | 56.8177 | 110.3677 | 0.9 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 78.199 | 30.3784 | 723006.218 | 60.2505 | 60.2505 | 113.013 | 1 | 71.5 | 16.5 | 623700 | 51.975 | 51.975 | 79.9299 | 32.1092 | 764199.82 | 63.6833 | 63.6833 | 115.6583 | 70 | 70 | 29.6501 | 30 | 69.2
9/27/20XX 6:00:00 PM | 0.75 | 2 | 69.9 | 73.7 | 76.4479 | 87.5989 | 11.151 | 70 | 69.9 |  | 69.9 | 80.5738 | 0.1 | 73.59 | 18.59 | 702702 | 58.5585 | 58.5585 | 64.4168 | 16.5962 | 394989.9662 | 32.9158 | 32.9158 | 91.4743 | 0.2 | 73.18 | 18.18 | 687204 | 57.267 | 57.267 | 66.2121 | 18.3914 | 437716.1324 | 36.4763 | 36.4763 | 93.7433 | 0.3 | 72.77 | 17.77 | 671706 | 55.9755 | 55.9755 | 68.0073 | 20.1867 | 480442.2985 | 40.0369 | 40.0369 | 96.0124 | 0.4 | 72.36 | 17.36 | 656208 | 54.684 | 54.684 | 69.8025 | 21.9819 | 523168.4647 | 43.5974 | 43.5974 | 98.2814 | 0.5 | 71.95 | 16.95 | 640710 | 53.3925 | 53.3925 | 71.5977 | 23.7771 | 565894.6309 | 47.1579 | 47.1579 | 100.5504 | 0.6 | 71.54 | 16.54 | 625212 | 52.101 | 52.101 | 73.3929 | 25.5723 | 608620.7971 | 50.7184 | 50.7184 | 102.8194 | 0.7 | 71.13 | 16.13 | 609714 | 50.8095 | 50.8095 | 75.1882 | 27.3675 | 651346.9633 | 54.2789 | 54.2789 | 105.0884 | 0.8 | 70.72 | 15.72 | 594216 | 49.518 | 49.518 | 76.9834 | 29.1627 | 694073.1294 | 57.8394 | 57.8394 | 107.3574 | 0.9 | 70.31 | 15.31 | 578718 | 48.2265 | 48.2265 | 78.7786 | 30.958 | 736799.2956 | 61.3999 | 61.3999 | 109.6264 | 1 | 69.9 | 14.9 | 563220 | 46.935 | 46.935 | 80.5738 | 32.7532 | 779525.4618 | 64.9605 | 64.9605 | 111.8955 | 70 | 75 | 29.3585 | 30 | 73.7
9/27/20XX 7:00:00 PM | 0.79167 | 2 | 69.7 | 75.3 | 75.9105 | 86.9813 | 11.0709 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/27/20XX 8:00:00 PM | 0.83333 | 2 | 69 | 76.8 | 74.0553 | 84.8499 | 10.7946 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/27/20XX 9:00:00 PM | 0.875 | 2 | 68.3 | 77.1 | 72.24 | 82.7647 | 10.5247 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/27/20XX 10:00:00 PM | 0.91667 | 2 | 68.4 | 78.3 | 72.4969 | 83.0598 | 10.5629 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/27/20XX 11:00:00 PM | 0.95833 | 2 | 67.8 | 78.2 | 70.9676 | 81.3033 | 10.3357 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/27/20XX 12:00:00 AM | 0 | 3 | 66.5 | 81.5 | 77.6107 | 87.4565 | 9.8458 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/28/20XX 1:00:00 AM | 0.041667 | 3 | 66.3 | 83.7 | 77.0561 | 86.8295 | 9.7734 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/28/20XX 2:00:00 AM | 0.083333 | 3 | 65.8 | 85.6 | 75.6853 | 85.2798 | 9.5945 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/28/20XX 3:00:00 AM | 0.125 | 3 | 65.5 | 87.5 | 74.8734 | 84.362 | 9.4886 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/28/20XX 4:00:00 AM | 0.16667 | 3 | 65.1 | 88.7 | 73.8031 | 83.1522 | 9.3491 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/28/20XX 5:00:00 AM | 0.20833 | 3 | 64.8 | 88.1 | 73.0095 | 82.2552 | 9.2457 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/28/20XX 6:00:00 AM | 0.25 | 3 | 64.5 | 87.8 | 72.2236 | 81.367 | 9.1434 | 80 | 64.5 |  | 64.5 | 79.3555 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 79.3555 | 31.5348 | 750528.8635 | 62.5441 | 62.5441 | 92.4691 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 79.3555 | 31.5348 | 750528.8635 | 62.5441 | 62.5441 | 92.4691 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 79.3555 | 31.5348 | 750528.8635 | 62.5441 | 62.5441 | 92.4691 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 79.3555 | 31.5348 | 750528.8635 | 62.5441 | 62.5441 | 92.4691 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 79.3555 | 31.5348 | 750528.8635 | 62.5441 | 62.5441 | 92.4691 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 79.3555 | 31.5348 | 750528.8635 | 62.5441 | 62.5441 | 92.4691 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 79.3555 | 31.5348 | 750528.8635 | 62.5441 | 62.5441 | 92.4691 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 79.3555 | 31.5348 | 750528.8635 | 62.5441 | 62.5441 | 92.4691 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 79.3555 | 31.5348 | 750528.8635 | 62.5441 | 62.5441 | 92.4691 | 1 | 64.5 | 9.5 | 359100 | 29.925 | 29.925 | 79.3555 | 31.5348 | 750528.8635 | 62.5441 | 62.5441 | 92.4691 | 65 | 90 | 27.845 | 28 | 87.8
9/28/20XX 7:00:00 AM | 0.29167 | 3 | 65 | 84.4 | 73.5377 | 82.8522 | 9.3145 | 80 | 65 |  | 65 | 77.6361 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 77.6361 | 29.8154 | 709607.2251 | 59.1339 | 59.1339 | 90.6339 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 77.6361 | 29.8154 | 709607.2251 | 59.1339 | 59.1339 | 90.6339 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 77.6361 | 29.8154 | 709607.2251 | 59.1339 | 59.1339 | 90.6339 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 77.6361 | 29.8154 | 709607.2251 | 59.1339 | 59.1339 | 90.6339 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 77.6361 | 29.8154 | 709607.2251 | 59.1339 | 59.1339 | 90.6339 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 77.6361 | 29.8154 | 709607.2251 | 59.1339 | 59.1339 | 90.6339 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 77.6361 | 29.8154 | 709607.2251 | 59.1339 | 59.1339 | 90.6339 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 77.6361 | 29.8154 | 709607.2251 | 59.1339 | 59.1339 | 90.6339 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 77.6361 | 29.8154 | 709607.2251 | 59.1339 | 59.1339 | 90.6339 | 1 | 65 | 10 | 378000 | 31.5 | 31.5 | 77.6361 | 29.8154 | 709607.2251 | 59.1339 | 59.1339 | 90.6339 | 65 | 85 | 27.6996 | 28 | 84.4
9/28/20XX 8:00:00 AM | 0.33333 | 3 | 65.6 | 81.8 | 75.1431 | 84.6669 | 9.5238 | 80 | 65.6 |  | 65.6 | 76.8574 | 0.1 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 64.0452 | 16.2246 | 386144.9902 | 32.1787 | 32.1787 | 89.3827 | 0.2 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 65.4688 | 17.6482 | 420026.1805 | 35.0022 | 35.0022 | 89.5602 | 0.3 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 66.8924 | 19.0717 | 453907.3707 | 37.8256 | 37.8256 | 89.7376 | 0.4 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 68.316 | 20.4953 | 487788.5609 | 40.649 | 40.649 | 89.915 | 0.5 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 69.7395 | 21.9189 | 521669.7511 | 43.4725 | 43.4725 | 90.0925 | 0.6 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 71.1631 | 23.3425 | 555550.9414 | 46.2959 | 46.2959 | 90.2699 | 0.7 | 68.12 | 13.12 | 495936 | 41.328 | 41.328 | 72.5867 | 24.7661 | 589432.1316 | 49.1193 | 49.1193 | 90.4473 | 0.8 | 67.28 | 12.28 | 464184 | 38.682 | 38.682 | 74.0103 | 26.1896 | 623313.3218 | 51.9428 | 51.9428 | 90.6248 | 0.9 | 66.44 | 11.44 | 432432 | 36.036 | 36.036 | 75.4338 | 27.6132 | 657194.512 | 54.7662 | 54.7662 | 90.8022 | 1 | 65.6 | 10.6 | 400680 | 33.39 | 33.39 | 76.8574 | 29.0368 | 691075.7023 | 57.5896 | 57.5896 | 90.9796 | 65 | 80 | 27.7252 | 28 | 81.8
9/28/20XX 9:00:00 AM | 0.375 | 3 | 66.7 | 78.4 | 68.238 | 78.1688 | 9.9308 | 70 | 66.7 |  | 66.7 | 76.5799 | 0.1 | 73.27 | 18.27 | 690606 | 57.5505 | 57.5505 | 64.0175 | 16.1968 | 385484.5007 | 32.1237 | 32.1237 | 89.6742 | 0.2 | 72.54 | 17.54 | 663012 | 55.251 | 55.251 | 65.4133 | 17.5927 | 418705.2014 | 34.8921 | 34.8921 | 90.1431 | 0.3 | 71.81 | 16.81 | 635418 | 52.9515 | 52.9515 | 66.8091 | 18.9885 | 451925.9022 | 37.6605 | 37.6605 | 90.612 | 0.4 | 71.08 | 16.08 | 607824 | 50.652 | 50.652 | 68.2049 | 20.3843 | 485146.6029 | 40.4289 | 40.4289 | 91.0809 | 0.5 | 70.35 | 15.35 | 580230 | 48.3525 | 48.3525 | 69.6008 | 21.7801 | 518367.3036 | 43.1973 | 43.1973 | 91.5498 | 0.6 | 69.62 | 14.62 | 552636 | 46.053 | 46.053 | 70.9966 | 23.176 | 551588.0043 | 45.9657 | 45.9657 | 92.0187 | 0.7 | 68.89 | 13.89 | 525042 | 43.7535 | 43.7535 | 72.3924 | 24.5718 | 584808.705 | 48.7341 | 48.7341 | 92.4876 | 0.8 | 68.16 | 13.16 | 497448 | 41.454 | 41.454 | 73.7883 | 25.9676 | 618029.4057 | 51.5025 | 51.5025 | 92.9565 | 0.9 | 67.43 | 12.43 | 469854 | 39.1545 | 39.1545 | 75.1841 | 27.3634 | 651250.1065 | 54.2708 | 54.2708 | 93.4253 | 1 | 66.7 | 11.7 | 442260 | 36.855 | 36.855 | 76.5799 | 28.7593 | 684470.8072 | 57.0392 | 57.0392 | 93.8942 | 65 | 80 | 27.9512 | 28 | 78.4
9/28/20XX 10:00:00 AM | 0.41667 | 3 | 68.2 | 74 | 71.984 | 82.4706 | 10.4866 | 70 | 68.2 |  | 68.2 | 76.1786 | 0.1 | 73.42 | 18.42 | 696276 | 58.023 | 58.023 | 63.9773 | 16.1567 | 384529.416 | 32.0441 | 32.0441 | 90.0671 | 0.2 | 72.84 | 17.84 | 674352 | 56.196 | 56.196 | 65.333 | 17.5124 | 416795.0321 | 34.7329 | 34.7329 | 90.9289 | 0.3 | 72.26 | 17.26 | 652428 | 54.369 | 54.369 | 66.6887 | 18.8681 | 449060.6481 | 37.4217 | 37.4217 | 91.7907 | 0.4 | 71.68 | 16.68 | 630504 | 52.542 | 52.542 | 68.0444 | 20.2238 | 481326.2641 | 40.1105 | 40.1105 | 92.6525 | 0.5 | 71.1 | 16.1 | 608580 | 50.715 | 50.715 | 69.4001 | 21.5795 | 513591.8802 | 42.7993 | 42.7993 | 93.5143 | 0.6 | 70.52 | 15.52 | 586656 | 48.888 | 48.888 | 70.7558 | 22.9352 | 545857.4962 | 45.4881 | 45.4881 | 94.3761 | 0.7 | 69.94 | 14.94 | 564732 | 47.061 | 47.061 | 72.1115 | 24.2909 | 578123.1123 | 48.1769 | 48.1769 | 95.2379 | 0.8 | 69.36 | 14.36 | 542808 | 45.234 | 45.234 | 73.4672 | 25.6466 | 610388.7283 | 50.8657 | 50.8657 | 96.0997 | 0.9 | 68.78 | 13.78 | 520884 | 43.407 | 43.407 | 74.8229 | 27.0023 | 642654.3443 | 53.5545 | 53.5545 | 96.9615 | 1 | 68.2 | 13.2 | 498960 | 41.58 | 41.58 | 76.1786 | 28.358 | 674919.9604 | 56.2433 | 56.2433 | 97.8233 | 70 | 75 | 28.2559 | 28 | 74
9/28/20XX 11:00:00 AM | 0.45833 | 3 | 70.1 | 70.7 | 76.9888 | 88.2203 | 11.2316 | 70 | 70.1 |  | 70.1 | 77.775 | 0.1 | 73.61 | 18.61 | 703458 | 58.6215 | 58.6215 | 64.137 | 16.3163 | 388328.742 | 32.3607 | 32.3607 | 90.9822 | 0.2 | 73.22 | 18.22 | 688716 | 57.393 | 57.393 | 65.6523 | 17.8317 | 424393.684 | 35.3661 | 35.3661 | 92.7591 | 0.3 | 72.83 | 17.83 | 673974 | 56.1645 | 56.1645 | 67.1676 | 19.347 | 460458.626 | 38.3716 | 38.3716 | 94.5361 | 0.4 | 72.44 | 17.44 | 659232 | 54.936 | 54.936 | 68.683 | 20.8623 | 496523.568 | 41.377 | 41.377 | 96.313 | 0.5 | 72.05 | 17.05 | 644490 | 53.7075 | 53.7075 | 70.1983 | 22.3777 | 532588.51 | 44.3824 | 44.3824 | 98.0899 | 0.6 | 71.66 | 16.66 | 629748 | 52.479 | 52.479 | 71.7136 | 23.893 | 568653.452 | 47.3878 | 47.3878 | 99.8668 | 0.7 | 71.27 | 16.27 | 615006 | 51.2505 | 51.2505 | 73.229 | 25.4083 | 604718.394 | 50.3932 | 50.3932 | 101.6437 | 0.8 | 70.88 | 15.88 | 600264 | 50.022 | 50.022 | 74.7443 | 26.9237 | 640783.336 | 53.3986 | 53.3986 | 103.4206 | 0.9 | 70.49 | 15.49 | 585522 | 48.7935 | 48.7935 | 76.2596 | 28.439 | 676848.278 | 56.404 | 56.404 | 105.1975 | 1 | 70.1 | 15.1 | 570780 | 47.565 | 47.565 | 77.775 | 29.9543 | 712913.22 | 59.4094 | 59.4094 | 106.9744 | 70 | 70 | 28.9704 | 28 | 70.7
9/28/20XX 12:00:00 PM | 0.5 | 3 | 70.8 | 69 | 67.4628 | 78.908 | 11.4452 | 60 | 70.8 |  | 70.8 | 77.7635 | 0.1 | 73.68 | 18.68 | 706104 | 58.842 | 58.842 | 64.1358 | 16.3152 | 388301.3556 | 32.3584 | 32.3584 | 91.2004 | 0.2 | 73.36 | 18.36 | 694008 | 57.834 | 57.834 | 65.65 | 17.8294 | 424338.9111 | 35.3616 | 35.3616 | 93.1956 | 0.3 | 73.04 | 18.04 | 681912 | 56.826 | 56.826 | 67.1642 | 19.3435 | 460376.4667 | 38.3647 | 38.3647 | 95.1907 | 0.4 | 72.72 | 17.72 | 669816 | 55.818 | 55.818 | 68.6784 | 20.8577 | 496414.0223 | 41.3678 | 41.3678 | 97.1858 | 0.5 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 70.1925 | 22.3719 | 532451.5779 | 44.371 | 44.371 | 99.181 | 0.6 | 72.08 | 17.08 | 645624 | 53.802 | 53.802 | 71.7067 | 23.8861 | 568489.1334 | 47.3741 | 47.3741 | 101.1761 | 0.7 | 71.76 | 16.76 | 633528 | 52.794 | 52.794 | 73.2209 | 25.4003 | 604526.689 | 50.3772 | 50.3772 | 103.1712 | 0.8 | 71.44 | 16.44 | 621432 | 51.786 | 51.786 | 74.7351 | 26.9145 | 640564.2446 | 53.3804 | 53.3804 | 105.1664 | 0.9 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 76.2493 | 28.4286 | 676601.8001 | 56.3835 | 56.3835 | 107.1615 | 1 | 70.8 | 15.8 | 597240 | 49.77 | 49.77 | 77.7635 | 29.9428 | 712639.3557 | 59.3866 | 59.3866 | 109.1566 | 70 | 70 | 29.1401 | 30 | 69
9/28/20XX 1:00:00 PM | 0.54167 | 3 | 71.9 | 68 | 70.104 | 82.008 | 11.904 | 60 | 71.9 |  | 71.9 | 79.6272 | 0.1 | 73.79 | 18.79 | 710262 | 59.1885 | 59.1885 | 64.3222 | 16.5016 | 392736.9583 | 32.7281 | 32.7281 | 91.9166 | 0.2 | 73.58 | 18.58 | 702324 | 58.527 | 58.527 | 66.0227 | 18.2021 | 433210.1167 | 36.1008 | 36.1008 | 94.6278 | 0.3 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 67.7233 | 19.9027 | 473683.275 | 39.4736 | 39.4736 | 97.3391 | 0.4 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 69.4238 | 21.6032 | 514156.4334 | 42.8464 | 42.8464 | 100.0504 | 0.5 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 71.1244 | 23.3038 | 554629.5917 | 46.2191 | 46.2191 | 102.7616 | 0.6 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 72.8249 | 25.0043 | 595102.75 | 49.5919 | 49.5919 | 105.4729 | 0.7 | 72.53 | 17.53 | 662634 | 55.2195 | 55.2195 | 74.5255 | 26.7049 | 635575.9084 | 52.9647 | 52.9647 | 108.1842 | 0.8 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 76.2261 | 28.4054 | 676049.0667 | 56.3374 | 56.3374 | 110.8954 | 0.9 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 77.9266 | 30.106 | 716522.2251 | 59.7102 | 59.7102 | 113.6067 | 1 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 79.6272 | 31.8065 | 756995.3834 | 63.0829 | 63.0829 | 116.3179 | 70 | 70 | 29.7008 | 30 | 68
9/28/20XX 2:00:00 PM | 0.58333 | 3 | 72.1 | 66.5 | 70.5937 | 82.5828 | 11.9891 | 60 | 72.1 |  | 72.1 | 78.3866 | 0.1 | 73.81 | 18.81 | 711018 | 59.2515 | 59.2515 | 64.1981 | 16.3775 | 389784.425 | 32.482 | 32.482 | 91.7335 | 0.2 | 73.62 | 18.62 | 703836 | 58.653 | 58.653 | 65.7746 | 17.954 | 427305.0501 | 35.6088 | 35.6088 | 94.2618 | 0.3 | 73.43 | 18.43 | 696654 | 58.0545 | 58.0545 | 67.3511 | 19.5305 | 464825.6751 | 38.7355 | 38.7355 | 96.79 | 0.4 | 73.24 | 18.24 | 689472 | 57.456 | 57.456 | 68.9276 | 21.107 | 502346.3001 | 41.8622 | 41.8622 | 99.3182 | 0.5 | 73.05 | 18.05 | 682290 | 56.8575 | 56.8575 | 70.5041 | 22.6835 | 539866.9251 | 44.9889 | 44.9889 | 101.8464 | 0.6 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 72.0806 | 24.26 | 577387.5502 | 48.1156 | 48.1156 | 104.3746 | 0.7 | 72.67 | 17.67 | 667926 | 55.6605 | 55.6605 | 73.6571 | 25.8365 | 614908.1752 | 51.2423 | 51.2423 | 106.9028 | 0.8 | 72.48 | 17.48 | 660744 | 55.062 | 55.062 | 75.2336 | 27.413 | 652428.8002 | 54.3691 | 54.3691 | 109.4311 | 0.9 | 72.29 | 17.29 | 653562 | 54.4635 | 54.4635 | 76.8101 | 28.9895 | 689949.4252 | 57.4958 | 57.4958 | 111.9593 | 1 | 72.1 | 17.1 | 646380 | 53.865 | 53.865 | 78.3866 | 30.566 | 727470.0503 | 60.6225 | 60.6225 | 114.4875 | 70 | 65 | 29.5559 | 30 | 66.5
9/28/20XX 3:00:00 PM | 0.625 | 3 | 72 | 67.1 | 70.3485 | 82.2949 | 11.9464 | 60 | 72 |  | 72 | 78.8305 | 0.1 | 73.8 | 18.8 | 710640 | 59.22 | 59.22 | 64.2425 | 16.4219 | 390840.808 | 32.5701 | 32.5701 | 91.7901 | 0.2 | 73.6 | 18.6 | 703080 | 58.59 | 58.59 | 65.8634 | 18.0428 | 429417.8161 | 35.7848 | 35.7848 | 94.3748 | 0.3 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 67.4843 | 19.6636 | 467994.8241 | 38.9996 | 38.9996 | 96.9596 | 0.4 | 73.2 | 18.2 | 687960 | 57.33 | 57.33 | 69.1052 | 21.2845 | 506571.8322 | 42.2143 | 42.2143 | 99.5443 | 0.5 | 73 | 18 | 680400 | 56.7 | 56.7 | 70.726 | 22.9054 | 545148.8402 | 45.4291 | 45.4291 | 102.1291 | 0.6 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 72.3469 | 24.5263 | 583725.8483 | 48.6438 | 48.6438 | 104.7138 | 0.7 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 73.9678 | 26.1472 | 622302.8563 | 51.8586 | 51.8586 | 107.2986 | 0.8 | 72.4 | 17.4 | 657720 | 54.81 | 54.81 | 75.5887 | 27.7681 | 660879.8644 | 55.0733 | 55.0733 | 109.8833 | 0.9 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 77.2096 | 29.3889 | 699456.8724 | 58.2881 | 58.2881 | 112.4681 | 1 | 72 | 17 | 642600 | 53.55 | 53.55 | 78.8305 | 31.0098 | 738033.8805 | 61.5028 | 61.5028 | 115.0528 | 70 | 65 | 29.6008 | 30 | 67.1
9/28/20XX 4:00:00 PM | 0.66667 | 3 | 71 | 68.4 | 67.9365 | 79.4639 | 11.5275 | 60 | 71 |  | 71 | 77.6195 | 0.1 | 73.7 | 18.7 | 706860 | 58.905 | 58.905 | 64.1214 | 16.3008 | 387958.8031 | 32.3299 | 32.3299 | 91.2349 | 0.2 | 73.4 | 18.4 | 695520 | 57.96 | 57.96 | 65.6212 | 17.8006 | 423653.8061 | 35.3045 | 35.3045 | 93.2645 | 0.3 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 67.121 | 19.3004 | 459348.8092 | 38.2791 | 38.2791 | 95.2941 | 0.4 | 72.8 | 17.8 | 672840 | 56.07 | 56.07 | 68.6208 | 20.8002 | 495043.8122 | 41.2537 | 41.2537 | 97.3237 | 0.5 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 70.1206 | 22.3 | 530738.8153 | 44.2282 | 44.2282 | 99.3532 | 0.6 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 71.6204 | 23.7997 | 566433.8183 | 47.2028 | 47.2028 | 101.3828 | 0.7 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 73.1202 | 25.2995 | 602128.8214 | 50.1774 | 50.1774 | 103.4124 | 0.8 | 71.6 | 16.6 | 627480 | 52.29 | 52.29 | 74.62 | 26.7993 | 637823.8245 | 53.152 | 53.152 | 105.442 | 0.9 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 76.1197 | 28.2991 | 673518.8275 | 56.1266 | 56.1266 | 107.4716 | 1 | 71 | 16 | 604800 | 50.4 | 50.4 | 77.6195 | 29.7989 | 709213.8306 | 59.1012 | 59.1012 | 109.5012 | 70 | 70 | 29.1666 | 30 | 68.4
9/28/20XX 5:00:00 PM | 0.70833 | 3 | 70.3 | 70 | 77.5329 | 88.8456 | 11.3127 | 70 | 70.3 |  | 70.3 | 77.5329 | 0.1 | 73.63 | 18.63 | 704214 | 58.6845 | 58.6845 | 64.1128 | 16.2921 | 387752.6398 | 32.3127 | 32.3127 | 90.9972 | 0.2 | 73.26 | 18.26 | 690228 | 57.519 | 57.519 | 65.6039 | 17.7833 | 423241.4795 | 35.2701 | 35.2701 | 92.7891 | 0.3 | 72.89 | 17.89 | 676242 | 56.3535 | 56.3535 | 67.095 | 19.2744 | 458730.3193 | 38.2275 | 38.2275 | 94.581 | 0.4 | 72.52 | 17.52 | 662256 | 55.188 | 55.188 | 68.5861 | 20.7655 | 494219.1591 | 41.1849 | 41.1849 | 96.3729 | 0.5 | 72.15 | 17.15 | 648270 | 54.0225 | 54.0225 | 70.0773 | 22.2566 | 529707.9989 | 44.1423 | 44.1423 | 98.1648 | 0.6 | 71.78 | 16.78 | 634284 | 52.857 | 52.857 | 71.5684 | 23.7478 | 565196.8386 | 47.0997 | 47.0997 | 99.9567 | 0.7 | 71.41 | 16.41 | 620298 | 51.6915 | 51.6915 | 73.0595 | 25.2389 | 600685.6784 | 50.0571 | 50.0571 | 101.7486 | 0.8 | 71.04 | 16.04 | 606312 | 50.526 | 50.526 | 74.5507 | 26.73 | 636174.5182 | 53.0145 | 53.0145 | 103.5405 | 0.9 | 70.67 | 15.67 | 592326 | 49.3605 | 49.3605 | 76.0418 | 28.2211 | 671663.3579 | 55.9719 | 55.9719 | 105.3324 | 1 | 70.3 | 15.3 | 578340 | 48.195 | 48.195 | 77.5329 | 29.7123 | 707152.1977 | 58.9293 | 58.9293 | 107.1243 | 70 | 70 | 28.9816 | 28 | 70
9/28/20XX 6:00:00 PM | 0.75 | 3 | 67.4 | 75.4 | 69.964 | 80.1508 | 10.1867 | 70 | 67.4 |  | 67.4 | 75.4649 | 0.1 | 73.34 | 18.34 | 693252 | 57.771 | 57.771 | 63.906 | 16.0853 | 382830.6677 | 31.9026 | 31.9026 | 89.6736 | 0.2 | 72.68 | 17.68 | 668304 | 55.692 | 55.692 | 65.1903 | 17.3696 | 413397.5353 | 34.4498 | 34.4498 | 90.1418 | 0.3 | 72.02 | 17.02 | 643356 | 53.613 | 53.613 | 66.4746 | 18.654 | 443964.403 | 36.997 | 36.997 | 90.61 | 0.4 | 71.36 | 16.36 | 618408 | 51.534 | 51.534 | 67.7589 | 19.9383 | 474531.2706 | 39.5443 | 39.5443 | 91.0783 | 0.5 | 70.7 | 15.7 | 593460 | 49.455 | 49.455 | 69.0432 | 21.2226 | 505098.1383 | 42.0915 | 42.0915 | 91.5465 | 0.6 | 70.04 | 15.04 | 568512 | 47.376 | 47.376 | 70.3276 | 22.5069 | 535665.006 | 44.6388 | 44.6388 | 92.0148 | 0.7 | 69.38 | 14.38 | 543564 | 45.297 | 45.297 | 71.6119 | 23.7913 | 566231.8736 | 47.186 | 47.186 | 92.483 | 0.8 | 68.72 | 13.72 | 518616 | 43.218 | 43.218 | 72.8962 | 25.0756 | 596798.7413 | 49.7332 | 49.7332 | 92.9512 | 0.9 | 68.06 | 13.06 | 493668 | 41.139 | 41.139 | 74.1805 | 26.3599 | 627365.609 | 52.2805 | 52.2805 | 93.4195 | 1 | 67.4 | 12.4 | 468720 | 39.06 | 39.06 | 75.4649 | 27.6442 | 657932.4766 | 54.8277 | 54.8277 | 93.8877 | 65 | 75 | 27.9487 | 28 | 75.4
9/28/20XX 7:00:00 PM | 0.79167 | 3 | 66.3 | 78.1 | 67.2689 | 77.0561 | 9.7873 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/28/20XX 8:00:00 PM | 0.83333 | 3 | 66.2 | 77.7 | 67.0285 | 76.7802 | 9.7517 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/28/20XX 9:00:00 PM | 0.875 | 3 | 65.5 | 79.6 | 65.3675 | 74.8734 | 9.5059 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/28/20XX 10:00:00 PM | 0.91667 | 3 | 65.1 | 79.3 | 64.435 | 73.8031 | 9.3681 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/28/20XX 11:00:00 PM | 0.95833 | 3 | 64.9 | 79 | 63.9732 | 73.2731 | 9.2999 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/28/20XX 12:00:00 AM | 0 | 4 | 64.2 | 79.6 | 62.3806 | 71.4454 | 9.0649 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/29/20XX 1:00:00 AM | 0.041667 | 4 | 63.7 | 80.7 | 70.1655 | 79.0412 | 8.8758 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/29/20XX 2:00:00 AM | 0.083333 | 4 | 63.5 | 80.4 | 69.6593 | 78.4694 | 8.81 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/29/20XX 3:00:00 AM | 0.125 | 4 | 63 | 79.7 | 59.7337 | 68.4087 | 8.6749 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/29/20XX 4:00:00 AM | 0.16667 | 4 | 62.9 | 78.8 | 59.5179 | 68.161 | 8.6432 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/29/20XX 5:00:00 AM | 0.20833 | 4 | 62.2 | 80.5 | 66.4504 | 74.8441 | 8.3937 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/29/20XX 6:00:00 AM | 0.25 | 4 | 61.7 | 81.9 | 65.2529 | 73.4915 | 8.2386 | 80 | 61.7 |  | 61.7 | 66.8183 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 66.8183 | 18.9976 | 452143.8193 | 37.6787 | 37.6787 | 58.7837 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 66.8183 | 18.9976 | 452143.8193 | 37.6787 | 37.6787 | 58.7837 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 66.8183 | 18.9976 | 452143.8193 | 37.6787 | 37.6787 | 58.7837 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 66.8183 | 18.9976 | 452143.8193 | 37.6787 | 37.6787 | 58.7837 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 66.8183 | 18.9976 | 452143.8193 | 37.6787 | 37.6787 | 58.7837 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 66.8183 | 18.9976 | 452143.8193 | 37.6787 | 37.6787 | 58.7837 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 66.8183 | 18.9976 | 452143.8193 | 37.6787 | 37.6787 | 58.7837 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 66.8183 | 18.9976 | 452143.8193 | 37.6787 | 37.6787 | 58.7837 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 66.8183 | 18.9976 | 452143.8193 | 37.6787 | 37.6787 | 58.7837 | 1 | 61.7 | 6.7 | 253260 | 21.105 | 21.105 | 66.8183 | 18.9976 | 452143.8193 | 37.6787 | 37.6787 | 58.7837 | 60 | 80 | 25.2076 | 26 | 81.9
9/29/20XX 7:00:00 AM | 0.29167 | 4 | 62.1 | 80.3 | 66.2093 | 74.5718 | 8.3625 | 80 | 62.1 |  | 62.1 | 66.4602 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 66.4602 | 18.6396 | 443621.9044 | 36.9685 | 36.9685 | 59.3335 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 66.4602 | 18.6396 | 443621.9044 | 36.9685 | 36.9685 | 59.3335 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 66.4602 | 18.6396 | 443621.9044 | 36.9685 | 36.9685 | 59.3335 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 66.4602 | 18.6396 | 443621.9044 | 36.9685 | 36.9685 | 59.3335 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 66.4602 | 18.6396 | 443621.9044 | 36.9685 | 36.9685 | 59.3335 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 66.4602 | 18.6396 | 443621.9044 | 36.9685 | 36.9685 | 59.3335 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 66.4602 | 18.6396 | 443621.9044 | 36.9685 | 36.9685 | 59.3335 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 66.4602 | 18.6396 | 443621.9044 | 36.9685 | 36.9685 | 59.3335 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 66.4602 | 18.6396 | 443621.9044 | 36.9685 | 36.9685 | 59.3335 | 1 | 62.1 | 7.1 | 268380 | 22.365 | 22.365 | 66.4602 | 18.6396 | 443621.9044 | 36.9685 | 36.9685 | 59.3335 | 60 | 80 | 25.2496 | 26 | 80.3
9/29/20XX 8:00:00 AM | 0.33333 | 4 | 63.7 | 75.5 | 61.265 | 70.1655 | 8.9004 | 70 | 63.7 |  | 63.7 | 66.1603 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 66.1603 | 18.3396 | 436483.2616 | 36.3736 | 36.3736 | 63.7786 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 66.1603 | 18.3396 | 436483.2616 | 36.3736 | 36.3736 | 63.7786 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 66.1603 | 18.3396 | 436483.2616 | 36.3736 | 36.3736 | 63.7786 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 66.1603 | 18.3396 | 436483.2616 | 36.3736 | 36.3736 | 63.7786 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 66.1603 | 18.3396 | 436483.2616 | 36.3736 | 36.3736 | 63.7786 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 66.1603 | 18.3396 | 436483.2616 | 36.3736 | 36.3736 | 63.7786 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 66.1603 | 18.3396 | 436483.2616 | 36.3736 | 36.3736 | 63.7786 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 66.1603 | 18.3396 | 436483.2616 | 36.3736 | 36.3736 | 63.7786 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 66.1603 | 18.3396 | 436483.2616 | 36.3736 | 36.3736 | 63.7786 | 1 | 63.7 | 8.7 | 328860 | 27.405 | 27.405 | 66.1603 | 18.3396 | 436483.2616 | 36.3736 | 36.3736 | 63.7786 | 65 | 75 | 25.5936 | 26 | 75.5
9/29/20XX 9:00:00 AM | 0.375 | 4 | 65.6 | 70.4 | 65.6025 | 75.1431 | 9.5407 | 70 | 65.6 |  | 65.6 | 65.9841 | 0.1 | 73.16 | 18.16 | 686448 | 57.204 | 57.204 | 62.9579 | 15.1372 | 360266.4781 | 30.0222 | 30.0222 | 87.2262 | 0.2 | 72.32 | 17.32 | 654696 | 54.558 | 54.558 | 63.2941 | 15.4735 | 368269.1562 | 30.6891 | 30.6891 | 85.2471 | 0.3 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 63.6304 | 15.8097 | 376271.8343 | 31.356 | 31.356 | 83.268 | 0.4 | 70.64 | 15.64 | 591192 | 49.266 | 49.266 | 63.9666 | 16.146 | 384274.5123 | 32.0229 | 32.0229 | 81.2889 | 0.5 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 64.3029 | 16.4822 | 392277.1904 | 32.6898 | 32.6898 | 79.3098 | 0.6 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 64.6391 | 16.8185 | 400279.8685 | 33.3567 | 33.3567 | 77.3307 | 0.7 | 68.12 | 13.12 | 495936 | 41.328 | 41.328 | 64.9754 | 17.1547 | 408282.5466 | 34.0235 | 34.0235 | 75.3515 | 0.8 | 67.28 | 12.28 | 464184 | 38.682 | 38.682 | 65.3116 | 17.491 | 416285.2247 | 34.6904 | 34.6904 | 73.3724 | 0.9 | 66.44 | 11.44 | 432432 | 36.036 | 36.036 | 65.6479 | 17.8272 | 424287.9028 | 35.3573 | 35.3573 | 71.3933 | 1 | 65.6 | 10.6 | 400680 | 33.39 | 33.39 | 65.9841 | 18.1635 | 432290.5809 | 36.0242 | 36.0242 | 69.4142 | 65 | 70 | 26.0301 | 26 | 70.4
9/29/20XX 10:00:00 AM | 0.41667 | 4 | 67.2 | 67.6 | 59.4176 | 69.467 | 10.0494 | 60 | 67.2 |  | 67.2 | 67.0551 | 0.1 | 73.32 | 18.32 | 692496 | 57.708 | 57.708 | 63.065 | 15.2443 | 362815.4848 | 30.2346 | 30.2346 | 87.9426 | 0.2 | 72.64 | 17.64 | 666792 | 55.566 | 55.566 | 63.5083 | 15.6877 | 373367.1696 | 31.1139 | 31.1139 | 86.6799 | 0.3 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 63.9517 | 16.131 | 383918.8543 | 31.9932 | 31.9932 | 85.4172 | 0.4 | 71.28 | 16.28 | 615384 | 51.282 | 51.282 | 64.395 | 16.5744 | 394470.5391 | 32.8725 | 32.8725 | 84.1545 | 0.5 | 70.6 | 15.6 | 589680 | 49.14 | 49.14 | 64.8384 | 17.0177 | 405022.2239 | 33.7519 | 33.7519 | 82.8919 | 0.6 | 69.92 | 14.92 | 563976 | 46.998 | 46.998 | 65.2817 | 17.4611 | 415573.9087 | 34.6312 | 34.6312 | 81.6292 | 0.7 | 69.24 | 14.24 | 538272 | 44.856 | 44.856 | 65.7251 | 17.9044 | 426125.5935 | 35.5105 | 35.5105 | 80.3665 | 0.8 | 68.56 | 13.56 | 512568 | 42.714 | 42.714 | 66.1684 | 18.3478 | 436677.2783 | 36.3898 | 36.3898 | 79.1038 | 0.9 | 67.88 | 12.88 | 486864 | 40.572 | 40.572 | 66.6118 | 18.7911 | 447228.963 | 37.2691 | 37.2691 | 77.8411 | 1 | 67.2 | 12.2 | 461160 | 38.43 | 38.43 | 67.0551 | 19.2345 | 457780.6478 | 38.1484 | 38.1484 | 76.5784 | 65 | 70 | 26.5879 | 26 | 67.6
9/29/20XX 11:00:00 AM | 0.45833 | 4 | 68.9 | 62.6 | 63.1047 | 73.7935 | 10.6888 | 60 | 68.9 |  | 68.9 | 65.8838 | 0.1 | 73.49 | 18.49 | 698922 | 58.2435 | 58.2435 | 62.9478 | 15.1272 | 360027.7711 | 30.0023 | 30.0023 | 88.2458 | 0.2 | 72.98 | 17.98 | 679644 | 56.637 | 56.637 | 63.2741 | 15.4534 | 367791.7421 | 30.6493 | 30.6493 | 87.2863 | 0.3 | 72.47 | 17.47 | 660366 | 55.0305 | 55.0305 | 63.6003 | 15.7797 | 375555.7132 | 31.2963 | 31.2963 | 86.3268 | 0.4 | 71.96 | 16.96 | 641088 | 53.424 | 53.424 | 63.9265 | 16.1059 | 383319.6842 | 31.9433 | 31.9433 | 85.3673 | 0.5 | 71.45 | 16.45 | 621810 | 51.8175 | 51.8175 | 64.2527 | 16.4321 | 391083.6553 | 32.5903 | 32.5903 | 84.4078 | 0.6 | 70.94 | 15.94 | 602532 | 50.211 | 50.211 | 64.5789 | 16.7583 | 398847.6264 | 33.2373 | 33.2373 | 83.4483 | 0.7 | 70.43 | 15.43 | 583254 | 48.6045 | 48.6045 | 64.9052 | 17.0845 | 406611.5974 | 33.8843 | 33.8843 | 82.4888 | 0.8 | 69.92 | 14.92 | 563976 | 46.998 | 46.998 | 65.2314 | 17.4107 | 414375.5685 | 34.5313 | 34.5313 | 81.5293 | 0.9 | 69.41 | 14.41 | 544698 | 45.3915 | 45.3915 | 65.5576 | 17.737 | 422139.5396 | 35.1783 | 35.1783 | 80.5698 | 1 | 68.9 | 13.9 | 525420 | 43.785 | 43.785 | 65.8838 | 18.0632 | 429903.5106 | 35.8253 | 35.8253 | 79.6103 | 70 | 65 | 26.8203 | 26 | 62.6
9/29/20XX 12:00:00 PM | 0.5 | 4 | 69.5 | 61.8 | 64.4535 | 75.3763 | 10.9228 | 60 | 69.5 |  | 69.5 | 66.4196 | 0.1 | 73.55 | 18.55 | 701190 | 58.4325 | 58.4325 | 63.0014 | 15.1808 | 361302.9123 | 30.1086 | 30.1086 | 88.5411 | 0.2 | 73.1 | 18.1 | 684180 | 57.015 | 57.015 | 63.3812 | 15.5606 | 370342.0246 | 30.8618 | 30.8618 | 87.8768 | 0.3 | 72.65 | 17.65 | 667170 | 55.5975 | 55.5975 | 63.761 | 15.9404 | 379381.1369 | 31.6151 | 31.6151 | 87.2126 | 0.4 | 72.2 | 17.2 | 650160 | 54.18 | 54.18 | 64.1408 | 16.3202 | 388420.2492 | 32.3684 | 32.3684 | 86.5484 | 0.5 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 64.5206 | 16.7 | 397459.3615 | 33.1216 | 33.1216 | 85.8841 | 0.6 | 71.3 | 16.3 | 616140 | 51.345 | 51.345 | 64.9004 | 17.0798 | 406498.4738 | 33.8749 | 33.8749 | 85.2199 | 0.7 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 65.2802 | 17.4596 | 415537.5861 | 34.6281 | 34.6281 | 84.5556 | 0.8 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 65.66 | 17.8394 | 424576.6984 | 35.3814 | 35.3814 | 83.8914 | 0.9 | 69.95 | 14.95 | 565110 | 47.0925 | 47.0925 | 66.0398 | 18.2192 | 433615.8107 | 36.1347 | 36.1347 | 83.2272 | 1 | 69.5 | 14.5 | 548100 | 45.675 | 45.675 | 66.4196 | 18.5989 | 442654.923 | 36.8879 | 36.8879 | 82.5629 | 70 | 60 | 27.0505 | 28 | 61.8
9/29/20XX 1:00:00 PM | 0.54167 | 4 | 70.5 | 59.7 | 55.4618 | 66.7576 | 11.2958 | 50 | 70.5 |  | 70.5 | 66.4188 | 0.1 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 63.0013 | 15.1807 | 361300.9534 | 30.1084 | 30.1084 | 88.8559 | 0.2 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 63.3811 | 15.5604 | 370338.1069 | 30.8615 | 30.8615 | 88.5065 | 0.3 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 63.7608 | 15.9401 | 379375.2603 | 31.6146 | 31.6146 | 88.1571 | 0.4 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 64.1405 | 16.3198 | 388412.4138 | 32.3677 | 32.3677 | 87.8077 | 0.5 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 64.5202 | 16.6996 | 397449.5672 | 33.1208 | 33.1208 | 87.4583 | 0.6 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 64.8999 | 17.0793 | 406486.7207 | 33.8739 | 33.8739 | 87.1089 | 0.7 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 65.2796 | 17.459 | 415523.8741 | 34.627 | 34.627 | 86.7595 | 0.8 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 65.6593 | 17.8387 | 424561.0276 | 35.3801 | 35.3801 | 86.4101 | 0.9 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 66.039 | 18.2184 | 433598.181 | 36.1332 | 36.1332 | 86.0607 | 1 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 66.4188 | 18.5981 | 442635.3344 | 36.8863 | 36.8863 | 85.7113 | 70 | 60 | 27.2946 | 28 | 59.7
9/29/20XX 2:00:00 PM | 0.58333 | 4 | 70.5 | 58.7 | 55.4618 | 66.7576 | 11.2958 | 50 | 70.5 |  | 70.5 | 65.2892 | 0.1 | 73.65 | 18.65 | 704970 | 58.7475 | 58.7475 | 62.8884 | 15.0678 | 358612.546 | 29.8844 | 29.8844 | 88.6319 | 0.2 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 63.1551 | 15.3345 | 364961.2919 | 30.4134 | 30.4134 | 88.0584 | 0.3 | 72.95 | 17.95 | 678510 | 56.5425 | 56.5425 | 63.4219 | 15.6013 | 371310.0379 | 30.9425 | 30.9425 | 87.485 | 0.4 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 63.6886 | 15.868 | 377658.7839 | 31.4716 | 31.4716 | 86.9116 | 0.5 | 72.25 | 17.25 | 652050 | 54.3375 | 54.3375 | 63.9554 | 16.1348 | 384007.5299 | 32.0006 | 32.0006 | 86.3381 | 0.6 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 64.2222 | 16.4015 | 390356.2758 | 32.5297 | 32.5297 | 85.7647 | 0.7 | 71.55 | 16.55 | 625590 | 52.1325 | 52.1325 | 64.4889 | 16.6683 | 396705.0218 | 33.0588 | 33.0588 | 85.1913 | 0.8 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 64.7557 | 16.935 | 403053.7678 | 33.5878 | 33.5878 | 84.6178 | 0.9 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 65.0224 | 17.2018 | 409402.5138 | 34.1169 | 34.1169 | 84.0444 | 1 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 65.2892 | 17.4685 | 415751.2597 | 34.6459 | 34.6459 | 83.4709 | 70 | 60 | 27.1181 | 28 | 58.7
9/29/20XX 3:00:00 PM | 0.625 | 4 | 69.7 | 58.2 | 53.9286 | 64.9086 | 10.98 | 50 | 69.7 |  | 69.7 | 62.9322 | 0.1 | 73.57 | 18.57 | 701946 | 58.4955 | 58.4955 | 62.6527 | 14.8321 | 353003.0519 | 29.4169 | 29.4169 | 87.9124 | 0.2 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 62.6838 | 14.8631 | 353742.3037 | 29.4785 | 29.4785 | 86.6195 | 0.3 | 72.71 | 17.71 | 669438 | 55.7865 | 55.7865 | 62.7148 | 14.8942 | 354481.5556 | 29.5401 | 29.5401 | 85.3266 | 0.4 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 62.7459 | 14.9252 | 355220.8075 | 29.6017 | 29.6017 | 84.0337 | 0.5 | 71.85 | 16.85 | 636930 | 53.0775 | 53.0775 | 62.7769 | 14.9563 | 355960.0594 | 29.6633 | 29.6633 | 82.7408 | 0.6 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 62.808 | 14.9874 | 356699.3112 | 29.7249 | 29.7249 | 81.4479 | 0.7 | 70.99 | 15.99 | 604422 | 50.3685 | 50.3685 | 62.8391 | 15.0184 | 357438.5631 | 29.7865 | 29.7865 | 80.155 | 0.8 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 62.8701 | 15.0495 | 358177.815 | 29.8482 | 29.8482 | 78.8622 | 0.9 | 70.13 | 15.13 | 571914 | 47.6595 | 47.6595 | 62.9012 | 15.0805 | 358917.0668 | 29.9098 | 29.9098 | 77.5693 | 1 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 62.9322 | 15.1116 | 359656.3187 | 29.9714 | 29.9714 | 76.2764 | 70 | 60 | 26.5548 | 26 | 58.2
9/29/20XX 4:00:00 PM | 0.66667 | 4 | 68.7 | 62.6 | 62.6607 | 73.2724 | 10.6117 | 60 | 68.7 |  | 68.7 | 65.4197 | 0.1 | 73.47 | 18.47 | 698166 | 58.1805 | 58.1805 | 62.9014 | 15.0808 | 358923.3156 | 29.9103 | 29.9103 | 88.0908 | 0.2 | 72.94 | 17.94 | 678132 | 56.511 | 56.511 | 63.1813 | 15.3606 | 365582.8311 | 30.4652 | 30.4652 | 86.9762 | 0.3 | 72.41 | 17.41 | 658098 | 54.8415 | 54.8415 | 63.4611 | 15.6404 | 372242.3467 | 31.0202 | 31.0202 | 85.8617 | 0.4 | 71.88 | 16.88 | 638064 | 53.172 | 53.172 | 63.7409 | 15.9202 | 378901.8623 | 31.5752 | 31.5752 | 84.7472 | 0.5 | 71.35 | 16.35 | 618030 | 51.5025 | 51.5025 | 64.0207 | 16.2001 | 385561.3779 | 32.1301 | 32.1301 | 83.6326 | 0.6 | 70.82 | 15.82 | 597996 | 49.833 | 49.833 | 64.3005 | 16.4799 | 392220.8934 | 32.6851 | 32.6851 | 82.5181 | 0.7 | 70.29 | 15.29 | 577962 | 48.1635 | 48.1635 | 64.5803 | 16.7597 | 398880.409 | 33.24 | 33.24 | 81.4035 | 0.8 | 69.76 | 14.76 | 557928 | 46.494 | 46.494 | 64.8601 | 17.0395 | 405539.9246 | 33.795 | 33.795 | 80.289 | 0.9 | 69.23 | 14.23 | 537894 | 44.8245 | 44.8245 | 65.1399 | 17.3193 | 412199.4402 | 34.35 | 34.35 | 79.1745 | 1 | 68.7 | 13.7 | 517860 | 43.155 | 43.155 | 65.4197 | 17.5991 | 418858.9557 | 34.9049 | 34.9049 | 78.0599 | 70 | 65 | 26.699 | 26 | 62.6
9/29/20XX 5:00:00 PM | 0.70833 | 4 | 67.7 | 64.8 | 60.4817 | 70.7155 | 10.2338 | 60 | 67.7 |  | 67.7 | 65.3939 | 0.1 | 73.37 | 18.37 | 694386 | 57.8655 | 57.8655 | 62.8989 | 15.0782 | 358861.8801 | 29.9052 | 29.9052 | 87.7707 | 0.2 | 72.74 | 17.74 | 670572 | 55.881 | 55.881 | 63.1761 | 15.3555 | 365459.9602 | 30.455 | 30.455 | 86.336 | 0.3 | 72.11 | 17.11 | 646758 | 53.8965 | 53.8965 | 63.4533 | 15.6327 | 372058.0403 | 31.0048 | 31.0048 | 84.9013 | 0.4 | 71.48 | 16.48 | 622944 | 51.912 | 51.912 | 63.7306 | 15.9099 | 378656.1204 | 31.5547 | 31.5547 | 83.4667 | 0.5 | 70.85 | 15.85 | 599130 | 49.9275 | 49.9275 | 64.0078 | 16.1872 | 385254.2005 | 32.1045 | 32.1045 | 82.032 | 0.6 | 70.22 | 15.22 | 575316 | 47.943 | 47.943 | 64.285 | 16.4644 | 391852.2806 | 32.6544 | 32.6544 | 80.5974 | 0.7 | 69.59 | 14.59 | 551502 | 45.9585 | 45.9585 | 64.5622 | 16.7416 | 398450.3607 | 33.2042 | 33.2042 | 79.1627 | 0.8 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 64.8395 | 17.0188 | 405048.4409 | 33.754 | 33.754 | 77.728 | 0.9 | 68.33 | 13.33 | 503874 | 41.9895 | 41.9895 | 65.1167 | 17.2961 | 411646.521 | 34.3039 | 34.3039 | 76.2934 | 1 | 67.7 | 12.7 | 480060 | 40.005 | 40.005 | 65.3939 | 17.5733 | 418244.6011 | 34.8537 | 34.8537 | 74.8587 | 70 | 65 | 26.4509 | 26 | 64.8
9/29/20XX 6:00:00 PM | 0.75 | 4 | 66.8 | 66 | 58.5784 | 68.4823 | 9.9039 | 60 | 66.8 |  | 66.8 | 64.5207 | 0.1 | 73.28 | 18.28 | 690984 | 57.582 | 57.582 | 62.8115 | 14.9909 | 356783.5683 | 29.732 | 29.732 | 87.314 | 0.2 | 72.56 | 17.56 | 663768 | 55.314 | 55.314 | 63.0014 | 15.1808 | 361303.3366 | 30.1086 | 30.1086 | 85.4226 | 0.3 | 71.84 | 16.84 | 636552 | 53.046 | 53.046 | 63.1914 | 15.3707 | 365823.105 | 30.4853 | 30.4853 | 83.5313 | 0.4 | 71.12 | 16.12 | 609336 | 50.778 | 50.778 | 63.3813 | 15.5606 | 370342.8733 | 30.8619 | 30.8619 | 81.6399 | 0.5 | 70.4 | 15.4 | 582120 | 48.51 | 48.51 | 63.5712 | 15.7505 | 374862.6416 | 31.2386 | 31.2386 | 79.7486 | 0.6 | 69.68 | 14.68 | 554904 | 46.242 | 46.242 | 63.7611 | 15.9404 | 379382.4099 | 31.6152 | 31.6152 | 77.8572 | 0.7 | 68.96 | 13.96 | 527688 | 43.974 | 43.974 | 63.951 | 16.1303 | 383902.1782 | 31.9918 | 31.9918 | 75.9658 | 0.8 | 68.24 | 13.24 | 500472 | 41.706 | 41.706 | 64.1409 | 16.3202 | 388421.9466 | 32.3685 | 32.3685 | 74.0745 | 0.9 | 67.52 | 12.52 | 473256 | 39.438 | 39.438 | 64.3308 | 16.5102 | 392941.7149 | 32.7451 | 32.7451 | 72.1831 | 1 | 66.8 | 11.8 | 446040 | 37.17 | 37.17 | 64.5207 | 16.7001 | 397461.4832 | 33.1218 | 33.1218 | 70.2918 | 65 | 65 | 26.0949 | 26 | 66
9/29/20XX 7:00:00 PM | 0.79167 | 4 | 65.9 | 66.2 | 56.7286 | 66.3121 | 9.5834 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/29/20XX 8:00:00 PM | 0.83333 | 4 | 65.3 | 67.8 | 55.5248 | 64.8997 | 9.3749 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/29/20XX 9:00:00 PM | 0.875 | 4 | 64.6 | 69.3 | 54.1494 | 63.2862 | 9.1368 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/29/20XX 10:00:00 PM | 0.91667 | 4 | 64 | 71 | 61.9322 | 70.9309 | 8.9987 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/29/20XX 11:00:00 PM | 0.95833 | 4 | 63.6 | 73.1 | 61.0441 | 69.912 | 8.8679 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/29/20XX 12:00:00 AM | 0 | 5 | 63 | 75.6 | 59.7337 | 68.4087 | 8.6749 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/30/20XX 1:00:00 AM | 0.041667 | 5 | 62.9 | 77.1 | 59.5179 | 68.161 | 8.6432 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/30/20XX 2:00:00 AM | 0.083333 | 5 | 61.8 | 79.7 | 57.1898 | 65.4908 | 8.301 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/30/20XX 3:00:00 AM | 0.125 | 5 | 61.8 | 80 | 65.4908 | 73.7602 | 8.2694 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/30/20XX 4:00:00 AM | 0.16667 | 5 | 61.5 | 79.5 | 56.5695 | 64.7795 | 8.21 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/30/20XX 5:00:00 AM | 0.20833 | 5 | 61 | 80.6 | 63.61 | 71.636 | 8.0261 | 80 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/30/20XX 6:00:00 AM | 0.25 | 5 | 61 | 81.6 | 63.61 | 71.636 | 8.0261 | 80 | 61 |  | 61 | 64.8941 | 1 | 61 | 6 | 226800 | 18.9 | 18.9 | 64.8941 | 17.0735 | 406349.314 | 33.8624 | 33.8624 | 52.7624 | 1 | 61 | 6 | 226800 | 18.9 | 18.9 | 64.8941 | 17.0735 | 406349.314 | 33.8624 | 33.8624 | 52.7624 | 1 | 61 | 6 | 226800 | 18.9 | 18.9 | 64.8941 | 17.0735 | 406349.314 | 33.8624 | 33.8624 | 52.7624 | 1 | 61 | 6 | 226800 | 18.9 | 18.9 | 64.8941 | 17.0735 | 406349.314 | 33.8624 | 33.8624 | 52.7624 | 1 | 61 | 6 | 226800 | 18.9 | 18.9 | 64.8941 | 17.0735 | 406349.314 | 33.8624 | 33.8624 | 52.7624 | 1 | 61 | 6 | 226800 | 18.9 | 18.9 | 64.8941 | 17.0735 | 406349.314 | 33.8624 | 33.8624 | 52.7624 | 1 | 61 | 6 | 226800 | 18.9 | 18.9 | 64.8941 | 17.0735 | 406349.314 | 33.8624 | 33.8624 | 52.7624 | 1 | 61 | 6 | 226800 | 18.9 | 18.9 | 64.8941 | 17.0735 | 406349.314 | 33.8624 | 33.8624 | 52.7624 | 1 | 61 | 6 | 226800 | 18.9 | 18.9 | 64.8941 | 17.0735 | 406349.314 | 33.8624 | 33.8624 | 52.7624 | 1 | 61 | 6 | 226800 | 18.9 | 18.9 | 64.8941 | 17.0735 | 406349.314 | 33.8624 | 33.8624 | 52.7624 | 60 | 80 | 24.7373 | 24 | 81.6
9/30/20XX 7:00:00 AM | 0.29167 | 5 | 61.9 | 81.1 | 65.7295 | 74.0298 | 8.3003 | 80 | 61.9 |  | 61.9 | 66.6426 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 66.6426 | 18.8219 | 447961.9227 | 37.3302 | 37.3302 | 59.0652 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 66.6426 | 18.8219 | 447961.9227 | 37.3302 | 37.3302 | 59.0652 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 66.6426 | 18.8219 | 447961.9227 | 37.3302 | 37.3302 | 59.0652 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 66.6426 | 18.8219 | 447961.9227 | 37.3302 | 37.3302 | 59.0652 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 66.6426 | 18.8219 | 447961.9227 | 37.3302 | 37.3302 | 59.0652 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 66.6426 | 18.8219 | 447961.9227 | 37.3302 | 37.3302 | 59.0652 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 66.6426 | 18.8219 | 447961.9227 | 37.3302 | 37.3302 | 59.0652 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 66.6426 | 18.8219 | 447961.9227 | 37.3302 | 37.3302 | 59.0652 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 66.6426 | 18.8219 | 447961.9227 | 37.3302 | 37.3302 | 59.0652 | 1 | 61.9 | 6.9 | 260820 | 21.735 | 21.735 | 66.6426 | 18.8219 | 447961.9227 | 37.3302 | 37.3302 | 59.0652 | 60 | 80 | 25.2291 | 26 | 81.1
9/30/20XX 8:00:00 AM | 0.33333 | 5 | 62.8 | 75.5 | 59.3027 | 67.9142 | 8.6115 | 70 | 62.8 |  | 62.8 | 64.039 | 1 | 62.8 | 7.8 | 294840 | 24.57 | 24.57 | 64.039 | 16.2184 | 385997.7346 | 32.1665 | 32.1665 | 56.7365 | 1 | 62.8 | 7.8 | 294840 | 24.57 | 24.57 | 64.039 | 16.2184 | 385997.7346 | 32.1665 | 32.1665 | 56.7365 | 1 | 62.8 | 7.8 | 294840 | 24.57 | 24.57 | 64.039 | 16.2184 | 385997.7346 | 32.1665 | 32.1665 | 56.7365 | 1 | 62.8 | 7.8 | 294840 | 24.57 | 24.57 | 64.039 | 16.2184 | 385997.7346 | 32.1665 | 32.1665 | 56.7365 | 1 | 62.8 | 7.8 | 294840 | 24.57 | 24.57 | 64.039 | 16.2184 | 385997.7346 | 32.1665 | 32.1665 | 56.7365 | 1 | 62.8 | 7.8 | 294840 | 24.57 | 24.57 | 64.039 | 16.2184 | 385997.7346 | 32.1665 | 32.1665 | 56.7365 | 1 | 62.8 | 7.8 | 294840 | 24.57 | 24.57 | 64.039 | 16.2184 | 385997.7346 | 32.1665 | 32.1665 | 56.7365 | 1 | 62.8 | 7.8 | 294840 | 24.57 | 24.57 | 64.039 | 16.2184 | 385997.7346 | 32.1665 | 32.1665 | 56.7365 | 1 | 62.8 | 7.8 | 294840 | 24.57 | 24.57 | 64.039 | 16.2184 | 385997.7346 | 32.1665 | 32.1665 | 56.7365 | 1 | 62.8 | 7.8 | 294840 | 24.57 | 24.57 | 64.039 | 16.2184 | 385997.7346 | 32.1665 | 32.1665 | 56.7365 | 65 | 75 | 25.0435 | 26 | 75.5
9/30/20XX 9:00:00 AM | 0.375 | 5 | 64.3 | 73.1 | 62.6059 | 71.704 | 9.0981 | 70 | 64.3 |  | 64.3 | 65.4263 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.4263 | 17.6057 | 419014.5744 | 34.9179 | 34.9179 | 64.2129 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.4263 | 17.6057 | 419014.5744 | 34.9179 | 34.9179 | 64.2129 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.4263 | 17.6057 | 419014.5744 | 34.9179 | 34.9179 | 64.2129 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.4263 | 17.6057 | 419014.5744 | 34.9179 | 34.9179 | 64.2129 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.4263 | 17.6057 | 419014.5744 | 34.9179 | 34.9179 | 64.2129 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.4263 | 17.6057 | 419014.5744 | 34.9179 | 34.9179 | 64.2129 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.4263 | 17.6057 | 419014.5744 | 34.9179 | 34.9179 | 64.2129 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.4263 | 17.6057 | 419014.5744 | 34.9179 | 34.9179 | 64.2129 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.4263 | 17.6057 | 419014.5744 | 34.9179 | 34.9179 | 64.2129 | 1 | 64.3 | 9.3 | 351540 | 29.295 | 29.295 | 65.4263 | 17.6057 | 419014.5744 | 34.9179 | 34.9179 | 64.2129 | 65 | 75 | 25.6258 | 26 | 73.1
9/30/20XX 10:00:00 AM | 0.41667 | 5 | 65.4 | 70.4 | 65.1332 | 74.6045 | 9.4713 | 70 | 65.4 |  | 65.4 | 65.5121 | 0.1 | 73.14 | 18.14 | 685692 | 57.141 | 57.141 | 62.9107 | 15.09 | 359143.0222 | 29.9286 | 29.9286 | 87.0696 | 0.2 | 72.28 | 17.28 | 653184 | 54.432 | 54.432 | 63.1997 | 15.3791 | 366022.2443 | 30.5019 | 30.5019 | 84.9339 | 0.3 | 71.42 | 16.42 | 620676 | 51.723 | 51.723 | 63.4888 | 15.6681 | 372901.4665 | 31.0751 | 31.0751 | 82.7981 | 0.4 | 70.56 | 15.56 | 588168 | 49.014 | 49.014 | 63.7778 | 15.9572 | 379780.6887 | 31.6484 | 31.6484 | 80.6624 | 0.5 | 69.7 | 14.7 | 555660 | 46.305 | 46.305 | 64.0668 | 16.2462 | 386659.9109 | 32.2217 | 32.2217 | 78.5267 | 0.6 | 68.84 | 13.84 | 523152 | 43.596 | 43.596 | 64.3559 | 16.5353 | 393539.133 | 32.7949 | 32.7949 | 76.3909 | 0.7 | 67.98 | 12.98 | 490644 | 40.887 | 40.887 | 64.6449 | 16.8243 | 400418.3552 | 33.3682 | 33.3682 | 74.2552 | 0.8 | 67.12 | 12.12 | 458136 | 38.178 | 38.178 | 64.934 | 17.1133 | 407297.5774 | 33.9415 | 33.9415 | 72.1195 | 0.9 | 66.26 | 11.26 | 425628 | 35.469 | 35.469 | 65.223 | 17.4024 | 414176.7995 | 34.5147 | 34.5147 | 69.9837 | 1 | 65.4 | 10.4 | 393120 | 32.76 | 32.76 | 65.5121 | 17.6914 | 421056.0217 | 35.088 | 35.088 | 67.848 | 65 | 70 | 25.9077 | 26 | 70.4
9/30/20XX 11:00:00 AM | 0.45833 | 5 | 67.1 | 66.2 | 59.2068 | 69.2196 | 10.0128 | 60 | 67.1 |  | 67.1 | 65.4147 | 0.1 | 73.31 | 18.31 | 692118 | 57.6765 | 57.6765 | 62.9009 | 15.0803 | 358911.3912 | 29.9093 | 29.9093 | 87.5858 | 0.2 | 72.62 | 17.62 | 666036 | 55.503 | 55.503 | 63.1803 | 15.3596 | 365558.9824 | 30.4632 | 30.4632 | 85.9662 | 0.3 | 71.93 | 16.93 | 639954 | 53.3295 | 53.3295 | 63.4596 | 15.6389 | 372206.5736 | 31.0172 | 31.0172 | 84.3467 | 0.4 | 71.24 | 16.24 | 613872 | 51.156 | 51.156 | 63.7389 | 15.9182 | 378854.1649 | 31.5712 | 31.5712 | 82.7272 | 0.5 | 70.55 | 15.55 | 587790 | 48.9825 | 48.9825 | 64.0182 | 16.1976 | 385501.7561 | 32.1251 | 32.1251 | 81.1076 | 0.6 | 69.86 | 14.86 | 561708 | 46.809 | 46.809 | 64.2975 | 16.4769 | 392149.3473 | 32.6791 | 32.6791 | 79.4881 | 0.7 | 69.17 | 14.17 | 535626 | 44.6355 | 44.6355 | 64.5768 | 16.7562 | 398796.9385 | 33.2331 | 33.2331 | 77.8686 | 0.8 | 68.48 | 13.48 | 509544 | 42.462 | 42.462 | 64.8561 | 17.0355 | 405444.5297 | 33.787 | 33.787 | 76.249 | 0.9 | 67.79 | 12.79 | 483462 | 40.2885 | 40.2885 | 65.1354 | 17.3148 | 412092.1209 | 34.341 | 34.341 | 74.6295 | 1 | 67.1 | 12.1 | 457380 | 38.115 | 38.115 | 65.4147 | 17.5941 | 418739.7122 | 34.895 | 34.895 | 73.01 | 65 | 65 | 26.3076 | 26 | 66.2
9/30/20XX 12:00:00 PM | 0.5 | 5 | 68.3 | 65.7 | 61.7809 | 72.24 | 10.4591 | 60 | 68.3 |  | 68.3 | 67.7426 | 0.1 | 73.43 | 18.43 | 696654 | 58.0545 | 58.0545 | 63.1337 | 15.3131 | 364451.726 | 30.371 | 30.371 | 88.4255 | 0.2 | 72.86 | 17.86 | 675108 | 56.259 | 56.259 | 63.6458 | 15.8252 | 376639.6519 | 31.3866 | 31.3866 | 87.6456 | 0.3 | 72.29 | 17.29 | 653562 | 54.4635 | 54.4635 | 64.1579 | 16.3373 | 388827.5779 | 32.4023 | 32.4023 | 86.8658 | 0.4 | 71.72 | 16.72 | 632016 | 52.668 | 52.668 | 64.67 | 16.8494 | 401015.5038 | 33.418 | 33.418 | 86.086 | 0.5 | 71.15 | 16.15 | 610470 | 50.8725 | 50.8725 | 65.1821 | 17.3615 | 413203.4298 | 34.4336 | 34.4336 | 85.3061 | 0.6 | 70.58 | 15.58 | 588924 | 49.077 | 49.077 | 65.6942 | 17.8736 | 425391.3558 | 35.4493 | 35.4493 | 84.5263 | 0.7 | 70.01 | 15.01 | 567378 | 47.2815 | 47.2815 | 66.2063 | 18.3857 | 437579.2817 | 36.4649 | 36.4649 | 83.7464 | 0.8 | 69.44 | 14.44 | 545832 | 45.486 | 45.486 | 66.7184 | 18.8978 | 449767.2077 | 37.4806 | 37.4806 | 82.9666 | 0.9 | 68.87 | 13.87 | 524286 | 43.6905 | 43.6905 | 67.2305 | 19.4099 | 461955.1336 | 38.4963 | 38.4963 | 82.1868 | 1 | 68.3 | 13.3 | 502740 | 41.895 | 41.895 | 67.7426 | 19.922 | 474143.0596 | 39.5119 | 39.5119 | 81.4069 | 70 | 65 | 26.9639 | 26 | 65.7
9/30/20XX 1:00:00 PM | 0.54167 | 5 | 67.8 | 66 | 60.6965 | 70.9676 | 10.2711 | 60 | 67.8 |  | 67.8 | 66.8592 | 0.1 | 73.38 | 18.38 | 694764 | 57.897 | 57.897 | 63.0454 | 15.2248 | 362349.1746 | 30.1958 | 30.1958 | 88.0928 | 0.2 | 72.76 | 17.76 | 671328 | 55.944 | 55.944 | 63.4691 | 15.6485 | 372434.5491 | 31.0362 | 31.0362 | 86.9802 | 0.3 | 72.14 | 17.14 | 647892 | 53.991 | 53.991 | 63.8929 | 16.0723 | 382519.9237 | 31.8767 | 31.8767 | 85.8677 | 0.4 | 71.52 | 16.52 | 624456 | 52.038 | 52.038 | 64.3167 | 16.496 | 392605.2983 | 32.7171 | 32.7171 | 84.7551 | 0.5 | 70.9 | 15.9 | 601020 | 50.085 | 50.085 | 64.7404 | 16.9198 | 402690.6728 | 33.5576 | 33.5576 | 83.6426 | 0.6 | 70.28 | 15.28 | 577584 | 48.132 | 48.132 | 65.1642 | 17.3435 | 412776.0474 | 34.398 | 34.398 | 82.53 | 0.7 | 69.66 | 14.66 | 554148 | 46.179 | 46.179 | 65.5879 | 17.7673 | 422861.422 | 35.2385 | 35.2385 | 81.4175 | 0.8 | 69.04 | 14.04 | 530712 | 44.226 | 44.226 | 66.0117 | 18.191 | 432946.7965 | 36.0789 | 36.0789 | 80.3049 | 0.9 | 68.42 | 13.42 | 507276 | 42.273 | 42.273 | 66.4354 | 18.6148 | 443032.1711 | 36.9193 | 36.9193 | 79.1923 | 1 | 67.8 | 12.8 | 483840 | 40.32 | 40.32 | 66.8592 | 19.0386 | 453117.5457 | 37.7598 | 37.7598 | 78.0798 | 70 | 65 | 26.7039 | 26 | 66
9/30/20XX 2:00:00 PM | 0.58333 | 5 | 66.6 | 68.1 | 58.1627 | 67.9946 | 9.8319 | 60 | 66.6 |  | 66.6 | 66.1265 | 0.1 | 73.26 | 18.26 | 690228 | 57.519 | 57.519 | 62.9721 | 15.1515 | 360605.4484 | 30.0505 | 30.0505 | 87.5695 | 0.2 | 72.52 | 17.52 | 662256 | 55.188 | 55.188 | 63.3226 | 15.502 | 368947.0968 | 30.7456 | 30.7456 | 85.9336 | 0.3 | 71.78 | 16.78 | 634284 | 52.857 | 52.857 | 63.6731 | 15.8525 | 377288.7452 | 31.4407 | 31.4407 | 84.2977 | 0.4 | 71.04 | 16.04 | 606312 | 50.526 | 50.526 | 64.0236 | 16.203 | 385630.3936 | 32.1359 | 32.1359 | 82.6619 | 0.5 | 70.3 | 15.3 | 578340 | 48.195 | 48.195 | 64.3741 | 16.5534 | 393972.042 | 32.831 | 32.831 | 81.026 | 0.6 | 69.56 | 14.56 | 550368 | 45.864 | 45.864 | 64.7246 | 16.9039 | 402313.6904 | 33.5261 | 33.5261 | 79.3901 | 0.7 | 68.82 | 13.82 | 522396 | 43.533 | 43.533 | 65.0751 | 17.2544 | 410655.3388 | 34.2213 | 34.2213 | 77.7543 | 0.8 | 68.08 | 13.08 | 494424 | 41.202 | 41.202 | 65.4255 | 17.6049 | 418996.9872 | 34.9164 | 34.9164 | 76.1184 | 0.9 | 67.34 | 12.34 | 466452 | 38.871 | 38.871 | 65.776 | 17.9554 | 427338.6357 | 35.6116 | 35.6116 | 74.4826 | 1 | 66.6 | 11.6 | 438480 | 36.54 | 36.54 | 66.1265 | 18.3059 | 435680.2841 | 36.3067 | 36.3067 | 72.8467 | 65 | 70 | 26.2965 | 26 | 68.1
9/30/20XX 3:00:00 PM | 0.625 | 5 | 67 | 66.2 | 58.9966 | 68.973 | 9.9764 | 60 | 67 |  | 67 | 65.182 | 0.1 | 73.3 | 18.3 | 691740 | 57.645 | 57.645 | 62.8777 | 15.057 | 358357.5044 | 29.8631 | 29.8631 | 87.5081 | 0.2 | 72.6 | 17.6 | 665280 | 55.44 | 55.44 | 63.1337 | 15.3131 | 364451.2088 | 30.3709 | 30.3709 | 85.8109 | 0.3 | 71.9 | 16.9 | 638820 | 53.235 | 53.235 | 63.3897 | 15.5691 | 370544.9131 | 30.8787 | 30.8787 | 84.1137 | 0.4 | 71.2 | 16.2 | 612360 | 51.03 | 51.03 | 63.6458 | 15.8252 | 376638.6175 | 31.3866 | 31.3866 | 82.4166 | 0.5 | 70.5 | 15.5 | 585900 | 48.825 | 48.825 | 63.9018 | 16.0812 | 382732.3219 | 31.8944 | 31.8944 | 80.7194 | 0.6 | 69.8 | 14.8 | 559440 | 46.62 | 46.62 | 64.1579 | 16.3372 | 388826.0263 | 32.4022 | 32.4022 | 79.0222 | 0.7 | 69.1 | 14.1 | 532980 | 44.415 | 44.415 | 64.4139 | 16.5933 | 394919.7307 | 32.91 | 32.91 | 77.325 | 0.8 | 68.4 | 13.4 | 506520 | 42.21 | 42.21 | 64.6699 | 16.8493 | 401013.435 | 33.4178 | 33.4178 | 75.6278 | 0.9 | 67.7 | 12.7 | 480060 | 40.005 | 40.005 | 64.926 | 17.1053 | 407107.1394 | 33.9256 | 33.9256 | 73.9306 | 1 | 67 | 12 | 453600 | 37.8 | 37.8 | 65.182 | 17.3614 | 413200.8438 | 34.4334 | 34.4334 | 72.2334 | 65 | 65 | 26.2469 | 26 | 66.2
9/30/20XX 4:00:00 PM | 0.66667 | 5 | 66.5 | 66.1 | 57.9559 | 67.7519 | 9.796 | 60 | 66.5 |  | 66.5 | 63.9315 | 0.1 | 73.25 | 18.25 | 689850 | 57.4875 | 57.4875 | 62.7526 | 14.932 | 355381.1839 | 29.6151 | 29.6151 | 87.1026 | 0.2 | 72.5 | 17.5 | 661500 | 55.125 | 55.125 | 62.8836 | 15.063 | 358498.5679 | 29.8749 | 29.8749 | 84.9999 | 0.3 | 71.75 | 16.75 | 633150 | 52.7625 | 52.7625 | 63.0146 | 15.1939 | 361615.9518 | 30.1347 | 30.1347 | 82.8972 | 0.4 | 71 | 16 | 604800 | 50.4 | 50.4 | 63.1456 | 15.3249 | 364733.3358 | 30.3944 | 30.3944 | 80.7944 | 0.5 | 70.25 | 15.25 | 576450 | 48.0375 | 48.0375 | 63.2765 | 15.4559 | 367850.7197 | 30.6542 | 30.6542 | 78.6917 | 0.6 | 69.5 | 14.5 | 548100 | 45.675 | 45.675 | 63.4075 | 15.5869 | 370968.1036 | 30.914 | 30.914 | 76.589 | 0.7 | 68.75 | 13.75 | 519750 | 43.3125 | 43.3125 | 63.5385 | 15.7179 | 374085.4876 | 31.1738 | 31.1738 | 74.4863 | 0.8 | 68 | 13 | 491400 | 40.95 | 40.95 | 63.6695 | 15.8489 | 377202.8715 | 31.4336 | 31.4336 | 72.3836 | 0.9 | 67.25 | 12.25 | 463050 | 38.5875 | 38.5875 | 63.8005 | 15.9798 | 380320.2555 | 31.6934 | 31.6934 | 70.2809 | 1 | 66.5 | 11.5 | 434700 | 36.225 | 36.225 | 63.9315 | 16.1108 | 383437.6394 | 31.9531 | 31.9531 | 68.1781 | 65 | 65 | 25.9298 | 26 | 66.1
9/30/20XX 5:00:00 PM | 0.70833 | 5 | 65.1 | 69.1 | 55.1286 | 64.435 | 9.3063 | 60 | 65.1 |  | 65.1 | 63.5974 | 0.1 | 73.11 | 18.11 | 684558 | 57.0465 | 57.0465 | 62.7192 | 14.8986 | 354586.1298 | 29.5488 | 29.5488 | 86.5953 | 0.2 | 72.22 | 17.22 | 650916 | 54.243 | 54.243 | 62.8168 | 14.9962 | 356908.4595 | 29.7424 | 29.7424 | 83.9854 | 0.3 | 71.33 | 16.33 | 617274 | 51.4395 | 51.4395 | 62.9144 | 15.0937 | 359230.7893 | 29.9359 | 29.9359 | 81.3754 | 0.4 | 70.44 | 15.44 | 583632 | 48.636 | 48.636 | 63.0119 | 15.1913 | 361553.119 | 30.1294 | 30.1294 | 78.7654 | 0.5 | 69.55 | 14.55 | 549990 | 45.8325 | 45.8325 | 63.1095 | 15.2889 | 363875.4488 | 30.323 | 30.323 | 76.1555 | 0.6 | 68.66 | 13.66 | 516348 | 43.029 | 43.029 | 63.2071 | 15.3865 | 366197.7785 | 30.5165 | 30.5165 | 73.5455 | 0.7 | 67.77 | 12.77 | 482706 | 40.2255 | 40.2255 | 63.3047 | 15.484 | 368520.1083 | 30.71 | 30.71 | 70.9355 | 0.8 | 66.88 | 11.88 | 449064 | 37.422 | 37.422 | 63.4022 | 15.5816 | 370842.438 | 30.9035 | 30.9035 | 68.3255 | 0.9 | 65.99 | 10.99 | 415422 | 34.6185 | 34.6185 | 63.4998 | 15.6792 | 373164.7678 | 31.0971 | 31.0971 | 65.7156 | 1 | 65.1 | 10.1 | 381780 | 31.815 | 31.815 | 63.5974 | 15.7768 | 375487.0976 | 31.2906 | 31.2906 | 63.1056 | 65 | 70 | 25.5361 | 26 | 69.1
9/30/20XX 6:00:00 PM | 0.75 | 5 | 64.2 | 68.7 | 53.3774 | 62.3806 | 9.0032 | 60 | 64.2 |  | 64.2 | 61.2102 | 1 | 64.2 | 9.2 | 347760 | 28.98 | 28.98 | 61.2102 | 13.3895 | 318670.6566 | 26.5559 | 26.5559 | 55.5359 | 1 | 64.2 | 9.2 | 347760 | 28.98 | 28.98 | 61.2102 | 13.3895 | 318670.6566 | 26.5559 | 26.5559 | 55.5359 | 1 | 64.2 | 9.2 | 347760 | 28.98 | 28.98 | 61.2102 | 13.3895 | 318670.6566 | 26.5559 | 26.5559 | 55.5359 | 1 | 64.2 | 9.2 | 347760 | 28.98 | 28.98 | 61.2102 | 13.3895 | 318670.6566 | 26.5559 | 26.5559 | 55.5359 | 1 | 64.2 | 9.2 | 347760 | 28.98 | 28.98 | 61.2102 | 13.3895 | 318670.6566 | 26.5559 | 26.5559 | 55.5359 | 1 | 64.2 | 9.2 | 347760 | 28.98 | 28.98 | 61.2102 | 13.3895 | 318670.6566 | 26.5559 | 26.5559 | 55.5359 | 1 | 64.2 | 9.2 | 347760 | 28.98 | 28.98 | 61.2102 | 13.3895 | 318670.6566 | 26.5559 | 26.5559 | 55.5359 | 1 | 64.2 | 9.2 | 347760 | 28.98 | 28.98 | 61.2102 | 13.3895 | 318670.6566 | 26.5559 | 26.5559 | 55.5359 | 1 | 64.2 | 9.2 | 347760 | 28.98 | 28.98 | 61.2102 | 13.3895 | 318670.6566 | 26.5559 | 26.5559 | 55.5359 | 1 | 64.2 | 9.2 | 347760 | 28.98 | 28.98 | 61.2102 | 13.3895 | 318670.6566 | 26.5559 | 26.5559 | 55.5359 | 65 | 70 | 24.9445 | 24 | 68.7
9/30/20XX 7:00:00 PM | 0.79167 | 5 | 63.5 | 70.5 | 60.8239 | 69.6593 | 8.8354 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/30/20XX 8:00:00 PM | 0.83333 | 5 | 62.7 | 71.2 | 59.0882 | 67.6682 | 8.58 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/30/20XX 9:00:00 PM | 0.875 | 5 | 61.4 | 75.7 | 56.3642 | 64.544 | 8.1799 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/30/20XX 10:00:00 PM | 0.91667 | 5 | 61.2 | 76.3 | 55.9555 | 64.0754 | 8.1199 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9/30/20XX 11:00:00 PM | 0.95833 | 5 | 60.3 | 77.9 | 54.1501 | 62.0055 | 7.8554 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 93490.9605 | [5 empty] | 146451.6496 | [11 empty] | 153420.903 | [11 empty] | 160390.1564 | [11 empty] | 167359.4098 | [11 empty] | 174328.6632 | [11 empty] | 181297.9165 | [11 empty] | 188267.1699 | [11 empty] | 195236.4233 | [11 empty] | 202205.6767 | [11 empty] | 209174.9301
Author:
why is it higher than its open OAD counterpart?
Author:
why is it higher than its open OAD counterpart?
Note on BO2933: Author: why is it higher than its open OAD counterpart?
Note on DR2933: Author: why is it higher than its open OAD counterpart?

## Heating Season calculations
User input is not required in this sheet.
These data are used for calculations.
[8 empty] | 10% OAF |  |  |  | 20% OAF |  |  |  | 30% OAF |  |  |  | 40% OAF |  |  |  | 50% OAF |  |  |  | 60% OAF |  |  |  | 70% OAF |  |  |  | 80% OAF |  |  |  | 90% OAF |  |  |  | 100% OAF
Date & Time | Time | Day | OAT | OA RH | OAT, sorted | HALF | OAT, sorted NEW | MAT (eq. 23) | dT (eq. 24) | Qs dot (eq. 25) | Qtotal | MAT (eq. 23) | dT (eq. 24) | Qs dot (eq. 25) | Qtotal | MAT (eq. 23) | dT (eq. 24) | Qs dot (eq. 25) | Qtotal | MAT (eq. 23) | dT (eq. 24) | Qs dot (eq. 25) | Qtotal | MAT (eq. 23) | dT (eq. 24) | Qs dot (eq. 25) | Qtotal (eq. 26) | MAT (eq. 23) | dT (eq. 24) | Qs dot (eq. 25) | Qtotal | MAT (eq. 23) | dT (eq. 24) | Qs dot (eq. 25) | Qtotal | MAT (eq. 23) | dT (eq. 24) | Qs dot (eq. 25) | Qtotal | MAT (eq. 23) | dT (eq. 24) | Qs dot (eq. 25) | Qtotal | MAT (eq. 23) | dT (eq. 24) | Qs dot (eq. 25) | Qtotal | OAT Bins | Schedule |  | User Input Variables (Heating Season)
10/15/20XX 12:00:00 AM | 0 | 7 | 57.5 | 75.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MHS |  | CFM in the Supply Duct | 35000
10/16/20XX 1:00:00 AM | 0.041667 | 7 | 57.1 | 74.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MCS |  | OAD Position in % | 10
10/16/20XX 2:00:00 AM | 0.083333 | 7 | 56.4 | 71.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MOS | 0.25 |  | 20
10/16/20XX 3:00:00 AM | 0.125 | 7 | 56 | 70.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | MOE | 0.79167 |  | 30
10/16/20XX 4:00:00 AM | 0.16667 | 7 | 55.1 | 72.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 40
10/16/20XX 5:00:00 AM | 0.20833 | 7 | 54.5 | 72.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | TUHS |  |  | 50
10/16/20XX 6:00:00 AM | 0.25 | 7 | 53.8 | 70.4 | 53.8 |  | 53.8 | 70.18 | 9.82 | 371196 | 371.196 | 68.36 | 11.64 | 439992 | 439.992 | 66.54 | 13.46 | 508788 | 508.788 | 64.72 | 15.28 | 577584 | 577.584 | 62.9 | 17.1 | 646380 | 646.38 | 61.08 | 18.92 | 715176 | 715.176 | 59.26 | 20.74 | 783972 | 783.972 | 57.44 | 22.56 | 852768 | 852.768 | 55.62 | 24.38 | 921564 | 921.564 | 53.8 | 26.2 | 990360 | 990.36 | 55 | TUCS |  |  | 60
10/16/20XX 7:00:00 AM | 0.29167 | 7 | 53.8 | 69 | 53.8 |  | 53.8 | 70.18 | 9.82 | 371196 | 371.196 | 68.36 | 11.64 | 439992 | 439.992 | 66.54 | 13.46 | 508788 | 508.788 | 64.72 | 15.28 | 577584 | 577.584 | 62.9 | 17.1 | 646380 | 646.38 | 61.08 | 18.92 | 715176 | 715.176 | 59.26 | 20.74 | 783972 | 783.972 | 57.44 | 22.56 | 852768 | 852.768 | 55.62 | 24.38 | 921564 | 921.564 | 53.8 | 26.2 | 990360 | 990.36 | 55 | TUOS | 0.25 |  | 70
10/16/20XX 8:00:00 AM | 0.33333 | 7 | 54.3 | 66 | 54.3 |  | 54.3 | 70.23 | 9.77 | 369306 | 369.306 | 68.46 | 11.54 | 436212 | 436.212 | 66.69 | 13.31 | 503118 | 503.118 | 64.92 | 15.08 | 570024 | 570.024 | 63.15 | 16.85 | 636930 | 636.93 | 61.38 | 18.62 | 703836 | 703.836 | 59.61 | 20.39 | 770742 | 770.742 | 57.84 | 22.16 | 837648 | 837.648 | 56.07 | 23.93 | 904554 | 904.554 | 54.3 | 25.7 | 971460 | 971.46 | 55 | TUOE | 0.79167 |  | 80
10/16/20XX 9:00:00 AM | 0.375 | 7 | 54.9 | 64 | 54.9 |  | 54.9 | 70.29 | 9.71 | 367038 | 367.038 | 68.58 | 11.42 | 431676 | 431.676 | 66.87 | 13.13 | 496314 | 496.314 | 65.16 | 14.84 | 560952 | 560.952 | 63.45 | 16.55 | 625590 | 625.59 | 61.74 | 18.26 | 690228 | 690.228 | 60.03 | 19.97 | 754866 | 754.866 | 58.32 | 21.68 | 819504 | 819.504 | 56.61 | 23.39 | 884142 | 884.142 | 54.9 | 25.1 | 948780 | 948.78 | 55 |  |  |  | 90
10/16/20XX 10:00:00 AM | 0.41667 | 7 | 56.3 | 61.6 | 56.3 |  | 56.3 | 70.43 | 9.57 | 361746 | 361.746 | 68.86 | 11.14 | 421092 | 421.092 | 67.29 | 12.71 | 480438 | 480.438 | 65.72 | 14.28 | 539784 | 539.784 | 64.15 | 15.85 | 599130 | 599.13 | 62.58 | 17.42 | 658476 | 658.476 | 61.01 | 18.99 | 717822 | 717.822 | 59.44 | 20.56 | 777168 | 777.168 | 57.87 | 22.13 | 836514 | 836.514 | 56.3 | 23.7 | 895860 | 895.86 | 55 | WHS |  |  | 100
10/16/20XX 11:00:00 AM | 0.45833 | 7 | 57.2 | 60.1 | 57.2 |  | 57.2 | 70.52 | 9.48 | 358344 | 358.344 | 69.04 | 10.96 | 414288 | 414.288 | 67.56 | 12.44 | 470232 | 470.232 | 66.08 | 13.92 | 526176 | 526.176 | 64.6 | 15.4 | 582120 | 582.12 | 63.12 | 16.88 | 638064 | 638.064 | 61.64 | 18.36 | 694008 | 694.008 | 60.16 | 19.84 | 749952 | 749.952 | 58.68 | 21.32 | 805896 | 805.896 | 57.2 | 22.8 | 861840 | 861.84 | 55 | WCS |  | RAT | 72
10/16/20XX 12:00:00 PM | 0.5 | 7 | 58.7 | 56.1 | 58.7 |  | 58.7 | 70.67 | 9.33 | 352674 | 352.674 | 69.34 | 10.66 | 402948 | 402.948 | 68.01 | 11.99 | 453222 | 453.222 | 66.68 | 13.32 | 503496 | 503.496 | 65.35 | 14.65 | 553770 | 553.77 | 64.02 | 15.98 | 604044 | 604.044 | 62.69 | 17.31 | 654318 | 654.318 | 61.36 | 18.64 | 704592 | 704.592 | 60.03 | 19.97 | 754866 | 754.866 | 58.7 | 21.3 | 805140 | 805.14 | 60 | WOS | 0.25 | DATSP (if available) | 80
10/16/20XX 1:00:00 PM | 0.54167 | 7 | 59.5 | 54 | 59.5 |  | 59.5 | 70.75 | 9.25 | 349650 | 349.65 | 69.5 | 10.5 | 396900 | 396.9 | 68.25 | 11.75 | 444150 | 444.15 | 67 | 13 | 491400 | 491.4 | 65.75 | 14.25 | 538650 | 538.65 | 64.5 | 15.5 | 585900 | 585.9 | 63.25 | 16.75 | 633150 | 633.15 | 62 | 18 | 680400 | 680.4 | 60.75 | 19.25 | 727650 | 727.65 | 59.5 | 20.5 | 774900 | 774.9 | 60 | WOE | 0.79167 | Boiler efficiency | 0.75
10/16/20XX 2:00:00 PM | 0.58333 | 7 | 60.7 | 52 | 60.7 |  | 60.7 | 70.87 | 9.13 | 345114 | 345.114 | 69.74 | 10.26 | 387828 | 387.828 | 68.61 | 11.39 | 430542 | 430.542 | 67.48 | 12.52 | 473256 | 473.256 | 66.35 | 13.65 | 515970 | 515.97 | 65.22 | 14.78 | 558684 | 558.684 | 64.09 | 15.91 | 601398 | 601.398 | 62.96 | 17.04 | 644112 | 644.112 | 61.83 | 18.17 | 686826 | 686.826 | 60.7 | 19.3 | 729540 | 729.54 | 60
10/16/20XX 3:00:00 PM | 0.625 | 7 | 59.9 | 53.9 | 59.9 |  | 59.9 | 70.79 | 9.21 | 348138 | 348.138 | 69.58 | 10.42 | 393876 | 393.876 | 68.37 | 11.63 | 439614 | 439.614 | 67.16 | 12.84 | 485352 | 485.352 | 65.95 | 14.05 | 531090 | 531.09 | 64.74 | 15.26 | 576828 | 576.828 | 63.53 | 16.47 | 622566 | 622.566 | 62.32 | 17.68 | 668304 | 668.304 | 61.11 | 18.89 | 714042 | 714.042 | 59.9 | 20.1 | 759780 | 759.78 | 60 | THHS
10/16/20XX 4:00:00 PM | 0.66667 | 7 | 59.7 | 54.2 | 59.7 |  | 59.7 | 70.77 | 9.23 | 348894 | 348.894 | 69.54 | 10.46 | 395388 | 395.388 | 68.31 | 11.69 | 441882 | 441.882 | 67.08 | 12.92 | 488376 | 488.376 | 65.85 | 14.15 | 534870 | 534.87 | 64.62 | 15.38 | 581364 | 581.364 | 63.39 | 16.61 | 627858 | 627.858 | 62.16 | 17.84 | 674352 | 674.352 | 60.93 | 19.07 | 720846 | 720.846 | 59.7 | 20.3 | 767340 | 767.34 | 60 | THCS
10/16/20XX 5:00:00 PM | 0.70833 | 7 | 58.9 | 55.1 | 58.9 |  | 58.9 | 70.69 | 9.31 | 351918 | 351.918 | 69.38 | 10.62 | 401436 | 401.436 | 68.07 | 11.93 | 450954 | 450.954 | 66.76 | 13.24 | 500472 | 500.472 | 65.45 | 14.55 | 549990 | 549.99 | 64.14 | 15.86 | 599508 | 599.508 | 62.83 | 17.17 | 649026 | 649.026 | 61.52 | 18.48 | 698544 | 698.544 | 60.21 | 19.79 | 748062 | 748.062 | 58.9 | 21.1 | 797580 | 797.58 | 60 | THOS | 0.25
10/16/20XX 6:00:00 PM | 0.75 | 7 | 58.1 | 56.8 | 58.1 |  | 58.1 | 70.61 | 9.39 | 354942 | 354.942 | 69.22 | 10.78 | 407484 | 407.484 | 67.83 | 12.17 | 460026 | 460.026 | 66.44 | 13.56 | 512568 | 512.568 | 65.05 | 14.95 | 565110 | 565.11 | 63.66 | 16.34 | 617652 | 617.652 | 62.27 | 17.73 | 670194 | 670.194 | 60.88 | 19.12 | 722736 | 722.736 | 59.49 | 20.51 | 775278 | 775.278 | 58.1 | 21.9 | 827820 | 827.82 | 60 | THOE | 0.79167
10/16/20XX 7:00:00 PM | 0.79167 | 7 | 57.6 | 57.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/16/20XX 8:00:00 PM | 0.83333 | 7 | 56.7 | 59.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FHS
10/16/20XX 9:00:00 PM | 0.875 | 7 | 56.3 | 60.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FCS
10/16/20XX 10:00:00 PM | 0.91667 | 7 | 55.6 | 61 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FOS | 0.25
10/16/20XX 11:00:00 PM | 0.95833 |  | 54.8 | 63.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | FOE | 0.79167
10/16/20XX 12:00:00 AM | 0 | 1 | 54.4 | 64.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/17/20XX 1:00:00 AM | 0.041667 | 1 | 53.9 | 65.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | SAHS | #REF!
10/17/20XX 2:00:00 AM | 0.083333 | 1 | 53.3 | 67.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | SACS | #REF!
10/17/20XX 3:00:00 AM | 0.125 | 1 | 52.7 | 69.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | SAOS | 0.25
10/17/20XX 4:00:00 AM | 0.16667 | 1 | 52.7 | 70.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | SAOE | 0.79167
10/17/20XX 5:00:00 AM | 0.20833 | 1 | 52.1 | 70.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/17/20XX 6:00:00 AM | 0.25 | 1 | 51.7 | 73.7 | 51.7 |  | 51.7 | 69.97 | 10.03 | 379134 | 379.134 | 67.94 | 12.06 | 455868 | 455.868 | 65.91 | 14.09 | 532602 | 532.602 | 63.88 | 16.12 | 609336 | 609.336 | 61.85 | 18.15 | 686070 | 686.07 | 59.82 | 20.18 | 762804 | 762.804 | 57.79 | 22.21 | 839538 | 839.538 | 55.76 | 24.24 | 916272 | 916.272 | 53.73 | 26.27 | 993006 | 993.006 | 51.7 | 28.3 | 1069740 | 1069.74 | 50 | SHS
10/17/20XX 7:00:00 AM | 0.29167 | 1 | 52.4 | 71.9 | 52.4 |  | 52.4 | 70.04 | 9.96 | 376488 | 376.488 | 68.08 | 11.92 | 450576 | 450.576 | 66.12 | 13.88 | 524664 | 524.664 | 64.16 | 15.84 | 598752 | 598.752 | 62.2 | 17.8 | 672840 | 672.84 | 60.24 | 19.76 | 746928 | 746.928 | 58.28 | 21.72 | 821016 | 821.016 | 56.32 | 23.68 | 895104 | 895.104 | 54.36 | 25.64 | 969192 | 969.192 | 52.4 | 27.6 | 1043280 | 1043.28 | 50 | SCS
10/17/20XX 8:00:00 AM | 0.33333 | 1 | 53.3 | 69.9 | 53.3 |  | 53.3 | 70.13 | 9.87 | 373086 | 373.086 | 68.26 | 11.74 | 443772 | 443.772 | 66.39 | 13.61 | 514458 | 514.458 | 64.52 | 15.48 | 585144 | 585.144 | 62.65 | 17.35 | 655830 | 655.83 | 60.78 | 19.22 | 726516 | 726.516 | 58.91 | 21.09 | 797202 | 797.202 | 57.04 | 22.96 | 867888 | 867.888 | 55.17 | 24.83 | 938574 | 938.574 | 53.3 | 26.7 | 1009260 | 1009.26 | 55 | SOS | 0.25
10/17/20XX 9:00:00 AM | 0.375 | 1 | 54.9 | 63.7 | 54.9 |  | 54.9 | 70.29 | 9.71 | 367038 | 367.038 | 68.58 | 11.42 | 431676 | 431.676 | 66.87 | 13.13 | 496314 | 496.314 | 65.16 | 14.84 | 560952 | 560.952 | 63.45 | 16.55 | 625590 | 625.59 | 61.74 | 18.26 | 690228 | 690.228 | 60.03 | 19.97 | 754866 | 754.866 | 58.32 | 21.68 | 819504 | 819.504 | 56.61 | 23.39 | 884142 | 884.142 | 54.9 | 25.1 | 948780 | 948.78 | 55 | SOE | 0.79167
10/17/20XX 10:00:00 AM | 0.41667 | 1 | 57 | 59 | 57 |  | 57 | 70.5 | 9.5 | 359100 | 359.1 | 69 | 11 | 415800 | 415.8 | 67.5 | 12.5 | 472500 | 472.5 | 66 | 14 | 529200 | 529.2 | 64.5 | 15.5 | 585900 | 585.9 | 63 | 17 | 642600 | 642.6 | 61.5 | 18.5 | 699300 | 699.3 | 60 | 20 | 756000 | 756 | 58.5 | 21.5 | 812700 | 812.7 | 57 | 23 | 869400 | 869.4 | 55
10/17/20XX 11:00:00 AM | 0.45833 | 1 | 59.8 | 52.6 | 59.8 |  | 59.8 | 70.78 | 9.22 | 348516 | 348.516 | 69.56 | 10.44 | 394632 | 394.632 | 68.34 | 11.66 | 440748 | 440.748 | 67.12 | 12.88 | 486864 | 486.864 | 65.9 | 14.1 | 532980 | 532.98 | 64.68 | 15.32 | 579096 | 579.096 | 63.46 | 16.54 | 625212 | 625.212 | 62.24 | 17.76 | 671328 | 671.328 | 61.02 | 18.98 | 717444 | 717.444 | 59.8 | 20.2 | 763560 | 763.56 | 60 | Hours_post BRT
10/17/20XX 12:00:00 PM | 0.5 | 1 | 61.5 | 48.6 | 61.5 |  | 61.5 | 70.95 | 9.05 | 342090 | 342.09 | 69.9 | 10.1 | 381780 | 381.78 | 68.85 | 11.15 | 421470 | 421.47 | 67.8 | 12.2 | 461160 | 461.16 | 66.75 | 13.25 | 500850 | 500.85 | 65.7 | 14.3 | 540540 | 540.54 | 64.65 | 15.35 | 580230 | 580.23 | 63.6 | 16.4 | 619920 | 619.92 | 62.55 | 17.45 | 659610 | 659.61 | 61.5 | 18.5 | 699300 | 699.3 | 60
10/17/20XX 1:00:00 PM | 0.54167 | 1 | 62.8 | 46.1 | 62.8 |  | 62.8 | 71.08 | 8.92 | 337176 | 337.176 | 70.16 | 9.84 | 371952 | 371.952 | 69.24 | 10.76 | 406728 | 406.728 | 68.32 | 11.68 | 441504 | 441.504 | 67.4 | 12.6 | 476280 | 476.28 | 66.48 | 13.52 | 511056 | 511.056 | 65.56 | 14.44 | 545832 | 545.832 | 64.64 | 15.36 | 580608 | 580.608 | 63.72 | 16.28 | 615384 | 615.384 | 62.8 | 17.2 | 650160 | 650.16 | 65 | Hours_heat
10/17/20XX 2:00:00 PM | 0.58333 | 1 | 63.6 | 44.9 | 63.6 |  | 63.6 | 71.16 | 8.84 | 334152 | 334.152 | 70.32 | 9.68 | 365904 | 365.904 | 69.48 | 10.52 | 397656 | 397.656 | 68.64 | 11.36 | 429408 | 429.408 | 67.8 | 12.2 | 461160 | 461.16 | 66.96 | 13.04 | 492912 | 492.912 | 66.12 | 13.88 | 524664 | 524.664 | 65.28 | 14.72 | 556416 | 556.416 | 64.44 | 15.56 | 588168 | 588.168 | 63.6 | 16.4 | 619920 | 619.92 | 65
10/17/20XX 3:00:00 PM | 0.625 | 1 | 63.3 | 45.4 | 63.3 |  | 63.3 | 71.13 | 8.87 | 335286 | 335.286 | 70.26 | 9.74 | 368172 | 368.172 | 69.39 | 10.61 | 401058 | 401.058 | 68.52 | 11.48 | 433944 | 433.944 | 67.65 | 12.35 | 466830 | 466.83 | 66.78 | 13.22 | 499716 | 499.716 | 65.91 | 14.09 | 532602 | 532.602 | 65.04 | 14.96 | 565488 | 565.488 | 64.17 | 15.83 | 598374 | 598.374 | 63.3 | 16.7 | 631260 | 631.26 | 65 | Hours_cool
10/17/20XX 4:00:00 PM | 0.66667 | 1 | 62.7 | 45.8 | 62.7 |  | 62.7 | 71.07 | 8.93 | 337554 | 337.554 | 70.14 | 9.86 | 372708 | 372.708 | 69.21 | 10.79 | 407862 | 407.862 | 68.28 | 11.72 | 443016 | 443.016 | 67.35 | 12.65 | 478170 | 478.17 | 66.42 | 13.58 | 513324 | 513.324 | 65.49 | 14.51 | 548478 | 548.478 | 64.56 | 15.44 | 583632 | 583.632 | 63.63 | 16.37 | 618786 | 618.786 | 62.7 | 17.3 | 653940 | 653.94 | 65
10/17/20XX 5:00:00 PM | 0.70833 | 1 | 61.3 | 49 | 61.3 |  | 61.3 | 70.93 | 9.07 | 342846 | 342.846 | 69.86 | 10.14 | 383292 | 383.292 | 68.79 | 11.21 | 423738 | 423.738 | 67.72 | 12.28 | 464184 | 464.184 | 66.65 | 13.35 | 504630 | 504.63 | 65.58 | 14.42 | 545076 | 545.076 | 64.51 | 15.49 | 585522 | 585.522 | 63.44 | 16.56 | 625968 | 625.968 | 62.37 | 17.63 | 666414 | 666.414 | 61.3 | 18.7 | 706860 | 706.86 | 60
10/17/20XX 6:00:00 PM | 0.75 | 1 | 60.1 | 52.6 | 60.1 |  | 60.1 | 70.81 | 9.19 | 347382 | 347.382 | 69.62 | 10.38 | 392364 | 392.364 | 68.43 | 11.57 | 437346 | 437.346 | 67.24 | 12.76 | 482328 | 482.328 | 66.05 | 13.95 | 527310 | 527.31 | 64.86 | 15.14 | 572292 | 572.292 | 63.67 | 16.33 | 617274 | 617.274 | 62.48 | 17.52 | 662256 | 662.256 | 61.29 | 18.71 | 707238 | 707.238 | 60.1 | 19.9 | 752220 | 752.22 | 60
10/17/20XX 7:00:00 PM | 0.79167 | 1 | 59.3 | 53.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/17/20XX 8:00:00 PM | 0.83333 | 1 | 58.7 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/17/20XX 9:00:00 PM | 0.875 | 1 | 57.9 | 54.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/17/20XX 10:00:00 PM | 0.91667 | 1 | 56.9 | 56.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/17/20XX 11:00:00 PM | 0.95833 | 1 | 56.2 | 57.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/17/20XX 12:00:00 AM | 0 | 2 | 55.1 | 62.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/18/20XX 1:00:00 AM | 0.041667 | 2 | 54.8 | 62.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/18/20XX 2:00:00 AM | 0.083333 | 2 | 54 | 63.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/18/20XX 3:00:00 AM | 0.125 | 2 | 53.4 | 63.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/18/20XX 4:00:00 AM | 0.16667 | 2 | 52.8 | 64.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/18/20XX 5:00:00 AM | 0.20833 | 2 | 52.1 | 67.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/18/20XX 6:00:00 AM | 0.25 | 2 | 51.7 | 68.2 | 51.7 |  | 51.7 | 69.97 | 10.03 | 379134 | 379.134 | 67.94 | 12.06 | 455868 | 455.868 | 65.91 | 14.09 | 532602 | 532.602 | 63.88 | 16.12 | 609336 | 609.336 | 61.85 | 18.15 | 686070 | 686.07 | 59.82 | 20.18 | 762804 | 762.804 | 57.79 | 22.21 | 839538 | 839.538 | 55.76 | 24.24 | 916272 | 916.272 | 53.73 | 26.27 | 993006 | 993.006 | 51.7 | 28.3 | 1069740 | 1069.74 | 50
10/18/20XX 7:00:00 AM | 0.29167 | 2 | 52 | 68.1 | 52 |  | 52 | 70 | 10 | 378000 | 378 | 68 | 12 | 453600 | 453.6 | 66 | 14 | 529200 | 529.2 | 64 | 16 | 604800 | 604.8 | 62 | 18 | 680400 | 680.4 | 60 | 20 | 756000 | 756 | 58 | 22 | 831600 | 831.6 | 56 | 24 | 907200 | 907.2 | 54 | 26 | 982800 | 982.8 | 52 | 28 | 1058400 | 1058.4 | 50
10/18/20XX 8:00:00 AM | 0.33333 | 2 | 52.8 | 68 | 52.8 |  | 52.8 | 70.08 | 9.92 | 374976 | 374.976 | 68.16 | 11.84 | 447552 | 447.552 | 66.24 | 13.76 | 520128 | 520.128 | 64.32 | 15.68 | 592704 | 592.704 | 62.4 | 17.6 | 665280 | 665.28 | 60.48 | 19.52 | 737856 | 737.856 | 58.56 | 21.44 | 810432 | 810.432 | 56.64 | 23.36 | 883008 | 883.008 | 54.72 | 25.28 | 955584 | 955.584 | 52.8 | 27.2 | 1028160 | 1028.16 | 55
10/18/20XX 9:00:00 AM | 0.375 | 2 | 54.4 | 62.9 | 54.4 |  | 54.4 | 70.24 | 9.76 | 368928 | 368.928 | 68.48 | 11.52 | 435456 | 435.456 | 66.72 | 13.28 | 501984 | 501.984 | 64.96 | 15.04 | 568512 | 568.512 | 63.2 | 16.8 | 635040 | 635.04 | 61.44 | 18.56 | 701568 | 701.568 | 59.68 | 20.32 | 768096 | 768.096 | 57.92 | 22.08 | 834624 | 834.624 | 56.16 | 23.84 | 901152 | 901.152 | 54.4 | 25.6 | 967680 | 967.68 | 55
10/18/20XX 10:00:00 AM | 0.41667 | 2 | 56.3 | 58.3 | 56.3 |  | 56.3 | 70.43 | 9.57 | 361746 | 361.746 | 68.86 | 11.14 | 421092 | 421.092 | 67.29 | 12.71 | 480438 | 480.438 | 65.72 | 14.28 | 539784 | 539.784 | 64.15 | 15.85 | 599130 | 599.13 | 62.58 | 17.42 | 658476 | 658.476 | 61.01 | 18.99 | 717822 | 717.822 | 59.44 | 20.56 | 777168 | 777.168 | 57.87 | 22.13 | 836514 | 836.514 | 56.3 | 23.7 | 895860 | 895.86 | 55
10/18/20XX 11:00:00 AM | 0.45833 | 2 | 59 | 53.1 | 59 |  | 59 | 70.7 | 9.3 | 351540 | 351.54 | 69.4 | 10.6 | 400680 | 400.68 | 68.1 | 11.9 | 449820 | 449.82 | 66.8 | 13.2 | 498960 | 498.96 | 65.5 | 14.5 | 548100 | 548.1 | 64.2 | 15.8 | 597240 | 597.24 | 62.9 | 17.1 | 646380 | 646.38 | 61.6 | 18.4 | 695520 | 695.52 | 60.3 | 19.7 | 744660 | 744.66 | 59 | 21 | 793800 | 793.8 | 60
10/18/20XX 12:00:00 PM | 0.5 | 2 | 60.9 | 48.2 | 60.9 |  | 60.9 | 70.89 | 9.11 | 344358 | 344.358 | 69.78 | 10.22 | 386316 | 386.316 | 68.67 | 11.33 | 428274 | 428.274 | 67.56 | 12.44 | 470232 | 470.232 | 66.45 | 13.55 | 512190 | 512.19 | 65.34 | 14.66 | 554148 | 554.148 | 64.23 | 15.77 | 596106 | 596.106 | 63.12 | 16.88 | 638064 | 638.064 | 62.01 | 17.99 | 680022 | 680.022 | 60.9 | 19.1 | 721980 | 721.98 | 60
10/18/20XX 1:00:00 PM | 0.54167 | 2 | 62.3 | 45.1 | 62.3 |  | 62.3 | 71.03 | 8.97 | 339066 | 339.066 | 70.06 | 9.94 | 375732 | 375.732 | 69.09 | 10.91 | 412398 | 412.398 | 68.12 | 11.88 | 449064 | 449.064 | 67.15 | 12.85 | 485730 | 485.73 | 66.18 | 13.82 | 522396 | 522.396 | 65.21 | 14.79 | 559062 | 559.062 | 64.24 | 15.76 | 595728 | 595.728 | 63.27 | 16.73 | 632394 | 632.394 | 62.3 | 17.7 | 669060 | 669.06 | 60
10/18/20XX 2:00:00 PM | 0.58333 | 2 | 61.2 | 46.5 | 61.2 |  | 61.2 | 70.92 | 9.08 | 343224 | 343.224 | 69.84 | 10.16 | 384048 | 384.048 | 68.76 | 11.24 | 424872 | 424.872 | 67.68 | 12.32 | 465696 | 465.696 | 66.6 | 13.4 | 506520 | 506.52 | 65.52 | 14.48 | 547344 | 547.344 | 64.44 | 15.56 | 588168 | 588.168 | 63.36 | 16.64 | 628992 | 628.992 | 62.28 | 17.72 | 669816 | 669.816 | 61.2 | 18.8 | 710640 | 710.64 | 60
10/18/20XX 3:00:00 PM | 0.625 | 2 | 61.3 | 46.3 | 61.3 |  | 61.3 | 70.93 | 9.07 | 342846 | 342.846 | 69.86 | 10.14 | 383292 | 383.292 | 68.79 | 11.21 | 423738 | 423.738 | 67.72 | 12.28 | 464184 | 464.184 | 66.65 | 13.35 | 504630 | 504.63 | 65.58 | 14.42 | 545076 | 545.076 | 64.51 | 15.49 | 585522 | 585.522 | 63.44 | 16.56 | 625968 | 625.968 | 62.37 | 17.63 | 666414 | 666.414 | 61.3 | 18.7 | 706860 | 706.86 | 60
10/18/20XX 4:00:00 PM | 0.66667 | 2 | 60.1 | 49.8 | 60.1 |  | 60.1 | 70.81 | 9.19 | 347382 | 347.382 | 69.62 | 10.38 | 392364 | 392.364 | 68.43 | 11.57 | 437346 | 437.346 | 67.24 | 12.76 | 482328 | 482.328 | 66.05 | 13.95 | 527310 | 527.31 | 64.86 | 15.14 | 572292 | 572.292 | 63.67 | 16.33 | 617274 | 617.274 | 62.48 | 17.52 | 662256 | 662.256 | 61.29 | 18.71 | 707238 | 707.238 | 60.1 | 19.9 | 752220 | 752.22 | 60
10/18/20XX 5:00:00 PM | 0.70833 | 2 | 58.6 | 52.4 | 58.6 |  | 58.6 | 70.66 | 9.34 | 353052 | 353.052 | 69.32 | 10.68 | 403704 | 403.704 | 67.98 | 12.02 | 454356 | 454.356 | 66.64 | 13.36 | 505008 | 505.008 | 65.3 | 14.7 | 555660 | 555.66 | 63.96 | 16.04 | 606312 | 606.312 | 62.62 | 17.38 | 656964 | 656.964 | 61.28 | 18.72 | 707616 | 707.616 | 59.94 | 20.06 | 758268 | 758.268 | 58.6 | 21.4 | 808920 | 808.92 | 60
10/18/20XX 6:00:00 PM | 0.75 | 2 | 57.9 | 53.7 | 57.9 |  | 57.9 | 70.59 | 9.41 | 355698 | 355.698 | 69.18 | 10.82 | 408996 | 408.996 | 67.77 | 12.23 | 462294 | 462.294 | 66.36 | 13.64 | 515592 | 515.592 | 64.95 | 15.05 | 568890 | 568.89 | 63.54 | 16.46 | 622188 | 622.188 | 62.13 | 17.87 | 675486 | 675.486 | 60.72 | 19.28 | 728784 | 728.784 | 59.31 | 20.69 | 782082 | 782.082 | 57.9 | 22.1 | 835380 | 835.38 | 60
10/18/20XX 7:00:00 PM | 0.79167 | 2 | 57 | 55.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/18/20XX 8:00:00 PM | 0.83333 | 2 | 56.5 | 58 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/18/20XX 9:00:00 PM | 0.875 | 2 | 55.9 | 61.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/18/20XX 10:00:00 PM | 0.91667 | 2 | 55.5 | 61.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/18/20XX 11:00:00 PM | 0.95833 | 2 | 54.7 | 64.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/18/20XX 12:00:00 AM | 0 | 3 | 54.3 | 65.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/19/20XX 1:00:00 AM | 0.041667 | 3 | 53.9 | 67.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/19/20XX 2:00:00 AM | 0.083333 | 3 | 53.5 | 66.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/19/20XX 3:00:00 AM | 0.125 | 3 | 53 | 69.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/19/20XX 4:00:00 AM | 0.16667 | 3 | 52.7 | 72 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/19/20XX 5:00:00 AM | 0.20833 | 3 | 52.4 | 73.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/19/20XX 6:00:00 AM | 0.25 | 3 | 51.8 | 74.9 | 51.8 |  | 51.8 | 69.98 | 10.02 | 378756 | 378.756 | 67.96 | 12.04 | 455112 | 455.112 | 65.94 | 14.06 | 531468 | 531.468 | 63.92 | 16.08 | 607824 | 607.824 | 61.9 | 18.1 | 684180 | 684.18 | 59.88 | 20.12 | 760536 | 760.536 | 57.86 | 22.14 | 836892 | 836.892 | 55.84 | 24.16 | 913248 | 913.248 | 53.82 | 26.18 | 989604 | 989.604 | 51.8 | 28.2 | 1065960 | 1065.96 | 50
10/19/20XX 7:00:00 AM | 0.29167 | 3 | 52.4 | 74.3 | 52.4 |  | 52.4 | 70.04 | 9.96 | 376488 | 376.488 | 68.08 | 11.92 | 450576 | 450.576 | 66.12 | 13.88 | 524664 | 524.664 | 64.16 | 15.84 | 598752 | 598.752 | 62.2 | 17.8 | 672840 | 672.84 | 60.24 | 19.76 | 746928 | 746.928 | 58.28 | 21.72 | 821016 | 821.016 | 56.32 | 23.68 | 895104 | 895.104 | 54.36 | 25.64 | 969192 | 969.192 | 52.4 | 27.6 | 1043280 | 1043.28 | 50
10/19/20XX 8:00:00 AM | 0.33333 | 3 | 53.1 | 72.3 | 53.1 |  | 53.1 | 70.11 | 9.89 | 373842 | 373.842 | 68.22 | 11.78 | 445284 | 445.284 | 66.33 | 13.67 | 516726 | 516.726 | 64.44 | 15.56 | 588168 | 588.168 | 62.55 | 17.45 | 659610 | 659.61 | 60.66 | 19.34 | 731052 | 731.052 | 58.77 | 21.23 | 802494 | 802.494 | 56.88 | 23.12 | 873936 | 873.936 | 54.99 | 25.01 | 945378 | 945.378 | 53.1 | 26.9 | 1016820 | 1016.82 | 55 |  |  |  |  | New OAD
10/19/20XX 9:00:00 AM | 0.375 | 3 | 55.1 | 68.6 | 55.1 |  | 55.1 | 70.31 | 9.69 | 366282 | 366.282 | 68.62 | 11.38 | 430164 | 430.164 | 66.93 | 13.07 | 494046 | 494.046 | 65.24 | 14.76 | 557928 | 557.928 | 63.55 | 16.45 | 621810 | 621.81 | 61.86 | 18.14 | 685692 | 685.692 | 60.17 | 19.83 | 749574 | 749.574 | 58.48 | 21.52 | 813456 | 813.456 | 56.79 | 23.21 | 877338 | 877.338 | 55.1 | 24.9 | 941220 | 941.22 | 55 |  |  |  |  | #REF!
10/19/20XX 10:00:00 AM | 0.41667 | 3 | 56.8 | 64.1 | 56.8 |  | 56.8 | 70.48 | 9.52 | 359856 | 359.856 | 68.96 | 11.04 | 417312 | 417.312 | 67.44 | 12.56 | 474768 | 474.768 | 65.92 | 14.08 | 532224 | 532.224 | 64.4 | 15.6 | 589680 | 589.68 | 62.88 | 17.12 | 647136 | 647.136 | 61.36 | 18.64 | 704592 | 704.592 | 59.84 | 20.16 | 762048 | 762.048 | 58.32 | 21.68 | 819504 | 819.504 | 56.8 | 23.2 | 876960 | 876.96 | 55 |  |  |  |  | #REF!
10/19/20XX 11:00:00 AM | 0.45833 | 3 | 58.7 | 60.1 | 58.7 |  | 58.7 | 70.67 | 9.33 | 352674 | 352.674 | 69.34 | 10.66 | 402948 | 402.948 | 68.01 | 11.99 | 453222 | 453.222 | 66.68 | 13.32 | 503496 | 503.496 | 65.35 | 14.65 | 553770 | 553.77 | 64.02 | 15.98 | 604044 | 604.044 | 62.69 | 17.31 | 654318 | 654.318 | 61.36 | 18.64 | 704592 | 704.592 | 60.03 | 19.97 | 754866 | 754.866 | 58.7 | 21.3 | 805140 | 805.14 | 60 |  |  |  |  | #REF!
10/19/20XX 12:00:00 PM | 0.5 | 3 | 60.4 | 56.3 | 60.4 |  | 60.4 | 70.84 | 9.16 | 346248 | 346.248 | 69.68 | 10.32 | 390096 | 390.096 | 68.52 | 11.48 | 433944 | 433.944 | 67.36 | 12.64 | 477792 | 477.792 | 66.2 | 13.8 | 521640 | 521.64 | 65.04 | 14.96 | 565488 | 565.488 | 63.88 | 16.12 | 609336 | 609.336 | 62.72 | 17.28 | 653184 | 653.184 | 61.56 | 18.44 | 697032 | 697.032 | 60.4 | 19.6 | 740880 | 740.88 | 60 |  |  |  |  | #REF!
10/19/20XX 1:00:00 PM | 0.54167 | 3 | 61.5 | 55 | 61.5 |  | 61.5 | 70.95 | 9.05 | 342090 | 342.09 | 69.9 | 10.1 | 381780 | 381.78 | 68.85 | 11.15 | 421470 | 421.47 | 67.8 | 12.2 | 461160 | 461.16 | 66.75 | 13.25 | 500850 | 500.85 | 65.7 | 14.3 | 540540 | 540.54 | 64.65 | 15.35 | 580230 | 580.23 | 63.6 | 16.4 | 619920 | 619.92 | 62.55 | 17.45 | 659610 | 659.61 | 61.5 | 18.5 | 699300 | 699.3 | 60
10/19/20XX 2:00:00 PM | 0.58333 | 3 | 61.7 | 54 | 61.7 |  | 61.7 | 70.97 | 9.03 | 341334 | 341.334 | 69.94 | 10.06 | 380268 | 380.268 | 68.91 | 11.09 | 419202 | 419.202 | 67.88 | 12.12 | 458136 | 458.136 | 66.85 | 13.15 | 497070 | 497.07 | 65.82 | 14.18 | 536004 | 536.004 | 64.79 | 15.21 | 574938 | 574.938 | 63.76 | 16.24 | 613872 | 613.872 | 62.73 | 17.27 | 652806 | 652.806 | 61.7 | 18.3 | 691740 | 691.74 | 60
10/19/20XX 3:00:00 PM | 0.625 | 3 | 61.6 | 52.5 | 61.6 |  | 61.6 | 70.96 | 9.04 | 341712 | 341.712 | 69.92 | 10.08 | 381024 | 381.024 | 68.88 | 11.12 | 420336 | 420.336 | 67.84 | 12.16 | 459648 | 459.648 | 66.8 | 13.2 | 498960 | 498.96 | 65.76 | 14.24 | 538272 | 538.272 | 64.72 | 15.28 | 577584 | 577.584 | 63.68 | 16.32 | 616896 | 616.896 | 62.64 | 17.36 | 656208 | 656.208 | 61.6 | 18.4 | 695520 | 695.52 | 60
10/19/20XX 4:00:00 PM | 0.66667 | 3 | 60.9 | 54.5 | 60.9 |  | 60.9 | 70.89 | 9.11 | 344358 | 344.358 | 69.78 | 10.22 | 386316 | 386.316 | 68.67 | 11.33 | 428274 | 428.274 | 67.56 | 12.44 | 470232 | 470.232 | 66.45 | 13.55 | 512190 | 512.19 | 65.34 | 14.66 | 554148 | 554.148 | 64.23 | 15.77 | 596106 | 596.106 | 63.12 | 16.88 | 638064 | 638.064 | 62.01 | 17.99 | 680022 | 680.022 | 60.9 | 19.1 | 721980 | 721.98 | 60
10/19/20XX 5:00:00 PM | 0.70833 | 3 | 59.8 | 57.2 | 59.8 |  | 59.8 | 70.78 | 9.22 | 348516 | 348.516 | 69.56 | 10.44 | 394632 | 394.632 | 68.34 | 11.66 | 440748 | 440.748 | 67.12 | 12.88 | 486864 | 486.864 | 65.9 | 14.1 | 532980 | 532.98 | 64.68 | 15.32 | 579096 | 579.096 | 63.46 | 16.54 | 625212 | 625.212 | 62.24 | 17.76 | 671328 | 671.328 | 61.02 | 18.98 | 717444 | 717.444 | 59.8 | 20.2 | 763560 | 763.56 | 60
10/19/20XX 6:00:00 PM | 0.75 | 3 | 58.9 | 58.2 | 58.9 |  | 58.9 | 70.69 | 9.31 | 351918 | 351.918 | 69.38 | 10.62 | 401436 | 401.436 | 68.07 | 11.93 | 450954 | 450.954 | 66.76 | 13.24 | 500472 | 500.472 | 65.45 | 14.55 | 549990 | 549.99 | 64.14 | 15.86 | 599508 | 599.508 | 62.83 | 17.17 | 649026 | 649.026 | 61.52 | 18.48 | 698544 | 698.544 | 60.21 | 19.79 | 748062 | 748.062 | 58.9 | 21.1 | 797580 | 797.58 | 60
10/19/20XX 7:00:00 PM | 0.79167 | 3 | 58.5 | 59.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/19/20XX 8:00:00 PM | 0.83333 | 3 | 58 | 61.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/19/20XX 9:00:00 PM | 0.875 | 3 | 57.8 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/19/20XX 10:00:00 PM | 0.91667 | 3 | 57.2 | 64.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/19/20XX 11:00:00 PM | 0.95833 | 3 | 56.4 | 67.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/19/20XX 12:00:00 AM | 0 | 4 | 56 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/20/20XX 1:00:00 AM | 0.041667 | 4 | 55.4 | 69.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/20/20XX 2:00:00 AM | 0.083333 | 4 | 55 | 69.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/20/20XX 3:00:00 AM | 0.125 | 4 | 54.6 | 70.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/20/20XX 4:00:00 AM | 0.16667 | 4 | 54.4 | 70.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/20/20XX 5:00:00 AM | 0.20833 | 4 | 53.8 | 72.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/20/20XX 6:00:00 AM | 0.25 | 4 | 53.6 | 72.9 | 53.6 |  | 53.6 | 70.16 | 9.84 | 371952 | 371.952 | 68.32 | 11.68 | 441504 | 441.504 | 66.48 | 13.52 | 511056 | 511.056 | 64.64 | 15.36 | 580608 | 580.608 | 62.8 | 17.2 | 650160 | 650.16 | 60.96 | 19.04 | 719712 | 719.712 | 59.12 | 20.88 | 789264 | 789.264 | 57.28 | 22.72 | 858816 | 858.816 | 55.44 | 24.56 | 928368 | 928.368 | 53.6 | 26.4 | 997920 | 997.92 | 55
10/20/20XX 7:00:00 AM | 0.29167 | 4 | 54 | 72.7 | 54 |  | 54 | 70.2 | 9.8 | 370440 | 370.44 | 68.4 | 11.6 | 438480 | 438.48 | 66.6 | 13.4 | 506520 | 506.52 | 64.8 | 15.2 | 574560 | 574.56 | 63 | 17 | 642600 | 642.6 | 61.2 | 18.8 | 710640 | 710.64 | 59.4 | 20.6 | 778680 | 778.68 | 57.6 | 22.4 | 846720 | 846.72 | 55.8 | 24.2 | 914760 | 914.76 | 54 | 26 | 982800 | 982.8 | 55
10/20/20XX 8:00:00 AM | 0.33333 | 4 | 55.2 | 68.9 | 55.2 |  | 55.2 | 70.32 | 9.68 | 365904 | 365.904 | 68.64 | 11.36 | 429408 | 429.408 | 66.96 | 13.04 | 492912 | 492.912 | 65.28 | 14.72 | 556416 | 556.416 | 63.6 | 16.4 | 619920 | 619.92 | 61.92 | 18.08 | 683424 | 683.424 | 60.24 | 19.76 | 746928 | 746.928 | 58.56 | 21.44 | 810432 | 810.432 | 56.88 | 23.12 | 873936 | 873.936 | 55.2 | 24.8 | 937440 | 937.44 | 55
10/20/20XX 9:00:00 AM | 0.375 | 4 | 56.7 | 63.3 | 56.7 |  | 56.7 | 70.47 | 9.53 | 360234 | 360.234 | 68.94 | 11.06 | 418068 | 418.068 | 67.41 | 12.59 | 475902 | 475.902 | 65.88 | 14.12 | 533736 | 533.736 | 64.35 | 15.65 | 591570 | 591.57 | 62.82 | 17.18 | 649404 | 649.404 | 61.29 | 18.71 | 707238 | 707.238 | 59.76 | 20.24 | 765072 | 765.072 | 58.23 | 21.77 | 822906 | 822.906 | 56.7 | 23.3 | 880740 | 880.74 | 55
10/20/20XX 10:00:00 AM | 0.41667 | 4 | 58.8 | 57.1 | 58.8 |  | 58.8 | 70.68 | 9.32 | 352296 | 352.296 | 69.36 | 10.64 | 402192 | 402.192 | 68.04 | 11.96 | 452088 | 452.088 | 66.72 | 13.28 | 501984 | 501.984 | 65.4 | 14.6 | 551880 | 551.88 | 64.08 | 15.92 | 601776 | 601.776 | 62.76 | 17.24 | 651672 | 651.672 | 61.44 | 18.56 | 701568 | 701.568 | 60.12 | 19.88 | 751464 | 751.464 | 58.8 | 21.2 | 801360 | 801.36 | 60
10/20/20XX 11:00:00 AM | 0.45833 | 4 | 60.6 | 53.2 | 60.6 |  | 60.6 | 70.86 | 9.14 | 345492 | 345.492 | 69.72 | 10.28 | 388584 | 388.584 | 68.58 | 11.42 | 431676 | 431.676 | 67.44 | 12.56 | 474768 | 474.768 | 66.3 | 13.7 | 517860 | 517.86 | 65.16 | 14.84 | 560952 | 560.952 | 64.02 | 15.98 | 604044 | 604.044 | 62.88 | 17.12 | 647136 | 647.136 | 61.74 | 18.26 | 690228 | 690.228 | 60.6 | 19.4 | 733320 | 733.32 | 60
10/20/20XX 12:00:00 PM | 0.5 | 4 | 63.2 | 47.3 | 63.2 |  | 63.2 | 71.12 | 8.88 | 335664 | 335.664 | 70.24 | 9.76 | 368928 | 368.928 | 69.36 | 10.64 | 402192 | 402.192 | 68.48 | 11.52 | 435456 | 435.456 | 67.6 | 12.4 | 468720 | 468.72 | 66.72 | 13.28 | 501984 | 501.984 | 65.84 | 14.16 | 535248 | 535.248 | 64.96 | 15.04 | 568512 | 568.512 | 64.08 | 15.92 | 601776 | 601.776 | 63.2 | 16.8 | 635040 | 635.04 | 65
10/20/20XX 1:00:00 PM | 0.54167 | 4 | 64.1 | 46.1 | 64.1 |  | 64.1 | 71.21 | 8.79 | 332262 | 332.262 | 70.42 | 9.58 | 362124 | 362.124 | 69.63 | 10.37 | 391986 | 391.986 | 68.84 | 11.16 | 421848 | 421.848 | 68.05 | 11.95 | 451710 | 451.71 | 67.26 | 12.74 | 481572 | 481.572 | 66.47 | 13.53 | 511434 | 511.434 | 65.68 | 14.32 | 541296 | 541.296 | 64.89 | 15.11 | 571158 | 571.158 | 64.1 | 15.9 | 601020 | 601.02 | 65
10/20/20XX 2:00:00 PM | 0.58333 | 4 | 64.6 | 45.6 | 64.6 |  | 64.6 | 71.26 | 8.74 | 330372 | 330.372 | 70.52 | 9.48 | 358344 | 358.344 | 69.78 | 10.22 | 386316 | 386.316 | 69.04 | 10.96 | 414288 | 414.288 | 68.3 | 11.7 | 442260 | 442.26 | 67.56 | 12.44 | 470232 | 470.232 | 66.82 | 13.18 | 498204 | 498.204 | 66.08 | 13.92 | 526176 | 526.176 | 65.34 | 14.66 | 554148 | 554.148 | 64.6 | 15.4 | 582120 | 582.12 | 65
10/20/20XX 3:00:00 PM | 0.625 | 4 | 64.1 | 45.8 | 64.1 |  | 64.1 | 71.21 | 8.79 | 332262 | 332.262 | 70.42 | 9.58 | 362124 | 362.124 | 69.63 | 10.37 | 391986 | 391.986 | 68.84 | 11.16 | 421848 | 421.848 | 68.05 | 11.95 | 451710 | 451.71 | 67.26 | 12.74 | 481572 | 481.572 | 66.47 | 13.53 | 511434 | 511.434 | 65.68 | 14.32 | 541296 | 541.296 | 64.89 | 15.11 | 571158 | 571.158 | 64.1 | 15.9 | 601020 | 601.02 | 65
10/20/20XX 4:00:00 PM | 0.66667 | 4 | 63.6 | 47.2 | 63.6 |  | 63.6 | 71.16 | 8.84 | 334152 | 334.152 | 70.32 | 9.68 | 365904 | 365.904 | 69.48 | 10.52 | 397656 | 397.656 | 68.64 | 11.36 | 429408 | 429.408 | 67.8 | 12.2 | 461160 | 461.16 | 66.96 | 13.04 | 492912 | 492.912 | 66.12 | 13.88 | 524664 | 524.664 | 65.28 | 14.72 | 556416 | 556.416 | 64.44 | 15.56 | 588168 | 588.168 | 63.6 | 16.4 | 619920 | 619.92 | 65
10/20/20XX 5:00:00 PM | 0.70833 | 4 | 62.6 | 48.5 | 62.6 |  | 62.6 | 71.06 | 8.94 | 337932 | 337.932 | 70.12 | 9.88 | 373464 | 373.464 | 69.18 | 10.82 | 408996 | 408.996 | 68.24 | 11.76 | 444528 | 444.528 | 67.3 | 12.7 | 480060 | 480.06 | 66.36 | 13.64 | 515592 | 515.592 | 65.42 | 14.58 | 551124 | 551.124 | 64.48 | 15.52 | 586656 | 586.656 | 63.54 | 16.46 | 622188 | 622.188 | 62.6 | 17.4 | 657720 | 657.72 | 65
10/20/20XX 6:00:00 PM | 0.75 | 4 | 61.2 | 50 | 61.2 |  | 61.2 | 70.92 | 9.08 | 343224 | 343.224 | 69.84 | 10.16 | 384048 | 384.048 | 68.76 | 11.24 | 424872 | 424.872 | 67.68 | 12.32 | 465696 | 465.696 | 66.6 | 13.4 | 506520 | 506.52 | 65.52 | 14.48 | 547344 | 547.344 | 64.44 | 15.56 | 588168 | 588.168 | 63.36 | 16.64 | 628992 | 628.992 | 62.28 | 17.72 | 669816 | 669.816 | 61.2 | 18.8 | 710640 | 710.64 | 60
10/20/20XX 7:00:00 PM | 0.79167 | 4 | 60.4 | 51.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/20/20XX 8:00:00 PM | 0.83333 | 4 | 59.5 | 55 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/20/20XX 9:00:00 PM | 0.875 | 4 | 58.6 | 58 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/20/20XX 10:00:00 PM | 0.91667 | 4 | 58.3 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/20/20XX 11:00:00 PM | 0.95833 | 4 | 57.9 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/20/20XX 12:00:00 AM | 0 | 5 | 57.2 | 61.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/21/20XX 1:00:00 AM | 0.041667 | 5 | 56.6 | 63.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/21/20XX 2:00:00 AM | 0.083333 | 5 | 55.8 | 65.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/21/20XX 3:00:00 AM | 0.125 | 5 | 55.5 | 65.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/21/20XX 4:00:00 AM | 0.16667 | 5 | 54.6 | 67.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/21/20XX 5:00:00 AM | 0.20833 | 5 | 54.4 | 66 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/21/20XX 6:00:00 AM | 0.25 | 5 | 54 | 68.5 | 54 |  | 54 | 70.2 | 9.8 | 370440 | 370.44 | 68.4 | 11.6 | 438480 | 438.48 | 66.6 | 13.4 | 506520 | 506.52 | 64.8 | 15.2 | 574560 | 574.56 | 63 | 17 | 642600 | 642.6 | 61.2 | 18.8 | 710640 | 710.64 | 59.4 | 20.6 | 778680 | 778.68 | 57.6 | 22.4 | 846720 | 846.72 | 55.8 | 24.2 | 914760 | 914.76 | 54 | 26 | 982800 | 982.8 | 55
10/21/20XX 7:00:00 AM | 0.29167 | 5 | 54.6 | 66.4 | 54.6 |  | 54.6 | 70.26 | 9.74 | 368172 | 368.172 | 68.52 | 11.48 | 433944 | 433.944 | 66.78 | 13.22 | 499716 | 499.716 | 65.04 | 14.96 | 565488 | 565.488 | 63.3 | 16.7 | 631260 | 631.26 | 61.56 | 18.44 | 697032 | 697.032 | 59.82 | 20.18 | 762804 | 762.804 | 58.08 | 21.92 | 828576 | 828.576 | 56.34 | 23.66 | 894348 | 894.348 | 54.6 | 25.4 | 960120 | 960.12 | 55
10/21/20XX 8:00:00 AM | 0.33333 | 5 | 55.7 | 63.7 | 55.7 |  | 55.7 | 70.37 | 9.63 | 364014 | 364.014 | 68.74 | 11.26 | 425628 | 425.628 | 67.11 | 12.89 | 487242 | 487.242 | 65.48 | 14.52 | 548856 | 548.856 | 63.85 | 16.15 | 610470 | 610.47 | 62.22 | 17.78 | 672084 | 672.084 | 60.59 | 19.41 | 733698 | 733.698 | 58.96 | 21.04 | 795312 | 795.312 | 57.33 | 22.67 | 856926 | 856.926 | 55.7 | 24.3 | 918540 | 918.54 | 55
10/21/20XX 9:00:00 AM | 0.375 | 5 | 57.6 | 59.7 | 57.6 |  | 57.6 | 70.56 | 9.44 | 356832 | 356.832 | 69.12 | 10.88 | 411264 | 411.264 | 67.68 | 12.32 | 465696 | 465.696 | 66.24 | 13.76 | 520128 | 520.128 | 64.8 | 15.2 | 574560 | 574.56 | 63.36 | 16.64 | 628992 | 628.992 | 61.92 | 18.08 | 683424 | 683.424 | 60.48 | 19.52 | 737856 | 737.856 | 59.04 | 20.96 | 792288 | 792.288 | 57.6 | 22.4 | 846720 | 846.72 | 60
10/21/20XX 10:00:00 AM | 0.41667 | 5 | 59.4 | 56.9 | 59.4 |  | 59.4 | 70.74 | 9.26 | 350028 | 350.028 | 69.48 | 10.52 | 397656 | 397.656 | 68.22 | 11.78 | 445284 | 445.284 | 66.96 | 13.04 | 492912 | 492.912 | 65.7 | 14.3 | 540540 | 540.54 | 64.44 | 15.56 | 588168 | 588.168 | 63.18 | 16.82 | 635796 | 635.796 | 61.92 | 18.08 | 683424 | 683.424 | 60.66 | 19.34 | 731052 | 731.052 | 59.4 | 20.6 | 778680 | 778.68 | 60
10/21/20XX 11:00:00 AM | 0.45833 | 5 | 61.4 | 54.1 | 61.4 |  | 61.4 | 70.94 | 9.06 | 342468 | 342.468 | 69.88 | 10.12 | 382536 | 382.536 | 68.82 | 11.18 | 422604 | 422.604 | 67.76 | 12.24 | 462672 | 462.672 | 66.7 | 13.3 | 502740 | 502.74 | 65.64 | 14.36 | 542808 | 542.808 | 64.58 | 15.42 | 582876 | 582.876 | 63.52 | 16.48 | 622944 | 622.944 | 62.46 | 17.54 | 663012 | 663.012 | 61.4 | 18.6 | 703080 | 703.08 | 60
10/21/20XX 12:00:00 PM | 0.5 | 5 | 63.1 | 50.7 | 63.1 |  | 63.1 | 71.11 | 8.89 | 336042 | 336.042 | 70.22 | 9.78 | 369684 | 369.684 | 69.33 | 10.67 | 403326 | 403.326 | 68.44 | 11.56 | 436968 | 436.968 | 67.55 | 12.45 | 470610 | 470.61 | 66.66 | 13.34 | 504252 | 504.252 | 65.77 | 14.23 | 537894 | 537.894 | 64.88 | 15.12 | 571536 | 571.536 | 63.99 | 16.01 | 605178 | 605.178 | 63.1 | 16.9 | 638820 | 638.82 | 65
10/21/20XX 1:00:00 PM | 0.54167 | 5 | 64.5 | 46.4 | 64.5 |  | 64.5 | 71.25 | 8.75 | 330750 | 330.75 | 70.5 | 9.5 | 359100 | 359.1 | 69.75 | 10.25 | 387450 | 387.45 | 69 | 11 | 415800 | 415.8 | 68.25 | 11.75 | 444150 | 444.15 | 67.5 | 12.5 | 472500 | 472.5 | 66.75 | 13.25 | 500850 | 500.85 | 66 | 14 | 529200 | 529.2 | 65.25 | 14.75 | 557550 | 557.55 | 64.5 | 15.5 | 585900 | 585.9 | 65
10/21/20XX 2:00:00 PM | 0.58333 | 5 | 64.5 | 46.8 | 64.5 |  | 64.5 | 71.25 | 8.75 | 330750 | 330.75 | 70.5 | 9.5 | 359100 | 359.1 | 69.75 | 10.25 | 387450 | 387.45 | 69 | 11 | 415800 | 415.8 | 68.25 | 11.75 | 444150 | 444.15 | 67.5 | 12.5 | 472500 | 472.5 | 66.75 | 13.25 | 500850 | 500.85 | 66 | 14 | 529200 | 529.2 | 65.25 | 14.75 | 557550 | 557.55 | 64.5 | 15.5 | 585900 | 585.9 | 65
10/21/20XX 3:00:00 PM | 0.625 | 5 | 63.9 | 46.5 | 63.9 |  | 63.9 | 71.19 | 8.81 | 333018 | 333.018 | 70.38 | 9.62 | 363636 | 363.636 | 69.57 | 10.43 | 394254 | 394.254 | 68.76 | 11.24 | 424872 | 424.872 | 67.95 | 12.05 | 455490 | 455.49 | 67.14 | 12.86 | 486108 | 486.108 | 66.33 | 13.67 | 516726 | 516.726 | 65.52 | 14.48 | 547344 | 547.344 | 64.71 | 15.29 | 577962 | 577.962 | 63.9 | 16.1 | 608580 | 608.58 | 65
10/21/20XX 4:00:00 PM | 0.66667 | 5 | 62.6 | 50.3 | 62.6 |  | 62.6 | 71.06 | 8.94 | 337932 | 337.932 | 70.12 | 9.88 | 373464 | 373.464 | 69.18 | 10.82 | 408996 | 408.996 | 68.24 | 11.76 | 444528 | 444.528 | 67.3 | 12.7 | 480060 | 480.06 | 66.36 | 13.64 | 515592 | 515.592 | 65.42 | 14.58 | 551124 | 551.124 | 64.48 | 15.52 | 586656 | 586.656 | 63.54 | 16.46 | 622188 | 622.188 | 62.6 | 17.4 | 657720 | 657.72 | 65
10/21/20XX 5:00:00 PM | 0.70833 | 5 | 60.8 | 52 | 60.8 |  | 60.8 | 70.88 | 9.12 | 344736 | 344.736 | 69.76 | 10.24 | 387072 | 387.072 | 68.64 | 11.36 | 429408 | 429.408 | 67.52 | 12.48 | 471744 | 471.744 | 66.4 | 13.6 | 514080 | 514.08 | 65.28 | 14.72 | 556416 | 556.416 | 64.16 | 15.84 | 598752 | 598.752 | 63.04 | 16.96 | 641088 | 641.088 | 61.92 | 18.08 | 683424 | 683.424 | 60.8 | 19.2 | 725760 | 725.76 | 60
10/21/20XX 6:00:00 PM | 0.75 | 5 | 59.6 | 54.4 | 59.6 |  | 59.6 | 70.76 | 9.24 | 349272 | 349.272 | 69.52 | 10.48 | 396144 | 396.144 | 68.28 | 11.72 | 443016 | 443.016 | 67.04 | 12.96 | 489888 | 489.888 | 65.8 | 14.2 | 536760 | 536.76 | 64.56 | 15.44 | 583632 | 583.632 | 63.32 | 16.68 | 630504 | 630.504 | 62.08 | 17.92 | 677376 | 677.376 | 60.84 | 19.16 | 724248 | 724.248 | 59.6 | 20.4 | 771120 | 771.12 | 60
10/21/20XX 7:00:00 PM | 0.79167 | 5 | 58.7 | 57.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/21/20XX 8:00:00 PM | 0.83333 | 5 | 57.9 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/21/20XX 9:00:00 PM | 0.875 | 5 | 57.5 | 62.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/21/20XX 10:00:00 PM | 0.91667 | 5 | 57 | 63.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/21/20XX 11:00:00 PM | 0.95833 | 5 | 56 | 65.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/21/20XX 12:00:00 AM | 0 | 6 | 54.9 | 67.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/22/20XX 1:00:00 AM | 0.041667 | 6 | 54.9 | 66.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/22/20XX 2:00:00 AM | 0.083333 | 6 | 54.1 | 67.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/22/20XX 3:00:00 AM | 0.125 | 6 | 53.5 | 68.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/22/20XX 4:00:00 AM | 0.16667 | 6 | 52.7 | 71.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/22/20XX 5:00:00 AM | 0.20833 | 6 | 52.2 | 72 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/22/20XX 6:00:00 AM | 0.25 | 6 | 51.8 | 72.9 | 51.8 |  | 51.8 | 69.98 | 10.02 | 378756 | 378.756 | 67.96 | 12.04 | 455112 | 455.112 | 65.94 | 14.06 | 531468 | 531.468 | 63.92 | 16.08 | 607824 | 607.824 | 61.9 | 18.1 | 684180 | 684.18 | 59.88 | 20.12 | 760536 | 760.536 | 57.86 | 22.14 | 836892 | 836.892 | 55.84 | 24.16 | 913248 | 913.248 | 53.82 | 26.18 | 989604 | 989.604 | 51.8 | 28.2 | 1065960 | 1065.96 | 50
10/22/20XX 7:00:00 AM | 0.29167 | 6 | 52 | 72.5 | 52 |  | 52 | 70 | 10 | 378000 | 378 | 68 | 12 | 453600 | 453.6 | 66 | 14 | 529200 | 529.2 | 64 | 16 | 604800 | 604.8 | 62 | 18 | 680400 | 680.4 | 60 | 20 | 756000 | 756 | 58 | 22 | 831600 | 831.6 | 56 | 24 | 907200 | 907.2 | 54 | 26 | 982800 | 982.8 | 52 | 28 | 1058400 | 1058.4 | 50
10/22/20XX 8:00:00 AM | 0.33333 | 6 | 53.1 | 69.8 | 53.1 |  | 53.1 | 70.11 | 9.89 | 373842 | 373.842 | 68.22 | 11.78 | 445284 | 445.284 | 66.33 | 13.67 | 516726 | 516.726 | 64.44 | 15.56 | 588168 | 588.168 | 62.55 | 17.45 | 659610 | 659.61 | 60.66 | 19.34 | 731052 | 731.052 | 58.77 | 21.23 | 802494 | 802.494 | 56.88 | 23.12 | 873936 | 873.936 | 54.99 | 25.01 | 945378 | 945.378 | 53.1 | 26.9 | 1016820 | 1016.82 | 55
10/22/20XX 9:00:00 AM | 0.375 | 6 | 54.7 | 64.8 | 54.7 |  | 54.7 | 70.27 | 9.73 | 367794 | 367.794 | 68.54 | 11.46 | 433188 | 433.188 | 66.81 | 13.19 | 498582 | 498.582 | 65.08 | 14.92 | 563976 | 563.976 | 63.35 | 16.65 | 629370 | 629.37 | 61.62 | 18.38 | 694764 | 694.764 | 59.89 | 20.11 | 760158 | 760.158 | 58.16 | 21.84 | 825552 | 825.552 | 56.43 | 23.57 | 890946 | 890.946 | 54.7 | 25.3 | 956340 | 956.34 | 55
10/22/20XX 10:00:00 AM | 0.41667 | 6 | 56.9 | 60.6 | 56.9 |  | 56.9 | 70.49 | 9.51 | 359478 | 359.478 | 68.98 | 11.02 | 416556 | 416.556 | 67.47 | 12.53 | 473634 | 473.634 | 65.96 | 14.04 | 530712 | 530.712 | 64.45 | 15.55 | 587790 | 587.79 | 62.94 | 17.06 | 644868 | 644.868 | 61.43 | 18.57 | 701946 | 701.946 | 59.92 | 20.08 | 759024 | 759.024 | 58.41 | 21.59 | 816102 | 816.102 | 56.9 | 23.1 | 873180 | 873.18 | 55
10/22/20XX 11:00:00 AM | 0.45833 | 6 | 58.8 | 55.5 | 58.8 |  | 58.8 | 70.68 | 9.32 | 352296 | 352.296 | 69.36 | 10.64 | 402192 | 402.192 | 68.04 | 11.96 | 452088 | 452.088 | 66.72 | 13.28 | 501984 | 501.984 | 65.4 | 14.6 | 551880 | 551.88 | 64.08 | 15.92 | 601776 | 601.776 | 62.76 | 17.24 | 651672 | 651.672 | 61.44 | 18.56 | 701568 | 701.568 | 60.12 | 19.88 | 751464 | 751.464 | 58.8 | 21.2 | 801360 | 801.36 | 60
10/22/20XX 12:00:00 PM | 0.5 | 6 | 60.5 | 52.2 | 60.5 |  | 60.5 | 70.85 | 9.15 | 345870 | 345.87 | 69.7 | 10.3 | 389340 | 389.34 | 68.55 | 11.45 | 432810 | 432.81 | 67.4 | 12.6 | 476280 | 476.28 | 66.25 | 13.75 | 519750 | 519.75 | 65.1 | 14.9 | 563220 | 563.22 | 63.95 | 16.05 | 606690 | 606.69 | 62.8 | 17.2 | 650160 | 650.16 | 61.65 | 18.35 | 693630 | 693.63 | 60.5 | 19.5 | 737100 | 737.1 | 60
10/22/20XX 1:00:00 PM | 0.54167 | 6 | 61.7 | 49.8 | 61.7 |  | 61.7 | 70.97 | 9.03 | 341334 | 341.334 | 69.94 | 10.06 | 380268 | 380.268 | 68.91 | 11.09 | 419202 | 419.202 | 67.88 | 12.12 | 458136 | 458.136 | 66.85 | 13.15 | 497070 | 497.07 | 65.82 | 14.18 | 536004 | 536.004 | 64.79 | 15.21 | 574938 | 574.938 | 63.76 | 16.24 | 613872 | 613.872 | 62.73 | 17.27 | 652806 | 652.806 | 61.7 | 18.3 | 691740 | 691.74 | 60
10/22/20XX 2:00:00 PM | 0.58333 | 6 | 61.5 | 48.7 | 61.5 |  | 61.5 | 70.95 | 9.05 | 342090 | 342.09 | 69.9 | 10.1 | 381780 | 381.78 | 68.85 | 11.15 | 421470 | 421.47 | 67.8 | 12.2 | 461160 | 461.16 | 66.75 | 13.25 | 500850 | 500.85 | 65.7 | 14.3 | 540540 | 540.54 | 64.65 | 15.35 | 580230 | 580.23 | 63.6 | 16.4 | 619920 | 619.92 | 62.55 | 17.45 | 659610 | 659.61 | 61.5 | 18.5 | 699300 | 699.3 | 60
10/22/20XX 3:00:00 PM | 0.625 | 6 | 60.9 | 48.7 | 60.9 |  | 60.9 | 70.89 | 9.11 | 344358 | 344.358 | 69.78 | 10.22 | 386316 | 386.316 | 68.67 | 11.33 | 428274 | 428.274 | 67.56 | 12.44 | 470232 | 470.232 | 66.45 | 13.55 | 512190 | 512.19 | 65.34 | 14.66 | 554148 | 554.148 | 64.23 | 15.77 | 596106 | 596.106 | 63.12 | 16.88 | 638064 | 638.064 | 62.01 | 17.99 | 680022 | 680.022 | 60.9 | 19.1 | 721980 | 721.98 | 60
10/22/20XX 4:00:00 PM | 0.66667 | 6 | 59.9 | 52.4 | 59.9 |  | 59.9 | 70.79 | 9.21 | 348138 | 348.138 | 69.58 | 10.42 | 393876 | 393.876 | 68.37 | 11.63 | 439614 | 439.614 | 67.16 | 12.84 | 485352 | 485.352 | 65.95 | 14.05 | 531090 | 531.09 | 64.74 | 15.26 | 576828 | 576.828 | 63.53 | 16.47 | 622566 | 622.566 | 62.32 | 17.68 | 668304 | 668.304 | 61.11 | 18.89 | 714042 | 714.042 | 59.9 | 20.1 | 759780 | 759.78 | 60
10/22/20XX 5:00:00 PM | 0.70833 | 6 | 58.6 | 54.8 | 58.6 |  | 58.6 | 70.66 | 9.34 | 353052 | 353.052 | 69.32 | 10.68 | 403704 | 403.704 | 67.98 | 12.02 | 454356 | 454.356 | 66.64 | 13.36 | 505008 | 505.008 | 65.3 | 14.7 | 555660 | 555.66 | 63.96 | 16.04 | 606312 | 606.312 | 62.62 | 17.38 | 656964 | 656.964 | 61.28 | 18.72 | 707616 | 707.616 | 59.94 | 20.06 | 758268 | 758.268 | 58.6 | 21.4 | 808920 | 808.92 | 60
10/22/20XX 6:00:00 PM | 0.75 | 6 | 57.9 | 55.1 | 57.9 |  | 57.9 | 70.59 | 9.41 | 355698 | 355.698 | 69.18 | 10.82 | 408996 | 408.996 | 67.77 | 12.23 | 462294 | 462.294 | 66.36 | 13.64 | 515592 | 515.592 | 64.95 | 15.05 | 568890 | 568.89 | 63.54 | 16.46 | 622188 | 622.188 | 62.13 | 17.87 | 675486 | 675.486 | 60.72 | 19.28 | 728784 | 728.784 | 59.31 | 20.69 | 782082 | 782.082 | 57.9 | 22.1 | 835380 | 835.38 | 60
10/22/20XX 7:00:00 PM | 0.79167 | 6 | 57.4 | 56.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/22/20XX 8:00:00 PM | 0.83333 | 6 | 57 | 55.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/22/20XX 9:00:00 PM | 0.875 | 6 | 56.4 | 55.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/22/20XX 10:00:00 PM | 0.91667 | 6 | 55.6 | 58.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/22/20XX 11:00:00 PM | 0.95833 | 6 | 55.1 | 60.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/22/20XX 12:00:00 AM | 0 | 7 | 54.5 | 62.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/23/20XX 1:00:00 AM | 0.041667 | 7 | 54.5 | 61.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/23/20XX 2:00:00 AM | 0.083333 | 7 | 53.9 | 61.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/23/20XX 3:00:00 AM | 0.125 | 7 | 53.4 | 64.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/23/20XX 4:00:00 AM | 0.16667 | 7 | 52.8 | 67.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/23/20XX 5:00:00 AM | 0.20833 | 7 | 53 | 66.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/23/20XX 6:00:00 AM | 0.25 | 7 | 52.2 | 67.9 | 52.2 |  | 52.2 | 70.02 | 9.98 | 377244 | 377.244 | 68.04 | 11.96 | 452088 | 452.088 | 66.06 | 13.94 | 526932 | 526.932 | 64.08 | 15.92 | 601776 | 601.776 | 62.1 | 17.9 | 676620 | 676.62 | 60.12 | 19.88 | 751464 | 751.464 | 58.14 | 21.86 | 826308 | 826.308 | 56.16 | 23.84 | 901152 | 901.152 | 54.18 | 25.82 | 975996 | 975.996 | 52.2 | 27.8 | 1050840 | 1050.84 | 50
10/23/20XX 7:00:00 AM | 0.29167 | 7 | 52.2 | 69.1 | 52.2 |  | 52.2 | 70.02 | 9.98 | 377244 | 377.244 | 68.04 | 11.96 | 452088 | 452.088 | 66.06 | 13.94 | 526932 | 526.932 | 64.08 | 15.92 | 601776 | 601.776 | 62.1 | 17.9 | 676620 | 676.62 | 60.12 | 19.88 | 751464 | 751.464 | 58.14 | 21.86 | 826308 | 826.308 | 56.16 | 23.84 | 901152 | 901.152 | 54.18 | 25.82 | 975996 | 975.996 | 52.2 | 27.8 | 1050840 | 1050.84 | 50
10/23/20XX 8:00:00 AM | 0.33333 | 7 | 53.3 | 67.2 | 53.3 |  | 53.3 | 70.13 | 9.87 | 373086 | 373.086 | 68.26 | 11.74 | 443772 | 443.772 | 66.39 | 13.61 | 514458 | 514.458 | 64.52 | 15.48 | 585144 | 585.144 | 62.65 | 17.35 | 655830 | 655.83 | 60.78 | 19.22 | 726516 | 726.516 | 58.91 | 21.09 | 797202 | 797.202 | 57.04 | 22.96 | 867888 | 867.888 | 55.17 | 24.83 | 938574 | 938.574 | 53.3 | 26.7 | 1009260 | 1009.26 | 55
10/23/20XX 9:00:00 AM | 0.375 | 7 | 55.2 | 61.3 | 55.2 |  | 55.2 | 70.32 | 9.68 | 365904 | 365.904 | 68.64 | 11.36 | 429408 | 429.408 | 66.96 | 13.04 | 492912 | 492.912 | 65.28 | 14.72 | 556416 | 556.416 | 63.6 | 16.4 | 619920 | 619.92 | 61.92 | 18.08 | 683424 | 683.424 | 60.24 | 19.76 | 746928 | 746.928 | 58.56 | 21.44 | 810432 | 810.432 | 56.88 | 23.12 | 873936 | 873.936 | 55.2 | 24.8 | 937440 | 937.44 | 55
10/23/20XX 10:00:00 AM | 0.41667 | 7 | 56.1 | 58.5 | 56.1 |  | 56.1 | 70.41 | 9.59 | 362502 | 362.502 | 68.82 | 11.18 | 422604 | 422.604 | 67.23 | 12.77 | 482706 | 482.706 | 65.64 | 14.36 | 542808 | 542.808 | 64.05 | 15.95 | 602910 | 602.91 | 62.46 | 17.54 | 663012 | 663.012 | 60.87 | 19.13 | 723114 | 723.114 | 59.28 | 20.72 | 783216 | 783.216 | 57.69 | 22.31 | 843318 | 843.318 | 56.1 | 23.9 | 903420 | 903.42 | 55
10/23/20XX 11:00:00 AM | 0.45833 | 7 | 57.2 | 58.1 | 57.2 |  | 57.2 | 70.52 | 9.48 | 358344 | 358.344 | 69.04 | 10.96 | 414288 | 414.288 | 67.56 | 12.44 | 470232 | 470.232 | 66.08 | 13.92 | 526176 | 526.176 | 64.6 | 15.4 | 582120 | 582.12 | 63.12 | 16.88 | 638064 | 638.064 | 61.64 | 18.36 | 694008 | 694.008 | 60.16 | 19.84 | 749952 | 749.952 | 58.68 | 21.32 | 805896 | 805.896 | 57.2 | 22.8 | 861840 | 861.84 | 55
10/23/20XX 12:00:00 PM | 0.5 | 7 | 58.6 | 55.1 | 58.6 |  | 58.6 | 70.66 | 9.34 | 353052 | 353.052 | 69.32 | 10.68 | 403704 | 403.704 | 67.98 | 12.02 | 454356 | 454.356 | 66.64 | 13.36 | 505008 | 505.008 | 65.3 | 14.7 | 555660 | 555.66 | 63.96 | 16.04 | 606312 | 606.312 | 62.62 | 17.38 | 656964 | 656.964 | 61.28 | 18.72 | 707616 | 707.616 | 59.94 | 20.06 | 758268 | 758.268 | 58.6 | 21.4 | 808920 | 808.92 | 60
10/23/20XX 1:00:00 PM | 0.54167 | 7 | 59.2 | 55.4 | 59.2 |  | 59.2 | 70.72 | 9.28 | 350784 | 350.784 | 69.44 | 10.56 | 399168 | 399.168 | 68.16 | 11.84 | 447552 | 447.552 | 66.88 | 13.12 | 495936 | 495.936 | 65.6 | 14.4 | 544320 | 544.32 | 64.32 | 15.68 | 592704 | 592.704 | 63.04 | 16.96 | 641088 | 641.088 | 61.76 | 18.24 | 689472 | 689.472 | 60.48 | 19.52 | 737856 | 737.856 | 59.2 | 20.8 | 786240 | 786.24 | 60
10/23/20XX 2:00:00 PM | 0.58333 | 7 | 59.1 | 55.1 | 59.1 |  | 59.1 | 70.71 | 9.29 | 351162 | 351.162 | 69.42 | 10.58 | 399924 | 399.924 | 68.13 | 11.87 | 448686 | 448.686 | 66.84 | 13.16 | 497448 | 497.448 | 65.55 | 14.45 | 546210 | 546.21 | 64.26 | 15.74 | 594972 | 594.972 | 62.97 | 17.03 | 643734 | 643.734 | 61.68 | 18.32 | 692496 | 692.496 | 60.39 | 19.61 | 741258 | 741.258 | 59.1 | 20.9 | 790020 | 790.02 | 60
10/23/20XX 3:00:00 PM | 0.625 | 7 | 58.9 | 54.2 | 58.9 |  | 58.9 | 70.69 | 9.31 | 351918 | 351.918 | 69.38 | 10.62 | 401436 | 401.436 | 68.07 | 11.93 | 450954 | 450.954 | 66.76 | 13.24 | 500472 | 500.472 | 65.45 | 14.55 | 549990 | 549.99 | 64.14 | 15.86 | 599508 | 599.508 | 62.83 | 17.17 | 649026 | 649.026 | 61.52 | 18.48 | 698544 | 698.544 | 60.21 | 19.79 | 748062 | 748.062 | 58.9 | 21.1 | 797580 | 797.58 | 60
10/23/20XX 4:00:00 PM | 0.66667 | 7 | 58.8 | 54.3 | 58.8 |  | 58.8 | 70.68 | 9.32 | 352296 | 352.296 | 69.36 | 10.64 | 402192 | 402.192 | 68.04 | 11.96 | 452088 | 452.088 | 66.72 | 13.28 | 501984 | 501.984 | 65.4 | 14.6 | 551880 | 551.88 | 64.08 | 15.92 | 601776 | 601.776 | 62.76 | 17.24 | 651672 | 651.672 | 61.44 | 18.56 | 701568 | 701.568 | 60.12 | 19.88 | 751464 | 751.464 | 58.8 | 21.2 | 801360 | 801.36 | 60
10/23/20XX 5:00:00 PM | 0.70833 | 7 | 57.9 | 56.2 | 57.9 |  | 57.9 | 70.59 | 9.41 | 355698 | 355.698 | 69.18 | 10.82 | 408996 | 408.996 | 67.77 | 12.23 | 462294 | 462.294 | 66.36 | 13.64 | 515592 | 515.592 | 64.95 | 15.05 | 568890 | 568.89 | 63.54 | 16.46 | 622188 | 622.188 | 62.13 | 17.87 | 675486 | 675.486 | 60.72 | 19.28 | 728784 | 728.784 | 59.31 | 20.69 | 782082 | 782.082 | 57.9 | 22.1 | 835380 | 835.38 | 60
10/23/20XX 6:00:00 PM | 0.75 | 7 | 56.9 | 58.8 | 56.9 |  | 56.9 | 70.49 | 9.51 | 359478 | 359.478 | 68.98 | 11.02 | 416556 | 416.556 | 67.47 | 12.53 | 473634 | 473.634 | 65.96 | 14.04 | 530712 | 530.712 | 64.45 | 15.55 | 587790 | 587.79 | 62.94 | 17.06 | 644868 | 644.868 | 61.43 | 18.57 | 701946 | 701.946 | 59.92 | 20.08 | 759024 | 759.024 | 58.41 | 21.59 | 816102 | 816.102 | 56.9 | 23.1 | 873180 | 873.18 | 55
10/23/20XX 7:00:00 PM | 0.79167 | 7 | 56.2 | 62.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/23/20XX 8:00:00 PM | 0.83333 | 7 | 55.6 | 64.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/23/20XX 9:00:00 PM | 0.875 | 7 | 54.9 | 67.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/23/20XX 10:00:00 PM | 0.91667 | 7 | 54.6 | 68.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/23/20XX 11:00:00 PM | 0.95833 | 7 | 54.3 | 69.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/23/20XX 12:00:00 AM | 0 | 1 | 53.7 | 72.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/24/20XX 1:00:00 AM | 0.041667 | 1 | 53.7 | 74 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/24/20XX 2:00:00 AM | 0.083333 | 1 | 53.1 | 74.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/24/20XX 3:00:00 AM | 0.125 | 1 | 52.7 | 75 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/24/20XX 4:00:00 AM | 0.16667 | 1 | 52.6 | 77.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/24/20XX 5:00:00 AM | 0.20833 | 1 | 52.7 | 77.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/24/20XX 6:00:00 AM | 0.25 | 1 | 52.4 | 78.2 | 52.4 |  | 52.4 | 70.04 | 9.96 | 376488 | 376.488 | 68.08 | 11.92 | 450576 | 450.576 | 66.12 | 13.88 | 524664 | 524.664 | 64.16 | 15.84 | 598752 | 598.752 | 62.2 | 17.8 | 672840 | 672.84 | 60.24 | 19.76 | 746928 | 746.928 | 58.28 | 21.72 | 821016 | 821.016 | 56.32 | 23.68 | 895104 | 895.104 | 54.36 | 25.64 | 969192 | 969.192 | 52.4 | 27.6 | 1043280 | 1043.28 | 50
10/24/20XX 7:00:00 AM | 0.29167 | 1 | 52.4 | 79 | 52.4 |  | 52.4 | 70.04 | 9.96 | 376488 | 376.488 | 68.08 | 11.92 | 450576 | 450.576 | 66.12 | 13.88 | 524664 | 524.664 | 64.16 | 15.84 | 598752 | 598.752 | 62.2 | 17.8 | 672840 | 672.84 | 60.24 | 19.76 | 746928 | 746.928 | 58.28 | 21.72 | 821016 | 821.016 | 56.32 | 23.68 | 895104 | 895.104 | 54.36 | 25.64 | 969192 | 969.192 | 52.4 | 27.6 | 1043280 | 1043.28 | 50
10/24/20XX 8:00:00 AM | 0.33333 | 1 | 53.8 | 75.6 | 53.8 |  | 53.8 | 70.18 | 9.82 | 371196 | 371.196 | 68.36 | 11.64 | 439992 | 439.992 | 66.54 | 13.46 | 508788 | 508.788 | 64.72 | 15.28 | 577584 | 577.584 | 62.9 | 17.1 | 646380 | 646.38 | 61.08 | 18.92 | 715176 | 715.176 | 59.26 | 20.74 | 783972 | 783.972 | 57.44 | 22.56 | 852768 | 852.768 | 55.62 | 24.38 | 921564 | 921.564 | 53.8 | 26.2 | 990360 | 990.36 | 55
10/24/20XX 9:00:00 AM | 0.375 | 1 | 55.5 | 72.6 | 55.5 |  | 55.5 | 70.35 | 9.65 | 364770 | 364.77 | 68.7 | 11.3 | 427140 | 427.14 | 67.05 | 12.95 | 489510 | 489.51 | 65.4 | 14.6 | 551880 | 551.88 | 63.75 | 16.25 | 614250 | 614.25 | 62.1 | 17.9 | 676620 | 676.62 | 60.45 | 19.55 | 738990 | 738.99 | 58.8 | 21.2 | 801360 | 801.36 | 57.15 | 22.85 | 863730 | 863.73 | 55.5 | 24.5 | 926100 | 926.1 | 55
10/24/20XX 10:00:00 AM | 0.41667 | 1 | 57.7 | 66.8 | 57.7 |  | 57.7 | 70.57 | 9.43 | 356454 | 356.454 | 69.14 | 10.86 | 410508 | 410.508 | 67.71 | 12.29 | 464562 | 464.562 | 66.28 | 13.72 | 518616 | 518.616 | 64.85 | 15.15 | 572670 | 572.67 | 63.42 | 16.58 | 626724 | 626.724 | 61.99 | 18.01 | 680778 | 680.778 | 60.56 | 19.44 | 734832 | 734.832 | 59.13 | 20.87 | 788886 | 788.886 | 57.7 | 22.3 | 842940 | 842.94 | 60
10/24/20XX 11:00:00 AM | 0.45833 | 1 | 59.1 | 62.8 | 59.1 |  | 59.1 | 70.71 | 9.29 | 351162 | 351.162 | 69.42 | 10.58 | 399924 | 399.924 | 68.13 | 11.87 | 448686 | 448.686 | 66.84 | 13.16 | 497448 | 497.448 | 65.55 | 14.45 | 546210 | 546.21 | 64.26 | 15.74 | 594972 | 594.972 | 62.97 | 17.03 | 643734 | 643.734 | 61.68 | 18.32 | 692496 | 692.496 | 60.39 | 19.61 | 741258 | 741.258 | 59.1 | 20.9 | 790020 | 790.02 | 60
10/24/20XX 12:00:00 PM | 0.5 | 1 | 59.8 | 62.6 | 59.8 |  | 59.8 | 70.78 | 9.22 | 348516 | 348.516 | 69.56 | 10.44 | 394632 | 394.632 | 68.34 | 11.66 | 440748 | 440.748 | 67.12 | 12.88 | 486864 | 486.864 | 65.9 | 14.1 | 532980 | 532.98 | 64.68 | 15.32 | 579096 | 579.096 | 63.46 | 16.54 | 625212 | 625.212 | 62.24 | 17.76 | 671328 | 671.328 | 61.02 | 18.98 | 717444 | 717.444 | 59.8 | 20.2 | 763560 | 763.56 | 60
10/24/20XX 1:00:00 PM | 0.54167 | 1 | 59.6 | 61.9 | 59.6 |  | 59.6 | 70.76 | 9.24 | 349272 | 349.272 | 69.52 | 10.48 | 396144 | 396.144 | 68.28 | 11.72 | 443016 | 443.016 | 67.04 | 12.96 | 489888 | 489.888 | 65.8 | 14.2 | 536760 | 536.76 | 64.56 | 15.44 | 583632 | 583.632 | 63.32 | 16.68 | 630504 | 630.504 | 62.08 | 17.92 | 677376 | 677.376 | 60.84 | 19.16 | 724248 | 724.248 | 59.6 | 20.4 | 771120 | 771.12 | 60
10/24/20XX 2:00:00 PM | 0.58333 | 1 | 60.1 | 61.8 | 60.1 |  | 60.1 | 70.81 | 9.19 | 347382 | 347.382 | 69.62 | 10.38 | 392364 | 392.364 | 68.43 | 11.57 | 437346 | 437.346 | 67.24 | 12.76 | 482328 | 482.328 | 66.05 | 13.95 | 527310 | 527.31 | 64.86 | 15.14 | 572292 | 572.292 | 63.67 | 16.33 | 617274 | 617.274 | 62.48 | 17.52 | 662256 | 662.256 | 61.29 | 18.71 | 707238 | 707.238 | 60.1 | 19.9 | 752220 | 752.22 | 60
10/24/20XX 3:00:00 PM | 0.625 | 1 | 59.8 | 62.6 | 59.8 |  | 59.8 | 70.78 | 9.22 | 348516 | 348.516 | 69.56 | 10.44 | 394632 | 394.632 | 68.34 | 11.66 | 440748 | 440.748 | 67.12 | 12.88 | 486864 | 486.864 | 65.9 | 14.1 | 532980 | 532.98 | 64.68 | 15.32 | 579096 | 579.096 | 63.46 | 16.54 | 625212 | 625.212 | 62.24 | 17.76 | 671328 | 671.328 | 61.02 | 18.98 | 717444 | 717.444 | 59.8 | 20.2 | 763560 | 763.56 | 60
10/24/20XX 4:00:00 PM | 0.66667 | 1 | 59.5 | 63.3 | 59.5 |  | 59.5 | 70.75 | 9.25 | 349650 | 349.65 | 69.5 | 10.5 | 396900 | 396.9 | 68.25 | 11.75 | 444150 | 444.15 | 67 | 13 | 491400 | 491.4 | 65.75 | 14.25 | 538650 | 538.65 | 64.5 | 15.5 | 585900 | 585.9 | 63.25 | 16.75 | 633150 | 633.15 | 62 | 18 | 680400 | 680.4 | 60.75 | 19.25 | 727650 | 727.65 | 59.5 | 20.5 | 774900 | 774.9 | 60
10/24/20XX 5:00:00 PM | 0.70833 | 1 | 58.1 | 65.6 | 58.1 |  | 58.1 | 70.61 | 9.39 | 354942 | 354.942 | 69.22 | 10.78 | 407484 | 407.484 | 67.83 | 12.17 | 460026 | 460.026 | 66.44 | 13.56 | 512568 | 512.568 | 65.05 | 14.95 | 565110 | 565.11 | 63.66 | 16.34 | 617652 | 617.652 | 62.27 | 17.73 | 670194 | 670.194 | 60.88 | 19.12 | 722736 | 722.736 | 59.49 | 20.51 | 775278 | 775.278 | 58.1 | 21.9 | 827820 | 827.82 | 60
10/24/20XX 6:00:00 PM | 0.75 | 1 | 57.4 | 68.4 | 57.4 |  | 57.4 | 70.54 | 9.46 | 357588 | 357.588 | 69.08 | 10.92 | 412776 | 412.776 | 67.62 | 12.38 | 467964 | 467.964 | 66.16 | 13.84 | 523152 | 523.152 | 64.7 | 15.3 | 578340 | 578.34 | 63.24 | 16.76 | 633528 | 633.528 | 61.78 | 18.22 | 688716 | 688.716 | 60.32 | 19.68 | 743904 | 743.904 | 58.86 | 21.14 | 799092 | 799.092 | 57.4 | 22.6 | 854280 | 854.28 | 55
10/24/20XX 7:00:00 PM | 0.79167 | 1 | 56.8 | 69.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/24/20XX 8:00:00 PM | 0.83333 | 1 | 56.4 | 70.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/24/20XX 9:00:00 PM | 0.875 | 1 | 56.2 | 69.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/24/20XX 10:00:00 PM | 0.91667 | 1 | 55.9 | 71 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/24/20XX 11:00:00 PM | 0.95833 | 1 | 55.4 | 71.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/24/20XX 12:00:00 AM | 0 | 2 | 54.9 | 69.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/25/20XX 1:00:00 AM | 0.041667 | 2 | 54.1 | 70.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/25/20XX 2:00:00 AM | 0.083333 | 2 | 53.5 | 69.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/25/20XX 3:00:00 AM | 0.125 | 2 | 53.1 | 70.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/25/20XX 4:00:00 AM | 0.16667 | 2 | 52.1 | 72.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/25/20XX 5:00:00 AM | 0.20833 | 2 | 51.7 | 72 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/25/20XX 6:00:00 AM | 0.25 | 2 | 51.2 | 72.3 | 51.2 |  | 51.2 | 69.92 | 10.08 | 381024 | 381.024 | 67.84 | 12.16 | 459648 | 459.648 | 65.76 | 14.24 | 538272 | 538.272 | 63.68 | 16.32 | 616896 | 616.896 | 61.6 | 18.4 | 695520 | 695.52 | 59.52 | 20.48 | 774144 | 774.144 | 57.44 | 22.56 | 852768 | 852.768 | 55.36 | 24.64 | 931392 | 931.392 | 53.28 | 26.72 | 1010016 | 1010.016 | 51.2 | 28.8 | 1088640 | 1088.64 | 50
10/25/20XX 7:00:00 AM | 0.29167 | 2 | 51 | 70.9 | 51 |  | 51 | 69.9 | 10.1 | 381780 | 381.78 | 67.8 | 12.2 | 461160 | 461.16 | 65.7 | 14.3 | 540540 | 540.54 | 63.6 | 16.4 | 619920 | 619.92 | 61.5 | 18.5 | 699300 | 699.3 | 59.4 | 20.6 | 778680 | 778.68 | 57.3 | 22.7 | 858060 | 858.06 | 55.2 | 24.8 | 937440 | 937.44 | 53.1 | 26.9 | 1016820 | 1016.82 | 51 | 29 | 1096200 | 1096.2 | 50
10/25/20XX 8:00:00 AM | 0.33333 | 2 | 51.6 | 69 | 51.6 |  | 51.6 | 69.96 | 10.04 | 379512 | 379.512 | 67.92 | 12.08 | 456624 | 456.624 | 65.88 | 14.12 | 533736 | 533.736 | 63.84 | 16.16 | 610848 | 610.848 | 61.8 | 18.2 | 687960 | 687.96 | 59.76 | 20.24 | 765072 | 765.072 | 57.72 | 22.28 | 842184 | 842.184 | 55.68 | 24.32 | 919296 | 919.296 | 53.64 | 26.36 | 996408 | 996.408 | 51.6 | 28.4 | 1073520 | 1073.52 | 50
10/25/20XX 9:00:00 AM | 0.375 | 2 | 53.4 | 64.2 | 53.4 |  | 53.4 | 70.14 | 9.86 | 372708 | 372.708 | 68.28 | 11.72 | 443016 | 443.016 | 66.42 | 13.58 | 513324 | 513.324 | 64.56 | 15.44 | 583632 | 583.632 | 62.7 | 17.3 | 653940 | 653.94 | 60.84 | 19.16 | 724248 | 724.248 | 58.98 | 21.02 | 794556 | 794.556 | 57.12 | 22.88 | 864864 | 864.864 | 55.26 | 24.74 | 935172 | 935.172 | 53.4 | 26.6 | 1005480 | 1005.48 | 55
10/25/20XX 10:00:00 AM | 0.41667 | 2 | 54.5 | 62.4 | 54.5 |  | 54.5 | 70.25 | 9.75 | 368550 | 368.55 | 68.5 | 11.5 | 434700 | 434.7 | 66.75 | 13.25 | 500850 | 500.85 | 65 | 15 | 567000 | 567 | 63.25 | 16.75 | 633150 | 633.15 | 61.5 | 18.5 | 699300 | 699.3 | 59.75 | 20.25 | 765450 | 765.45 | 58 | 22 | 831600 | 831.6 | 56.25 | 23.75 | 897750 | 897.75 | 54.5 | 25.5 | 963900 | 963.9 | 55
10/25/20XX 11:00:00 AM | 0.45833 | 2 | 56.9 | 56.6 | 56.9 |  | 56.9 | 70.49 | 9.51 | 359478 | 359.478 | 68.98 | 11.02 | 416556 | 416.556 | 67.47 | 12.53 | 473634 | 473.634 | 65.96 | 14.04 | 530712 | 530.712 | 64.45 | 15.55 | 587790 | 587.79 | 62.94 | 17.06 | 644868 | 644.868 | 61.43 | 18.57 | 701946 | 701.946 | 59.92 | 20.08 | 759024 | 759.024 | 58.41 | 21.59 | 816102 | 816.102 | 56.9 | 23.1 | 873180 | 873.18 | 55
10/25/20XX 12:00:00 PM | 0.5 | 2 | 58.4 | 53.5 | 58.4 |  | 58.4 | 70.64 | 9.36 | 353808 | 353.808 | 69.28 | 10.72 | 405216 | 405.216 | 67.92 | 12.08 | 456624 | 456.624 | 66.56 | 13.44 | 508032 | 508.032 | 65.2 | 14.8 | 559440 | 559.44 | 63.84 | 16.16 | 610848 | 610.848 | 62.48 | 17.52 | 662256 | 662.256 | 61.12 | 18.88 | 713664 | 713.664 | 59.76 | 20.24 | 765072 | 765.072 | 58.4 | 21.6 | 816480 | 816.48 | 60
10/25/20XX 1:00:00 PM | 0.54167 | 2 | 59.9 | 49.8 | 59.9 |  | 59.9 | 70.79 | 9.21 | 348138 | 348.138 | 69.58 | 10.42 | 393876 | 393.876 | 68.37 | 11.63 | 439614 | 439.614 | 67.16 | 12.84 | 485352 | 485.352 | 65.95 | 14.05 | 531090 | 531.09 | 64.74 | 15.26 | 576828 | 576.828 | 63.53 | 16.47 | 622566 | 622.566 | 62.32 | 17.68 | 668304 | 668.304 | 61.11 | 18.89 | 714042 | 714.042 | 59.9 | 20.1 | 759780 | 759.78 | 60
10/25/20XX 2:00:00 PM | 0.58333 | 2 | 60.5 | 48.5 | 60.5 |  | 60.5 | 70.85 | 9.15 | 345870 | 345.87 | 69.7 | 10.3 | 389340 | 389.34 | 68.55 | 11.45 | 432810 | 432.81 | 67.4 | 12.6 | 476280 | 476.28 | 66.25 | 13.75 | 519750 | 519.75 | 65.1 | 14.9 | 563220 | 563.22 | 63.95 | 16.05 | 606690 | 606.69 | 62.8 | 17.2 | 650160 | 650.16 | 61.65 | 18.35 | 693630 | 693.63 | 60.5 | 19.5 | 737100 | 737.1 | 60
10/25/20XX 3:00:00 PM | 0.625 | 2 | 60.6 | 47.5 | 60.6 |  | 60.6 | 70.86 | 9.14 | 345492 | 345.492 | 69.72 | 10.28 | 388584 | 388.584 | 68.58 | 11.42 | 431676 | 431.676 | 67.44 | 12.56 | 474768 | 474.768 | 66.3 | 13.7 | 517860 | 517.86 | 65.16 | 14.84 | 560952 | 560.952 | 64.02 | 15.98 | 604044 | 604.044 | 62.88 | 17.12 | 647136 | 647.136 | 61.74 | 18.26 | 690228 | 690.228 | 60.6 | 19.4 | 733320 | 733.32 | 60
10/25/20XX 4:00:00 PM | 0.66667 | 2 | 60.1 | 46.6 | 60.1 |  | 60.1 | 70.81 | 9.19 | 347382 | 347.382 | 69.62 | 10.38 | 392364 | 392.364 | 68.43 | 11.57 | 437346 | 437.346 | 67.24 | 12.76 | 482328 | 482.328 | 66.05 | 13.95 | 527310 | 527.31 | 64.86 | 15.14 | 572292 | 572.292 | 63.67 | 16.33 | 617274 | 617.274 | 62.48 | 17.52 | 662256 | 662.256 | 61.29 | 18.71 | 707238 | 707.238 | 60.1 | 19.9 | 752220 | 752.22 | 60
10/25/20XX 5:00:00 PM | 0.70833 | 2 | 58.8 | 48.7 | 58.8 |  | 58.8 | 70.68 | 9.32 | 352296 | 352.296 | 69.36 | 10.64 | 402192 | 402.192 | 68.04 | 11.96 | 452088 | 452.088 | 66.72 | 13.28 | 501984 | 501.984 | 65.4 | 14.6 | 551880 | 551.88 | 64.08 | 15.92 | 601776 | 601.776 | 62.76 | 17.24 | 651672 | 651.672 | 61.44 | 18.56 | 701568 | 701.568 | 60.12 | 19.88 | 751464 | 751.464 | 58.8 | 21.2 | 801360 | 801.36 | 60
10/25/20XX 6:00:00 PM | 0.75 | 2 | 57.4 | 51.3 | 57.4 |  | 57.4 | 70.54 | 9.46 | 357588 | 357.588 | 69.08 | 10.92 | 412776 | 412.776 | 67.62 | 12.38 | 467964 | 467.964 | 66.16 | 13.84 | 523152 | 523.152 | 64.7 | 15.3 | 578340 | 578.34 | 63.24 | 16.76 | 633528 | 633.528 | 61.78 | 18.22 | 688716 | 688.716 | 60.32 | 19.68 | 743904 | 743.904 | 58.86 | 21.14 | 799092 | 799.092 | 57.4 | 22.6 | 854280 | 854.28 | 55
10/25/20XX 7:00:00 PM | 0.79167 | 2 | 56.7 | 51.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/25/20XX 8:00:00 PM | 0.83333 | 2 | 55.9 | 53.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/25/20XX 9:00:00 PM | 0.875 | 2 | 55.2 | 54.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/25/20XX 10:00:00 PM | 0.91667 | 2 | 54.1 | 56.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/25/20XX 11:00:00 PM | 0.95833 | 2 | 53.4 | 57.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/25/20XX 12:00:00 AM | 0 | 3 | 53 | 59.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/26/20XX 1:00:00 AM | 0.041667 | 3 | 52 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/26/20XX 2:00:00 AM | 0.083333 | 3 | 51.7 | 64.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/26/20XX 3:00:00 AM | 0.125 | 3 | 51.4 | 64.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/26/20XX 4:00:00 AM | 0.16667 | 3 | 50.5 | 67.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/26/20XX 5:00:00 AM | 0.20833 | 3 | 50 | 66.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/26/20XX 6:00:00 AM | 0.25 | 3 | 49.5 | 66.7 | 49.5 |  | 49.5 | 69.75 | 10.25 | 387450 | 387.45 | 67.5 | 12.5 | 472500 | 472.5 | 65.25 | 14.75 | 557550 | 557.55 | 63 | 17 | 642600 | 642.6 | 60.75 | 19.25 | 727650 | 727.65 | 58.5 | 21.5 | 812700 | 812.7 | 56.25 | 23.75 | 897750 | 897.75 | 54 | 26 | 982800 | 982.8 | 51.75 | 28.25 | 1067850 | 1067.85 | 49.5 | 30.5 | 1152900 | 1152.9 | 50
10/26/20XX 7:00:00 AM | 0.29167 | 3 | 49.6 | 68.9 | 49.6 |  | 49.6 | 69.76 | 10.24 | 387072 | 387.072 | 67.52 | 12.48 | 471744 | 471.744 | 65.28 | 14.72 | 556416 | 556.416 | 63.04 | 16.96 | 641088 | 641.088 | 60.8 | 19.2 | 725760 | 725.76 | 58.56 | 21.44 | 810432 | 810.432 | 56.32 | 23.68 | 895104 | 895.104 | 54.08 | 25.92 | 979776 | 979.776 | 51.84 | 28.16 | 1064448 | 1064.448 | 49.6 | 30.4 | 1149120 | 1149.12 | 50
10/26/20XX 8:00:00 AM | 0.33333 | 3 | 50.7 | 66.2 | 50.7 |  | 50.7 | 69.87 | 10.13 | 382914 | 382.914 | 67.74 | 12.26 | 463428 | 463.428 | 65.61 | 14.39 | 543942 | 543.942 | 63.48 | 16.52 | 624456 | 624.456 | 61.35 | 18.65 | 704970 | 704.97 | 59.22 | 20.78 | 785484 | 785.484 | 57.09 | 22.91 | 865998 | 865.998 | 54.96 | 25.04 | 946512 | 946.512 | 52.83 | 27.17 | 1027026 | 1027.026 | 50.7 | 29.3 | 1107540 | 1107.54 | 50
10/26/20XX 9:00:00 AM | 0.375 | 3 | 52.2 | 63.4 | 52.2 |  | 52.2 | 70.02 | 9.98 | 377244 | 377.244 | 68.04 | 11.96 | 452088 | 452.088 | 66.06 | 13.94 | 526932 | 526.932 | 64.08 | 15.92 | 601776 | 601.776 | 62.1 | 17.9 | 676620 | 676.62 | 60.12 | 19.88 | 751464 | 751.464 | 58.14 | 21.86 | 826308 | 826.308 | 56.16 | 23.84 | 901152 | 901.152 | 54.18 | 25.82 | 975996 | 975.996 | 52.2 | 27.8 | 1050840 | 1050.84 | 50
10/26/20XX 10:00:00 AM | 0.41667 | 3 | 53.9 | 58.5 | 53.9 |  | 53.9 | 70.19 | 9.81 | 370818 | 370.818 | 68.38 | 11.62 | 439236 | 439.236 | 66.57 | 13.43 | 507654 | 507.654 | 64.76 | 15.24 | 576072 | 576.072 | 62.95 | 17.05 | 644490 | 644.49 | 61.14 | 18.86 | 712908 | 712.908 | 59.33 | 20.67 | 781326 | 781.326 | 57.52 | 22.48 | 849744 | 849.744 | 55.71 | 24.29 | 918162 | 918.162 | 53.9 | 26.1 | 986580 | 986.58 | 55
10/26/20XX 11:00:00 AM | 0.45833 | 3 | 55.2 | 56.7 | 55.2 |  | 55.2 | 70.32 | 9.68 | 365904 | 365.904 | 68.64 | 11.36 | 429408 | 429.408 | 66.96 | 13.04 | 492912 | 492.912 | 65.28 | 14.72 | 556416 | 556.416 | 63.6 | 16.4 | 619920 | 619.92 | 61.92 | 18.08 | 683424 | 683.424 | 60.24 | 19.76 | 746928 | 746.928 | 58.56 | 21.44 | 810432 | 810.432 | 56.88 | 23.12 | 873936 | 873.936 | 55.2 | 24.8 | 937440 | 937.44 | 55
10/26/20XX 12:00:00 PM | 0.5 | 3 | 56.9 | 52.5 | 56.9 |  | 56.9 | 70.49 | 9.51 | 359478 | 359.478 | 68.98 | 11.02 | 416556 | 416.556 | 67.47 | 12.53 | 473634 | 473.634 | 65.96 | 14.04 | 530712 | 530.712 | 64.45 | 15.55 | 587790 | 587.79 | 62.94 | 17.06 | 644868 | 644.868 | 61.43 | 18.57 | 701946 | 701.946 | 59.92 | 20.08 | 759024 | 759.024 | 58.41 | 21.59 | 816102 | 816.102 | 56.9 | 23.1 | 873180 | 873.18 | 55
10/26/20XX 1:00:00 PM | 0.54167 | 3 | 57.7 | 51.5 | 57.7 |  | 57.7 | 70.57 | 9.43 | 356454 | 356.454 | 69.14 | 10.86 | 410508 | 410.508 | 67.71 | 12.29 | 464562 | 464.562 | 66.28 | 13.72 | 518616 | 518.616 | 64.85 | 15.15 | 572670 | 572.67 | 63.42 | 16.58 | 626724 | 626.724 | 61.99 | 18.01 | 680778 | 680.778 | 60.56 | 19.44 | 734832 | 734.832 | 59.13 | 20.87 | 788886 | 788.886 | 57.7 | 22.3 | 842940 | 842.94 | 60
10/26/20XX 2:00:00 PM | 0.58333 | 3 | 58.4 | 49.9 | 58.4 |  | 58.4 | 70.64 | 9.36 | 353808 | 353.808 | 69.28 | 10.72 | 405216 | 405.216 | 67.92 | 12.08 | 456624 | 456.624 | 66.56 | 13.44 | 508032 | 508.032 | 65.2 | 14.8 | 559440 | 559.44 | 63.84 | 16.16 | 610848 | 610.848 | 62.48 | 17.52 | 662256 | 662.256 | 61.12 | 18.88 | 713664 | 713.664 | 59.76 | 20.24 | 765072 | 765.072 | 58.4 | 21.6 | 816480 | 816.48 | 60
10/26/20XX 3:00:00 PM | 0.625 | 3 | 57.8 | 52.7 | 57.8 |  | 57.8 | 70.58 | 9.42 | 356076 | 356.076 | 69.16 | 10.84 | 409752 | 409.752 | 67.74 | 12.26 | 463428 | 463.428 | 66.32 | 13.68 | 517104 | 517.104 | 64.9 | 15.1 | 570780 | 570.78 | 63.48 | 16.52 | 624456 | 624.456 | 62.06 | 17.94 | 678132 | 678.132 | 60.64 | 19.36 | 731808 | 731.808 | 59.22 | 20.78 | 785484 | 785.484 | 57.8 | 22.2 | 839160 | 839.16 | 60
10/26/20XX 4:00:00 PM | 0.66667 | 3 | 57.2 | 54.4 | 57.2 |  | 57.2 | 70.52 | 9.48 | 358344 | 358.344 | 69.04 | 10.96 | 414288 | 414.288 | 67.56 | 12.44 | 470232 | 470.232 | 66.08 | 13.92 | 526176 | 526.176 | 64.6 | 15.4 | 582120 | 582.12 | 63.12 | 16.88 | 638064 | 638.064 | 61.64 | 18.36 | 694008 | 694.008 | 60.16 | 19.84 | 749952 | 749.952 | 58.68 | 21.32 | 805896 | 805.896 | 57.2 | 22.8 | 861840 | 861.84 | 55
10/26/20XX 5:00:00 PM | 0.70833 | 3 | 56.3 | 56.5 | 56.3 |  | 56.3 | 70.43 | 9.57 | 361746 | 361.746 | 68.86 | 11.14 | 421092 | 421.092 | 67.29 | 12.71 | 480438 | 480.438 | 65.72 | 14.28 | 539784 | 539.784 | 64.15 | 15.85 | 599130 | 599.13 | 62.58 | 17.42 | 658476 | 658.476 | 61.01 | 18.99 | 717822 | 717.822 | 59.44 | 20.56 | 777168 | 777.168 | 57.87 | 22.13 | 836514 | 836.514 | 56.3 | 23.7 | 895860 | 895.86 | 55
10/26/20XX 6:00:00 PM | 0.75 | 3 | 55.9 | 56.1 | 55.9 |  | 55.9 | 70.39 | 9.61 | 363258 | 363.258 | 68.78 | 11.22 | 424116 | 424.116 | 67.17 | 12.83 | 484974 | 484.974 | 65.56 | 14.44 | 545832 | 545.832 | 63.95 | 16.05 | 606690 | 606.69 | 62.34 | 17.66 | 667548 | 667.548 | 60.73 | 19.27 | 728406 | 728.406 | 59.12 | 20.88 | 789264 | 789.264 | 57.51 | 22.49 | 850122 | 850.122 | 55.9 | 24.1 | 910980 | 910.98 | 55
10/26/20XX 7:00:00 PM | 0.79167 | 3 | 55.2 | 57.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/26/20XX 8:00:00 PM | 0.83333 | 3 | 54.5 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/26/20XX 9:00:00 PM | 0.875 | 3 | 54.3 | 59.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/26/20XX 10:00:00 PM | 0.91667 | 3 | 53.7 | 61.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/26/20XX 11:00:00 PM | 0.95833 | 3 | 53.7 | 61.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/26/20XX 12:00:00 AM | 0 | 4 | 53.3 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/27/20XX 1:00:00 AM | 0.041667 | 4 | 53 | 64.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/27/20XX 2:00:00 AM | 0.083333 | 4 | 52.5 | 67.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/27/20XX 3:00:00 AM | 0.125 | 4 | 52.2 | 69.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/27/20XX 4:00:00 AM | 0.16667 | 4 | 52.1 | 72.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/27/20XX 5:00:00 AM | 0.20833 | 4 | 52.1 | 73.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/27/20XX 6:00:00 AM | 0.25 | 4 | 52.4 | 74.3 | 52.4 |  | 52.4 | 70.04 | 9.96 | 376488 | 376.488 | 68.08 | 11.92 | 450576 | 450.576 | 66.12 | 13.88 | 524664 | 524.664 | 64.16 | 15.84 | 598752 | 598.752 | 62.2 | 17.8 | 672840 | 672.84 | 60.24 | 19.76 | 746928 | 746.928 | 58.28 | 21.72 | 821016 | 821.016 | 56.32 | 23.68 | 895104 | 895.104 | 54.36 | 25.64 | 969192 | 969.192 | 52.4 | 27.6 | 1043280 | 1043.28 | 50
10/27/20XX 7:00:00 AM | 0.29167 | 4 | 52.3 | 75.5 | 52.3 |  | 52.3 | 70.03 | 9.97 | 376866 | 376.866 | 68.06 | 11.94 | 451332 | 451.332 | 66.09 | 13.91 | 525798 | 525.798 | 64.12 | 15.88 | 600264 | 600.264 | 62.15 | 17.85 | 674730 | 674.73 | 60.18 | 19.82 | 749196 | 749.196 | 58.21 | 21.79 | 823662 | 823.662 | 56.24 | 23.76 | 898128 | 898.128 | 54.27 | 25.73 | 972594 | 972.594 | 52.3 | 27.7 | 1047060 | 1047.06 | 50
10/27/20XX 8:00:00 AM | 0.33333 | 4 | 52.3 | 77 | 52.3 |  | 52.3 | 70.03 | 9.97 | 376866 | 376.866 | 68.06 | 11.94 | 451332 | 451.332 | 66.09 | 13.91 | 525798 | 525.798 | 64.12 | 15.88 | 600264 | 600.264 | 62.15 | 17.85 | 674730 | 674.73 | 60.18 | 19.82 | 749196 | 749.196 | 58.21 | 21.79 | 823662 | 823.662 | 56.24 | 23.76 | 898128 | 898.128 | 54.27 | 25.73 | 972594 | 972.594 | 52.3 | 27.7 | 1047060 | 1047.06 | 50
10/27/20XX 9:00:00 AM | 0.375 | 4 | 53.2 | 74.8 | 53.2 |  | 53.2 | 70.12 | 9.88 | 373464 | 373.464 | 68.24 | 11.76 | 444528 | 444.528 | 66.36 | 13.64 | 515592 | 515.592 | 64.48 | 15.52 | 586656 | 586.656 | 62.6 | 17.4 | 657720 | 657.72 | 60.72 | 19.28 | 728784 | 728.784 | 58.84 | 21.16 | 799848 | 799.848 | 56.96 | 23.04 | 870912 | 870.912 | 55.08 | 24.92 | 941976 | 941.976 | 53.2 | 26.8 | 1013040 | 1013.04 | 55
10/27/20XX 10:00:00 AM | 0.41667 | 4 | 54.3 | 73.9 | 54.3 |  | 54.3 | 70.23 | 9.77 | 369306 | 369.306 | 68.46 | 11.54 | 436212 | 436.212 | 66.69 | 13.31 | 503118 | 503.118 | 64.92 | 15.08 | 570024 | 570.024 | 63.15 | 16.85 | 636930 | 636.93 | 61.38 | 18.62 | 703836 | 703.836 | 59.61 | 20.39 | 770742 | 770.742 | 57.84 | 22.16 | 837648 | 837.648 | 56.07 | 23.93 | 904554 | 904.554 | 54.3 | 25.7 | 971460 | 971.46 | 55
10/27/20XX 11:00:00 AM | 0.45833 | 4 | 55.4 | 71.8 | 55.4 |  | 55.4 | 70.34 | 9.66 | 365148 | 365.148 | 68.68 | 11.32 | 427896 | 427.896 | 67.02 | 12.98 | 490644 | 490.644 | 65.36 | 14.64 | 553392 | 553.392 | 63.7 | 16.3 | 616140 | 616.14 | 62.04 | 17.96 | 678888 | 678.888 | 60.38 | 19.62 | 741636 | 741.636 | 58.72 | 21.28 | 804384 | 804.384 | 57.06 | 22.94 | 867132 | 867.132 | 55.4 | 24.6 | 929880 | 929.88 | 55
10/27/20XX 12:00:00 PM | 0.5 | 4 | 56.6 | 69.3 | 56.6 |  | 56.6 | 70.46 | 9.54 | 360612 | 360.612 | 68.92 | 11.08 | 418824 | 418.824 | 67.38 | 12.62 | 477036 | 477.036 | 65.84 | 14.16 | 535248 | 535.248 | 64.3 | 15.7 | 593460 | 593.46 | 62.76 | 17.24 | 651672 | 651.672 | 61.22 | 18.78 | 709884 | 709.884 | 59.68 | 20.32 | 768096 | 768.096 | 58.14 | 21.86 | 826308 | 826.308 | 56.6 | 23.4 | 884520 | 884.52 | 55
10/27/20XX 1:00:00 PM | 0.54167 | 4 | 57 | 68.5 | 57 |  | 57 | 70.5 | 9.5 | 359100 | 359.1 | 69 | 11 | 415800 | 415.8 | 67.5 | 12.5 | 472500 | 472.5 | 66 | 14 | 529200 | 529.2 | 64.5 | 15.5 | 585900 | 585.9 | 63 | 17 | 642600 | 642.6 | 61.5 | 18.5 | 699300 | 699.3 | 60 | 20 | 756000 | 756 | 58.5 | 21.5 | 812700 | 812.7 | 57 | 23 | 869400 | 869.4 | 55
10/27/20XX 2:00:00 PM | 0.58333 | 4 | 57 | 68.4 | 57 |  | 57 | 70.5 | 9.5 | 359100 | 359.1 | 69 | 11 | 415800 | 415.8 | 67.5 | 12.5 | 472500 | 472.5 | 66 | 14 | 529200 | 529.2 | 64.5 | 15.5 | 585900 | 585.9 | 63 | 17 | 642600 | 642.6 | 61.5 | 18.5 | 699300 | 699.3 | 60 | 20 | 756000 | 756 | 58.5 | 21.5 | 812700 | 812.7 | 57 | 23 | 869400 | 869.4 | 55
10/27/20XX 3:00:00 PM | 0.625 | 4 | 57 | 69 | 57 |  | 57 | 70.5 | 9.5 | 359100 | 359.1 | 69 | 11 | 415800 | 415.8 | 67.5 | 12.5 | 472500 | 472.5 | 66 | 14 | 529200 | 529.2 | 64.5 | 15.5 | 585900 | 585.9 | 63 | 17 | 642600 | 642.6 | 61.5 | 18.5 | 699300 | 699.3 | 60 | 20 | 756000 | 756 | 58.5 | 21.5 | 812700 | 812.7 | 57 | 23 | 869400 | 869.4 | 55
10/27/20XX 4:00:00 PM | 0.66667 | 4 | 56.6 | 69 | 56.6 |  | 56.6 | 70.46 | 9.54 | 360612 | 360.612 | 68.92 | 11.08 | 418824 | 418.824 | 67.38 | 12.62 | 477036 | 477.036 | 65.84 | 14.16 | 535248 | 535.248 | 64.3 | 15.7 | 593460 | 593.46 | 62.76 | 17.24 | 651672 | 651.672 | 61.22 | 18.78 | 709884 | 709.884 | 59.68 | 20.32 | 768096 | 768.096 | 58.14 | 21.86 | 826308 | 826.308 | 56.6 | 23.4 | 884520 | 884.52 | 55
10/27/20XX 5:00:00 PM | 0.70833 | 4 | 56 | 72.1 | 56 |  | 56 | 70.4 | 9.6 | 362880 | 362.88 | 68.8 | 11.2 | 423360 | 423.36 | 67.2 | 12.8 | 483840 | 483.84 | 65.6 | 14.4 | 544320 | 544.32 | 64 | 16 | 604800 | 604.8 | 62.4 | 17.6 | 665280 | 665.28 | 60.8 | 19.2 | 725760 | 725.76 | 59.2 | 20.8 | 786240 | 786.24 | 57.6 | 22.4 | 846720 | 846.72 | 56 | 24 | 907200 | 907.2 | 55
10/27/20XX 6:00:00 PM | 0.75 | 4 | 55.6 | 73.3 | 55.6 |  | 55.6 | 70.36 | 9.64 | 364392 | 364.392 | 68.72 | 11.28 | 426384 | 426.384 | 67.08 | 12.92 | 488376 | 488.376 | 65.44 | 14.56 | 550368 | 550.368 | 63.8 | 16.2 | 612360 | 612.36 | 62.16 | 17.84 | 674352 | 674.352 | 60.52 | 19.48 | 736344 | 736.344 | 58.88 | 21.12 | 798336 | 798.336 | 57.24 | 22.76 | 860328 | 860.328 | 55.6 | 24.4 | 922320 | 922.32 | 55
10/27/20XX 7:00:00 PM | 0.79167 | 4 | 55.2 | 74.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/27/20XX 8:00:00 PM | 0.83333 | 4 | 54.9 | 74.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/27/20XX 9:00:00 PM | 0.875 | 4 | 54.4 | 74.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/27/20XX 10:00:00 PM | 0.91667 | 4 | 54 | 74 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/27/20XX 11:00:00 PM | 0.95833 | 4 | 53.5 | 76 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/27/20XX 12:00:00 AM | 0 | 5 | 52.6 | 76.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/28/20XX 1:00:00 AM | 0.041667 | 5 | 52.3 | 76.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/28/20XX 2:00:00 AM | 0.083333 | 5 | 51.5 | 78.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/28/20XX 3:00:00 AM | 0.125 | 5 | 51.1 | 80.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/28/20XX 4:00:00 AM | 0.16667 | 5 | 51.4 | 76.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/28/20XX 5:00:00 AM | 0.20833 | 5 | 51.5 | 77.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/28/20XX 6:00:00 AM | 0.25 | 5 | 51.1 | 76.9 | 51.1 |  | 51.1 | 69.91 | 10.09 | 381402 | 381.402 | 67.82 | 12.18 | 460404 | 460.404 | 65.73 | 14.27 | 539406 | 539.406 | 63.64 | 16.36 | 618408 | 618.408 | 61.55 | 18.45 | 697410 | 697.41 | 59.46 | 20.54 | 776412 | 776.412 | 57.37 | 22.63 | 855414 | 855.414 | 55.28 | 24.72 | 934416 | 934.416 | 53.19 | 26.81 | 1013418 | 1013.418 | 51.1 | 28.9 | 1092420 | 1092.42 | 50
10/28/20XX 7:00:00 AM | 0.29167 | 5 | 51.4 | 74 | 51.4 |  | 51.4 | 69.94 | 10.06 | 380268 | 380.268 | 67.88 | 12.12 | 458136 | 458.136 | 65.82 | 14.18 | 536004 | 536.004 | 63.76 | 16.24 | 613872 | 613.872 | 61.7 | 18.3 | 691740 | 691.74 | 59.64 | 20.36 | 769608 | 769.608 | 57.58 | 22.42 | 847476 | 847.476 | 55.52 | 24.48 | 925344 | 925.344 | 53.46 | 26.54 | 1003212 | 1003.212 | 51.4 | 28.6 | 1081080 | 1081.08 | 50
10/28/20XX 8:00:00 AM | 0.33333 | 5 | 52.3 | 72.8 | 52.3 |  | 52.3 | 70.03 | 9.97 | 376866 | 376.866 | 68.06 | 11.94 | 451332 | 451.332 | 66.09 | 13.91 | 525798 | 525.798 | 64.12 | 15.88 | 600264 | 600.264 | 62.15 | 17.85 | 674730 | 674.73 | 60.18 | 19.82 | 749196 | 749.196 | 58.21 | 21.79 | 823662 | 823.662 | 56.24 | 23.76 | 898128 | 898.128 | 54.27 | 25.73 | 972594 | 972.594 | 52.3 | 27.7 | 1047060 | 1047.06 | 50
10/28/20XX 9:00:00 AM | 0.375 | 5 | 54 | 67.1 | 54 |  | 54 | 70.2 | 9.8 | 370440 | 370.44 | 68.4 | 11.6 | 438480 | 438.48 | 66.6 | 13.4 | 506520 | 506.52 | 64.8 | 15.2 | 574560 | 574.56 | 63 | 17 | 642600 | 642.6 | 61.2 | 18.8 | 710640 | 710.64 | 59.4 | 20.6 | 778680 | 778.68 | 57.6 | 22.4 | 846720 | 846.72 | 55.8 | 24.2 | 914760 | 914.76 | 54 | 26 | 982800 | 982.8 | 55
10/28/20XX 10:00:00 AM | 0.41667 | 5 | 55.4 | 63.8 | 55.4 |  | 55.4 | 70.34 | 9.66 | 365148 | 365.148 | 68.68 | 11.32 | 427896 | 427.896 | 67.02 | 12.98 | 490644 | 490.644 | 65.36 | 14.64 | 553392 | 553.392 | 63.7 | 16.3 | 616140 | 616.14 | 62.04 | 17.96 | 678888 | 678.888 | 60.38 | 19.62 | 741636 | 741.636 | 58.72 | 21.28 | 804384 | 804.384 | 57.06 | 22.94 | 867132 | 867.132 | 55.4 | 24.6 | 929880 | 929.88 | 55
10/28/20XX 11:00:00 AM | 0.45833 | 5 | 56.8 | 60.1 | 56.8 |  | 56.8 | 70.48 | 9.52 | 359856 | 359.856 | 68.96 | 11.04 | 417312 | 417.312 | 67.44 | 12.56 | 474768 | 474.768 | 65.92 | 14.08 | 532224 | 532.224 | 64.4 | 15.6 | 589680 | 589.68 | 62.88 | 17.12 | 647136 | 647.136 | 61.36 | 18.64 | 704592 | 704.592 | 59.84 | 20.16 | 762048 | 762.048 | 58.32 | 21.68 | 819504 | 819.504 | 56.8 | 23.2 | 876960 | 876.96 | 55
10/28/20XX 12:00:00 PM | 0.5 | 5 | 57.9 | 60.2 | 57.9 |  | 57.9 | 70.59 | 9.41 | 355698 | 355.698 | 69.18 | 10.82 | 408996 | 408.996 | 67.77 | 12.23 | 462294 | 462.294 | 66.36 | 13.64 | 515592 | 515.592 | 64.95 | 15.05 | 568890 | 568.89 | 63.54 | 16.46 | 622188 | 622.188 | 62.13 | 17.87 | 675486 | 675.486 | 60.72 | 19.28 | 728784 | 728.784 | 59.31 | 20.69 | 782082 | 782.082 | 57.9 | 22.1 | 835380 | 835.38 | 60
10/28/20XX 1:00:00 PM | 0.54167 | 5 | 59.1 | 57.7 | 59.1 |  | 59.1 | 70.71 | 9.29 | 351162 | 351.162 | 69.42 | 10.58 | 399924 | 399.924 | 68.13 | 11.87 | 448686 | 448.686 | 66.84 | 13.16 | 497448 | 497.448 | 65.55 | 14.45 | 546210 | 546.21 | 64.26 | 15.74 | 594972 | 594.972 | 62.97 | 17.03 | 643734 | 643.734 | 61.68 | 18.32 | 692496 | 692.496 | 60.39 | 19.61 | 741258 | 741.258 | 59.1 | 20.9 | 790020 | 790.02 | 60
10/28/20XX 2:00:00 PM | 0.58333 | 5 | 59.3 | 57.1 | 59.3 |  | 59.3 | 70.73 | 9.27 | 350406 | 350.406 | 69.46 | 10.54 | 398412 | 398.412 | 68.19 | 11.81 | 446418 | 446.418 | 66.92 | 13.08 | 494424 | 494.424 | 65.65 | 14.35 | 542430 | 542.43 | 64.38 | 15.62 | 590436 | 590.436 | 63.11 | 16.89 | 638442 | 638.442 | 61.84 | 18.16 | 686448 | 686.448 | 60.57 | 19.43 | 734454 | 734.454 | 59.3 | 20.7 | 782460 | 782.46 | 60
10/28/20XX 3:00:00 PM | 0.625 | 5 | 59.2 | 58.8 | 59.2 |  | 59.2 | 70.72 | 9.28 | 350784 | 350.784 | 69.44 | 10.56 | 399168 | 399.168 | 68.16 | 11.84 | 447552 | 447.552 | 66.88 | 13.12 | 495936 | 495.936 | 65.6 | 14.4 | 544320 | 544.32 | 64.32 | 15.68 | 592704 | 592.704 | 63.04 | 16.96 | 641088 | 641.088 | 61.76 | 18.24 | 689472 | 689.472 | 60.48 | 19.52 | 737856 | 737.856 | 59.2 | 20.8 | 786240 | 786.24 | 60
10/28/20XX 4:00:00 PM | 0.66667 | 5 | 58.4 | 60.6 | 58.4 |  | 58.4 | 70.64 | 9.36 | 353808 | 353.808 | 69.28 | 10.72 | 405216 | 405.216 | 67.92 | 12.08 | 456624 | 456.624 | 66.56 | 13.44 | 508032 | 508.032 | 65.2 | 14.8 | 559440 | 559.44 | 63.84 | 16.16 | 610848 | 610.848 | 62.48 | 17.52 | 662256 | 662.256 | 61.12 | 18.88 | 713664 | 713.664 | 59.76 | 20.24 | 765072 | 765.072 | 58.4 | 21.6 | 816480 | 816.48 | 60
10/28/20XX 5:00:00 PM | 0.70833 | 5 | 57.5 | 63 | 57.5 |  | 57.5 | 70.55 | 9.45 | 357210 | 357.21 | 69.1 | 10.9 | 412020 | 412.02 | 67.65 | 12.35 | 466830 | 466.83 | 66.2 | 13.8 | 521640 | 521.64 | 64.75 | 15.25 | 576450 | 576.45 | 63.3 | 16.7 | 631260 | 631.26 | 61.85 | 18.15 | 686070 | 686.07 | 60.4 | 19.6 | 740880 | 740.88 | 58.95 | 21.05 | 795690 | 795.69 | 57.5 | 22.5 | 850500 | 850.5 | 55
10/28/20XX 6:00:00 PM | 0.75 | 5 | 57.5 | 62.5 | 57.5 |  | 57.5 | 70.55 | 9.45 | 357210 | 357.21 | 69.1 | 10.9 | 412020 | 412.02 | 67.65 | 12.35 | 466830 | 466.83 | 66.2 | 13.8 | 521640 | 521.64 | 64.75 | 15.25 | 576450 | 576.45 | 63.3 | 16.7 | 631260 | 631.26 | 61.85 | 18.15 | 686070 | 686.07 | 60.4 | 19.6 | 740880 | 740.88 | 58.95 | 21.05 | 795690 | 795.69 | 57.5 | 22.5 | 850500 | 850.5 | 55
10/28/20XX 7:00:00 PM | 0.79167 | 5 | 57 | 65.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/28/20XX 8:00:00 PM | 0.83333 | 5 | 56.4 | 66.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/28/20XX 9:00:00 PM | 0.875 | 5 | 56.3 | 67.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/28/20XX 10:00:00 PM | 0.91667 | 5 | 55.8 | 68.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/28/20XX 11:00:00 PM | 0.95833 | 5 | 55.4 | 70.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/28/20XX 12:00:00 AM | 0 | 6 | 55 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/29/20XX 1:00:00 AM | 0.041667 | 6 | 54.4 | 71 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/29/20XX 2:00:00 AM | 0.083333 | 6 | 54 | 71.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/29/20XX 3:00:00 AM | 0.125 | 6 | 53.6 | 72.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/29/20XX 4:00:00 AM | 0.16667 | 6 | 53.2 | 73.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/29/20XX 5:00:00 AM | 0.20833 | 6 | 52.4 | 76.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/29/20XX 6:00:00 AM | 0.25 | 6 | 51.9 | 77.2 | 51.9 |  | 51.9 | 69.99 | 10.01 | 378378 | 378.378 | 67.98 | 12.02 | 454356 | 454.356 | 65.97 | 14.03 | 530334 | 530.334 | 63.96 | 16.04 | 606312 | 606.312 | 61.95 | 18.05 | 682290 | 682.29 | 59.94 | 20.06 | 758268 | 758.268 | 57.93 | 22.07 | 834246 | 834.246 | 55.92 | 24.08 | 910224 | 910.224 | 53.91 | 26.09 | 986202 | 986.202 | 51.9 | 28.1 | 1062180 | 1062.18 | 50
10/29/20XX 7:00:00 AM | 0.29167 | 6 | 52.1 | 77.1 | 52.1 |  | 52.1 | 70.01 | 9.99 | 377622 | 377.622 | 68.02 | 11.98 | 452844 | 452.844 | 66.03 | 13.97 | 528066 | 528.066 | 64.04 | 15.96 | 603288 | 603.288 | 62.05 | 17.95 | 678510 | 678.51 | 60.06 | 19.94 | 753732 | 753.732 | 58.07 | 21.93 | 828954 | 828.954 | 56.08 | 23.92 | 904176 | 904.176 | 54.09 | 25.91 | 979398 | 979.398 | 52.1 | 27.9 | 1054620 | 1054.62 | 50
10/29/20XX 8:00:00 AM | 0.33333 | 6 | 52.9 | 75.7 | 52.9 |  | 52.9 | 70.09 | 9.91 | 374598 | 374.598 | 68.18 | 11.82 | 446796 | 446.796 | 66.27 | 13.73 | 518994 | 518.994 | 64.36 | 15.64 | 591192 | 591.192 | 62.45 | 17.55 | 663390 | 663.39 | 60.54 | 19.46 | 735588 | 735.588 | 58.63 | 21.37 | 807786 | 807.786 | 56.72 | 23.28 | 879984 | 879.984 | 54.81 | 25.19 | 952182 | 952.182 | 52.9 | 27.1 | 1024380 | 1024.38 | 55
10/29/20XX 9:00:00 AM | 0.375 | 6 | 54.2 | 73.4 | 54.2 |  | 54.2 | 70.22 | 9.78 | 369684 | 369.684 | 68.44 | 11.56 | 436968 | 436.968 | 66.66 | 13.34 | 504252 | 504.252 | 64.88 | 15.12 | 571536 | 571.536 | 63.1 | 16.9 | 638820 | 638.82 | 61.32 | 18.68 | 706104 | 706.104 | 59.54 | 20.46 | 773388 | 773.388 | 57.76 | 22.24 | 840672 | 840.672 | 55.98 | 24.02 | 907956 | 907.956 | 54.2 | 25.8 | 975240 | 975.24 | 55
10/29/20XX 10:00:00 AM | 0.41667 | 6 | 54.8 | 70.1 | 54.8 |  | 54.8 | 70.28 | 9.72 | 367416 | 367.416 | 68.56 | 11.44 | 432432 | 432.432 | 66.84 | 13.16 | 497448 | 497.448 | 65.12 | 14.88 | 562464 | 562.464 | 63.4 | 16.6 | 627480 | 627.48 | 61.68 | 18.32 | 692496 | 692.496 | 59.96 | 20.04 | 757512 | 757.512 | 58.24 | 21.76 | 822528 | 822.528 | 56.52 | 23.48 | 887544 | 887.544 | 54.8 | 25.2 | 952560 | 952.56 | 55
10/29/20XX 11:00:00 AM | 0.45833 | 6 | 55.4 | 69.6 | 55.4 |  | 55.4 | 70.34 | 9.66 | 365148 | 365.148 | 68.68 | 11.32 | 427896 | 427.896 | 67.02 | 12.98 | 490644 | 490.644 | 65.36 | 14.64 | 553392 | 553.392 | 63.7 | 16.3 | 616140 | 616.14 | 62.04 | 17.96 | 678888 | 678.888 | 60.38 | 19.62 | 741636 | 741.636 | 58.72 | 21.28 | 804384 | 804.384 | 57.06 | 22.94 | 867132 | 867.132 | 55.4 | 24.6 | 929880 | 929.88 | 55
10/29/20XX 12:00:00 PM | 0.5 | 6 | 56.6 | 65.5 | 56.6 |  | 56.6 | 70.46 | 9.54 | 360612 | 360.612 | 68.92 | 11.08 | 418824 | 418.824 | 67.38 | 12.62 | 477036 | 477.036 | 65.84 | 14.16 | 535248 | 535.248 | 64.3 | 15.7 | 593460 | 593.46 | 62.76 | 17.24 | 651672 | 651.672 | 61.22 | 18.78 | 709884 | 709.884 | 59.68 | 20.32 | 768096 | 768.096 | 58.14 | 21.86 | 826308 | 826.308 | 56.6 | 23.4 | 884520 | 884.52 | 55
10/29/20XX 1:00:00 PM | 0.54167 | 6 | 57.2 | 63.9 | 57.2 |  | 57.2 | 70.52 | 9.48 | 358344 | 358.344 | 69.04 | 10.96 | 414288 | 414.288 | 67.56 | 12.44 | 470232 | 470.232 | 66.08 | 13.92 | 526176 | 526.176 | 64.6 | 15.4 | 582120 | 582.12 | 63.12 | 16.88 | 638064 | 638.064 | 61.64 | 18.36 | 694008 | 694.008 | 60.16 | 19.84 | 749952 | 749.952 | 58.68 | 21.32 | 805896 | 805.896 | 57.2 | 22.8 | 861840 | 861.84 | 55
10/29/20XX 2:00:00 PM | 0.58333 | 6 | 57.3 | 62 | 57.3 |  | 57.3 | 70.53 | 9.47 | 357966 | 357.966 | 69.06 | 10.94 | 413532 | 413.532 | 67.59 | 12.41 | 469098 | 469.098 | 66.12 | 13.88 | 524664 | 524.664 | 64.65 | 15.35 | 580230 | 580.23 | 63.18 | 16.82 | 635796 | 635.796 | 61.71 | 18.29 | 691362 | 691.362 | 60.24 | 19.76 | 746928 | 746.928 | 58.77 | 21.23 | 802494 | 802.494 | 57.3 | 22.7 | 858060 | 858.06 | 55
10/29/20XX 3:00:00 PM | 0.625 | 6 | 57.3 | 61.7 | 57.3 |  | 57.3 | 70.53 | 9.47 | 357966 | 357.966 | 69.06 | 10.94 | 413532 | 413.532 | 67.59 | 12.41 | 469098 | 469.098 | 66.12 | 13.88 | 524664 | 524.664 | 64.65 | 15.35 | 580230 | 580.23 | 63.18 | 16.82 | 635796 | 635.796 | 61.71 | 18.29 | 691362 | 691.362 | 60.24 | 19.76 | 746928 | 746.928 | 58.77 | 21.23 | 802494 | 802.494 | 57.3 | 22.7 | 858060 | 858.06 | 55
10/29/20XX 4:00:00 PM | 0.66667 | 6 | 56.9 | 62.2 | 56.9 |  | 56.9 | 70.49 | 9.51 | 359478 | 359.478 | 68.98 | 11.02 | 416556 | 416.556 | 67.47 | 12.53 | 473634 | 473.634 | 65.96 | 14.04 | 530712 | 530.712 | 64.45 | 15.55 | 587790 | 587.79 | 62.94 | 17.06 | 644868 | 644.868 | 61.43 | 18.57 | 701946 | 701.946 | 59.92 | 20.08 | 759024 | 759.024 | 58.41 | 21.59 | 816102 | 816.102 | 56.9 | 23.1 | 873180 | 873.18 | 55
10/29/20XX 5:00:00 PM | 0.70833 | 6 | 55.4 | 67.8 | 55.4 |  | 55.4 | 70.34 | 9.66 | 365148 | 365.148 | 68.68 | 11.32 | 427896 | 427.896 | 67.02 | 12.98 | 490644 | 490.644 | 65.36 | 14.64 | 553392 | 553.392 | 63.7 | 16.3 | 616140 | 616.14 | 62.04 | 17.96 | 678888 | 678.888 | 60.38 | 19.62 | 741636 | 741.636 | 58.72 | 21.28 | 804384 | 804.384 | 57.06 | 22.94 | 867132 | 867.132 | 55.4 | 24.6 | 929880 | 929.88 | 55
10/29/20XX 6:00:00 PM | 0.75 | 6 | 54.7 | 67 | 54.7 |  | 54.7 | 70.27 | 9.73 | 367794 | 367.794 | 68.54 | 11.46 | 433188 | 433.188 | 66.81 | 13.19 | 498582 | 498.582 | 65.08 | 14.92 | 563976 | 563.976 | 63.35 | 16.65 | 629370 | 629.37 | 61.62 | 18.38 | 694764 | 694.764 | 59.89 | 20.11 | 760158 | 760.158 | 58.16 | 21.84 | 825552 | 825.552 | 56.43 | 23.57 | 890946 | 890.946 | 54.7 | 25.3 | 956340 | 956.34 | 55
10/29/20XX 7:00:00 PM | 0.79167 | 6 | 53.9 | 68.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/29/20XX 8:00:00 PM | 0.83333 | 6 | 53.6 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/29/20XX 9:00:00 PM | 0.875 | 6 | 53.3 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/29/20XX 10:00:00 PM | 0.91667 | 6 | 53.1 | 67.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/29/20XX 11:00:00 PM | 0.95833 | 6 | 51.7 | 70.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/29/20XX 12:00:00 AM | 0 | 7 | 51 | 72.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/30/20XX 1:00:00 AM | 0.041667 | 7 | 51 | 69.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/30/20XX 2:00:00 AM | 0.083333 | 7 | 50.4 | 70.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/30/20XX 3:00:00 AM | 0.125 | 7 | 50 | 72.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/30/20XX 4:00:00 AM | 0.16667 | 7 | 49.5 | 73.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/30/20XX 5:00:00 AM | 0.20833 | 7 | 48.8 | 72.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/30/20XX 6:00:00 AM | 0.25 | 7 | 48.7 | 73.3 | 48.7 |  | 48.7 | 69.67 | 10.33 | 390474 | 390.474 | 67.34 | 12.66 | 478548 | 478.548 | 65.01 | 14.99 | 566622 | 566.622 | 62.68 | 17.32 | 654696 | 654.696 | 60.35 | 19.65 | 742770 | 742.77 | 58.02 | 21.98 | 830844 | 830.844 | 55.69 | 24.31 | 918918 | 918.918 | 53.36 | 26.64 | 1006992 | 1006.992 | 51.03 | 28.97 | 1095066 | 1095.066 | 48.7 | 31.3 | 1183140 | 1183.14 | 50
10/30/20XX 7:00:00 AM | 0.29167 | 7 | 48 | 73.5 | 48 |  | 48 | 69.6 | 10.4 | 393120 | 393.12 | 67.2 | 12.8 | 483840 | 483.84 | 64.8 | 15.2 | 574560 | 574.56 | 62.4 | 17.6 | 665280 | 665.28 | 60 | 20 | 756000 | 756 | 57.6 | 22.4 | 846720 | 846.72 | 55.2 | 24.8 | 937440 | 937.44 | 52.8 | 27.2 | 1028160 | 1028.16 | 50.4 | 29.6 | 1118880 | 1118.88 | 48 | 32 | 1209600 | 1209.6 | 50
10/30/20XX 8:00:00 AM | 0.33333 | 7 | 49.6 | 68.5 | 49.6 |  | 49.6 | 69.76 | 10.24 | 387072 | 387.072 | 67.52 | 12.48 | 471744 | 471.744 | 65.28 | 14.72 | 556416 | 556.416 | 63.04 | 16.96 | 641088 | 641.088 | 60.8 | 19.2 | 725760 | 725.76 | 58.56 | 21.44 | 810432 | 810.432 | 56.32 | 23.68 | 895104 | 895.104 | 54.08 | 25.92 | 979776 | 979.776 | 51.84 | 28.16 | 1064448 | 1064.448 | 49.6 | 30.4 | 1149120 | 1149.12 | 50
10/30/20XX 9:00:00 AM | 0.375 | 7 | 50.6 | 66 | 50.6 |  | 50.6 | 69.86 | 10.14 | 383292 | 383.292 | 67.72 | 12.28 | 464184 | 464.184 | 65.58 | 14.42 | 545076 | 545.076 | 63.44 | 16.56 | 625968 | 625.968 | 61.3 | 18.7 | 706860 | 706.86 | 59.16 | 20.84 | 787752 | 787.752 | 57.02 | 22.98 | 868644 | 868.644 | 54.88 | 25.12 | 949536 | 949.536 | 52.74 | 27.26 | 1030428 | 1030.428 | 50.6 | 29.4 | 1111320 | 1111.32 | 50
10/30/20XX 10:00:00 AM | 0.41667 | 7 | 52.2 | 62.4 | 52.2 |  | 52.2 | 70.02 | 9.98 | 377244 | 377.244 | 68.04 | 11.96 | 452088 | 452.088 | 66.06 | 13.94 | 526932 | 526.932 | 64.08 | 15.92 | 601776 | 601.776 | 62.1 | 17.9 | 676620 | 676.62 | 60.12 | 19.88 | 751464 | 751.464 | 58.14 | 21.86 | 826308 | 826.308 | 56.16 | 23.84 | 901152 | 901.152 | 54.18 | 25.82 | 975996 | 975.996 | 52.2 | 27.8 | 1050840 | 1050.84 | 50
10/30/20XX 11:00:00 AM | 0.45833 | 7 | 54.5 | 56.3 | 54.5 |  | 54.5 | 70.25 | 9.75 | 368550 | 368.55 | 68.5 | 11.5 | 434700 | 434.7 | 66.75 | 13.25 | 500850 | 500.85 | 65 | 15 | 567000 | 567 | 63.25 | 16.75 | 633150 | 633.15 | 61.5 | 18.5 | 699300 | 699.3 | 59.75 | 20.25 | 765450 | 765.45 | 58 | 22 | 831600 | 831.6 | 56.25 | 23.75 | 897750 | 897.75 | 54.5 | 25.5 | 963900 | 963.9 | 55
10/30/20XX 12:00:00 PM | 0.5 | 7 | 55.9 | 53.2 | 55.9 |  | 55.9 | 70.39 | 9.61 | 363258 | 363.258 | 68.78 | 11.22 | 424116 | 424.116 | 67.17 | 12.83 | 484974 | 484.974 | 65.56 | 14.44 | 545832 | 545.832 | 63.95 | 16.05 | 606690 | 606.69 | 62.34 | 17.66 | 667548 | 667.548 | 60.73 | 19.27 | 728406 | 728.406 | 59.12 | 20.88 | 789264 | 789.264 | 57.51 | 22.49 | 850122 | 850.122 | 55.9 | 24.1 | 910980 | 910.98 | 55
10/30/20XX 1:00:00 PM | 0.54167 | 7 | 56.8 | 51.5 | 56.8 |  | 56.8 | 70.48 | 9.52 | 359856 | 359.856 | 68.96 | 11.04 | 417312 | 417.312 | 67.44 | 12.56 | 474768 | 474.768 | 65.92 | 14.08 | 532224 | 532.224 | 64.4 | 15.6 | 589680 | 589.68 | 62.88 | 17.12 | 647136 | 647.136 | 61.36 | 18.64 | 704592 | 704.592 | 59.84 | 20.16 | 762048 | 762.048 | 58.32 | 21.68 | 819504 | 819.504 | 56.8 | 23.2 | 876960 | 876.96 | 55
10/30/20XX 2:00:00 PM | 0.58333 | 7 | 57.2 | 50.5 | 57.2 |  | 57.2 | 70.52 | 9.48 | 358344 | 358.344 | 69.04 | 10.96 | 414288 | 414.288 | 67.56 | 12.44 | 470232 | 470.232 | 66.08 | 13.92 | 526176 | 526.176 | 64.6 | 15.4 | 582120 | 582.12 | 63.12 | 16.88 | 638064 | 638.064 | 61.64 | 18.36 | 694008 | 694.008 | 60.16 | 19.84 | 749952 | 749.952 | 58.68 | 21.32 | 805896 | 805.896 | 57.2 | 22.8 | 861840 | 861.84 | 55
10/30/20XX 3:00:00 PM | 0.625 | 7 | 56.5 | 51.6 | 56.5 |  | 56.5 | 70.45 | 9.55 | 360990 | 360.99 | 68.9 | 11.1 | 419580 | 419.58 | 67.35 | 12.65 | 478170 | 478.17 | 65.8 | 14.2 | 536760 | 536.76 | 64.25 | 15.75 | 595350 | 595.35 | 62.7 | 17.3 | 653940 | 653.94 | 61.15 | 18.85 | 712530 | 712.53 | 59.6 | 20.4 | 771120 | 771.12 | 58.05 | 21.95 | 829710 | 829.71 | 56.5 | 23.5 | 888300 | 888.3 | 55
10/30/20XX 4:00:00 PM | 0.66667 | 7 | 54.8 | 55.4 | 54.8 |  | 54.8 | 70.28 | 9.72 | 367416 | 367.416 | 68.56 | 11.44 | 432432 | 432.432 | 66.84 | 13.16 | 497448 | 497.448 | 65.12 | 14.88 | 562464 | 562.464 | 63.4 | 16.6 | 627480 | 627.48 | 61.68 | 18.32 | 692496 | 692.496 | 59.96 | 20.04 | 757512 | 757.512 | 58.24 | 21.76 | 822528 | 822.528 | 56.52 | 23.48 | 887544 | 887.544 | 54.8 | 25.2 | 952560 | 952.56 | 55
10/30/20XX 5:00:00 PM | 0.70833 | 7 | 53.6 | 59.2 | 53.6 |  | 53.6 | 70.16 | 9.84 | 371952 | 371.952 | 68.32 | 11.68 | 441504 | 441.504 | 66.48 | 13.52 | 511056 | 511.056 | 64.64 | 15.36 | 580608 | 580.608 | 62.8 | 17.2 | 650160 | 650.16 | 60.96 | 19.04 | 719712 | 719.712 | 59.12 | 20.88 | 789264 | 789.264 | 57.28 | 22.72 | 858816 | 858.816 | 55.44 | 24.56 | 928368 | 928.368 | 53.6 | 26.4 | 997920 | 997.92 | 55
10/30/20XX 6:00:00 PM | 0.75 | 7 | 53.2 | 59.2 | 53.2 |  | 53.2 | 70.12 | 9.88 | 373464 | 373.464 | 68.24 | 11.76 | 444528 | 444.528 | 66.36 | 13.64 | 515592 | 515.592 | 64.48 | 15.52 | 586656 | 586.656 | 62.6 | 17.4 | 657720 | 657.72 | 60.72 | 19.28 | 728784 | 728.784 | 58.84 | 21.16 | 799848 | 799.848 | 56.96 | 23.04 | 870912 | 870.912 | 55.08 | 24.92 | 941976 | 941.976 | 53.2 | 26.8 | 1013040 | 1013.04 | 55
10/30/20XX 7:00:00 PM | 0.79167 | 7 | 52.8 | 60.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/30/20XX 8:00:00 PM | 0.83333 | 7 | 52.6 | 60.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/30/20XX 9:00:00 PM | 0.875 | 7 | 51.9 | 61.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/30/20XX 10:00:00 PM | 0.91667 | 7 | 50.8 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/30/20XX 11:00:00 PM | 0.95833 | 7 | 50.3 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/30/20XX 12:00:00 AM | 0 | 1 | 49.5 | 67.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/31/20XX 1:00:00 AM | 0.041667 | 1 | 49.1 | 67.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/31/20XX 2:00:00 AM | 0.083333 | 1 | 48.4 | 69.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/31/20XX 3:00:00 AM | 0.125 | 1 | 47.8 | 70.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/31/20XX 4:00:00 AM | 0.16667 | 1 | 47.5 | 71.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/31/20XX 5:00:00 AM | 0.20833 | 1 | 47.3 | 71.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/31/20XX 6:00:00 AM | 0.25 | 1 | 47.5 | 71.5 | 47.5 |  | 47.5 | 69.55 | 10.45 | 395010 | 395.01 | 67.1 | 12.9 | 487620 | 487.62 | 64.65 | 15.35 | 580230 | 580.23 | 62.2 | 17.8 | 672840 | 672.84 | 59.75 | 20.25 | 765450 | 765.45 | 57.3 | 22.7 | 858060 | 858.06 | 54.85 | 25.15 | 950670 | 950.67 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.95 | 30.05 | 1135890 | 1135.89 | 47.5 | 32.5 | 1228500 | 1228.5 | 45
10/31/20XX 7:00:00 AM | 0.29167 | 1 | 47.6 | 71.3 | 47.6 |  | 47.6 | 69.56 | 10.44 | 394632 | 394.632 | 67.12 | 12.88 | 486864 | 486.864 | 64.68 | 15.32 | 579096 | 579.096 | 62.24 | 17.76 | 671328 | 671.328 | 59.8 | 20.2 | 763560 | 763.56 | 57.36 | 22.64 | 855792 | 855.792 | 54.92 | 25.08 | 948024 | 948.024 | 52.48 | 27.52 | 1040256 | 1040.256 | 50.04 | 29.96 | 1132488 | 1132.488 | 47.6 | 32.4 | 1224720 | 1224.72 | 50
10/31/20XX 8:00:00 AM | 0.33333 | 1 | 49.6 | 67.2 | 49.6 |  | 49.6 | 69.76 | 10.24 | 387072 | 387.072 | 67.52 | 12.48 | 471744 | 471.744 | 65.28 | 14.72 | 556416 | 556.416 | 63.04 | 16.96 | 641088 | 641.088 | 60.8 | 19.2 | 725760 | 725.76 | 58.56 | 21.44 | 810432 | 810.432 | 56.32 | 23.68 | 895104 | 895.104 | 54.08 | 25.92 | 979776 | 979.776 | 51.84 | 28.16 | 1064448 | 1064.448 | 49.6 | 30.4 | 1149120 | 1149.12 | 50
10/31/20XX 9:00:00 AM | 0.375 | 1 | 51.6 | 63.4 | 51.6 |  | 51.6 | 69.96 | 10.04 | 379512 | 379.512 | 67.92 | 12.08 | 456624 | 456.624 | 65.88 | 14.12 | 533736 | 533.736 | 63.84 | 16.16 | 610848 | 610.848 | 61.8 | 18.2 | 687960 | 687.96 | 59.76 | 20.24 | 765072 | 765.072 | 57.72 | 22.28 | 842184 | 842.184 | 55.68 | 24.32 | 919296 | 919.296 | 53.64 | 26.36 | 996408 | 996.408 | 51.6 | 28.4 | 1073520 | 1073.52 | 50
10/31/20XX 10:00:00 AM | 0.41667 | 1 | 53.4 | 59.3 | 53.4 |  | 53.4 | 70.14 | 9.86 | 372708 | 372.708 | 68.28 | 11.72 | 443016 | 443.016 | 66.42 | 13.58 | 513324 | 513.324 | 64.56 | 15.44 | 583632 | 583.632 | 62.7 | 17.3 | 653940 | 653.94 | 60.84 | 19.16 | 724248 | 724.248 | 58.98 | 21.02 | 794556 | 794.556 | 57.12 | 22.88 | 864864 | 864.864 | 55.26 | 24.74 | 935172 | 935.172 | 53.4 | 26.6 | 1005480 | 1005.48 | 55
10/31/20XX 11:00:00 AM | 0.45833 | 1 | 55 | 58 | 55 |  | 55 | 70.3 | 9.7 | 366660 | 366.66 | 68.6 | 11.4 | 430920 | 430.92 | 66.9 | 13.1 | 495180 | 495.18 | 65.2 | 14.8 | 559440 | 559.44 | 63.5 | 16.5 | 623700 | 623.7 | 61.8 | 18.2 | 687960 | 687.96 | 60.1 | 19.9 | 752220 | 752.22 | 58.4 | 21.6 | 816480 | 816.48 | 56.7 | 23.3 | 880740 | 880.74 | 55 | 25 | 945000 | 945 | 55
10/31/20XX 12:00:00 PM | 0.5 | 1 | 56.6 | 55.6 | 56.6 |  | 56.6 | 70.46 | 9.54 | 360612 | 360.612 | 68.92 | 11.08 | 418824 | 418.824 | 67.38 | 12.62 | 477036 | 477.036 | 65.84 | 14.16 | 535248 | 535.248 | 64.3 | 15.7 | 593460 | 593.46 | 62.76 | 17.24 | 651672 | 651.672 | 61.22 | 18.78 | 709884 | 709.884 | 59.68 | 20.32 | 768096 | 768.096 | 58.14 | 21.86 | 826308 | 826.308 | 56.6 | 23.4 | 884520 | 884.52 | 55
10/31/20XX 1:00:00 PM | 0.54167 | 1 | 57.4 | 54.1 | 57.4 |  | 57.4 | 70.54 | 9.46 | 357588 | 357.588 | 69.08 | 10.92 | 412776 | 412.776 | 67.62 | 12.38 | 467964 | 467.964 | 66.16 | 13.84 | 523152 | 523.152 | 64.7 | 15.3 | 578340 | 578.34 | 63.24 | 16.76 | 633528 | 633.528 | 61.78 | 18.22 | 688716 | 688.716 | 60.32 | 19.68 | 743904 | 743.904 | 58.86 | 21.14 | 799092 | 799.092 | 57.4 | 22.6 | 854280 | 854.28 | 55
10/31/20XX 2:00:00 PM | 0.58333 | 1 | 56.6 | 54.9 | 56.6 |  | 56.6 | 70.46 | 9.54 | 360612 | 360.612 | 68.92 | 11.08 | 418824 | 418.824 | 67.38 | 12.62 | 477036 | 477.036 | 65.84 | 14.16 | 535248 | 535.248 | 64.3 | 15.7 | 593460 | 593.46 | 62.76 | 17.24 | 651672 | 651.672 | 61.22 | 18.78 | 709884 | 709.884 | 59.68 | 20.32 | 768096 | 768.096 | 58.14 | 21.86 | 826308 | 826.308 | 56.6 | 23.4 | 884520 | 884.52 | 55
10/31/20XX 3:00:00 PM | 0.625 | 1 | 56.7 | 55.1 | 56.7 |  | 56.7 | 70.47 | 9.53 | 360234 | 360.234 | 68.94 | 11.06 | 418068 | 418.068 | 67.41 | 12.59 | 475902 | 475.902 | 65.88 | 14.12 | 533736 | 533.736 | 64.35 | 15.65 | 591570 | 591.57 | 62.82 | 17.18 | 649404 | 649.404 | 61.29 | 18.71 | 707238 | 707.238 | 59.76 | 20.24 | 765072 | 765.072 | 58.23 | 21.77 | 822906 | 822.906 | 56.7 | 23.3 | 880740 | 880.74 | 55
10/31/20XX 4:00:00 PM | 0.66667 | 1 | 56 | 57.5 | 56 |  | 56 | 70.4 | 9.6 | 362880 | 362.88 | 68.8 | 11.2 | 423360 | 423.36 | 67.2 | 12.8 | 483840 | 483.84 | 65.6 | 14.4 | 544320 | 544.32 | 64 | 16 | 604800 | 604.8 | 62.4 | 17.6 | 665280 | 665.28 | 60.8 | 19.2 | 725760 | 725.76 | 59.2 | 20.8 | 786240 | 786.24 | 57.6 | 22.4 | 846720 | 846.72 | 56 | 24 | 907200 | 907.2 | 55
10/31/20XX 5:00:00 PM | 0.70833 | 1 | 54.8 | 61.4 | 54.8 |  | 54.8 | 70.28 | 9.72 | 367416 | 367.416 | 68.56 | 11.44 | 432432 | 432.432 | 66.84 | 13.16 | 497448 | 497.448 | 65.12 | 14.88 | 562464 | 562.464 | 63.4 | 16.6 | 627480 | 627.48 | 61.68 | 18.32 | 692496 | 692.496 | 59.96 | 20.04 | 757512 | 757.512 | 58.24 | 21.76 | 822528 | 822.528 | 56.52 | 23.48 | 887544 | 887.544 | 54.8 | 25.2 | 952560 | 952.56 | 55
10/31/20XX 6:00:00 PM | 0.75 | 1 | 54.9 | 61.6 | 54.9 |  | 54.9 | 70.29 | 9.71 | 367038 | 367.038 | 68.58 | 11.42 | 431676 | 431.676 | 66.87 | 13.13 | 496314 | 496.314 | 65.16 | 14.84 | 560952 | 560.952 | 63.45 | 16.55 | 625590 | 625.59 | 61.74 | 18.26 | 690228 | 690.228 | 60.03 | 19.97 | 754866 | 754.866 | 58.32 | 21.68 | 819504 | 819.504 | 56.61 | 23.39 | 884142 | 884.142 | 54.9 | 25.1 | 948780 | 948.78 | 55
10/31/20XX 7:00:00 PM | 0.79167 | 1 | 54.1 | 63.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/31/20XX 8:00:00 PM | 0.83333 | 1 | 53.6 | 62.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/31/20XX 9:00:00 PM | 0.875 | 1 | 52.7 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/31/20XX 10:00:00 PM | 0.91667 | 1 | 52.1 | 64.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/31/20XX 11:00:00 PM | 0.95833 | 1 | 51.4 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10/31/20XX 12:00:00 AM | 0 | 2 | 50.8 | 69 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/1/20XX 1:00:00 AM | 0.041667 | 2 | 50.6 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/1/20XX 2:00:00 AM | 0.083333 | 2 | 50.2 | 68.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/1/20XX 3:00:00 AM | 0.125 | 2 | 50.1 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/1/20XX 4:00:00 AM | 0.16667 | 2 | 49.6 | 71.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/1/20XX 5:00:00 AM | 0.20833 | 2 | 49.2 | 71.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/1/20XX 6:00:00 AM | 0.25 | 2 | 49.2 | 71.8 | 49.2 |  | 49.2 | 69.72 | 10.28 | 388584 | 388.584 | 67.44 | 12.56 | 474768 | 474.768 | 65.16 | 14.84 | 560952 | 560.952 | 62.88 | 17.12 | 647136 | 647.136 | 60.6 | 19.4 | 733320 | 733.32 | 58.32 | 21.68 | 819504 | 819.504 | 56.04 | 23.96 | 905688 | 905.688 | 53.76 | 26.24 | 991872 | 991.872 | 51.48 | 28.52 | 1078056 | 1078.056 | 49.2 | 30.8 | 1164240 | 1164.24 | 50
11/1/20XX 7:00:00 AM | 0.29167 | 2 | 49.5 | 70.7 | 49.5 |  | 49.5 | 69.75 | 10.25 | 387450 | 387.45 | 67.5 | 12.5 | 472500 | 472.5 | 65.25 | 14.75 | 557550 | 557.55 | 63 | 17 | 642600 | 642.6 | 60.75 | 19.25 | 727650 | 727.65 | 58.5 | 21.5 | 812700 | 812.7 | 56.25 | 23.75 | 897750 | 897.75 | 54 | 26 | 982800 | 982.8 | 51.75 | 28.25 | 1067850 | 1067.85 | 49.5 | 30.5 | 1152900 | 1152.9 | 50
11/1/20XX 8:00:00 AM | 0.33333 | 2 | 50.4 | 70.7 | 50.4 |  | 50.4 | 69.84 | 10.16 | 384048 | 384.048 | 67.68 | 12.32 | 465696 | 465.696 | 65.52 | 14.48 | 547344 | 547.344 | 63.36 | 16.64 | 628992 | 628.992 | 61.2 | 18.8 | 710640 | 710.64 | 59.04 | 20.96 | 792288 | 792.288 | 56.88 | 23.12 | 873936 | 873.936 | 54.72 | 25.28 | 955584 | 955.584 | 52.56 | 27.44 | 1037232 | 1037.232 | 50.4 | 29.6 | 1118880 | 1118.88 | 50
11/1/20XX 9:00:00 AM | 0.375 | 2 | 51.7 | 68.7 | 51.7 |  | 51.7 | 69.97 | 10.03 | 379134 | 379.134 | 67.94 | 12.06 | 455868 | 455.868 | 65.91 | 14.09 | 532602 | 532.602 | 63.88 | 16.12 | 609336 | 609.336 | 61.85 | 18.15 | 686070 | 686.07 | 59.82 | 20.18 | 762804 | 762.804 | 57.79 | 22.21 | 839538 | 839.538 | 55.76 | 24.24 | 916272 | 916.272 | 53.73 | 26.27 | 993006 | 993.006 | 51.7 | 28.3 | 1069740 | 1069.74 | 50
11/1/20XX 10:00:00 AM | 0.41667 | 2 | 51.7 | 66 | 51.7 |  | 51.7 | 69.97 | 10.03 | 379134 | 379.134 | 67.94 | 12.06 | 455868 | 455.868 | 65.91 | 14.09 | 532602 | 532.602 | 63.88 | 16.12 | 609336 | 609.336 | 61.85 | 18.15 | 686070 | 686.07 | 59.82 | 20.18 | 762804 | 762.804 | 57.79 | 22.21 | 839538 | 839.538 | 55.76 | 24.24 | 916272 | 916.272 | 53.73 | 26.27 | 993006 | 993.006 | 51.7 | 28.3 | 1069740 | 1069.74 | 50
11/1/20XX 11:00:00 AM | 0.45833 | 2 | 53.8 | 61.6 | 53.8 |  | 53.8 | 70.18 | 9.82 | 371196 | 371.196 | 68.36 | 11.64 | 439992 | 439.992 | 66.54 | 13.46 | 508788 | 508.788 | 64.72 | 15.28 | 577584 | 577.584 | 62.9 | 17.1 | 646380 | 646.38 | 61.08 | 18.92 | 715176 | 715.176 | 59.26 | 20.74 | 783972 | 783.972 | 57.44 | 22.56 | 852768 | 852.768 | 55.62 | 24.38 | 921564 | 921.564 | 53.8 | 26.2 | 990360 | 990.36 | 55
11/1/20XX 12:00:00 PM | 0.5 | 2 | 55.3 | 57.2 | 55.3 |  | 55.3 | 70.33 | 9.67 | 365526 | 365.526 | 68.66 | 11.34 | 428652 | 428.652 | 66.99 | 13.01 | 491778 | 491.778 | 65.32 | 14.68 | 554904 | 554.904 | 63.65 | 16.35 | 618030 | 618.03 | 61.98 | 18.02 | 681156 | 681.156 | 60.31 | 19.69 | 744282 | 744.282 | 58.64 | 21.36 | 807408 | 807.408 | 56.97 | 23.03 | 870534 | 870.534 | 55.3 | 24.7 | 933660 | 933.66 | 55
11/1/20XX 1:00:00 PM | 0.54167 | 2 | 56.1 | 58 | 56.1 |  | 56.1 | 70.41 | 9.59 | 362502 | 362.502 | 68.82 | 11.18 | 422604 | 422.604 | 67.23 | 12.77 | 482706 | 482.706 | 65.64 | 14.36 | 542808 | 542.808 | 64.05 | 15.95 | 602910 | 602.91 | 62.46 | 17.54 | 663012 | 663.012 | 60.87 | 19.13 | 723114 | 723.114 | 59.28 | 20.72 | 783216 | 783.216 | 57.69 | 22.31 | 843318 | 843.318 | 56.1 | 23.9 | 903420 | 903.42 | 55
11/1/20XX 2:00:00 PM | 0.58333 | 2 | 56.6 | 55.8 | 56.6 |  | 56.6 | 70.46 | 9.54 | 360612 | 360.612 | 68.92 | 11.08 | 418824 | 418.824 | 67.38 | 12.62 | 477036 | 477.036 | 65.84 | 14.16 | 535248 | 535.248 | 64.3 | 15.7 | 593460 | 593.46 | 62.76 | 17.24 | 651672 | 651.672 | 61.22 | 18.78 | 709884 | 709.884 | 59.68 | 20.32 | 768096 | 768.096 | 58.14 | 21.86 | 826308 | 826.308 | 56.6 | 23.4 | 884520 | 884.52 | 55
11/1/20XX 3:00:00 PM | 0.625 | 2 | 56.3 | 56.8 | 56.3 |  | 56.3 | 70.43 | 9.57 | 361746 | 361.746 | 68.86 | 11.14 | 421092 | 421.092 | 67.29 | 12.71 | 480438 | 480.438 | 65.72 | 14.28 | 539784 | 539.784 | 64.15 | 15.85 | 599130 | 599.13 | 62.58 | 17.42 | 658476 | 658.476 | 61.01 | 18.99 | 717822 | 717.822 | 59.44 | 20.56 | 777168 | 777.168 | 57.87 | 22.13 | 836514 | 836.514 | 56.3 | 23.7 | 895860 | 895.86 | 55
11/1/20XX 4:00:00 PM | 0.66667 | 2 | 56.5 | 55.3 | 56.5 |  | 56.5 | 70.45 | 9.55 | 360990 | 360.99 | 68.9 | 11.1 | 419580 | 419.58 | 67.35 | 12.65 | 478170 | 478.17 | 65.8 | 14.2 | 536760 | 536.76 | 64.25 | 15.75 | 595350 | 595.35 | 62.7 | 17.3 | 653940 | 653.94 | 61.15 | 18.85 | 712530 | 712.53 | 59.6 | 20.4 | 771120 | 771.12 | 58.05 | 21.95 | 829710 | 829.71 | 56.5 | 23.5 | 888300 | 888.3 | 55
11/1/20XX 5:00:00 PM | 0.70833 | 2 | 55.6 | 56.4 | 55.6 |  | 55.6 | 70.36 | 9.64 | 364392 | 364.392 | 68.72 | 11.28 | 426384 | 426.384 | 67.08 | 12.92 | 488376 | 488.376 | 65.44 | 14.56 | 550368 | 550.368 | 63.8 | 16.2 | 612360 | 612.36 | 62.16 | 17.84 | 674352 | 674.352 | 60.52 | 19.48 | 736344 | 736.344 | 58.88 | 21.12 | 798336 | 798.336 | 57.24 | 22.76 | 860328 | 860.328 | 55.6 | 24.4 | 922320 | 922.32 | 55
11/1/20XX 6:00:00 PM | 0.75 | 2 | 54.5 | 60.5 | 54.5 |  | 54.5 | 70.25 | 9.75 | 368550 | 368.55 | 68.5 | 11.5 | 434700 | 434.7 | 66.75 | 13.25 | 500850 | 500.85 | 65 | 15 | 567000 | 567 | 63.25 | 16.75 | 633150 | 633.15 | 61.5 | 18.5 | 699300 | 699.3 | 59.75 | 20.25 | 765450 | 765.45 | 58 | 22 | 831600 | 831.6 | 56.25 | 23.75 | 897750 | 897.75 | 54.5 | 25.5 | 963900 | 963.9 | 55
11/1/20XX 7:00:00 PM | 0.79167 | 2 | 53.8 | 63.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/1/20XX 8:00:00 PM | 0.83333 | 2 | 53.2 | 65.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/1/20XX 9:00:00 PM | 0.875 | 2 | 52.8 | 67.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/1/20XX 10:00:00 PM | 0.91667 | 2 | 52.7 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/1/20XX 11:00:00 PM | 0.95833 | 2 | 52.8 | 69.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/1/20XX 12:00:00 AM | 0 | 3 | 52.3 | 71.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/2/20XX 1:00:00 AM | 0.041667 | 3 | 52 | 70.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/2/20XX 2:00:00 AM | 0.083333 | 3 | 51.8 | 69.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/2/20XX 3:00:00 AM | 0.125 | 3 | 51.7 | 71.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/2/20XX 4:00:00 AM | 0.16667 | 3 | 51.3 | 72.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/2/20XX 5:00:00 AM | 0.20833 | 3 | 51.1 | 71.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/2/20XX 6:00:00 AM | 0.25 | 3 | 50.9 | 72 | 50.9 |  | 50.9 | 69.89 | 10.11 | 382158 | 382.158 | 67.78 | 12.22 | 461916 | 461.916 | 65.67 | 14.33 | 541674 | 541.674 | 63.56 | 16.44 | 621432 | 621.432 | 61.45 | 18.55 | 701190 | 701.19 | 59.34 | 20.66 | 780948 | 780.948 | 57.23 | 22.77 | 860706 | 860.706 | 55.12 | 24.88 | 940464 | 940.464 | 53.01 | 26.99 | 1020222 | 1020.222 | 50.9 | 29.1 | 1099980 | 1099.98 | 50
11/2/20XX 7:00:00 AM | 0.29167 | 3 | 51.3 | 70.5 | 51.3 |  | 51.3 | 69.93 | 10.07 | 380646 | 380.646 | 67.86 | 12.14 | 458892 | 458.892 | 65.79 | 14.21 | 537138 | 537.138 | 63.72 | 16.28 | 615384 | 615.384 | 61.65 | 18.35 | 693630 | 693.63 | 59.58 | 20.42 | 771876 | 771.876 | 57.51 | 22.49 | 850122 | 850.122 | 55.44 | 24.56 | 928368 | 928.368 | 53.37 | 26.63 | 1006614 | 1006.614 | 51.3 | 28.7 | 1084860 | 1084.86 | 50
11/2/20XX 8:00:00 AM | 0.33333 | 3 | 52 | 70.6 | 52 |  | 52 | 70 | 10 | 378000 | 378 | 68 | 12 | 453600 | 453.6 | 66 | 14 | 529200 | 529.2 | 64 | 16 | 604800 | 604.8 | 62 | 18 | 680400 | 680.4 | 60 | 20 | 756000 | 756 | 58 | 22 | 831600 | 831.6 | 56 | 24 | 907200 | 907.2 | 54 | 26 | 982800 | 982.8 | 52 | 28 | 1058400 | 1058.4 | 50
11/2/20XX 9:00:00 AM | 0.375 | 3 | 53.6 | 66.2 | 53.6 |  | 53.6 | 70.16 | 9.84 | 371952 | 371.952 | 68.32 | 11.68 | 441504 | 441.504 | 66.48 | 13.52 | 511056 | 511.056 | 64.64 | 15.36 | 580608 | 580.608 | 62.8 | 17.2 | 650160 | 650.16 | 60.96 | 19.04 | 719712 | 719.712 | 59.12 | 20.88 | 789264 | 789.264 | 57.28 | 22.72 | 858816 | 858.816 | 55.44 | 24.56 | 928368 | 928.368 | 53.6 | 26.4 | 997920 | 997.92 | 55
11/2/20XX 10:00:00 AM | 0.41667 | 3 | 55.4 | 62.2 | 55.4 |  | 55.4 | 70.34 | 9.66 | 365148 | 365.148 | 68.68 | 11.32 | 427896 | 427.896 | 67.02 | 12.98 | 490644 | 490.644 | 65.36 | 14.64 | 553392 | 553.392 | 63.7 | 16.3 | 616140 | 616.14 | 62.04 | 17.96 | 678888 | 678.888 | 60.38 | 19.62 | 741636 | 741.636 | 58.72 | 21.28 | 804384 | 804.384 | 57.06 | 22.94 | 867132 | 867.132 | 55.4 | 24.6 | 929880 | 929.88 | 55
11/2/20XX 11:00:00 AM | 0.45833 | 3 | 57 | 58.7 | 57 |  | 57 | 70.5 | 9.5 | 359100 | 359.1 | 69 | 11 | 415800 | 415.8 | 67.5 | 12.5 | 472500 | 472.5 | 66 | 14 | 529200 | 529.2 | 64.5 | 15.5 | 585900 | 585.9 | 63 | 17 | 642600 | 642.6 | 61.5 | 18.5 | 699300 | 699.3 | 60 | 20 | 756000 | 756 | 58.5 | 21.5 | 812700 | 812.7 | 57 | 23 | 869400 | 869.4 | 55
11/2/20XX 12:00:00 PM | 0.5 | 3 | 58.7 | 55.9 | 58.7 |  | 58.7 | 70.67 | 9.33 | 352674 | 352.674 | 69.34 | 10.66 | 402948 | 402.948 | 68.01 | 11.99 | 453222 | 453.222 | 66.68 | 13.32 | 503496 | 503.496 | 65.35 | 14.65 | 553770 | 553.77 | 64.02 | 15.98 | 604044 | 604.044 | 62.69 | 17.31 | 654318 | 654.318 | 61.36 | 18.64 | 704592 | 704.592 | 60.03 | 19.97 | 754866 | 754.866 | 58.7 | 21.3 | 805140 | 805.14 | 60
11/2/20XX 1:00:00 PM | 0.54167 | 3 | 59.3 | 52.6 | 59.3 |  | 59.3 | 70.73 | 9.27 | 350406 | 350.406 | 69.46 | 10.54 | 398412 | 398.412 | 68.19 | 11.81 | 446418 | 446.418 | 66.92 | 13.08 | 494424 | 494.424 | 65.65 | 14.35 | 542430 | 542.43 | 64.38 | 15.62 | 590436 | 590.436 | 63.11 | 16.89 | 638442 | 638.442 | 61.84 | 18.16 | 686448 | 686.448 | 60.57 | 19.43 | 734454 | 734.454 | 59.3 | 20.7 | 782460 | 782.46 | 60
11/2/20XX 2:00:00 PM | 0.58333 | 3 | 59.4 | 51.9 | 59.4 |  | 59.4 | 70.74 | 9.26 | 350028 | 350.028 | 69.48 | 10.52 | 397656 | 397.656 | 68.22 | 11.78 | 445284 | 445.284 | 66.96 | 13.04 | 492912 | 492.912 | 65.7 | 14.3 | 540540 | 540.54 | 64.44 | 15.56 | 588168 | 588.168 | 63.18 | 16.82 | 635796 | 635.796 | 61.92 | 18.08 | 683424 | 683.424 | 60.66 | 19.34 | 731052 | 731.052 | 59.4 | 20.6 | 778680 | 778.68 | 60
11/2/20XX 3:00:00 PM | 0.625 | 3 | 59.3 | 51.6 | 59.3 |  | 59.3 | 70.73 | 9.27 | 350406 | 350.406 | 69.46 | 10.54 | 398412 | 398.412 | 68.19 | 11.81 | 446418 | 446.418 | 66.92 | 13.08 | 494424 | 494.424 | 65.65 | 14.35 | 542430 | 542.43 | 64.38 | 15.62 | 590436 | 590.436 | 63.11 | 16.89 | 638442 | 638.442 | 61.84 | 18.16 | 686448 | 686.448 | 60.57 | 19.43 | 734454 | 734.454 | 59.3 | 20.7 | 782460 | 782.46 | 60
11/2/20XX 4:00:00 PM | 0.66667 | 3 | 58.7 | 54.1 | 58.7 |  | 58.7 | 70.67 | 9.33 | 352674 | 352.674 | 69.34 | 10.66 | 402948 | 402.948 | 68.01 | 11.99 | 453222 | 453.222 | 66.68 | 13.32 | 503496 | 503.496 | 65.35 | 14.65 | 553770 | 553.77 | 64.02 | 15.98 | 604044 | 604.044 | 62.69 | 17.31 | 654318 | 654.318 | 61.36 | 18.64 | 704592 | 704.592 | 60.03 | 19.97 | 754866 | 754.866 | 58.7 | 21.3 | 805140 | 805.14 | 60
11/2/20XX 5:00:00 PM | 0.70833 | 3 | 57.8 | 54.9 | 57.8 |  | 57.8 | 70.58 | 9.42 | 356076 | 356.076 | 69.16 | 10.84 | 409752 | 409.752 | 67.74 | 12.26 | 463428 | 463.428 | 66.32 | 13.68 | 517104 | 517.104 | 64.9 | 15.1 | 570780 | 570.78 | 63.48 | 16.52 | 624456 | 624.456 | 62.06 | 17.94 | 678132 | 678.132 | 60.64 | 19.36 | 731808 | 731.808 | 59.22 | 20.78 | 785484 | 785.484 | 57.8 | 22.2 | 839160 | 839.16 | 60
11/2/20XX 6:00:00 PM | 0.75 | 3 | 56.2 | 58.8 | 56.2 |  | 56.2 | 70.42 | 9.58 | 362124 | 362.124 | 68.84 | 11.16 | 421848 | 421.848 | 67.26 | 12.74 | 481572 | 481.572 | 65.68 | 14.32 | 541296 | 541.296 | 64.1 | 15.9 | 601020 | 601.02 | 62.52 | 17.48 | 660744 | 660.744 | 60.94 | 19.06 | 720468 | 720.468 | 59.36 | 20.64 | 780192 | 780.192 | 57.78 | 22.22 | 839916 | 839.916 | 56.2 | 23.8 | 899640 | 899.64 | 55
11/2/20XX 7:00:00 PM | 0.79167 | 3 | 55.7 | 59.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/2/20XX 8:00:00 PM | 0.83333 | 3 | 54.9 | 60.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/2/20XX 9:00:00 PM | 0.875 | 3 | 54.2 | 61.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/2/20XX 10:00:00 PM | 0.91667 | 3 | 53.3 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/2/20XX 11:00:00 PM | 0.95833 | 3 | 53 | 66.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/2/20XX 12:00:00 AM | 0 | 4 | 52.5 | 68.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/3/20XX 1:00:00 AM | 0.041667 | 4 | 52 | 68.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/3/20XX 2:00:00 AM | 0.083333 | 4 | 51.1 | 69.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/3/20XX 3:00:00 AM | 0.125 | 4 | 50.7 | 71.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/3/20XX 4:00:00 AM | 0.16667 | 4 | 50.4 | 72.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/3/20XX 5:00:00 AM | 0.20833 | 4 | 50.1 | 74.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/3/20XX 6:00:00 AM | 0.25 | 4 | 49.4 | 74.6 | 49.4 |  | 49.4 | 69.74 | 10.26 | 387828 | 387.828 | 67.48 | 12.52 | 473256 | 473.256 | 65.22 | 14.78 | 558684 | 558.684 | 62.96 | 17.04 | 644112 | 644.112 | 60.7 | 19.3 | 729540 | 729.54 | 58.44 | 21.56 | 814968 | 814.968 | 56.18 | 23.82 | 900396 | 900.396 | 53.92 | 26.08 | 985824 | 985.824 | 51.66 | 28.34 | 1071252 | 1071.252 | 49.4 | 30.6 | 1156680 | 1156.68 | 50
11/3/20XX 7:00:00 AM | 0.29167 | 4 | 49.7 | 74.2 | 49.7 |  | 49.7 | 69.77 | 10.23 | 386694 | 386.694 | 67.54 | 12.46 | 470988 | 470.988 | 65.31 | 14.69 | 555282 | 555.282 | 63.08 | 16.92 | 639576 | 639.576 | 60.85 | 19.15 | 723870 | 723.87 | 58.62 | 21.38 | 808164 | 808.164 | 56.39 | 23.61 | 892458 | 892.458 | 54.16 | 25.84 | 976752 | 976.752 | 51.93 | 28.07 | 1061046 | 1061.046 | 49.7 | 30.3 | 1145340 | 1145.34 | 50
11/3/20XX 8:00:00 AM | 0.33333 | 4 | 51.4 | 70.8 | 51.4 |  | 51.4 | 69.94 | 10.06 | 380268 | 380.268 | 67.88 | 12.12 | 458136 | 458.136 | 65.82 | 14.18 | 536004 | 536.004 | 63.76 | 16.24 | 613872 | 613.872 | 61.7 | 18.3 | 691740 | 691.74 | 59.64 | 20.36 | 769608 | 769.608 | 57.58 | 22.42 | 847476 | 847.476 | 55.52 | 24.48 | 925344 | 925.344 | 53.46 | 26.54 | 1003212 | 1003.212 | 51.4 | 28.6 | 1081080 | 1081.08 | 50
11/3/20XX 9:00:00 AM | 0.375 | 4 | 52.6 | 66.3 | 52.6 |  | 52.6 | 70.06 | 9.94 | 375732 | 375.732 | 68.12 | 11.88 | 449064 | 449.064 | 66.18 | 13.82 | 522396 | 522.396 | 64.24 | 15.76 | 595728 | 595.728 | 62.3 | 17.7 | 669060 | 669.06 | 60.36 | 19.64 | 742392 | 742.392 | 58.42 | 21.58 | 815724 | 815.724 | 56.48 | 23.52 | 889056 | 889.056 | 54.54 | 25.46 | 962388 | 962.388 | 52.6 | 27.4 | 1035720 | 1035.72 | 55
11/3/20XX 10:00:00 AM | 0.41667 | 4 | 54.2 | 60 | 54.2 |  | 54.2 | 70.22 | 9.78 | 369684 | 369.684 | 68.44 | 11.56 | 436968 | 436.968 | 66.66 | 13.34 | 504252 | 504.252 | 64.88 | 15.12 | 571536 | 571.536 | 63.1 | 16.9 | 638820 | 638.82 | 61.32 | 18.68 | 706104 | 706.104 | 59.54 | 20.46 | 773388 | 773.388 | 57.76 | 22.24 | 840672 | 840.672 | 55.98 | 24.02 | 907956 | 907.956 | 54.2 | 25.8 | 975240 | 975.24 | 55
11/3/20XX 11:00:00 AM | 0.45833 | 4 | 56.3 | 56.1 | 56.3 |  | 56.3 | 70.43 | 9.57 | 361746 | 361.746 | 68.86 | 11.14 | 421092 | 421.092 | 67.29 | 12.71 | 480438 | 480.438 | 65.72 | 14.28 | 539784 | 539.784 | 64.15 | 15.85 | 599130 | 599.13 | 62.58 | 17.42 | 658476 | 658.476 | 61.01 | 18.99 | 717822 | 717.822 | 59.44 | 20.56 | 777168 | 777.168 | 57.87 | 22.13 | 836514 | 836.514 | 56.3 | 23.7 | 895860 | 895.86 | 55
11/3/20XX 12:00:00 PM | 0.5 | 4 | 57.9 | 52.7 | 57.9 |  | 57.9 | 70.59 | 9.41 | 355698 | 355.698 | 69.18 | 10.82 | 408996 | 408.996 | 67.77 | 12.23 | 462294 | 462.294 | 66.36 | 13.64 | 515592 | 515.592 | 64.95 | 15.05 | 568890 | 568.89 | 63.54 | 16.46 | 622188 | 622.188 | 62.13 | 17.87 | 675486 | 675.486 | 60.72 | 19.28 | 728784 | 728.784 | 59.31 | 20.69 | 782082 | 782.082 | 57.9 | 22.1 | 835380 | 835.38 | 60
11/3/20XX 1:00:00 PM | 0.54167 | 4 | 59.6 | 48.1 | 59.6 |  | 59.6 | 70.76 | 9.24 | 349272 | 349.272 | 69.52 | 10.48 | 396144 | 396.144 | 68.28 | 11.72 | 443016 | 443.016 | 67.04 | 12.96 | 489888 | 489.888 | 65.8 | 14.2 | 536760 | 536.76 | 64.56 | 15.44 | 583632 | 583.632 | 63.32 | 16.68 | 630504 | 630.504 | 62.08 | 17.92 | 677376 | 677.376 | 60.84 | 19.16 | 724248 | 724.248 | 59.6 | 20.4 | 771120 | 771.12 | 60
11/3/20XX 2:00:00 PM | 0.58333 | 4 | 60.2 | 47.1 | 60.2 |  | 60.2 | 70.82 | 9.18 | 347004 | 347.004 | 69.64 | 10.36 | 391608 | 391.608 | 68.46 | 11.54 | 436212 | 436.212 | 67.28 | 12.72 | 480816 | 480.816 | 66.1 | 13.9 | 525420 | 525.42 | 64.92 | 15.08 | 570024 | 570.024 | 63.74 | 16.26 | 614628 | 614.628 | 62.56 | 17.44 | 659232 | 659.232 | 61.38 | 18.62 | 703836 | 703.836 | 60.2 | 19.8 | 748440 | 748.44 | 60
11/3/20XX 3:00:00 PM | 0.625 | 4 | 60.2 | 46.5 | 60.2 |  | 60.2 | 70.82 | 9.18 | 347004 | 347.004 | 69.64 | 10.36 | 391608 | 391.608 | 68.46 | 11.54 | 436212 | 436.212 | 67.28 | 12.72 | 480816 | 480.816 | 66.1 | 13.9 | 525420 | 525.42 | 64.92 | 15.08 | 570024 | 570.024 | 63.74 | 16.26 | 614628 | 614.628 | 62.56 | 17.44 | 659232 | 659.232 | 61.38 | 18.62 | 703836 | 703.836 | 60.2 | 19.8 | 748440 | 748.44 | 60
11/3/20XX 4:00:00 PM | 0.66667 | 4 | 59.3 | 47.5 | 59.3 |  | 59.3 | 70.73 | 9.27 | 350406 | 350.406 | 69.46 | 10.54 | 398412 | 398.412 | 68.19 | 11.81 | 446418 | 446.418 | 66.92 | 13.08 | 494424 | 494.424 | 65.65 | 14.35 | 542430 | 542.43 | 64.38 | 15.62 | 590436 | 590.436 | 63.11 | 16.89 | 638442 | 638.442 | 61.84 | 18.16 | 686448 | 686.448 | 60.57 | 19.43 | 734454 | 734.454 | 59.3 | 20.7 | 782460 | 782.46 | 60
11/3/20XX 5:00:00 PM | 0.70833 | 4 | 57.8 | 48.7 | 57.8 |  | 57.8 | 70.58 | 9.42 | 356076 | 356.076 | 69.16 | 10.84 | 409752 | 409.752 | 67.74 | 12.26 | 463428 | 463.428 | 66.32 | 13.68 | 517104 | 517.104 | 64.9 | 15.1 | 570780 | 570.78 | 63.48 | 16.52 | 624456 | 624.456 | 62.06 | 17.94 | 678132 | 678.132 | 60.64 | 19.36 | 731808 | 731.808 | 59.22 | 20.78 | 785484 | 785.484 | 57.8 | 22.2 | 839160 | 839.16 | 60
11/3/20XX 6:00:00 PM | 0.75 | 4 | 55.8 | 50.2 | 55.8 |  | 55.8 | 70.38 | 9.62 | 363636 | 363.636 | 68.76 | 11.24 | 424872 | 424.872 | 67.14 | 12.86 | 486108 | 486.108 | 65.52 | 14.48 | 547344 | 547.344 | 63.9 | 16.1 | 608580 | 608.58 | 62.28 | 17.72 | 669816 | 669.816 | 60.66 | 19.34 | 731052 | 731.052 | 59.04 | 20.96 | 792288 | 792.288 | 57.42 | 22.58 | 853524 | 853.524 | 55.8 | 24.2 | 914760 | 914.76 | 55
11/3/20XX 7:00:00 PM | 0.79167 | 4 | 54.2 | 50.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/3/20XX 8:00:00 PM | 0.83333 | 4 | 53 | 50.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/3/20XX 9:00:00 PM | 0.875 | 4 | 52.5 | 51.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/3/20XX 10:00:00 PM | 0.91667 | 4 | 51.6 | 52.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/3/20XX 11:00:00 PM | 0.95833 | 4 | 50.6 | 54.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/3/20XX 12:00:00 AM | 0 | 5 | 49.9 | 55.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/4/20XX 1:00:00 AM | 0.041667 | 5 | 49.5 | 56.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/4/20XX 2:00:00 AM | 0.083333 | 5 | 48.6 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/4/20XX 3:00:00 AM | 0.125 | 5 | 48.2 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/4/20XX 4:00:00 AM | 0.16667 | 5 | 47.9 | 61 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/4/20XX 5:00:00 AM | 0.20833 | 5 | 47.4 | 63.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/4/20XX 6:00:00 AM | 0.25 | 5 | 46.9 | 64.4 | 46.9 |  | 46.9 | 69.49 | 10.51 | 397278 | 397.278 | 66.98 | 13.02 | 492156 | 492.156 | 64.47 | 15.53 | 587034 | 587.034 | 61.96 | 18.04 | 681912 | 681.912 | 59.45 | 20.55 | 776790 | 776.79 | 56.94 | 23.06 | 871668 | 871.668 | 54.43 | 25.57 | 966546 | 966.546 | 51.92 | 28.08 | 1061424 | 1061.424 | 49.41 | 30.59 | 1156302 | 1156.302 | 46.9 | 33.1 | 1251180 | 1251.18 | 45
11/4/20XX 7:00:00 AM | 0.29167 | 5 | 46.6 | 64 | 46.6 |  | 46.6 | 69.46 | 10.54 | 398412 | 398.412 | 66.92 | 13.08 | 494424 | 494.424 | 64.38 | 15.62 | 590436 | 590.436 | 61.84 | 18.16 | 686448 | 686.448 | 59.3 | 20.7 | 782460 | 782.46 | 56.76 | 23.24 | 878472 | 878.472 | 54.22 | 25.78 | 974484 | 974.484 | 51.68 | 28.32 | 1070496 | 1070.496 | 49.14 | 30.86 | 1166508 | 1166.508 | 46.6 | 33.4 | 1262520 | 1262.52 | 45
11/4/20XX 8:00:00 AM | 0.33333 | 5 | 47.8 | 61.2 | 47.8 |  | 47.8 | 69.58 | 10.42 | 393876 | 393.876 | 67.16 | 12.84 | 485352 | 485.352 | 64.74 | 15.26 | 576828 | 576.828 | 62.32 | 17.68 | 668304 | 668.304 | 59.9 | 20.1 | 759780 | 759.78 | 57.48 | 22.52 | 851256 | 851.256 | 55.06 | 24.94 | 942732 | 942.732 | 52.64 | 27.36 | 1034208 | 1034.208 | 50.22 | 29.78 | 1125684 | 1125.684 | 47.8 | 32.2 | 1217160 | 1217.16 | 50
11/4/20XX 9:00:00 AM | 0.375 | 5 | 48.8 | 58 | 48.8 |  | 48.8 | 69.68 | 10.32 | 390096 | 390.096 | 67.36 | 12.64 | 477792 | 477.792 | 65.04 | 14.96 | 565488 | 565.488 | 62.72 | 17.28 | 653184 | 653.184 | 60.4 | 19.6 | 740880 | 740.88 | 58.08 | 21.92 | 828576 | 828.576 | 55.76 | 24.24 | 916272 | 916.272 | 53.44 | 26.56 | 1003968 | 1003.968 | 51.12 | 28.88 | 1091664 | 1091.664 | 48.8 | 31.2 | 1179360 | 1179.36 | 50
11/4/20XX 10:00:00 AM | 0.41667 | 5 | 50.7 | 53.4 | 50.7 |  | 50.7 | 69.87 | 10.13 | 382914 | 382.914 | 67.74 | 12.26 | 463428 | 463.428 | 65.61 | 14.39 | 543942 | 543.942 | 63.48 | 16.52 | 624456 | 624.456 | 61.35 | 18.65 | 704970 | 704.97 | 59.22 | 20.78 | 785484 | 785.484 | 57.09 | 22.91 | 865998 | 865.998 | 54.96 | 25.04 | 946512 | 946.512 | 52.83 | 27.17 | 1027026 | 1027.026 | 50.7 | 29.3 | 1107540 | 1107.54 | 50
11/4/20XX 11:00:00 AM | 0.45833 | 5 | 52.2 | 49.1 | 52.2 |  | 52.2 | 70.02 | 9.98 | 377244 | 377.244 | 68.04 | 11.96 | 452088 | 452.088 | 66.06 | 13.94 | 526932 | 526.932 | 64.08 | 15.92 | 601776 | 601.776 | 62.1 | 17.9 | 676620 | 676.62 | 60.12 | 19.88 | 751464 | 751.464 | 58.14 | 21.86 | 826308 | 826.308 | 56.16 | 23.84 | 901152 | 901.152 | 54.18 | 25.82 | 975996 | 975.996 | 52.2 | 27.8 | 1050840 | 1050.84 | 50
11/4/20XX 12:00:00 PM | 0.5 | 5 | 54.2 | 46.2 | 54.2 |  | 54.2 | 70.22 | 9.78 | 369684 | 369.684 | 68.44 | 11.56 | 436968 | 436.968 | 66.66 | 13.34 | 504252 | 504.252 | 64.88 | 15.12 | 571536 | 571.536 | 63.1 | 16.9 | 638820 | 638.82 | 61.32 | 18.68 | 706104 | 706.104 | 59.54 | 20.46 | 773388 | 773.388 | 57.76 | 22.24 | 840672 | 840.672 | 55.98 | 24.02 | 907956 | 907.956 | 54.2 | 25.8 | 975240 | 975.24 | 55
11/4/20XX 1:00:00 PM | 0.54167 | 5 | 55.2 | 44.2 | 55.2 |  | 55.2 | 70.32 | 9.68 | 365904 | 365.904 | 68.64 | 11.36 | 429408 | 429.408 | 66.96 | 13.04 | 492912 | 492.912 | 65.28 | 14.72 | 556416 | 556.416 | 63.6 | 16.4 | 619920 | 619.92 | 61.92 | 18.08 | 683424 | 683.424 | 60.24 | 19.76 | 746928 | 746.928 | 58.56 | 21.44 | 810432 | 810.432 | 56.88 | 23.12 | 873936 | 873.936 | 55.2 | 24.8 | 937440 | 937.44 | 55
11/4/20XX 2:00:00 PM | 0.58333 | 5 | 55 | 43.3 | 55 |  | 55 | 70.3 | 9.7 | 366660 | 366.66 | 68.6 | 11.4 | 430920 | 430.92 | 66.9 | 13.1 | 495180 | 495.18 | 65.2 | 14.8 | 559440 | 559.44 | 63.5 | 16.5 | 623700 | 623.7 | 61.8 | 18.2 | 687960 | 687.96 | 60.1 | 19.9 | 752220 | 752.22 | 58.4 | 21.6 | 816480 | 816.48 | 56.7 | 23.3 | 880740 | 880.74 | 55 | 25 | 945000 | 945 | 55
11/4/20XX 3:00:00 PM | 0.625 | 5 | 54.9 | 43.6 | 54.9 |  | 54.9 | 70.29 | 9.71 | 367038 | 367.038 | 68.58 | 11.42 | 431676 | 431.676 | 66.87 | 13.13 | 496314 | 496.314 | 65.16 | 14.84 | 560952 | 560.952 | 63.45 | 16.55 | 625590 | 625.59 | 61.74 | 18.26 | 690228 | 690.228 | 60.03 | 19.97 | 754866 | 754.866 | 58.32 | 21.68 | 819504 | 819.504 | 56.61 | 23.39 | 884142 | 884.142 | 54.9 | 25.1 | 948780 | 948.78 | 55
11/4/20XX 4:00:00 PM | 0.66667 | 5 | 53.5 | 45.7 | 53.5 |  | 53.5 | 70.15 | 9.85 | 372330 | 372.33 | 68.3 | 11.7 | 442260 | 442.26 | 66.45 | 13.55 | 512190 | 512.19 | 64.6 | 15.4 | 582120 | 582.12 | 62.75 | 17.25 | 652050 | 652.05 | 60.9 | 19.1 | 721980 | 721.98 | 59.05 | 20.95 | 791910 | 791.91 | 57.2 | 22.8 | 861840 | 861.84 | 55.35 | 24.65 | 931770 | 931.77 | 53.5 | 26.5 | 1001700 | 1001.7 | 55
11/4/20XX 5:00:00 PM | 0.70833 | 5 | 51.9 | 48.5 | 51.9 |  | 51.9 | 69.99 | 10.01 | 378378 | 378.378 | 67.98 | 12.02 | 454356 | 454.356 | 65.97 | 14.03 | 530334 | 530.334 | 63.96 | 16.04 | 606312 | 606.312 | 61.95 | 18.05 | 682290 | 682.29 | 59.94 | 20.06 | 758268 | 758.268 | 57.93 | 22.07 | 834246 | 834.246 | 55.92 | 24.08 | 910224 | 910.224 | 53.91 | 26.09 | 986202 | 986.202 | 51.9 | 28.1 | 1062180 | 1062.18 | 50
11/4/20XX 6:00:00 PM | 0.75 | 5 | 51.6 | 52.1 | 51.6 |  | 51.6 | 69.96 | 10.04 | 379512 | 379.512 | 67.92 | 12.08 | 456624 | 456.624 | 65.88 | 14.12 | 533736 | 533.736 | 63.84 | 16.16 | 610848 | 610.848 | 61.8 | 18.2 | 687960 | 687.96 | 59.76 | 20.24 | 765072 | 765.072 | 57.72 | 22.28 | 842184 | 842.184 | 55.68 | 24.32 | 919296 | 919.296 | 53.64 | 26.36 | 996408 | 996.408 | 51.6 | 28.4 | 1073520 | 1073.52 | 50
11/4/20XX 7:00:00 PM | 0.79167 | 5 | 50.7 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/4/20XX 8:00:00 PM | 0.83333 | 5 | 50.6 | 55.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/4/20XX 9:00:00 PM | 0.875 | 5 | 50.4 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/4/20XX 10:00:00 PM | 0.91667 | 5 | 49.9 | 58.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/4/20XX 11:00:00 PM | 0.95833 | 5 | 49.3 | 61.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/4/20XX 12:00:00 AM | 0 | 6 | 48.9 | 61.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/5/20XX 1:00:00 AM | 0.041667 | 6 | 48.1 | 65.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/5/20XX 2:00:00 AM | 0.083333 | 6 | 47.8 | 66.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/5/20XX 3:00:00 AM | 0.125 | 6 | 47.3 | 69.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/5/20XX 4:00:00 AM | 0.16667 | 6 | 47.6 | 69.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/5/20XX 5:00:00 AM | 0.20833 | 6 | 47.6 | 70.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/5/20XX 6:00:00 AM | 0.25 | 6 | 47.2 | 71.5 | 47.2 |  | 47.2 | 69.52 | 10.48 | 396144 | 396.144 | 67.04 | 12.96 | 489888 | 489.888 | 64.56 | 15.44 | 583632 | 583.632 | 62.08 | 17.92 | 677376 | 677.376 | 59.6 | 20.4 | 771120 | 771.12 | 57.12 | 22.88 | 864864 | 864.864 | 54.64 | 25.36 | 958608 | 958.608 | 52.16 | 27.84 | 1052352 | 1052.352 | 49.68 | 30.32 | 1146096 | 1146.096 | 47.2 | 32.8 | 1239840 | 1239.84 | 45
11/5/20XX 7:00:00 AM | 0.29167 | 6 | 47.7 | 70.7 | 47.7 |  | 47.7 | 69.57 | 10.43 | 394254 | 394.254 | 67.14 | 12.86 | 486108 | 486.108 | 64.71 | 15.29 | 577962 | 577.962 | 62.28 | 17.72 | 669816 | 669.816 | 59.85 | 20.15 | 761670 | 761.67 | 57.42 | 22.58 | 853524 | 853.524 | 54.99 | 25.01 | 945378 | 945.378 | 52.56 | 27.44 | 1037232 | 1037.232 | 50.13 | 29.87 | 1129086 | 1129.086 | 47.7 | 32.3 | 1220940 | 1220.94 | 50
11/5/20XX 8:00:00 AM | 0.33333 | 6 | 48.8 | 68.5 | 48.8 |  | 48.8 | 69.68 | 10.32 | 390096 | 390.096 | 67.36 | 12.64 | 477792 | 477.792 | 65.04 | 14.96 | 565488 | 565.488 | 62.72 | 17.28 | 653184 | 653.184 | 60.4 | 19.6 | 740880 | 740.88 | 58.08 | 21.92 | 828576 | 828.576 | 55.76 | 24.24 | 916272 | 916.272 | 53.44 | 26.56 | 1003968 | 1003.968 | 51.12 | 28.88 | 1091664 | 1091.664 | 48.8 | 31.2 | 1179360 | 1179.36 | 50
11/5/20XX 9:00:00 AM | 0.375 | 6 | 50 | 66.6 | 50 |  | 50 | 69.8 | 10.2 | 385560 | 385.56 | 67.6 | 12.4 | 468720 | 468.72 | 65.4 | 14.6 | 551880 | 551.88 | 63.2 | 16.8 | 635040 | 635.04 | 61 | 19 | 718200 | 718.2 | 58.8 | 21.2 | 801360 | 801.36 | 56.6 | 23.4 | 884520 | 884.52 | 54.4 | 25.6 | 967680 | 967.68 | 52.2 | 27.8 | 1050840 | 1050.84 | 50 | 30 | 1134000 | 1134 | 50
11/5/20XX 10:00:00 AM | 0.41667 | 6 | 51.1 | 64.5 | 51.1 |  | 51.1 | 69.91 | 10.09 | 381402 | 381.402 | 67.82 | 12.18 | 460404 | 460.404 | 65.73 | 14.27 | 539406 | 539.406 | 63.64 | 16.36 | 618408 | 618.408 | 61.55 | 18.45 | 697410 | 697.41 | 59.46 | 20.54 | 776412 | 776.412 | 57.37 | 22.63 | 855414 | 855.414 | 55.28 | 24.72 | 934416 | 934.416 | 53.19 | 26.81 | 1013418 | 1013.418 | 51.1 | 28.9 | 1092420 | 1092.42 | 50
11/5/20XX 11:00:00 AM | 0.45833 | 6 | 52.5 | 64.1 | 52.5 |  | 52.5 | 70.05 | 9.95 | 376110 | 376.11 | 68.1 | 11.9 | 449820 | 449.82 | 66.15 | 13.85 | 523530 | 523.53 | 64.2 | 15.8 | 597240 | 597.24 | 62.25 | 17.75 | 670950 | 670.95 | 60.3 | 19.7 | 744660 | 744.66 | 58.35 | 21.65 | 818370 | 818.37 | 56.4 | 23.6 | 892080 | 892.08 | 54.45 | 25.55 | 965790 | 965.79 | 52.5 | 27.5 | 1039500 | 1039.5 | 50
11/5/20XX 12:00:00 PM | 0.5 | 6 | 54 | 62.2 | 54 |  | 54 | 70.2 | 9.8 | 370440 | 370.44 | 68.4 | 11.6 | 438480 | 438.48 | 66.6 | 13.4 | 506520 | 506.52 | 64.8 | 15.2 | 574560 | 574.56 | 63 | 17 | 642600 | 642.6 | 61.2 | 18.8 | 710640 | 710.64 | 59.4 | 20.6 | 778680 | 778.68 | 57.6 | 22.4 | 846720 | 846.72 | 55.8 | 24.2 | 914760 | 914.76 | 54 | 26 | 982800 | 982.8 | 55
11/5/20XX 1:00:00 PM | 0.54167 | 6 | 54.8 | 61 | 54.8 |  | 54.8 | 70.28 | 9.72 | 367416 | 367.416 | 68.56 | 11.44 | 432432 | 432.432 | 66.84 | 13.16 | 497448 | 497.448 | 65.12 | 14.88 | 562464 | 562.464 | 63.4 | 16.6 | 627480 | 627.48 | 61.68 | 18.32 | 692496 | 692.496 | 59.96 | 20.04 | 757512 | 757.512 | 58.24 | 21.76 | 822528 | 822.528 | 56.52 | 23.48 | 887544 | 887.544 | 54.8 | 25.2 | 952560 | 952.56 | 55
11/5/20XX 2:00:00 PM | 0.58333 | 6 | 55.2 | 58.5 | 55.2 |  | 55.2 | 70.32 | 9.68 | 365904 | 365.904 | 68.64 | 11.36 | 429408 | 429.408 | 66.96 | 13.04 | 492912 | 492.912 | 65.28 | 14.72 | 556416 | 556.416 | 63.6 | 16.4 | 619920 | 619.92 | 61.92 | 18.08 | 683424 | 683.424 | 60.24 | 19.76 | 746928 | 746.928 | 58.56 | 21.44 | 810432 | 810.432 | 56.88 | 23.12 | 873936 | 873.936 | 55.2 | 24.8 | 937440 | 937.44 | 55
11/5/20XX 3:00:00 PM | 0.625 | 6 | 55.4 | 57.6 | 55.4 |  | 55.4 | 70.34 | 9.66 | 365148 | 365.148 | 68.68 | 11.32 | 427896 | 427.896 | 67.02 | 12.98 | 490644 | 490.644 | 65.36 | 14.64 | 553392 | 553.392 | 63.7 | 16.3 | 616140 | 616.14 | 62.04 | 17.96 | 678888 | 678.888 | 60.38 | 19.62 | 741636 | 741.636 | 58.72 | 21.28 | 804384 | 804.384 | 57.06 | 22.94 | 867132 | 867.132 | 55.4 | 24.6 | 929880 | 929.88 | 55
11/5/20XX 4:00:00 PM | 0.66667 | 6 | 54.9 | 59.2 | 54.9 |  | 54.9 | 70.29 | 9.71 | 367038 | 367.038 | 68.58 | 11.42 | 431676 | 431.676 | 66.87 | 13.13 | 496314 | 496.314 | 65.16 | 14.84 | 560952 | 560.952 | 63.45 | 16.55 | 625590 | 625.59 | 61.74 | 18.26 | 690228 | 690.228 | 60.03 | 19.97 | 754866 | 754.866 | 58.32 | 21.68 | 819504 | 819.504 | 56.61 | 23.39 | 884142 | 884.142 | 54.9 | 25.1 | 948780 | 948.78 | 55
11/5/20XX 5:00:00 PM | 0.70833 | 6 | 53.2 | 61.3 | 53.2 |  | 53.2 | 70.12 | 9.88 | 373464 | 373.464 | 68.24 | 11.76 | 444528 | 444.528 | 66.36 | 13.64 | 515592 | 515.592 | 64.48 | 15.52 | 586656 | 586.656 | 62.6 | 17.4 | 657720 | 657.72 | 60.72 | 19.28 | 728784 | 728.784 | 58.84 | 21.16 | 799848 | 799.848 | 56.96 | 23.04 | 870912 | 870.912 | 55.08 | 24.92 | 941976 | 941.976 | 53.2 | 26.8 | 1013040 | 1013.04 | 55
11/5/20XX 6:00:00 PM | 0.75 | 6 | 53.1 | 62.2 | 53.1 |  | 53.1 | 70.11 | 9.89 | 373842 | 373.842 | 68.22 | 11.78 | 445284 | 445.284 | 66.33 | 13.67 | 516726 | 516.726 | 64.44 | 15.56 | 588168 | 588.168 | 62.55 | 17.45 | 659610 | 659.61 | 60.66 | 19.34 | 731052 | 731.052 | 58.77 | 21.23 | 802494 | 802.494 | 56.88 | 23.12 | 873936 | 873.936 | 54.99 | 25.01 | 945378 | 945.378 | 53.1 | 26.9 | 1016820 | 1016.82 | 55
11/5/20XX 7:00:00 PM | 0.79167 | 6 | 52.8 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/5/20XX 8:00:00 PM | 0.83333 | 6 | 51.8 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/5/20XX 9:00:00 PM | 0.875 | 6 | 51.5 | 68.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/5/20XX 10:00:00 PM | 0.91667 | 6 | 51.5 | 67.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/5/20XX 11:00:00 PM | 0.95833 | 6 | 51 | 67.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/5/20XX 12:00:00 AM | 0 | 7 | 50.9 | 66.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/6/20XX 1:00:00 AM | 0.041667 | 7 | 50.5 | 68.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/6/20XX 2:00:00 AM | 0.083333 | 7 | 49.7 | 70.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/6/20XX 3:00:00 AM | 0.125 | 7 | 49.4 | 70.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/6/20XX 4:00:00 AM | 0.16667 | 7 | 48.9 | 72.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/6/20XX 5:00:00 AM | 0.20833 | 7 | 48.5 | 73.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/6/20XX 6:00:00 AM | 0.25 | 7 | 48.3 | 74.6 | 48.3 |  | 48.3 | 69.63 | 10.37 | 391986 | 391.986 | 67.26 | 12.74 | 481572 | 481.572 | 64.89 | 15.11 | 571158 | 571.158 | 62.52 | 17.48 | 660744 | 660.744 | 60.15 | 19.85 | 750330 | 750.33 | 57.78 | 22.22 | 839916 | 839.916 | 55.41 | 24.59 | 929502 | 929.502 | 53.04 | 26.96 | 1019088 | 1019.088 | 50.67 | 29.33 | 1108674 | 1108.674 | 48.3 | 31.7 | 1198260 | 1198.26 | 50
11/6/20XX 7:00:00 AM | 0.29167 | 7 | 48.4 | 74.2 | 48.4 |  | 48.4 | 69.64 | 10.36 | 391608 | 391.608 | 67.28 | 12.72 | 480816 | 480.816 | 64.92 | 15.08 | 570024 | 570.024 | 62.56 | 17.44 | 659232 | 659.232 | 60.2 | 19.8 | 748440 | 748.44 | 57.84 | 22.16 | 837648 | 837.648 | 55.48 | 24.52 | 926856 | 926.856 | 53.12 | 26.88 | 1016064 | 1016.064 | 50.76 | 29.24 | 1105272 | 1105.272 | 48.4 | 31.6 | 1194480 | 1194.48 | 50
11/6/20XX 8:00:00 AM | 0.33333 | 7 | 49.8 | 70.7 | 49.8 |  | 49.8 | 69.78 | 10.22 | 386316 | 386.316 | 67.56 | 12.44 | 470232 | 470.232 | 65.34 | 14.66 | 554148 | 554.148 | 63.12 | 16.88 | 638064 | 638.064 | 60.9 | 19.1 | 721980 | 721.98 | 58.68 | 21.32 | 805896 | 805.896 | 56.46 | 23.54 | 889812 | 889.812 | 54.24 | 25.76 | 973728 | 973.728 | 52.02 | 27.98 | 1057644 | 1057.644 | 49.8 | 30.2 | 1141560 | 1141.56 | 50
11/6/20XX 9:00:00 AM | 0.375 | 7 | 50.9 | 68.4 | 50.9 |  | 50.9 | 69.89 | 10.11 | 382158 | 382.158 | 67.78 | 12.22 | 461916 | 461.916 | 65.67 | 14.33 | 541674 | 541.674 | 63.56 | 16.44 | 621432 | 621.432 | 61.45 | 18.55 | 701190 | 701.19 | 59.34 | 20.66 | 780948 | 780.948 | 57.23 | 22.77 | 860706 | 860.706 | 55.12 | 24.88 | 940464 | 940.464 | 53.01 | 26.99 | 1020222 | 1020.222 | 50.9 | 29.1 | 1099980 | 1099.98 | 50
11/6/20XX 10:00:00 AM | 0.41667 | 7 | 52 | 65.9 | 52 |  | 52 | 70 | 10 | 378000 | 378 | 68 | 12 | 453600 | 453.6 | 66 | 14 | 529200 | 529.2 | 64 | 16 | 604800 | 604.8 | 62 | 18 | 680400 | 680.4 | 60 | 20 | 756000 | 756 | 58 | 22 | 831600 | 831.6 | 56 | 24 | 907200 | 907.2 | 54 | 26 | 982800 | 982.8 | 52 | 28 | 1058400 | 1058.4 | 50
11/6/20XX 11:00:00 AM | 0.45833 | 7 | 53.6 | 64.2 | 53.6 |  | 53.6 | 70.16 | 9.84 | 371952 | 371.952 | 68.32 | 11.68 | 441504 | 441.504 | 66.48 | 13.52 | 511056 | 511.056 | 64.64 | 15.36 | 580608 | 580.608 | 62.8 | 17.2 | 650160 | 650.16 | 60.96 | 19.04 | 719712 | 719.712 | 59.12 | 20.88 | 789264 | 789.264 | 57.28 | 22.72 | 858816 | 858.816 | 55.44 | 24.56 | 928368 | 928.368 | 53.6 | 26.4 | 997920 | 997.92 | 55
11/6/20XX 12:00:00 PM | 0.5 | 7 | 55.1 | 62.1 | 55.1 |  | 55.1 | 70.31 | 9.69 | 366282 | 366.282 | 68.62 | 11.38 | 430164 | 430.164 | 66.93 | 13.07 | 494046 | 494.046 | 65.24 | 14.76 | 557928 | 557.928 | 63.55 | 16.45 | 621810 | 621.81 | 61.86 | 18.14 | 685692 | 685.692 | 60.17 | 19.83 | 749574 | 749.574 | 58.48 | 21.52 | 813456 | 813.456 | 56.79 | 23.21 | 877338 | 877.338 | 55.1 | 24.9 | 941220 | 941.22 | 55
11/6/20XX 1:00:00 PM | 0.54167 | 7 | 55.4 | 61.2 | 55.4 |  | 55.4 | 70.34 | 9.66 | 365148 | 365.148 | 68.68 | 11.32 | 427896 | 427.896 | 67.02 | 12.98 | 490644 | 490.644 | 65.36 | 14.64 | 553392 | 553.392 | 63.7 | 16.3 | 616140 | 616.14 | 62.04 | 17.96 | 678888 | 678.888 | 60.38 | 19.62 | 741636 | 741.636 | 58.72 | 21.28 | 804384 | 804.384 | 57.06 | 22.94 | 867132 | 867.132 | 55.4 | 24.6 | 929880 | 929.88 | 55
11/6/20XX 2:00:00 PM | 0.58333 | 7 | 55.3 | 61.8 | 55.3 |  | 55.3 | 70.33 | 9.67 | 365526 | 365.526 | 68.66 | 11.34 | 428652 | 428.652 | 66.99 | 13.01 | 491778 | 491.778 | 65.32 | 14.68 | 554904 | 554.904 | 63.65 | 16.35 | 618030 | 618.03 | 61.98 | 18.02 | 681156 | 681.156 | 60.31 | 19.69 | 744282 | 744.282 | 58.64 | 21.36 | 807408 | 807.408 | 56.97 | 23.03 | 870534 | 870.534 | 55.3 | 24.7 | 933660 | 933.66 | 55
11/6/20XX 3:00:00 PM | 0.625 | 7 | 55.1 | 61.5 | 55.1 |  | 55.1 | 70.31 | 9.69 | 366282 | 366.282 | 68.62 | 11.38 | 430164 | 430.164 | 66.93 | 13.07 | 494046 | 494.046 | 65.24 | 14.76 | 557928 | 557.928 | 63.55 | 16.45 | 621810 | 621.81 | 61.86 | 18.14 | 685692 | 685.692 | 60.17 | 19.83 | 749574 | 749.574 | 58.48 | 21.52 | 813456 | 813.456 | 56.79 | 23.21 | 877338 | 877.338 | 55.1 | 24.9 | 941220 | 941.22 | 55
11/6/20XX 4:00:00 PM | 0.66667 | 7 | 54.6 | 62.7 | 54.6 |  | 54.6 | 70.26 | 9.74 | 368172 | 368.172 | 68.52 | 11.48 | 433944 | 433.944 | 66.78 | 13.22 | 499716 | 499.716 | 65.04 | 14.96 | 565488 | 565.488 | 63.3 | 16.7 | 631260 | 631.26 | 61.56 | 18.44 | 697032 | 697.032 | 59.82 | 20.18 | 762804 | 762.804 | 58.08 | 21.92 | 828576 | 828.576 | 56.34 | 23.66 | 894348 | 894.348 | 54.6 | 25.4 | 960120 | 960.12 | 55
11/6/20XX 5:00:00 PM | 0.70833 | 7 | 53.3 | 66.3 | 53.3 |  | 53.3 | 70.13 | 9.87 | 373086 | 373.086 | 68.26 | 11.74 | 443772 | 443.772 | 66.39 | 13.61 | 514458 | 514.458 | 64.52 | 15.48 | 585144 | 585.144 | 62.65 | 17.35 | 655830 | 655.83 | 60.78 | 19.22 | 726516 | 726.516 | 58.91 | 21.09 | 797202 | 797.202 | 57.04 | 22.96 | 867888 | 867.888 | 55.17 | 24.83 | 938574 | 938.574 | 53.3 | 26.7 | 1009260 | 1009.26 | 55
11/6/20XX 6:00:00 PM | 0.75 | 7 | 52.9 | 64.8 | 52.9 |  | 52.9 | 70.09 | 9.91 | 374598 | 374.598 | 68.18 | 11.82 | 446796 | 446.796 | 66.27 | 13.73 | 518994 | 518.994 | 64.36 | 15.64 | 591192 | 591.192 | 62.45 | 17.55 | 663390 | 663.39 | 60.54 | 19.46 | 735588 | 735.588 | 58.63 | 21.37 | 807786 | 807.786 | 56.72 | 23.28 | 879984 | 879.984 | 54.81 | 25.19 | 952182 | 952.182 | 52.9 | 27.1 | 1024380 | 1024.38 | 55
11/6/20XX 7:00:00 PM | 0.79167 | 7 | 51.8 | 66.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/6/20XX 8:00:00 PM | 0.83333 | 7 | 51.2 | 66.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/6/20XX 9:00:00 PM | 0.875 | 7 | 50.6 | 68.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/6/20XX 10:00:00 PM | 0.91667 | 7 | 50.2 | 68.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/6/20XX 11:00:00 PM | 0.95833 | 7 | 49.4 | 70.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/6/20XX 12:00:00 AM | 0 | 1 | 48.7 | 69.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/7/20XX 1:00:00 AM | 0.041667 | 1 | 48.8 | 69.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/7/20XX 2:00:00 AM | 0.083333 | 1 | 48.4 | 69.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/7/20XX 3:00:00 AM | 0.125 | 1 | 47.8 | 67.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/7/20XX 4:00:00 AM | 0.16667 | 1 | 47.7 | 67.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/7/20XX 5:00:00 AM | 0.20833 | 1 | 46.9 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/7/20XX 6:00:00 AM | 0.25 | 1 | 46.5 | 68.4 | 46.5 |  | 46.5 | 69.45 | 10.55 | 398790 | 398.79 | 66.9 | 13.1 | 495180 | 495.18 | 64.35 | 15.65 | 591570 | 591.57 | 61.8 | 18.2 | 687960 | 687.96 | 59.25 | 20.75 | 784350 | 784.35 | 56.7 | 23.3 | 880740 | 880.74 | 54.15 | 25.85 | 977130 | 977.13 | 51.6 | 28.4 | 1073520 | 1073.52 | 49.05 | 30.95 | 1169910 | 1169.91 | 46.5 | 33.5 | 1266300 | 1266.3 | 45
11/7/20XX 7:00:00 AM | 0.29167 | 1 | 46.4 | 68.7 | 46.4 |  | 46.4 | 69.44 | 10.56 | 399168 | 399.168 | 66.88 | 13.12 | 495936 | 495.936 | 64.32 | 15.68 | 592704 | 592.704 | 61.76 | 18.24 | 689472 | 689.472 | 59.2 | 20.8 | 786240 | 786.24 | 56.64 | 23.36 | 883008 | 883.008 | 54.08 | 25.92 | 979776 | 979.776 | 51.52 | 28.48 | 1076544 | 1076.544 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.4 | 33.6 | 1270080 | 1270.08 | 45
11/7/20XX 8:00:00 AM | 0.33333 | 1 | 47.2 | 66.1 | 47.2 |  | 47.2 | 69.52 | 10.48 | 396144 | 396.144 | 67.04 | 12.96 | 489888 | 489.888 | 64.56 | 15.44 | 583632 | 583.632 | 62.08 | 17.92 | 677376 | 677.376 | 59.6 | 20.4 | 771120 | 771.12 | 57.12 | 22.88 | 864864 | 864.864 | 54.64 | 25.36 | 958608 | 958.608 | 52.16 | 27.84 | 1052352 | 1052.352 | 49.68 | 30.32 | 1146096 | 1146.096 | 47.2 | 32.8 | 1239840 | 1239.84 | 45
11/7/20XX 9:00:00 AM | 0.375 | 1 | 48.8 | 61.2 | 48.8 |  | 48.8 | 69.68 | 10.32 | 390096 | 390.096 | 67.36 | 12.64 | 477792 | 477.792 | 65.04 | 14.96 | 565488 | 565.488 | 62.72 | 17.28 | 653184 | 653.184 | 60.4 | 19.6 | 740880 | 740.88 | 58.08 | 21.92 | 828576 | 828.576 | 55.76 | 24.24 | 916272 | 916.272 | 53.44 | 26.56 | 1003968 | 1003.968 | 51.12 | 28.88 | 1091664 | 1091.664 | 48.8 | 31.2 | 1179360 | 1179.36 | 50
11/7/20XX 10:00:00 AM | 0.41667 | 1 | 50 | 57.5 | 50 |  | 50 | 69.8 | 10.2 | 385560 | 385.56 | 67.6 | 12.4 | 468720 | 468.72 | 65.4 | 14.6 | 551880 | 551.88 | 63.2 | 16.8 | 635040 | 635.04 | 61 | 19 | 718200 | 718.2 | 58.8 | 21.2 | 801360 | 801.36 | 56.6 | 23.4 | 884520 | 884.52 | 54.4 | 25.6 | 967680 | 967.68 | 52.2 | 27.8 | 1050840 | 1050.84 | 50 | 30 | 1134000 | 1134 | 50
11/7/20XX 11:00:00 AM | 0.45833 | 1 | 51.5 | 55.6 | 51.5 |  | 51.5 | 69.95 | 10.05 | 379890 | 379.89 | 67.9 | 12.1 | 457380 | 457.38 | 65.85 | 14.15 | 534870 | 534.87 | 63.8 | 16.2 | 612360 | 612.36 | 61.75 | 18.25 | 689850 | 689.85 | 59.7 | 20.3 | 767340 | 767.34 | 57.65 | 22.35 | 844830 | 844.83 | 55.6 | 24.4 | 922320 | 922.32 | 53.55 | 26.45 | 999810 | 999.81 | 51.5 | 28.5 | 1077300 | 1077.3 | 50
11/7/20XX 12:00:00 PM | 0.5 | 1 | 52.1 | 56.5 | 52.1 |  | 52.1 | 70.01 | 9.99 | 377622 | 377.622 | 68.02 | 11.98 | 452844 | 452.844 | 66.03 | 13.97 | 528066 | 528.066 | 64.04 | 15.96 | 603288 | 603.288 | 62.05 | 17.95 | 678510 | 678.51 | 60.06 | 19.94 | 753732 | 753.732 | 58.07 | 21.93 | 828954 | 828.954 | 56.08 | 23.92 | 904176 | 904.176 | 54.09 | 25.91 | 979398 | 979.398 | 52.1 | 27.9 | 1054620 | 1054.62 | 50
11/7/20XX 1:00:00 PM | 0.54167 | 1 | 53 | 54.7 | 53 |  | 53 | 70.1 | 9.9 | 374220 | 374.22 | 68.2 | 11.8 | 446040 | 446.04 | 66.3 | 13.7 | 517860 | 517.86 | 64.4 | 15.6 | 589680 | 589.68 | 62.5 | 17.5 | 661500 | 661.5 | 60.6 | 19.4 | 733320 | 733.32 | 58.7 | 21.3 | 805140 | 805.14 | 56.8 | 23.2 | 876960 | 876.96 | 54.9 | 25.1 | 948780 | 948.78 | 53 | 27 | 1020600 | 1020.6 | 55
11/7/20XX 2:00:00 PM | 0.58333 | 1 | 53.2 | 54.9 | 53.2 |  | 53.2 | 70.12 | 9.88 | 373464 | 373.464 | 68.24 | 11.76 | 444528 | 444.528 | 66.36 | 13.64 | 515592 | 515.592 | 64.48 | 15.52 | 586656 | 586.656 | 62.6 | 17.4 | 657720 | 657.72 | 60.72 | 19.28 | 728784 | 728.784 | 58.84 | 21.16 | 799848 | 799.848 | 56.96 | 23.04 | 870912 | 870.912 | 55.08 | 24.92 | 941976 | 941.976 | 53.2 | 26.8 | 1013040 | 1013.04 | 55
11/7/20XX 3:00:00 PM | 0.625 | 1 | 52.1 | 55.5 | 52.1 |  | 52.1 | 70.01 | 9.99 | 377622 | 377.622 | 68.02 | 11.98 | 452844 | 452.844 | 66.03 | 13.97 | 528066 | 528.066 | 64.04 | 15.96 | 603288 | 603.288 | 62.05 | 17.95 | 678510 | 678.51 | 60.06 | 19.94 | 753732 | 753.732 | 58.07 | 21.93 | 828954 | 828.954 | 56.08 | 23.92 | 904176 | 904.176 | 54.09 | 25.91 | 979398 | 979.398 | 52.1 | 27.9 | 1054620 | 1054.62 | 50
11/7/20XX 4:00:00 PM | 0.66667 | 1 | 51 | 56.1 | 51 |  | 51 | 69.9 | 10.1 | 381780 | 381.78 | 67.8 | 12.2 | 461160 | 461.16 | 65.7 | 14.3 | 540540 | 540.54 | 63.6 | 16.4 | 619920 | 619.92 | 61.5 | 18.5 | 699300 | 699.3 | 59.4 | 20.6 | 778680 | 778.68 | 57.3 | 22.7 | 858060 | 858.06 | 55.2 | 24.8 | 937440 | 937.44 | 53.1 | 26.9 | 1016820 | 1016.82 | 51 | 29 | 1096200 | 1096.2 | 50
11/7/20XX 5:00:00 PM | 0.70833 | 1 | 49.5 | 58 | 49.5 |  | 49.5 | 69.75 | 10.25 | 387450 | 387.45 | 67.5 | 12.5 | 472500 | 472.5 | 65.25 | 14.75 | 557550 | 557.55 | 63 | 17 | 642600 | 642.6 | 60.75 | 19.25 | 727650 | 727.65 | 58.5 | 21.5 | 812700 | 812.7 | 56.25 | 23.75 | 897750 | 897.75 | 54 | 26 | 982800 | 982.8 | 51.75 | 28.25 | 1067850 | 1067.85 | 49.5 | 30.5 | 1152900 | 1152.9 | 50
11/7/20XX 6:00:00 PM | 0.75 | 1 | 49.1 | 58.7 | 49.1 |  | 49.1 | 69.71 | 10.29 | 388962 | 388.962 | 67.42 | 12.58 | 475524 | 475.524 | 65.13 | 14.87 | 562086 | 562.086 | 62.84 | 17.16 | 648648 | 648.648 | 60.55 | 19.45 | 735210 | 735.21 | 58.26 | 21.74 | 821772 | 821.772 | 55.97 | 24.03 | 908334 | 908.334 | 53.68 | 26.32 | 994896 | 994.896 | 51.39 | 28.61 | 1081458 | 1081.458 | 49.1 | 30.9 | 1168020 | 1168.02 | 50
11/7/20XX 7:00:00 PM | 0.79167 | 1 | 48.4 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/7/20XX 8:00:00 PM | 0.83333 | 1 | 47.7 | 59.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/7/20XX 9:00:00 PM | 0.875 | 1 | 47.5 | 60.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/7/20XX 10:00:00 PM | 0.91667 | 1 | 47 | 61.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/7/20XX 11:00:00 PM | 0.95833 | 1 | 46.3 | 63 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/7/20XX 12:00:00 AM | 0 | 2 | 46.2 | 61.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/8/20XX 1:00:00 AM | 0.041667 | 2 | 45.5 | 62.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/8/20XX 2:00:00 AM | 0.083333 | 2 | 44.7 | 63.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/8/20XX 3:00:00 AM | 0.125 | 2 | 44.2 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/8/20XX 4:00:00 AM | 0.16667 | 2 | 43.7 | 64.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/8/20XX 5:00:00 AM | 0.20833 | 2 | 43.6 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/8/20XX 6:00:00 AM | 0.25 | 2 | 43.3 | 65.4 | 43.3 |  | 43.3 | 69.13 | 10.87 | 410886 | 410.886 | 66.26 | 13.74 | 519372 | 519.372 | 63.39 | 16.61 | 627858 | 627.858 | 60.52 | 19.48 | 736344 | 736.344 | 57.65 | 22.35 | 844830 | 844.83 | 54.78 | 25.22 | 953316 | 953.316 | 51.91 | 28.09 | 1061802 | 1061.802 | 49.04 | 30.96 | 1170288 | 1170.288 | 46.17 | 33.83 | 1278774 | 1278.774 | 43.3 | 36.7 | 1387260 | 1387.26 | 45
11/8/20XX 7:00:00 AM | 0.29167 | 2 | 42.8 | 65.5 | 42.8 |  | 42.8 | 69.08 | 10.92 | 412776 | 412.776 | 66.16 | 13.84 | 523152 | 523.152 | 63.24 | 16.76 | 633528 | 633.528 | 60.32 | 19.68 | 743904 | 743.904 | 57.4 | 22.6 | 854280 | 854.28 | 54.48 | 25.52 | 964656 | 964.656 | 51.56 | 28.44 | 1075032 | 1075.032 | 48.64 | 31.36 | 1185408 | 1185.408 | 45.72 | 34.28 | 1295784 | 1295.784 | 42.8 | 37.2 | 1406160 | 1406.16 | 45
11/8/20XX 8:00:00 AM | 0.33333 | 2 | 43.9 | 62.6 | 43.9 |  | 43.9 | 69.19 | 10.81 | 408618 | 408.618 | 66.38 | 13.62 | 514836 | 514.836 | 63.57 | 16.43 | 621054 | 621.054 | 60.76 | 19.24 | 727272 | 727.272 | 57.95 | 22.05 | 833490 | 833.49 | 55.14 | 24.86 | 939708 | 939.708 | 52.33 | 27.67 | 1045926 | 1045.926 | 49.52 | 30.48 | 1152144 | 1152.144 | 46.71 | 33.29 | 1258362 | 1258.362 | 43.9 | 36.1 | 1364580 | 1364.58 | 45
11/8/20XX 9:00:00 AM | 0.375 | 2 | 45.4 | 56.9 | 45.4 |  | 45.4 | 69.34 | 10.66 | 402948 | 402.948 | 66.68 | 13.32 | 503496 | 503.496 | 64.02 | 15.98 | 604044 | 604.044 | 61.36 | 18.64 | 704592 | 704.592 | 58.7 | 21.3 | 805140 | 805.14 | 56.04 | 23.96 | 905688 | 905.688 | 53.38 | 26.62 | 1006236 | 1006.236 | 50.72 | 29.28 | 1106784 | 1106.784 | 48.06 | 31.94 | 1207332 | 1207.332 | 45.4 | 34.6 | 1307880 | 1307.88 | 45
11/8/20XX 10:00:00 AM | 0.41667 | 2 | 46.8 | 56.2 | 46.8 |  | 46.8 | 69.48 | 10.52 | 397656 | 397.656 | 66.96 | 13.04 | 492912 | 492.912 | 64.44 | 15.56 | 588168 | 588.168 | 61.92 | 18.08 | 683424 | 683.424 | 59.4 | 20.6 | 778680 | 778.68 | 56.88 | 23.12 | 873936 | 873.936 | 54.36 | 25.64 | 969192 | 969.192 | 51.84 | 28.16 | 1064448 | 1064.448 | 49.32 | 30.68 | 1159704 | 1159.704 | 46.8 | 33.2 | 1254960 | 1254.96 | 45
11/8/20XX 11:00:00 AM | 0.45833 | 2 | 49.4 | 51.3 | 49.4 |  | 49.4 | 69.74 | 10.26 | 387828 | 387.828 | 67.48 | 12.52 | 473256 | 473.256 | 65.22 | 14.78 | 558684 | 558.684 | 62.96 | 17.04 | 644112 | 644.112 | 60.7 | 19.3 | 729540 | 729.54 | 58.44 | 21.56 | 814968 | 814.968 | 56.18 | 23.82 | 900396 | 900.396 | 53.92 | 26.08 | 985824 | 985.824 | 51.66 | 28.34 | 1071252 | 1071.252 | 49.4 | 30.6 | 1156680 | 1156.68 | 50
11/8/20XX 12:00:00 PM | 0.5 | 2 | 52.1 | 47.8 | 52.1 |  | 52.1 | 70.01 | 9.99 | 377622 | 377.622 | 68.02 | 11.98 | 452844 | 452.844 | 66.03 | 13.97 | 528066 | 528.066 | 64.04 | 15.96 | 603288 | 603.288 | 62.05 | 17.95 | 678510 | 678.51 | 60.06 | 19.94 | 753732 | 753.732 | 58.07 | 21.93 | 828954 | 828.954 | 56.08 | 23.92 | 904176 | 904.176 | 54.09 | 25.91 | 979398 | 979.398 | 52.1 | 27.9 | 1054620 | 1054.62 | 50
11/8/20XX 1:00:00 PM | 0.54167 | 2 | 53.5 | 46.7 | 53.5 |  | 53.5 | 70.15 | 9.85 | 372330 | 372.33 | 68.3 | 11.7 | 442260 | 442.26 | 66.45 | 13.55 | 512190 | 512.19 | 64.6 | 15.4 | 582120 | 582.12 | 62.75 | 17.25 | 652050 | 652.05 | 60.9 | 19.1 | 721980 | 721.98 | 59.05 | 20.95 | 791910 | 791.91 | 57.2 | 22.8 | 861840 | 861.84 | 55.35 | 24.65 | 931770 | 931.77 | 53.5 | 26.5 | 1001700 | 1001.7 | 55
11/8/20XX 2:00:00 PM | 0.58333 | 2 | 54 | 45.6 | 54 |  | 54 | 70.2 | 9.8 | 370440 | 370.44 | 68.4 | 11.6 | 438480 | 438.48 | 66.6 | 13.4 | 506520 | 506.52 | 64.8 | 15.2 | 574560 | 574.56 | 63 | 17 | 642600 | 642.6 | 61.2 | 18.8 | 710640 | 710.64 | 59.4 | 20.6 | 778680 | 778.68 | 57.6 | 22.4 | 846720 | 846.72 | 55.8 | 24.2 | 914760 | 914.76 | 54 | 26 | 982800 | 982.8 | 55
11/8/20XX 3:00:00 PM | 0.625 | 2 | 54.5 | 45 | 54.5 |  | 54.5 | 70.25 | 9.75 | 368550 | 368.55 | 68.5 | 11.5 | 434700 | 434.7 | 66.75 | 13.25 | 500850 | 500.85 | 65 | 15 | 567000 | 567 | 63.25 | 16.75 | 633150 | 633.15 | 61.5 | 18.5 | 699300 | 699.3 | 59.75 | 20.25 | 765450 | 765.45 | 58 | 22 | 831600 | 831.6 | 56.25 | 23.75 | 897750 | 897.75 | 54.5 | 25.5 | 963900 | 963.9 | 55
11/8/20XX 4:00:00 PM | 0.66667 | 2 | 53.6 | 47.6 | 53.6 |  | 53.6 | 70.16 | 9.84 | 371952 | 371.952 | 68.32 | 11.68 | 441504 | 441.504 | 66.48 | 13.52 | 511056 | 511.056 | 64.64 | 15.36 | 580608 | 580.608 | 62.8 | 17.2 | 650160 | 650.16 | 60.96 | 19.04 | 719712 | 719.712 | 59.12 | 20.88 | 789264 | 789.264 | 57.28 | 22.72 | 858816 | 858.816 | 55.44 | 24.56 | 928368 | 928.368 | 53.6 | 26.4 | 997920 | 997.92 | 55
11/8/20XX 5:00:00 PM | 0.70833 | 2 | 52.1 | 48.9 | 52.1 |  | 52.1 | 70.01 | 9.99 | 377622 | 377.622 | 68.02 | 11.98 | 452844 | 452.844 | 66.03 | 13.97 | 528066 | 528.066 | 64.04 | 15.96 | 603288 | 603.288 | 62.05 | 17.95 | 678510 | 678.51 | 60.06 | 19.94 | 753732 | 753.732 | 58.07 | 21.93 | 828954 | 828.954 | 56.08 | 23.92 | 904176 | 904.176 | 54.09 | 25.91 | 979398 | 979.398 | 52.1 | 27.9 | 1054620 | 1054.62 | 50
11/8/20XX 6:00:00 PM | 0.75 | 2 | 51.3 | 50.3 | 51.3 |  | 51.3 | 69.93 | 10.07 | 380646 | 380.646 | 67.86 | 12.14 | 458892 | 458.892 | 65.79 | 14.21 | 537138 | 537.138 | 63.72 | 16.28 | 615384 | 615.384 | 61.65 | 18.35 | 693630 | 693.63 | 59.58 | 20.42 | 771876 | 771.876 | 57.51 | 22.49 | 850122 | 850.122 | 55.44 | 24.56 | 928368 | 928.368 | 53.37 | 26.63 | 1006614 | 1006.614 | 51.3 | 28.7 | 1084860 | 1084.86 | 50
11/8/20XX 7:00:00 PM | 0.79167 | 2 | 50.5 | 51 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/8/20XX 8:00:00 PM | 0.83333 | 2 | 49.7 | 52.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/8/20XX 9:00:00 PM | 0.875 | 2 | 49.2 | 53.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/8/20XX 10:00:00 PM | 0.91667 | 2 | 48.5 | 55.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/8/20XX 11:00:00 PM | 0.95833 | 2 | 47.8 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/8/20XX 12:00:00 AM | 0 | 3 | 47.6 | 59.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/9/20XX 1:00:00 AM | 0.041667 | 3 | 46.9 | 61.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/9/20XX 2:00:00 AM | 0.083333 | 3 | 46.5 | 62.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/9/20XX 3:00:00 AM | 0.125 | 3 | 45.9 | 64.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/9/20XX 4:00:00 AM | 0.16667 | 3 | 45.4 | 66.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/9/20XX 5:00:00 AM | 0.20833 | 3 | 45.3 | 68.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/9/20XX 6:00:00 AM | 0.25 | 3 | 44.5 | 70.2 | 44.5 |  | 44.5 | 69.25 | 10.75 | 406350 | 406.35 | 66.5 | 13.5 | 510300 | 510.3 | 63.75 | 16.25 | 614250 | 614.25 | 61 | 19 | 718200 | 718.2 | 58.25 | 21.75 | 822150 | 822.15 | 55.5 | 24.5 | 926100 | 926.1 | 52.75 | 27.25 | 1030050 | 1030.05 | 50 | 30 | 1134000 | 1134 | 47.25 | 32.75 | 1237950 | 1237.95 | 44.5 | 35.5 | 1341900 | 1341.9 | 45
11/9/20XX 7:00:00 AM | 0.29167 | 3 | 44.6 | 69.6 | 44.6 |  | 44.6 | 69.26 | 10.74 | 405972 | 405.972 | 66.52 | 13.48 | 509544 | 509.544 | 63.78 | 16.22 | 613116 | 613.116 | 61.04 | 18.96 | 716688 | 716.688 | 58.3 | 21.7 | 820260 | 820.26 | 55.56 | 24.44 | 923832 | 923.832 | 52.82 | 27.18 | 1027404 | 1027.404 | 50.08 | 29.92 | 1130976 | 1130.976 | 47.34 | 32.66 | 1234548 | 1234.548 | 44.6 | 35.4 | 1338120 | 1338.12 | 45
11/9/20XX 8:00:00 AM | 0.33333 | 3 | 46.5 | 67.3 | 46.5 |  | 46.5 | 69.45 | 10.55 | 398790 | 398.79 | 66.9 | 13.1 | 495180 | 495.18 | 64.35 | 15.65 | 591570 | 591.57 | 61.8 | 18.2 | 687960 | 687.96 | 59.25 | 20.75 | 784350 | 784.35 | 56.7 | 23.3 | 880740 | 880.74 | 54.15 | 25.85 | 977130 | 977.13 | 51.6 | 28.4 | 1073520 | 1073.52 | 49.05 | 30.95 | 1169910 | 1169.91 | 46.5 | 33.5 | 1266300 | 1266.3 | 45
11/9/20XX 9:00:00 AM | 0.375 | 3 | 49 | 62.2 | 49 |  | 49 | 69.7 | 10.3 | 389340 | 389.34 | 67.4 | 12.6 | 476280 | 476.28 | 65.1 | 14.9 | 563220 | 563.22 | 62.8 | 17.2 | 650160 | 650.16 | 60.5 | 19.5 | 737100 | 737.1 | 58.2 | 21.8 | 824040 | 824.04 | 55.9 | 24.1 | 910980 | 910.98 | 53.6 | 26.4 | 997920 | 997.92 | 51.3 | 28.7 | 1084860 | 1084.86 | 49 | 31 | 1171800 | 1171.8 | 50
11/9/20XX 10:00:00 AM | 0.41667 | 3 | 50.8 | 58.6 | 50.8 |  | 50.8 | 69.88 | 10.12 | 382536 | 382.536 | 67.76 | 12.24 | 462672 | 462.672 | 65.64 | 14.36 | 542808 | 542.808 | 63.52 | 16.48 | 622944 | 622.944 | 61.4 | 18.6 | 703080 | 703.08 | 59.28 | 20.72 | 783216 | 783.216 | 57.16 | 22.84 | 863352 | 863.352 | 55.04 | 24.96 | 943488 | 943.488 | 52.92 | 27.08 | 1023624 | 1023.624 | 50.8 | 29.2 | 1103760 | 1103.76 | 50
11/9/20XX 11:00:00 AM | 0.45833 | 3 | 52.8 | 53.7 | 52.8 |  | 52.8 | 70.08 | 9.92 | 374976 | 374.976 | 68.16 | 11.84 | 447552 | 447.552 | 66.24 | 13.76 | 520128 | 520.128 | 64.32 | 15.68 | 592704 | 592.704 | 62.4 | 17.6 | 665280 | 665.28 | 60.48 | 19.52 | 737856 | 737.856 | 58.56 | 21.44 | 810432 | 810.432 | 56.64 | 23.36 | 883008 | 883.008 | 54.72 | 25.28 | 955584 | 955.584 | 52.8 | 27.2 | 1028160 | 1028.16 | 55
11/9/20XX 12:00:00 PM | 0.5 | 3 | 54.9 | 52.4 | 54.9 |  | 54.9 | 70.29 | 9.71 | 367038 | 367.038 | 68.58 | 11.42 | 431676 | 431.676 | 66.87 | 13.13 | 496314 | 496.314 | 65.16 | 14.84 | 560952 | 560.952 | 63.45 | 16.55 | 625590 | 625.59 | 61.74 | 18.26 | 690228 | 690.228 | 60.03 | 19.97 | 754866 | 754.866 | 58.32 | 21.68 | 819504 | 819.504 | 56.61 | 23.39 | 884142 | 884.142 | 54.9 | 25.1 | 948780 | 948.78 | 55
11/9/20XX 1:00:00 PM | 0.54167 | 3 | 55.6 | 50.8 | 55.6 |  | 55.6 | 70.36 | 9.64 | 364392 | 364.392 | 68.72 | 11.28 | 426384 | 426.384 | 67.08 | 12.92 | 488376 | 488.376 | 65.44 | 14.56 | 550368 | 550.368 | 63.8 | 16.2 | 612360 | 612.36 | 62.16 | 17.84 | 674352 | 674.352 | 60.52 | 19.48 | 736344 | 736.344 | 58.88 | 21.12 | 798336 | 798.336 | 57.24 | 22.76 | 860328 | 860.328 | 55.6 | 24.4 | 922320 | 922.32 | 55
11/9/20XX 2:00:00 PM | 0.58333 | 3 | 55.6 | 51.5 | 55.6 |  | 55.6 | 70.36 | 9.64 | 364392 | 364.392 | 68.72 | 11.28 | 426384 | 426.384 | 67.08 | 12.92 | 488376 | 488.376 | 65.44 | 14.56 | 550368 | 550.368 | 63.8 | 16.2 | 612360 | 612.36 | 62.16 | 17.84 | 674352 | 674.352 | 60.52 | 19.48 | 736344 | 736.344 | 58.88 | 21.12 | 798336 | 798.336 | 57.24 | 22.76 | 860328 | 860.328 | 55.6 | 24.4 | 922320 | 922.32 | 55
11/9/20XX 3:00:00 PM | 0.625 | 3 | 55.5 | 52.8 | 55.5 |  | 55.5 | 70.35 | 9.65 | 364770 | 364.77 | 68.7 | 11.3 | 427140 | 427.14 | 67.05 | 12.95 | 489510 | 489.51 | 65.4 | 14.6 | 551880 | 551.88 | 63.75 | 16.25 | 614250 | 614.25 | 62.1 | 17.9 | 676620 | 676.62 | 60.45 | 19.55 | 738990 | 738.99 | 58.8 | 21.2 | 801360 | 801.36 | 57.15 | 22.85 | 863730 | 863.73 | 55.5 | 24.5 | 926100 | 926.1 | 55
11/9/20XX 4:00:00 PM | 0.66667 | 3 | 54.1 | 58.7 | 54.1 |  | 54.1 | 70.21 | 9.79 | 370062 | 370.062 | 68.42 | 11.58 | 437724 | 437.724 | 66.63 | 13.37 | 505386 | 505.386 | 64.84 | 15.16 | 573048 | 573.048 | 63.05 | 16.95 | 640710 | 640.71 | 61.26 | 18.74 | 708372 | 708.372 | 59.47 | 20.53 | 776034 | 776.034 | 57.68 | 22.32 | 843696 | 843.696 | 55.89 | 24.11 | 911358 | 911.358 | 54.1 | 25.9 | 979020 | 979.02 | 55
11/9/20XX 5:00:00 PM | 0.70833 | 3 | 53.5 | 62 | 53.5 |  | 53.5 | 70.15 | 9.85 | 372330 | 372.33 | 68.3 | 11.7 | 442260 | 442.26 | 66.45 | 13.55 | 512190 | 512.19 | 64.6 | 15.4 | 582120 | 582.12 | 62.75 | 17.25 | 652050 | 652.05 | 60.9 | 19.1 | 721980 | 721.98 | 59.05 | 20.95 | 791910 | 791.91 | 57.2 | 22.8 | 861840 | 861.84 | 55.35 | 24.65 | 931770 | 931.77 | 53.5 | 26.5 | 1001700 | 1001.7 | 55
11/9/20XX 6:00:00 PM | 0.75 | 3 | 52.8 | 64.8 | 52.8 |  | 52.8 | 70.08 | 9.92 | 374976 | 374.976 | 68.16 | 11.84 | 447552 | 447.552 | 66.24 | 13.76 | 520128 | 520.128 | 64.32 | 15.68 | 592704 | 592.704 | 62.4 | 17.6 | 665280 | 665.28 | 60.48 | 19.52 | 737856 | 737.856 | 58.56 | 21.44 | 810432 | 810.432 | 56.64 | 23.36 | 883008 | 883.008 | 54.72 | 25.28 | 955584 | 955.584 | 52.8 | 27.2 | 1028160 | 1028.16 | 55
11/9/20XX 7:00:00 PM | 0.79167 | 3 | 52.9 | 65.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/9/20XX 8:00:00 PM | 0.83333 | 3 | 52.5 | 67.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/9/20XX 9:00:00 PM | 0.875 | 3 | 52.6 | 67.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/9/20XX 10:00:00 PM | 0.91667 | 3 | 52.3 | 68.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/9/20XX 11:00:00 PM | 0.95833 | 3 | 51.8 | 69.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/9/20XX 12:00:00 AM | 0 | 4 | 51.3 | 71.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/10/20XX 1:00:00 AM | 0.041667 | 4 | 50.4 | 73.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/10/20XX 2:00:00 AM | 0.083333 | 4 | 50 | 71.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/10/20XX 3:00:00 AM | 0.125 | 4 | 49.3 | 72.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/10/20XX 4:00:00 AM | 0.16667 | 4 | 48.8 | 73.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/10/20XX 5:00:00 AM | 0.20833 | 4 | 48.1 | 72.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/10/20XX 6:00:00 AM | 0.25 | 4 | 47.8 | 72.4 | 47.8 |  | 47.8 | 69.58 | 10.42 | 393876 | 393.876 | 67.16 | 12.84 | 485352 | 485.352 | 64.74 | 15.26 | 576828 | 576.828 | 62.32 | 17.68 | 668304 | 668.304 | 59.9 | 20.1 | 759780 | 759.78 | 57.48 | 22.52 | 851256 | 851.256 | 55.06 | 24.94 | 942732 | 942.732 | 52.64 | 27.36 | 1034208 | 1034.208 | 50.22 | 29.78 | 1125684 | 1125.684 | 47.8 | 32.2 | 1217160 | 1217.16 | 50
11/10/20XX 7:00:00 AM | 0.29167 | 4 | 47.2 | 70.1 | 47.2 |  | 47.2 | 69.52 | 10.48 | 396144 | 396.144 | 67.04 | 12.96 | 489888 | 489.888 | 64.56 | 15.44 | 583632 | 583.632 | 62.08 | 17.92 | 677376 | 677.376 | 59.6 | 20.4 | 771120 | 771.12 | 57.12 | 22.88 | 864864 | 864.864 | 54.64 | 25.36 | 958608 | 958.608 | 52.16 | 27.84 | 1052352 | 1052.352 | 49.68 | 30.32 | 1146096 | 1146.096 | 47.2 | 32.8 | 1239840 | 1239.84 | 45
11/10/20XX 8:00:00 AM | 0.33333 | 4 | 48.1 | 67.1 | 48.1 |  | 48.1 | 69.61 | 10.39 | 392742 | 392.742 | 67.22 | 12.78 | 483084 | 483.084 | 64.83 | 15.17 | 573426 | 573.426 | 62.44 | 17.56 | 663768 | 663.768 | 60.05 | 19.95 | 754110 | 754.11 | 57.66 | 22.34 | 844452 | 844.452 | 55.27 | 24.73 | 934794 | 934.794 | 52.88 | 27.12 | 1025136 | 1025.136 | 50.49 | 29.51 | 1115478 | 1115.478 | 48.1 | 31.9 | 1205820 | 1205.82 | 50
11/10/20XX 9:00:00 AM | 0.375 | 4 | 49.4 | 62.6 | 49.4 |  | 49.4 | 69.74 | 10.26 | 387828 | 387.828 | 67.48 | 12.52 | 473256 | 473.256 | 65.22 | 14.78 | 558684 | 558.684 | 62.96 | 17.04 | 644112 | 644.112 | 60.7 | 19.3 | 729540 | 729.54 | 58.44 | 21.56 | 814968 | 814.968 | 56.18 | 23.82 | 900396 | 900.396 | 53.92 | 26.08 | 985824 | 985.824 | 51.66 | 28.34 | 1071252 | 1071.252 | 49.4 | 30.6 | 1156680 | 1156.68 | 50
11/10/20XX 10:00:00 AM | 0.41667 | 4 | 50.8 | 58.9 | 50.8 |  | 50.8 | 69.88 | 10.12 | 382536 | 382.536 | 67.76 | 12.24 | 462672 | 462.672 | 65.64 | 14.36 | 542808 | 542.808 | 63.52 | 16.48 | 622944 | 622.944 | 61.4 | 18.6 | 703080 | 703.08 | 59.28 | 20.72 | 783216 | 783.216 | 57.16 | 22.84 | 863352 | 863.352 | 55.04 | 24.96 | 943488 | 943.488 | 52.92 | 27.08 | 1023624 | 1023.624 | 50.8 | 29.2 | 1103760 | 1103.76 | 50
11/10/20XX 11:00:00 AM | 0.45833 | 4 | 52.3 | 54.7 | 52.3 |  | 52.3 | 70.03 | 9.97 | 376866 | 376.866 | 68.06 | 11.94 | 451332 | 451.332 | 66.09 | 13.91 | 525798 | 525.798 | 64.12 | 15.88 | 600264 | 600.264 | 62.15 | 17.85 | 674730 | 674.73 | 60.18 | 19.82 | 749196 | 749.196 | 58.21 | 21.79 | 823662 | 823.662 | 56.24 | 23.76 | 898128 | 898.128 | 54.27 | 25.73 | 972594 | 972.594 | 52.3 | 27.7 | 1047060 | 1047.06 | 50
11/10/20XX 12:00:00 PM | 0.5 | 4 | 53.9 | 51.8 | 53.9 |  | 53.9 | 70.19 | 9.81 | 370818 | 370.818 | 68.38 | 11.62 | 439236 | 439.236 | 66.57 | 13.43 | 507654 | 507.654 | 64.76 | 15.24 | 576072 | 576.072 | 62.95 | 17.05 | 644490 | 644.49 | 61.14 | 18.86 | 712908 | 712.908 | 59.33 | 20.67 | 781326 | 781.326 | 57.52 | 22.48 | 849744 | 849.744 | 55.71 | 24.29 | 918162 | 918.162 | 53.9 | 26.1 | 986580 | 986.58 | 55
11/10/20XX 1:00:00 PM | 0.54167 | 4 | 54.4 | 49.7 | 54.4 |  | 54.4 | 70.24 | 9.76 | 368928 | 368.928 | 68.48 | 11.52 | 435456 | 435.456 | 66.72 | 13.28 | 501984 | 501.984 | 64.96 | 15.04 | 568512 | 568.512 | 63.2 | 16.8 | 635040 | 635.04 | 61.44 | 18.56 | 701568 | 701.568 | 59.68 | 20.32 | 768096 | 768.096 | 57.92 | 22.08 | 834624 | 834.624 | 56.16 | 23.84 | 901152 | 901.152 | 54.4 | 25.6 | 967680 | 967.68 | 55
11/10/20XX 2:00:00 PM | 0.58333 | 4 | 54.3 | 48.2 | 54.3 |  | 54.3 | 70.23 | 9.77 | 369306 | 369.306 | 68.46 | 11.54 | 436212 | 436.212 | 66.69 | 13.31 | 503118 | 503.118 | 64.92 | 15.08 | 570024 | 570.024 | 63.15 | 16.85 | 636930 | 636.93 | 61.38 | 18.62 | 703836 | 703.836 | 59.61 | 20.39 | 770742 | 770.742 | 57.84 | 22.16 | 837648 | 837.648 | 56.07 | 23.93 | 904554 | 904.554 | 54.3 | 25.7 | 971460 | 971.46 | 55
11/10/20XX 3:00:00 PM | 0.625 | 4 | 53.7 | 49.1 | 53.7 |  | 53.7 | 70.17 | 9.83 | 371574 | 371.574 | 68.34 | 11.66 | 440748 | 440.748 | 66.51 | 13.49 | 509922 | 509.922 | 64.68 | 15.32 | 579096 | 579.096 | 62.85 | 17.15 | 648270 | 648.27 | 61.02 | 18.98 | 717444 | 717.444 | 59.19 | 20.81 | 786618 | 786.618 | 57.36 | 22.64 | 855792 | 855.792 | 55.53 | 24.47 | 924966 | 924.966 | 53.7 | 26.3 | 994140 | 994.14 | 55
11/10/20XX 4:00:00 PM | 0.66667 | 4 | 52.9 | 49.5 | 52.9 |  | 52.9 | 70.09 | 9.91 | 374598 | 374.598 | 68.18 | 11.82 | 446796 | 446.796 | 66.27 | 13.73 | 518994 | 518.994 | 64.36 | 15.64 | 591192 | 591.192 | 62.45 | 17.55 | 663390 | 663.39 | 60.54 | 19.46 | 735588 | 735.588 | 58.63 | 21.37 | 807786 | 807.786 | 56.72 | 23.28 | 879984 | 879.984 | 54.81 | 25.19 | 952182 | 952.182 | 52.9 | 27.1 | 1024380 | 1024.38 | 55
11/10/20XX 5:00:00 PM | 0.70833 | 4 | 51.3 | 51.8 | 51.3 |  | 51.3 | 69.93 | 10.07 | 380646 | 380.646 | 67.86 | 12.14 | 458892 | 458.892 | 65.79 | 14.21 | 537138 | 537.138 | 63.72 | 16.28 | 615384 | 615.384 | 61.65 | 18.35 | 693630 | 693.63 | 59.58 | 20.42 | 771876 | 771.876 | 57.51 | 22.49 | 850122 | 850.122 | 55.44 | 24.56 | 928368 | 928.368 | 53.37 | 26.63 | 1006614 | 1006.614 | 51.3 | 28.7 | 1084860 | 1084.86 | 50
11/10/20XX 6:00:00 PM | 0.75 | 4 | 50.3 | 52.7 | 50.3 |  | 50.3 | 69.83 | 10.17 | 384426 | 384.426 | 67.66 | 12.34 | 466452 | 466.452 | 65.49 | 14.51 | 548478 | 548.478 | 63.32 | 16.68 | 630504 | 630.504 | 61.15 | 18.85 | 712530 | 712.53 | 58.98 | 21.02 | 794556 | 794.556 | 56.81 | 23.19 | 876582 | 876.582 | 54.64 | 25.36 | 958608 | 958.608 | 52.47 | 27.53 | 1040634 | 1040.634 | 50.3 | 29.7 | 1122660 | 1122.66 | 50
11/10/20XX 7:00:00 PM | 0.79167 | 4 | 49.8 | 53.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/10/20XX 8:00:00 PM | 0.83333 | 4 | 49.1 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/10/20XX 9:00:00 PM | 0.875 | 4 | 48.4 | 56.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/10/20XX 10:00:00 PM | 0.91667 | 4 | 47.7 | 58 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/10/20XX 11:00:00 PM | 0.95833 | 4 | 47.2 | 59.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/10/20XX 12:00:00 AM | 0 | 5 | 46.6 | 62.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/11/20XX 1:00:00 AM | 0.041667 | 5 | 46 | 63.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/11/20XX 2:00:00 AM | 0.083333 | 5 | 45.8 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/11/20XX 3:00:00 AM | 0.125 | 5 | 44.8 | 65.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/11/20XX 4:00:00 AM | 0.16667 | 5 | 44.5 | 66 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/11/20XX 5:00:00 AM | 0.20833 | 5 | 44.4 | 64.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/11/20XX 6:00:00 AM | 0.25 | 5 | 44.1 | 65.3 | 44.1 |  | 44.1 | 69.21 | 10.79 | 407862 | 407.862 | 66.42 | 13.58 | 513324 | 513.324 | 63.63 | 16.37 | 618786 | 618.786 | 60.84 | 19.16 | 724248 | 724.248 | 58.05 | 21.95 | 829710 | 829.71 | 55.26 | 24.74 | 935172 | 935.172 | 52.47 | 27.53 | 1040634 | 1040.634 | 49.68 | 30.32 | 1146096 | 1146.096 | 46.89 | 33.11 | 1251558 | 1251.558 | 44.1 | 35.9 | 1357020 | 1357.02 | 45
11/11/20XX 7:00:00 AM | 0.29167 | 5 | 44 | 65.7 | 44 |  | 44 | 69.2 | 10.8 | 408240 | 408.24 | 66.4 | 13.6 | 514080 | 514.08 | 63.6 | 16.4 | 619920 | 619.92 | 60.8 | 19.2 | 725760 | 725.76 | 58 | 22 | 831600 | 831.6 | 55.2 | 24.8 | 937440 | 937.44 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.6 | 30.4 | 1149120 | 1149.12 | 46.8 | 33.2 | 1254960 | 1254.96 | 44 | 36 | 1360800 | 1360.8 | 45
11/11/20XX 8:00:00 AM | 0.33333 | 5 | 44.9 | 62.5 | 44.9 |  | 44.9 | 69.29 | 10.71 | 404838 | 404.838 | 66.58 | 13.42 | 507276 | 507.276 | 63.87 | 16.13 | 609714 | 609.714 | 61.16 | 18.84 | 712152 | 712.152 | 58.45 | 21.55 | 814590 | 814.59 | 55.74 | 24.26 | 917028 | 917.028 | 53.03 | 26.97 | 1019466 | 1019.466 | 50.32 | 29.68 | 1121904 | 1121.904 | 47.61 | 32.39 | 1224342 | 1224.342 | 44.9 | 35.1 | 1326780 | 1326.78 | 45
11/11/20XX 9:00:00 AM | 0.375 | 5 | 46.6 | 57.7 | 46.6 |  | 46.6 | 69.46 | 10.54 | 398412 | 398.412 | 66.92 | 13.08 | 494424 | 494.424 | 64.38 | 15.62 | 590436 | 590.436 | 61.84 | 18.16 | 686448 | 686.448 | 59.3 | 20.7 | 782460 | 782.46 | 56.76 | 23.24 | 878472 | 878.472 | 54.22 | 25.78 | 974484 | 974.484 | 51.68 | 28.32 | 1070496 | 1070.496 | 49.14 | 30.86 | 1166508 | 1166.508 | 46.6 | 33.4 | 1262520 | 1262.52 | 45
11/11/20XX 10:00:00 AM | 0.41667 | 5 | 48.6 | 54.4 | 48.6 |  | 48.6 | 69.66 | 10.34 | 390852 | 390.852 | 67.32 | 12.68 | 479304 | 479.304 | 64.98 | 15.02 | 567756 | 567.756 | 62.64 | 17.36 | 656208 | 656.208 | 60.3 | 19.7 | 744660 | 744.66 | 57.96 | 22.04 | 833112 | 833.112 | 55.62 | 24.38 | 921564 | 921.564 | 53.28 | 26.72 | 1010016 | 1010.016 | 50.94 | 29.06 | 1098468 | 1098.468 | 48.6 | 31.4 | 1186920 | 1186.92 | 50
11/11/20XX 11:00:00 AM | 0.45833 | 5 | 50.5 | 50.5 | 50.5 |  | 50.5 | 69.85 | 10.15 | 383670 | 383.67 | 67.7 | 12.3 | 464940 | 464.94 | 65.55 | 14.45 | 546210 | 546.21 | 63.4 | 16.6 | 627480 | 627.48 | 61.25 | 18.75 | 708750 | 708.75 | 59.1 | 20.9 | 790020 | 790.02 | 56.95 | 23.05 | 871290 | 871.29 | 54.8 | 25.2 | 952560 | 952.56 | 52.65 | 27.35 | 1033830 | 1033.83 | 50.5 | 29.5 | 1115100 | 1115.1 | 50
11/11/20XX 12:00:00 PM | 0.5 | 5 | 52 | 47.1 | 52 |  | 52 | 70 | 10 | 378000 | 378 | 68 | 12 | 453600 | 453.6 | 66 | 14 | 529200 | 529.2 | 64 | 16 | 604800 | 604.8 | 62 | 18 | 680400 | 680.4 | 60 | 20 | 756000 | 756 | 58 | 22 | 831600 | 831.6 | 56 | 24 | 907200 | 907.2 | 54 | 26 | 982800 | 982.8 | 52 | 28 | 1058400 | 1058.4 | 50
11/11/20XX 1:00:00 PM | 0.54167 | 5 | 52.8 | 45.1 | 52.8 |  | 52.8 | 70.08 | 9.92 | 374976 | 374.976 | 68.16 | 11.84 | 447552 | 447.552 | 66.24 | 13.76 | 520128 | 520.128 | 64.32 | 15.68 | 592704 | 592.704 | 62.4 | 17.6 | 665280 | 665.28 | 60.48 | 19.52 | 737856 | 737.856 | 58.56 | 21.44 | 810432 | 810.432 | 56.64 | 23.36 | 883008 | 883.008 | 54.72 | 25.28 | 955584 | 955.584 | 52.8 | 27.2 | 1028160 | 1028.16 | 55
11/11/20XX 2:00:00 PM | 0.58333 | 5 | 52.9 | 45.1 | 52.9 |  | 52.9 | 70.09 | 9.91 | 374598 | 374.598 | 68.18 | 11.82 | 446796 | 446.796 | 66.27 | 13.73 | 518994 | 518.994 | 64.36 | 15.64 | 591192 | 591.192 | 62.45 | 17.55 | 663390 | 663.39 | 60.54 | 19.46 | 735588 | 735.588 | 58.63 | 21.37 | 807786 | 807.786 | 56.72 | 23.28 | 879984 | 879.984 | 54.81 | 25.19 | 952182 | 952.182 | 52.9 | 27.1 | 1024380 | 1024.38 | 55
11/11/20XX 3:00:00 PM | 0.625 | 5 | 52.6 | 45.4 | 52.6 |  | 52.6 | 70.06 | 9.94 | 375732 | 375.732 | 68.12 | 11.88 | 449064 | 449.064 | 66.18 | 13.82 | 522396 | 522.396 | 64.24 | 15.76 | 595728 | 595.728 | 62.3 | 17.7 | 669060 | 669.06 | 60.36 | 19.64 | 742392 | 742.392 | 58.42 | 21.58 | 815724 | 815.724 | 56.48 | 23.52 | 889056 | 889.056 | 54.54 | 25.46 | 962388 | 962.388 | 52.6 | 27.4 | 1035720 | 1035.72 | 55
11/11/20XX 4:00:00 PM | 0.66667 | 5 | 52.1 | 45.9 | 52.1 |  | 52.1 | 70.01 | 9.99 | 377622 | 377.622 | 68.02 | 11.98 | 452844 | 452.844 | 66.03 | 13.97 | 528066 | 528.066 | 64.04 | 15.96 | 603288 | 603.288 | 62.05 | 17.95 | 678510 | 678.51 | 60.06 | 19.94 | 753732 | 753.732 | 58.07 | 21.93 | 828954 | 828.954 | 56.08 | 23.92 | 904176 | 904.176 | 54.09 | 25.91 | 979398 | 979.398 | 52.1 | 27.9 | 1054620 | 1054.62 | 50
11/11/20XX 5:00:00 PM | 0.70833 | 5 | 51.2 | 48.3 | 51.2 |  | 51.2 | 69.92 | 10.08 | 381024 | 381.024 | 67.84 | 12.16 | 459648 | 459.648 | 65.76 | 14.24 | 538272 | 538.272 | 63.68 | 16.32 | 616896 | 616.896 | 61.6 | 18.4 | 695520 | 695.52 | 59.52 | 20.48 | 774144 | 774.144 | 57.44 | 22.56 | 852768 | 852.768 | 55.36 | 24.64 | 931392 | 931.392 | 53.28 | 26.72 | 1010016 | 1010.016 | 51.2 | 28.8 | 1088640 | 1088.64 | 50
11/11/20XX 6:00:00 PM | 0.75 | 5 | 50.1 | 50.5 | 50.1 |  | 50.1 | 69.81 | 10.19 | 385182 | 385.182 | 67.62 | 12.38 | 467964 | 467.964 | 65.43 | 14.57 | 550746 | 550.746 | 63.24 | 16.76 | 633528 | 633.528 | 61.05 | 18.95 | 716310 | 716.31 | 58.86 | 21.14 | 799092 | 799.092 | 56.67 | 23.33 | 881874 | 881.874 | 54.48 | 25.52 | 964656 | 964.656 | 52.29 | 27.71 | 1047438 | 1047.438 | 50.1 | 29.9 | 1130220 | 1130.22 | 50
11/11/20XX 7:00:00 PM | 0.79167 | 5 | 49.7 | 51.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/11/20XX 8:00:00 PM | 0.83333 | 5 | 49.2 | 51.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/11/20XX 9:00:00 PM | 0.875 | 5 | 48.6 | 52.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/11/20XX 10:00:00 PM | 0.91667 | 5 | 48 | 53 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/11/20XX 11:00:00 PM | 0.95833 | 5 | 47.5 | 55.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/11/20XX 12:00:00 AM | 0 | 6 | 47.3 | 56.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/12/20XX 1:00:00 AM | 0.041667 | 6 | 46.6 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/12/20XX 2:00:00 AM | 0.083333 | 6 | 46.4 | 60.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/12/20XX 3:00:00 AM | 0.125 | 6 | 45.7 | 61.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/12/20XX 4:00:00 AM | 0.16667 | 6 | 45.3 | 63.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/12/20XX 5:00:00 AM | 0.20833 | 6 | 44.9 | 65.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/12/20XX 6:00:00 AM | 0.25 | 6 | 44.2 | 67.9 | 44.2 |  | 44.2 | 69.22 | 10.78 | 407484 | 407.484 | 66.44 | 13.56 | 512568 | 512.568 | 63.66 | 16.34 | 617652 | 617.652 | 60.88 | 19.12 | 722736 | 722.736 | 58.1 | 21.9 | 827820 | 827.82 | 55.32 | 24.68 | 932904 | 932.904 | 52.54 | 27.46 | 1037988 | 1037.988 | 49.76 | 30.24 | 1143072 | 1143.072 | 46.98 | 33.02 | 1248156 | 1248.156 | 44.2 | 35.8 | 1353240 | 1353.24 | 45
11/12/20XX 7:00:00 AM | 0.29167 | 6 | 43.7 | 68.8 | 43.7 |  | 43.7 | 69.17 | 10.83 | 409374 | 409.374 | 66.34 | 13.66 | 516348 | 516.348 | 63.51 | 16.49 | 623322 | 623.322 | 60.68 | 19.32 | 730296 | 730.296 | 57.85 | 22.15 | 837270 | 837.27 | 55.02 | 24.98 | 944244 | 944.244 | 52.19 | 27.81 | 1051218 | 1051.218 | 49.36 | 30.64 | 1158192 | 1158.192 | 46.53 | 33.47 | 1265166 | 1265.166 | 43.7 | 36.3 | 1372140 | 1372.14 | 45
11/12/20XX 8:00:00 AM | 0.33333 | 6 | 44.3 | 66.9 | 44.3 |  | 44.3 | 69.23 | 10.77 | 407106 | 407.106 | 66.46 | 13.54 | 511812 | 511.812 | 63.69 | 16.31 | 616518 | 616.518 | 60.92 | 19.08 | 721224 | 721.224 | 58.15 | 21.85 | 825930 | 825.93 | 55.38 | 24.62 | 930636 | 930.636 | 52.61 | 27.39 | 1035342 | 1035.342 | 49.84 | 30.16 | 1140048 | 1140.048 | 47.07 | 32.93 | 1244754 | 1244.754 | 44.3 | 35.7 | 1349460 | 1349.46 | 45
11/12/20XX 9:00:00 AM | 0.375 | 6 | 46.1 | 60.9 | 46.1 |  | 46.1 | 69.41 | 10.59 | 400302 | 400.302 | 66.82 | 13.18 | 498204 | 498.204 | 64.23 | 15.77 | 596106 | 596.106 | 61.64 | 18.36 | 694008 | 694.008 | 59.05 | 20.95 | 791910 | 791.91 | 56.46 | 23.54 | 889812 | 889.812 | 53.87 | 26.13 | 987714 | 987.714 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.69 | 31.31 | 1183518 | 1183.518 | 46.1 | 33.9 | 1281420 | 1281.42 | 45
11/12/20XX 10:00:00 AM | 0.41667 | 6 | 48.6 | 55.9 | 48.6 |  | 48.6 | 69.66 | 10.34 | 390852 | 390.852 | 67.32 | 12.68 | 479304 | 479.304 | 64.98 | 15.02 | 567756 | 567.756 | 62.64 | 17.36 | 656208 | 656.208 | 60.3 | 19.7 | 744660 | 744.66 | 57.96 | 22.04 | 833112 | 833.112 | 55.62 | 24.38 | 921564 | 921.564 | 53.28 | 26.72 | 1010016 | 1010.016 | 50.94 | 29.06 | 1098468 | 1098.468 | 48.6 | 31.4 | 1186920 | 1186.92 | 50
11/12/20XX 11:00:00 AM | 0.45833 | 6 | 49.9 | 53.4 | 49.9 |  | 49.9 | 69.79 | 10.21 | 385938 | 385.938 | 67.58 | 12.42 | 469476 | 469.476 | 65.37 | 14.63 | 553014 | 553.014 | 63.16 | 16.84 | 636552 | 636.552 | 60.95 | 19.05 | 720090 | 720.09 | 58.74 | 21.26 | 803628 | 803.628 | 56.53 | 23.47 | 887166 | 887.166 | 54.32 | 25.68 | 970704 | 970.704 | 52.11 | 27.89 | 1054242 | 1054.242 | 49.9 | 30.1 | 1137780 | 1137.78 | 50
11/12/20XX 12:00:00 PM | 0.5 | 6 | 51.3 | 51.7 | 51.3 |  | 51.3 | 69.93 | 10.07 | 380646 | 380.646 | 67.86 | 12.14 | 458892 | 458.892 | 65.79 | 14.21 | 537138 | 537.138 | 63.72 | 16.28 | 615384 | 615.384 | 61.65 | 18.35 | 693630 | 693.63 | 59.58 | 20.42 | 771876 | 771.876 | 57.51 | 22.49 | 850122 | 850.122 | 55.44 | 24.56 | 928368 | 928.368 | 53.37 | 26.63 | 1006614 | 1006.614 | 51.3 | 28.7 | 1084860 | 1084.86 | 50
11/12/20XX 1:00:00 PM | 0.54167 | 6 | 52.9 | 49.5 | 52.9 |  | 52.9 | 70.09 | 9.91 | 374598 | 374.598 | 68.18 | 11.82 | 446796 | 446.796 | 66.27 | 13.73 | 518994 | 518.994 | 64.36 | 15.64 | 591192 | 591.192 | 62.45 | 17.55 | 663390 | 663.39 | 60.54 | 19.46 | 735588 | 735.588 | 58.63 | 21.37 | 807786 | 807.786 | 56.72 | 23.28 | 879984 | 879.984 | 54.81 | 25.19 | 952182 | 952.182 | 52.9 | 27.1 | 1024380 | 1024.38 | 55
11/12/20XX 2:00:00 PM | 0.58333 | 6 | 53 | 48.7 | 53 |  | 53 | 70.1 | 9.9 | 374220 | 374.22 | 68.2 | 11.8 | 446040 | 446.04 | 66.3 | 13.7 | 517860 | 517.86 | 64.4 | 15.6 | 589680 | 589.68 | 62.5 | 17.5 | 661500 | 661.5 | 60.6 | 19.4 | 733320 | 733.32 | 58.7 | 21.3 | 805140 | 805.14 | 56.8 | 23.2 | 876960 | 876.96 | 54.9 | 25.1 | 948780 | 948.78 | 53 | 27 | 1020600 | 1020.6 | 55
11/12/20XX 3:00:00 PM | 0.625 | 6 | 52.6 | 48.1 | 52.6 |  | 52.6 | 70.06 | 9.94 | 375732 | 375.732 | 68.12 | 11.88 | 449064 | 449.064 | 66.18 | 13.82 | 522396 | 522.396 | 64.24 | 15.76 | 595728 | 595.728 | 62.3 | 17.7 | 669060 | 669.06 | 60.36 | 19.64 | 742392 | 742.392 | 58.42 | 21.58 | 815724 | 815.724 | 56.48 | 23.52 | 889056 | 889.056 | 54.54 | 25.46 | 962388 | 962.388 | 52.6 | 27.4 | 1035720 | 1035.72 | 55
11/12/20XX 4:00:00 PM | 0.66667 | 6 | 52.5 | 48.4 | 52.5 |  | 52.5 | 70.05 | 9.95 | 376110 | 376.11 | 68.1 | 11.9 | 449820 | 449.82 | 66.15 | 13.85 | 523530 | 523.53 | 64.2 | 15.8 | 597240 | 597.24 | 62.25 | 17.75 | 670950 | 670.95 | 60.3 | 19.7 | 744660 | 744.66 | 58.35 | 21.65 | 818370 | 818.37 | 56.4 | 23.6 | 892080 | 892.08 | 54.45 | 25.55 | 965790 | 965.79 | 52.5 | 27.5 | 1039500 | 1039.5 | 50
11/12/20XX 5:00:00 PM | 0.70833 | 6 | 51.7 | 49.9 | 51.7 |  | 51.7 | 69.97 | 10.03 | 379134 | 379.134 | 67.94 | 12.06 | 455868 | 455.868 | 65.91 | 14.09 | 532602 | 532.602 | 63.88 | 16.12 | 609336 | 609.336 | 61.85 | 18.15 | 686070 | 686.07 | 59.82 | 20.18 | 762804 | 762.804 | 57.79 | 22.21 | 839538 | 839.538 | 55.76 | 24.24 | 916272 | 916.272 | 53.73 | 26.27 | 993006 | 993.006 | 51.7 | 28.3 | 1069740 | 1069.74 | 50
11/12/20XX 6:00:00 PM | 0.75 | 6 | 50.9 | 51.2 | 50.9 |  | 50.9 | 69.89 | 10.11 | 382158 | 382.158 | 67.78 | 12.22 | 461916 | 461.916 | 65.67 | 14.33 | 541674 | 541.674 | 63.56 | 16.44 | 621432 | 621.432 | 61.45 | 18.55 | 701190 | 701.19 | 59.34 | 20.66 | 780948 | 780.948 | 57.23 | 22.77 | 860706 | 860.706 | 55.12 | 24.88 | 940464 | 940.464 | 53.01 | 26.99 | 1020222 | 1020.222 | 50.9 | 29.1 | 1099980 | 1099.98 | 50
11/12/20XX 7:00:00 PM | 0.79167 | 6 | 50.7 | 52.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/12/20XX 8:00:00 PM | 0.83333 | 6 | 50.3 | 54.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/12/20XX 9:00:00 PM | 0.875 | 6 | 49.5 | 56.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/12/20XX 10:00:00 PM | 0.91667 | 6 | 49.4 | 56.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/12/20XX 11:00:00 PM | 0.95833 | 6 | 48.8 | 58 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/12/20XX 12:00:00 AM | 0 | 7 | 48.1 | 59.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/13/20XX 1:00:00 AM | 0.041667 | 7 | 47.7 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/13/20XX 2:00:00 AM | 0.083333 | 7 | 47.3 | 60.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/13/20XX 3:00:00 AM | 0.125 | 7 | 47 | 61.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/13/20XX 4:00:00 AM | 0.16667 | 7 | 46.7 | 63.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/13/20XX 5:00:00 AM | 0.20833 | 7 | 45.2 | 64.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/13/20XX 6:00:00 AM | 0.25 | 7 | 45 | 64.8 | 45 |  | 45 | 69.3 | 10.7 | 404460 | 404.46 | 66.6 | 13.4 | 506520 | 506.52 | 63.9 | 16.1 | 608580 | 608.58 | 61.2 | 18.8 | 710640 | 710.64 | 58.5 | 21.5 | 812700 | 812.7 | 55.8 | 24.2 | 914760 | 914.76 | 53.1 | 26.9 | 1016820 | 1016.82 | 50.4 | 29.6 | 1118880 | 1118.88 | 47.7 | 32.3 | 1220940 | 1220.94 | 45 | 35 | 1323000 | 1323 | 45
11/13/20XX 7:00:00 AM | 0.29167 | 7 | 44.9 | 64.6 | 44.9 |  | 44.9 | 69.29 | 10.71 | 404838 | 404.838 | 66.58 | 13.42 | 507276 | 507.276 | 63.87 | 16.13 | 609714 | 609.714 | 61.16 | 18.84 | 712152 | 712.152 | 58.45 | 21.55 | 814590 | 814.59 | 55.74 | 24.26 | 917028 | 917.028 | 53.03 | 26.97 | 1019466 | 1019.466 | 50.32 | 29.68 | 1121904 | 1121.904 | 47.61 | 32.39 | 1224342 | 1224.342 | 44.9 | 35.1 | 1326780 | 1326.78 | 45
11/13/20XX 8:00:00 AM | 0.33333 | 7 | 45.3 | 66.1 | 45.3 |  | 45.3 | 69.33 | 10.67 | 403326 | 403.326 | 66.66 | 13.34 | 504252 | 504.252 | 63.99 | 16.01 | 605178 | 605.178 | 61.32 | 18.68 | 706104 | 706.104 | 58.65 | 21.35 | 807030 | 807.03 | 55.98 | 24.02 | 907956 | 907.956 | 53.31 | 26.69 | 1008882 | 1008.882 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.97 | 32.03 | 1210734 | 1210.734 | 45.3 | 34.7 | 1311660 | 1311.66 | 45
11/13/20XX 9:00:00 AM | 0.375 | 7 | 46.6 | 62.6 | 46.6 |  | 46.6 | 69.46 | 10.54 | 398412 | 398.412 | 66.92 | 13.08 | 494424 | 494.424 | 64.38 | 15.62 | 590436 | 590.436 | 61.84 | 18.16 | 686448 | 686.448 | 59.3 | 20.7 | 782460 | 782.46 | 56.76 | 23.24 | 878472 | 878.472 | 54.22 | 25.78 | 974484 | 974.484 | 51.68 | 28.32 | 1070496 | 1070.496 | 49.14 | 30.86 | 1166508 | 1166.508 | 46.6 | 33.4 | 1262520 | 1262.52 | 45
11/13/20XX 10:00:00 AM | 0.41667 | 7 | 47.5 | 60.6 | 47.5 |  | 47.5 | 69.55 | 10.45 | 395010 | 395.01 | 67.1 | 12.9 | 487620 | 487.62 | 64.65 | 15.35 | 580230 | 580.23 | 62.2 | 17.8 | 672840 | 672.84 | 59.75 | 20.25 | 765450 | 765.45 | 57.3 | 22.7 | 858060 | 858.06 | 54.85 | 25.15 | 950670 | 950.67 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.95 | 30.05 | 1135890 | 1135.89 | 47.5 | 32.5 | 1228500 | 1228.5 | 45
11/13/20XX 11:00:00 AM | 0.45833 | 7 | 48.5 | 59.2 | 48.5 |  | 48.5 | 69.65 | 10.35 | 391230 | 391.23 | 67.3 | 12.7 | 480060 | 480.06 | 64.95 | 15.05 | 568890 | 568.89 | 62.6 | 17.4 | 657720 | 657.72 | 60.25 | 19.75 | 746550 | 746.55 | 57.9 | 22.1 | 835380 | 835.38 | 55.55 | 24.45 | 924210 | 924.21 | 53.2 | 26.8 | 1013040 | 1013.04 | 50.85 | 29.15 | 1101870 | 1101.87 | 48.5 | 31.5 | 1190700 | 1190.7 | 50
11/13/20XX 12:00:00 PM | 0.5 | 7 | 49.7 | 56.9 | 49.7 |  | 49.7 | 69.77 | 10.23 | 386694 | 386.694 | 67.54 | 12.46 | 470988 | 470.988 | 65.31 | 14.69 | 555282 | 555.282 | 63.08 | 16.92 | 639576 | 639.576 | 60.85 | 19.15 | 723870 | 723.87 | 58.62 | 21.38 | 808164 | 808.164 | 56.39 | 23.61 | 892458 | 892.458 | 54.16 | 25.84 | 976752 | 976.752 | 51.93 | 28.07 | 1061046 | 1061.046 | 49.7 | 30.3 | 1145340 | 1145.34 | 50
11/13/20XX 1:00:00 PM | 0.54167 | 7 | 51.2 | 52.1 | 51.2 |  | 51.2 | 69.92 | 10.08 | 381024 | 381.024 | 67.84 | 12.16 | 459648 | 459.648 | 65.76 | 14.24 | 538272 | 538.272 | 63.68 | 16.32 | 616896 | 616.896 | 61.6 | 18.4 | 695520 | 695.52 | 59.52 | 20.48 | 774144 | 774.144 | 57.44 | 22.56 | 852768 | 852.768 | 55.36 | 24.64 | 931392 | 931.392 | 53.28 | 26.72 | 1010016 | 1010.016 | 51.2 | 28.8 | 1088640 | 1088.64 | 50
11/13/20XX 2:00:00 PM | 0.58333 | 7 | 51.5 | 50.3 | 51.5 |  | 51.5 | 69.95 | 10.05 | 379890 | 379.89 | 67.9 | 12.1 | 457380 | 457.38 | 65.85 | 14.15 | 534870 | 534.87 | 63.8 | 16.2 | 612360 | 612.36 | 61.75 | 18.25 | 689850 | 689.85 | 59.7 | 20.3 | 767340 | 767.34 | 57.65 | 22.35 | 844830 | 844.83 | 55.6 | 24.4 | 922320 | 922.32 | 53.55 | 26.45 | 999810 | 999.81 | 51.5 | 28.5 | 1077300 | 1077.3 | 50
11/13/20XX 3:00:00 PM | 0.625 | 7 | 52.2 | 48.1 | 52.2 |  | 52.2 | 70.02 | 9.98 | 377244 | 377.244 | 68.04 | 11.96 | 452088 | 452.088 | 66.06 | 13.94 | 526932 | 526.932 | 64.08 | 15.92 | 601776 | 601.776 | 62.1 | 17.9 | 676620 | 676.62 | 60.12 | 19.88 | 751464 | 751.464 | 58.14 | 21.86 | 826308 | 826.308 | 56.16 | 23.84 | 901152 | 901.152 | 54.18 | 25.82 | 975996 | 975.996 | 52.2 | 27.8 | 1050840 | 1050.84 | 50
11/13/20XX 4:00:00 PM | 0.66667 | 7 | 51.5 | 48.4 | 51.5 |  | 51.5 | 69.95 | 10.05 | 379890 | 379.89 | 67.9 | 12.1 | 457380 | 457.38 | 65.85 | 14.15 | 534870 | 534.87 | 63.8 | 16.2 | 612360 | 612.36 | 61.75 | 18.25 | 689850 | 689.85 | 59.7 | 20.3 | 767340 | 767.34 | 57.65 | 22.35 | 844830 | 844.83 | 55.6 | 24.4 | 922320 | 922.32 | 53.55 | 26.45 | 999810 | 999.81 | 51.5 | 28.5 | 1077300 | 1077.3 | 50
11/13/20XX 5:00:00 PM | 0.70833 | 7 | 50.2 | 48.2 | 50.2 |  | 50.2 | 69.82 | 10.18 | 384804 | 384.804 | 67.64 | 12.36 | 467208 | 467.208 | 65.46 | 14.54 | 549612 | 549.612 | 63.28 | 16.72 | 632016 | 632.016 | 61.1 | 18.9 | 714420 | 714.42 | 58.92 | 21.08 | 796824 | 796.824 | 56.74 | 23.26 | 879228 | 879.228 | 54.56 | 25.44 | 961632 | 961.632 | 52.38 | 27.62 | 1044036 | 1044.036 | 50.2 | 29.8 | 1126440 | 1126.44 | 50
11/13/20XX 6:00:00 PM | 0.75 | 7 | 49.3 | 50.9 | 49.3 |  | 49.3 | 69.73 | 10.27 | 388206 | 388.206 | 67.46 | 12.54 | 474012 | 474.012 | 65.19 | 14.81 | 559818 | 559.818 | 62.92 | 17.08 | 645624 | 645.624 | 60.65 | 19.35 | 731430 | 731.43 | 58.38 | 21.62 | 817236 | 817.236 | 56.11 | 23.89 | 903042 | 903.042 | 53.84 | 26.16 | 988848 | 988.848 | 51.57 | 28.43 | 1074654 | 1074.654 | 49.3 | 30.7 | 1160460 | 1160.46 | 50
11/13/20XX 7:00:00 PM | 0.79167 | 7 | 48.1 | 53 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/13/20XX 8:00:00 PM | 0.83333 | 7 | 47.6 | 54.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/13/20XX 9:00:00 PM | 0.875 | 7 | 47.5 | 55.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/13/20XX 10:00:00 PM | 0.91667 | 7 | 46.5 | 56.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/13/20XX 11:00:00 PM | 0.95833 | 7 | 45.9 | 57.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/13/20XX 12:00:00 AM | 0 | 1 | 45.3 | 58.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/14/20XX 1:00:00 AM | 0.041667 | 1 | 44.9 | 56.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/14/20XX 2:00:00 AM | 0.083333 | 1 | 44.1 | 59.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/14/20XX 3:00:00 AM | 0.125 | 1 | 43.5 | 60.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/14/20XX 4:00:00 AM | 0.16667 | 1 | 43.2 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/14/20XX 5:00:00 AM | 0.20833 | 1 | 42.9 | 62.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/14/20XX 6:00:00 AM | 0.25 | 1 | 42.6 | 63.5 | 42.6 |  | 42.6 | 69.06 | 10.94 | 413532 | 413.532 | 66.12 | 13.88 | 524664 | 524.664 | 63.18 | 16.82 | 635796 | 635.796 | 60.24 | 19.76 | 746928 | 746.928 | 57.3 | 22.7 | 858060 | 858.06 | 54.36 | 25.64 | 969192 | 969.192 | 51.42 | 28.58 | 1080324 | 1080.324 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.54 | 34.46 | 1302588 | 1302.588 | 42.6 | 37.4 | 1413720 | 1413.72 | 45
11/14/20XX 7:00:00 AM | 0.29167 | 1 | 42.5 | 63 | 42.5 |  | 42.5 | 69.05 | 10.95 | 413910 | 413.91 | 66.1 | 13.9 | 525420 | 525.42 | 63.15 | 16.85 | 636930 | 636.93 | 60.2 | 19.8 | 748440 | 748.44 | 57.25 | 22.75 | 859950 | 859.95 | 54.3 | 25.7 | 971460 | 971.46 | 51.35 | 28.65 | 1082970 | 1082.97 | 48.4 | 31.6 | 1194480 | 1194.48 | 45.45 | 34.55 | 1305990 | 1305.99 | 42.5 | 37.5 | 1417500 | 1417.5 | 40
11/14/20XX 8:00:00 AM | 0.33333 | 1 | 43.4 | 59.5 | 43.4 |  | 43.4 | 69.14 | 10.86 | 410508 | 410.508 | 66.28 | 13.72 | 518616 | 518.616 | 63.42 | 16.58 | 626724 | 626.724 | 60.56 | 19.44 | 734832 | 734.832 | 57.7 | 22.3 | 842940 | 842.94 | 54.84 | 25.16 | 951048 | 951.048 | 51.98 | 28.02 | 1059156 | 1059.156 | 49.12 | 30.88 | 1167264 | 1167.264 | 46.26 | 33.74 | 1275372 | 1275.372 | 43.4 | 36.6 | 1383480 | 1383.48 | 45
11/14/20XX 9:00:00 AM | 0.375 | 1 | 44.6 | 56.1 | 44.6 |  | 44.6 | 69.26 | 10.74 | 405972 | 405.972 | 66.52 | 13.48 | 509544 | 509.544 | 63.78 | 16.22 | 613116 | 613.116 | 61.04 | 18.96 | 716688 | 716.688 | 58.3 | 21.7 | 820260 | 820.26 | 55.56 | 24.44 | 923832 | 923.832 | 52.82 | 27.18 | 1027404 | 1027.404 | 50.08 | 29.92 | 1130976 | 1130.976 | 47.34 | 32.66 | 1234548 | 1234.548 | 44.6 | 35.4 | 1338120 | 1338.12 | 45
11/14/20XX 10:00:00 AM | 0.41667 | 1 | 46.3 | 53.8 | 46.3 |  | 46.3 | 69.43 | 10.57 | 399546 | 399.546 | 66.86 | 13.14 | 496692 | 496.692 | 64.29 | 15.71 | 593838 | 593.838 | 61.72 | 18.28 | 690984 | 690.984 | 59.15 | 20.85 | 788130 | 788.13 | 56.58 | 23.42 | 885276 | 885.276 | 54.01 | 25.99 | 982422 | 982.422 | 51.44 | 28.56 | 1079568 | 1079.568 | 48.87 | 31.13 | 1176714 | 1176.714 | 46.3 | 33.7 | 1273860 | 1273.86 | 45
11/14/20XX 11:00:00 AM | 0.45833 | 1 | 48.5 | 49.9 | 48.5 |  | 48.5 | 69.65 | 10.35 | 391230 | 391.23 | 67.3 | 12.7 | 480060 | 480.06 | 64.95 | 15.05 | 568890 | 568.89 | 62.6 | 17.4 | 657720 | 657.72 | 60.25 | 19.75 | 746550 | 746.55 | 57.9 | 22.1 | 835380 | 835.38 | 55.55 | 24.45 | 924210 | 924.21 | 53.2 | 26.8 | 1013040 | 1013.04 | 50.85 | 29.15 | 1101870 | 1101.87 | 48.5 | 31.5 | 1190700 | 1190.7 | 50
11/14/20XX 12:00:00 PM | 0.5 | 1 | 50.4 | 47.3 | 50.4 |  | 50.4 | 69.84 | 10.16 | 384048 | 384.048 | 67.68 | 12.32 | 465696 | 465.696 | 65.52 | 14.48 | 547344 | 547.344 | 63.36 | 16.64 | 628992 | 628.992 | 61.2 | 18.8 | 710640 | 710.64 | 59.04 | 20.96 | 792288 | 792.288 | 56.88 | 23.12 | 873936 | 873.936 | 54.72 | 25.28 | 955584 | 955.584 | 52.56 | 27.44 | 1037232 | 1037.232 | 50.4 | 29.6 | 1118880 | 1118.88 | 50
11/14/20XX 1:00:00 PM | 0.54167 | 1 | 51.3 | 45.6 | 51.3 |  | 51.3 | 69.93 | 10.07 | 380646 | 380.646 | 67.86 | 12.14 | 458892 | 458.892 | 65.79 | 14.21 | 537138 | 537.138 | 63.72 | 16.28 | 615384 | 615.384 | 61.65 | 18.35 | 693630 | 693.63 | 59.58 | 20.42 | 771876 | 771.876 | 57.51 | 22.49 | 850122 | 850.122 | 55.44 | 24.56 | 928368 | 928.368 | 53.37 | 26.63 | 1006614 | 1006.614 | 51.3 | 28.7 | 1084860 | 1084.86 | 50
11/14/20XX 2:00:00 PM | 0.58333 | 1 | 51.9 | 45.6 | 51.9 |  | 51.9 | 69.99 | 10.01 | 378378 | 378.378 | 67.98 | 12.02 | 454356 | 454.356 | 65.97 | 14.03 | 530334 | 530.334 | 63.96 | 16.04 | 606312 | 606.312 | 61.95 | 18.05 | 682290 | 682.29 | 59.94 | 20.06 | 758268 | 758.268 | 57.93 | 22.07 | 834246 | 834.246 | 55.92 | 24.08 | 910224 | 910.224 | 53.91 | 26.09 | 986202 | 986.202 | 51.9 | 28.1 | 1062180 | 1062.18 | 50
11/14/20XX 3:00:00 PM | 0.625 | 1 | 51.5 | 45.7 | 51.5 |  | 51.5 | 69.95 | 10.05 | 379890 | 379.89 | 67.9 | 12.1 | 457380 | 457.38 | 65.85 | 14.15 | 534870 | 534.87 | 63.8 | 16.2 | 612360 | 612.36 | 61.75 | 18.25 | 689850 | 689.85 | 59.7 | 20.3 | 767340 | 767.34 | 57.65 | 22.35 | 844830 | 844.83 | 55.6 | 24.4 | 922320 | 922.32 | 53.55 | 26.45 | 999810 | 999.81 | 51.5 | 28.5 | 1077300 | 1077.3 | 50
11/14/20XX 4:00:00 PM | 0.66667 | 1 | 50.4 | 48.5 | 50.4 |  | 50.4 | 69.84 | 10.16 | 384048 | 384.048 | 67.68 | 12.32 | 465696 | 465.696 | 65.52 | 14.48 | 547344 | 547.344 | 63.36 | 16.64 | 628992 | 628.992 | 61.2 | 18.8 | 710640 | 710.64 | 59.04 | 20.96 | 792288 | 792.288 | 56.88 | 23.12 | 873936 | 873.936 | 54.72 | 25.28 | 955584 | 955.584 | 52.56 | 27.44 | 1037232 | 1037.232 | 50.4 | 29.6 | 1118880 | 1118.88 | 50
11/14/20XX 5:00:00 PM | 0.70833 | 1 | 49.5 | 49.4 | 49.5 |  | 49.5 | 69.75 | 10.25 | 387450 | 387.45 | 67.5 | 12.5 | 472500 | 472.5 | 65.25 | 14.75 | 557550 | 557.55 | 63 | 17 | 642600 | 642.6 | 60.75 | 19.25 | 727650 | 727.65 | 58.5 | 21.5 | 812700 | 812.7 | 56.25 | 23.75 | 897750 | 897.75 | 54 | 26 | 982800 | 982.8 | 51.75 | 28.25 | 1067850 | 1067.85 | 49.5 | 30.5 | 1152900 | 1152.9 | 50
11/14/20XX 6:00:00 PM | 0.75 | 1 | 48.8 | 50.9 | 48.8 |  | 48.8 | 69.68 | 10.32 | 390096 | 390.096 | 67.36 | 12.64 | 477792 | 477.792 | 65.04 | 14.96 | 565488 | 565.488 | 62.72 | 17.28 | 653184 | 653.184 | 60.4 | 19.6 | 740880 | 740.88 | 58.08 | 21.92 | 828576 | 828.576 | 55.76 | 24.24 | 916272 | 916.272 | 53.44 | 26.56 | 1003968 | 1003.968 | 51.12 | 28.88 | 1091664 | 1091.664 | 48.8 | 31.2 | 1179360 | 1179.36 | 50
11/14/20XX 7:00:00 PM | 0.79167 | 1 | 48.4 | 51.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/14/20XX 8:00:00 PM | 0.83333 | 1 | 48.1 | 53.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/14/20XX 9:00:00 PM | 0.875 | 1 | 47.2 | 55.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/14/20XX 10:00:00 PM | 0.91667 | 1 | 47.2 | 55.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/14/20XX 11:00:00 PM | 0.95833 | 1 | 46.9 | 56.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/14/20XX 12:00:00 AM | 0 | 2 | 46.2 | 57.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/15/20XX 1:00:00 AM | 0.041667 | 2 | 45.9 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/15/20XX 2:00:00 AM | 0.083333 | 2 | 45.6 | 60.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/15/20XX 3:00:00 AM | 0.125 | 2 | 44.9 | 61.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/15/20XX 4:00:00 AM | 0.16667 | 2 | 44.7 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/15/20XX 5:00:00 AM | 0.20833 | 2 | 44.2 | 67.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/15/20XX 6:00:00 AM | 0.25 | 2 | 44.6 | 66.9 | 44.6 |  | 44.6 | 69.26 | 10.74 | 405972 | 405.972 | 66.52 | 13.48 | 509544 | 509.544 | 63.78 | 16.22 | 613116 | 613.116 | 61.04 | 18.96 | 716688 | 716.688 | 58.3 | 21.7 | 820260 | 820.26 | 55.56 | 24.44 | 923832 | 923.832 | 52.82 | 27.18 | 1027404 | 1027.404 | 50.08 | 29.92 | 1130976 | 1130.976 | 47.34 | 32.66 | 1234548 | 1234.548 | 44.6 | 35.4 | 1338120 | 1338.12 | 45
11/15/20XX 7:00:00 AM | 0.29167 | 2 | 44 | 68.7 | 44 |  | 44 | 69.2 | 10.8 | 408240 | 408.24 | 66.4 | 13.6 | 514080 | 514.08 | 63.6 | 16.4 | 619920 | 619.92 | 60.8 | 19.2 | 725760 | 725.76 | 58 | 22 | 831600 | 831.6 | 55.2 | 24.8 | 937440 | 937.44 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.6 | 30.4 | 1149120 | 1149.12 | 46.8 | 33.2 | 1254960 | 1254.96 | 44 | 36 | 1360800 | 1360.8 | 45
11/15/20XX 8:00:00 AM | 0.33333 | 2 | 44.6 | 67.6 | 44.6 |  | 44.6 | 69.26 | 10.74 | 405972 | 405.972 | 66.52 | 13.48 | 509544 | 509.544 | 63.78 | 16.22 | 613116 | 613.116 | 61.04 | 18.96 | 716688 | 716.688 | 58.3 | 21.7 | 820260 | 820.26 | 55.56 | 24.44 | 923832 | 923.832 | 52.82 | 27.18 | 1027404 | 1027.404 | 50.08 | 29.92 | 1130976 | 1130.976 | 47.34 | 32.66 | 1234548 | 1234.548 | 44.6 | 35.4 | 1338120 | 1338.12 | 45
11/15/20XX 9:00:00 AM | 0.375 | 2 | 46 | 65.8 | 46 |  | 46 | 69.4 | 10.6 | 400680 | 400.68 | 66.8 | 13.2 | 498960 | 498.96 | 64.2 | 15.8 | 597240 | 597.24 | 61.6 | 18.4 | 695520 | 695.52 | 59 | 21 | 793800 | 793.8 | 56.4 | 23.6 | 892080 | 892.08 | 53.8 | 26.2 | 990360 | 990.36 | 51.2 | 28.8 | 1088640 | 1088.64 | 48.6 | 31.4 | 1186920 | 1186.92 | 46 | 34 | 1285200 | 1285.2 | 45
11/15/20XX 10:00:00 AM | 0.41667 | 2 | 47.1 | 64.6 | 47.1 |  | 47.1 | 69.51 | 10.49 | 396522 | 396.522 | 67.02 | 12.98 | 490644 | 490.644 | 64.53 | 15.47 | 584766 | 584.766 | 62.04 | 17.96 | 678888 | 678.888 | 59.55 | 20.45 | 773010 | 773.01 | 57.06 | 22.94 | 867132 | 867.132 | 54.57 | 25.43 | 961254 | 961.254 | 52.08 | 27.92 | 1055376 | 1055.376 | 49.59 | 30.41 | 1149498 | 1149.498 | 47.1 | 32.9 | 1243620 | 1243.62 | 45
11/15/20XX 11:00:00 AM | 0.45833 | 2 | 48.3 | 61 | 48.3 |  | 48.3 | 69.63 | 10.37 | 391986 | 391.986 | 67.26 | 12.74 | 481572 | 481.572 | 64.89 | 15.11 | 571158 | 571.158 | 62.52 | 17.48 | 660744 | 660.744 | 60.15 | 19.85 | 750330 | 750.33 | 57.78 | 22.22 | 839916 | 839.916 | 55.41 | 24.59 | 929502 | 929.502 | 53.04 | 26.96 | 1019088 | 1019.088 | 50.67 | 29.33 | 1108674 | 1108.674 | 48.3 | 31.7 | 1198260 | 1198.26 | 50
11/15/20XX 12:00:00 PM | 0.5 | 2 | 50.1 | 57.8 | 50.1 |  | 50.1 | 69.81 | 10.19 | 385182 | 385.182 | 67.62 | 12.38 | 467964 | 467.964 | 65.43 | 14.57 | 550746 | 550.746 | 63.24 | 16.76 | 633528 | 633.528 | 61.05 | 18.95 | 716310 | 716.31 | 58.86 | 21.14 | 799092 | 799.092 | 56.67 | 23.33 | 881874 | 881.874 | 54.48 | 25.52 | 964656 | 964.656 | 52.29 | 27.71 | 1047438 | 1047.438 | 50.1 | 29.9 | 1130220 | 1130.22 | 50
11/15/20XX 1:00:00 PM | 0.54167 | 2 | 51 | 56.3 | 51 |  | 51 | 69.9 | 10.1 | 381780 | 381.78 | 67.8 | 12.2 | 461160 | 461.16 | 65.7 | 14.3 | 540540 | 540.54 | 63.6 | 16.4 | 619920 | 619.92 | 61.5 | 18.5 | 699300 | 699.3 | 59.4 | 20.6 | 778680 | 778.68 | 57.3 | 22.7 | 858060 | 858.06 | 55.2 | 24.8 | 937440 | 937.44 | 53.1 | 26.9 | 1016820 | 1016.82 | 51 | 29 | 1096200 | 1096.2 | 50
11/15/20XX 2:00:00 PM | 0.58333 | 2 | 51.6 | 56.5 | 51.6 |  | 51.6 | 69.96 | 10.04 | 379512 | 379.512 | 67.92 | 12.08 | 456624 | 456.624 | 65.88 | 14.12 | 533736 | 533.736 | 63.84 | 16.16 | 610848 | 610.848 | 61.8 | 18.2 | 687960 | 687.96 | 59.76 | 20.24 | 765072 | 765.072 | 57.72 | 22.28 | 842184 | 842.184 | 55.68 | 24.32 | 919296 | 919.296 | 53.64 | 26.36 | 996408 | 996.408 | 51.6 | 28.4 | 1073520 | 1073.52 | 50
11/15/20XX 3:00:00 PM | 0.625 | 2 | 51.7 | 58.7 | 51.7 |  | 51.7 | 69.97 | 10.03 | 379134 | 379.134 | 67.94 | 12.06 | 455868 | 455.868 | 65.91 | 14.09 | 532602 | 532.602 | 63.88 | 16.12 | 609336 | 609.336 | 61.85 | 18.15 | 686070 | 686.07 | 59.82 | 20.18 | 762804 | 762.804 | 57.79 | 22.21 | 839538 | 839.538 | 55.76 | 24.24 | 916272 | 916.272 | 53.73 | 26.27 | 993006 | 993.006 | 51.7 | 28.3 | 1069740 | 1069.74 | 50
11/15/20XX 4:00:00 PM | 0.66667 | 2 | 50.9 | 60 | 50.9 |  | 50.9 | 69.89 | 10.11 | 382158 | 382.158 | 67.78 | 12.22 | 461916 | 461.916 | 65.67 | 14.33 | 541674 | 541.674 | 63.56 | 16.44 | 621432 | 621.432 | 61.45 | 18.55 | 701190 | 701.19 | 59.34 | 20.66 | 780948 | 780.948 | 57.23 | 22.77 | 860706 | 860.706 | 55.12 | 24.88 | 940464 | 940.464 | 53.01 | 26.99 | 1020222 | 1020.222 | 50.9 | 29.1 | 1099980 | 1099.98 | 50
11/15/20XX 5:00:00 PM | 0.70833 | 2 | 49.8 | 61.2 | 49.8 |  | 49.8 | 69.78 | 10.22 | 386316 | 386.316 | 67.56 | 12.44 | 470232 | 470.232 | 65.34 | 14.66 | 554148 | 554.148 | 63.12 | 16.88 | 638064 | 638.064 | 60.9 | 19.1 | 721980 | 721.98 | 58.68 | 21.32 | 805896 | 805.896 | 56.46 | 23.54 | 889812 | 889.812 | 54.24 | 25.76 | 973728 | 973.728 | 52.02 | 27.98 | 1057644 | 1057.644 | 49.8 | 30.2 | 1141560 | 1141.56 | 50
11/15/20XX 6:00:00 PM | 0.75 | 2 | 49.5 | 61.8 | 49.5 |  | 49.5 | 69.75 | 10.25 | 387450 | 387.45 | 67.5 | 12.5 | 472500 | 472.5 | 65.25 | 14.75 | 557550 | 557.55 | 63 | 17 | 642600 | 642.6 | 60.75 | 19.25 | 727650 | 727.65 | 58.5 | 21.5 | 812700 | 812.7 | 56.25 | 23.75 | 897750 | 897.75 | 54 | 26 | 982800 | 982.8 | 51.75 | 28.25 | 1067850 | 1067.85 | 49.5 | 30.5 | 1152900 | 1152.9 | 50
11/15/20XX 7:00:00 PM | 0.79167 | 2 | 49.4 | 62.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/15/20XX 8:00:00 PM | 0.83333 | 2 | 49.1 | 64 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/15/20XX 9:00:00 PM | 0.875 | 2 | 49.2 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/15/20XX 10:00:00 PM | 0.91667 | 2 | 49.2 | 64.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/15/20XX 11:00:00 PM | 0.95833 | 2 | 49.1 | 65.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/15/20XX 12:00:00 AM | 0 | 3 | 48.8 | 66.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/16/20XX 1:00:00 AM | 0.041667 | 3 | 49 | 67.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/16/20XX 2:00:00 AM | 0.083333 | 3 | 48.8 | 68.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/16/20XX 3:00:00 AM | 0.125 | 3 | 48.7 | 68.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/16/20XX 4:00:00 AM | 0.16667 | 3 | 48.1 | 72.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/16/20XX 5:00:00 AM | 0.20833 | 3 | 47.8 | 72.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/16/20XX 6:00:00 AM | 0.25 | 3 | 47.2 | 73.9 | 47.2 |  | 47.2 | 69.52 | 10.48 | 396144 | 396.144 | 67.04 | 12.96 | 489888 | 489.888 | 64.56 | 15.44 | 583632 | 583.632 | 62.08 | 17.92 | 677376 | 677.376 | 59.6 | 20.4 | 771120 | 771.12 | 57.12 | 22.88 | 864864 | 864.864 | 54.64 | 25.36 | 958608 | 958.608 | 52.16 | 27.84 | 1052352 | 1052.352 | 49.68 | 30.32 | 1146096 | 1146.096 | 47.2 | 32.8 | 1239840 | 1239.84 | 45
11/16/20XX 7:00:00 AM | 0.29167 | 3 | 47 | 74.5 | 47 |  | 47 | 69.5 | 10.5 | 396900 | 396.9 | 67 | 13 | 491400 | 491.4 | 64.5 | 15.5 | 585900 | 585.9 | 62 | 18 | 680400 | 680.4 | 59.5 | 20.5 | 774900 | 774.9 | 57 | 23 | 869400 | 869.4 | 54.5 | 25.5 | 963900 | 963.9 | 52 | 28 | 1058400 | 1058.4 | 49.5 | 30.5 | 1152900 | 1152.9 | 47 | 33 | 1247400 | 1247.4 | 45
11/16/20XX 8:00:00 AM | 0.33333 | 3 | 47.2 | 74.8 | 47.2 |  | 47.2 | 69.52 | 10.48 | 396144 | 396.144 | 67.04 | 12.96 | 489888 | 489.888 | 64.56 | 15.44 | 583632 | 583.632 | 62.08 | 17.92 | 677376 | 677.376 | 59.6 | 20.4 | 771120 | 771.12 | 57.12 | 22.88 | 864864 | 864.864 | 54.64 | 25.36 | 958608 | 958.608 | 52.16 | 27.84 | 1052352 | 1052.352 | 49.68 | 30.32 | 1146096 | 1146.096 | 47.2 | 32.8 | 1239840 | 1239.84 | 45
11/16/20XX 9:00:00 AM | 0.375 | 3 | 48.9 | 71 | 48.9 |  | 48.9 | 69.69 | 10.31 | 389718 | 389.718 | 67.38 | 12.62 | 477036 | 477.036 | 65.07 | 14.93 | 564354 | 564.354 | 62.76 | 17.24 | 651672 | 651.672 | 60.45 | 19.55 | 738990 | 738.99 | 58.14 | 21.86 | 826308 | 826.308 | 55.83 | 24.17 | 913626 | 913.626 | 53.52 | 26.48 | 1000944 | 1000.944 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.9 | 31.1 | 1175580 | 1175.58 | 50
11/16/20XX 10:00:00 AM | 0.41667 | 3 | 50.2 | 66.1 | 50.2 |  | 50.2 | 69.82 | 10.18 | 384804 | 384.804 | 67.64 | 12.36 | 467208 | 467.208 | 65.46 | 14.54 | 549612 | 549.612 | 63.28 | 16.72 | 632016 | 632.016 | 61.1 | 18.9 | 714420 | 714.42 | 58.92 | 21.08 | 796824 | 796.824 | 56.74 | 23.26 | 879228 | 879.228 | 54.56 | 25.44 | 961632 | 961.632 | 52.38 | 27.62 | 1044036 | 1044.036 | 50.2 | 29.8 | 1126440 | 1126.44 | 50
11/16/20XX 11:00:00 AM | 0.45833 | 3 | 51.5 | 61.8 | 51.5 |  | 51.5 | 69.95 | 10.05 | 379890 | 379.89 | 67.9 | 12.1 | 457380 | 457.38 | 65.85 | 14.15 | 534870 | 534.87 | 63.8 | 16.2 | 612360 | 612.36 | 61.75 | 18.25 | 689850 | 689.85 | 59.7 | 20.3 | 767340 | 767.34 | 57.65 | 22.35 | 844830 | 844.83 | 55.6 | 24.4 | 922320 | 922.32 | 53.55 | 26.45 | 999810 | 999.81 | 51.5 | 28.5 | 1077300 | 1077.3 | 50
11/16/20XX 12:00:00 PM | 0.5 | 3 | 53.1 | 58.9 | 53.1 |  | 53.1 | 70.11 | 9.89 | 373842 | 373.842 | 68.22 | 11.78 | 445284 | 445.284 | 66.33 | 13.67 | 516726 | 516.726 | 64.44 | 15.56 | 588168 | 588.168 | 62.55 | 17.45 | 659610 | 659.61 | 60.66 | 19.34 | 731052 | 731.052 | 58.77 | 21.23 | 802494 | 802.494 | 56.88 | 23.12 | 873936 | 873.936 | 54.99 | 25.01 | 945378 | 945.378 | 53.1 | 26.9 | 1016820 | 1016.82 | 55
11/16/20XX 1:00:00 PM | 0.54167 | 3 | 53.9 | 55.1 | 53.9 |  | 53.9 | 70.19 | 9.81 | 370818 | 370.818 | 68.38 | 11.62 | 439236 | 439.236 | 66.57 | 13.43 | 507654 | 507.654 | 64.76 | 15.24 | 576072 | 576.072 | 62.95 | 17.05 | 644490 | 644.49 | 61.14 | 18.86 | 712908 | 712.908 | 59.33 | 20.67 | 781326 | 781.326 | 57.52 | 22.48 | 849744 | 849.744 | 55.71 | 24.29 | 918162 | 918.162 | 53.9 | 26.1 | 986580 | 986.58 | 55
11/16/20XX 2:00:00 PM | 0.58333 | 3 | 54.6 | 54.4 | 54.6 |  | 54.6 | 70.26 | 9.74 | 368172 | 368.172 | 68.52 | 11.48 | 433944 | 433.944 | 66.78 | 13.22 | 499716 | 499.716 | 65.04 | 14.96 | 565488 | 565.488 | 63.3 | 16.7 | 631260 | 631.26 | 61.56 | 18.44 | 697032 | 697.032 | 59.82 | 20.18 | 762804 | 762.804 | 58.08 | 21.92 | 828576 | 828.576 | 56.34 | 23.66 | 894348 | 894.348 | 54.6 | 25.4 | 960120 | 960.12 | 55
11/16/20XX 3:00:00 PM | 0.625 | 3 | 54.1 | 54.9 | 54.1 |  | 54.1 | 70.21 | 9.79 | 370062 | 370.062 | 68.42 | 11.58 | 437724 | 437.724 | 66.63 | 13.37 | 505386 | 505.386 | 64.84 | 15.16 | 573048 | 573.048 | 63.05 | 16.95 | 640710 | 640.71 | 61.26 | 18.74 | 708372 | 708.372 | 59.47 | 20.53 | 776034 | 776.034 | 57.68 | 22.32 | 843696 | 843.696 | 55.89 | 24.11 | 911358 | 911.358 | 54.1 | 25.9 | 979020 | 979.02 | 55
11/16/20XX 4:00:00 PM | 0.66667 | 3 | 53.2 | 57.5 | 53.2 |  | 53.2 | 70.12 | 9.88 | 373464 | 373.464 | 68.24 | 11.76 | 444528 | 444.528 | 66.36 | 13.64 | 515592 | 515.592 | 64.48 | 15.52 | 586656 | 586.656 | 62.6 | 17.4 | 657720 | 657.72 | 60.72 | 19.28 | 728784 | 728.784 | 58.84 | 21.16 | 799848 | 799.848 | 56.96 | 23.04 | 870912 | 870.912 | 55.08 | 24.92 | 941976 | 941.976 | 53.2 | 26.8 | 1013040 | 1013.04 | 55
11/16/20XX 5:00:00 PM | 0.70833 | 3 | 52.2 | 58.3 | 52.2 |  | 52.2 | 70.02 | 9.98 | 377244 | 377.244 | 68.04 | 11.96 | 452088 | 452.088 | 66.06 | 13.94 | 526932 | 526.932 | 64.08 | 15.92 | 601776 | 601.776 | 62.1 | 17.9 | 676620 | 676.62 | 60.12 | 19.88 | 751464 | 751.464 | 58.14 | 21.86 | 826308 | 826.308 | 56.16 | 23.84 | 901152 | 901.152 | 54.18 | 25.82 | 975996 | 975.996 | 52.2 | 27.8 | 1050840 | 1050.84 | 50
11/16/20XX 6:00:00 PM | 0.75 | 3 | 51.6 | 60.5 | 51.6 |  | 51.6 | 69.96 | 10.04 | 379512 | 379.512 | 67.92 | 12.08 | 456624 | 456.624 | 65.88 | 14.12 | 533736 | 533.736 | 63.84 | 16.16 | 610848 | 610.848 | 61.8 | 18.2 | 687960 | 687.96 | 59.76 | 20.24 | 765072 | 765.072 | 57.72 | 22.28 | 842184 | 842.184 | 55.68 | 24.32 | 919296 | 919.296 | 53.64 | 26.36 | 996408 | 996.408 | 51.6 | 28.4 | 1073520 | 1073.52 | 50
11/16/20XX 7:00:00 PM | 0.79167 | 3 | 50.9 | 62.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/16/20XX 8:00:00 PM | 0.83333 | 3 | 50.2 | 62.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/16/20XX 9:00:00 PM | 0.875 | 3 | 49.5 | 63.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/16/20XX 10:00:00 PM | 0.91667 | 3 | 49.4 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/16/20XX 11:00:00 PM | 0.95833 | 3 | 48.6 | 65.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/16/20XX 12:00:00 AM | 0 | 4 | 47.9 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/17/20XX 1:00:00 AM | 0.041667 | 4 | 47.3 | 68.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/17/20XX 2:00:00 AM | 0.083333 | 4 | 47.2 | 67.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/17/20XX 3:00:00 AM | 0.125 | 4 | 46.7 | 67.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/17/20XX 4:00:00 AM | 0.16667 | 4 | 46.3 | 67.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/17/20XX 5:00:00 AM | 0.20833 | 4 | 46 | 67.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/17/20XX 6:00:00 AM | 0.25 | 4 | 45.8 | 66.5 | 45.8 |  | 45.8 | 69.38 | 10.62 | 401436 | 401.436 | 66.76 | 13.24 | 500472 | 500.472 | 64.14 | 15.86 | 599508 | 599.508 | 61.52 | 18.48 | 698544 | 698.544 | 58.9 | 21.1 | 797580 | 797.58 | 56.28 | 23.72 | 896616 | 896.616 | 53.66 | 26.34 | 995652 | 995.652 | 51.04 | 28.96 | 1094688 | 1094.688 | 48.42 | 31.58 | 1193724 | 1193.724 | 45.8 | 34.2 | 1292760 | 1292.76 | 45
11/17/20XX 7:00:00 AM | 0.29167 | 4 | 45.1 | 67.6 | 45.1 |  | 45.1 | 69.31 | 10.69 | 404082 | 404.082 | 66.62 | 13.38 | 505764 | 505.764 | 63.93 | 16.07 | 607446 | 607.446 | 61.24 | 18.76 | 709128 | 709.128 | 58.55 | 21.45 | 810810 | 810.81 | 55.86 | 24.14 | 912492 | 912.492 | 53.17 | 26.83 | 1014174 | 1014.174 | 50.48 | 29.52 | 1115856 | 1115.856 | 47.79 | 32.21 | 1217538 | 1217.538 | 45.1 | 34.9 | 1319220 | 1319.22 | 45
11/17/20XX 8:00:00 AM | 0.33333 | 4 | 45.7 | 66.9 | 45.7 |  | 45.7 | 69.37 | 10.63 | 401814 | 401.814 | 66.74 | 13.26 | 501228 | 501.228 | 64.11 | 15.89 | 600642 | 600.642 | 61.48 | 18.52 | 700056 | 700.056 | 58.85 | 21.15 | 799470 | 799.47 | 56.22 | 23.78 | 898884 | 898.884 | 53.59 | 26.41 | 998298 | 998.298 | 50.96 | 29.04 | 1097712 | 1097.712 | 48.33 | 31.67 | 1197126 | 1197.126 | 45.7 | 34.3 | 1296540 | 1296.54 | 45
11/17/20XX 9:00:00 AM | 0.375 | 4 | 47.1 | 64.5 | 47.1 |  | 47.1 | 69.51 | 10.49 | 396522 | 396.522 | 67.02 | 12.98 | 490644 | 490.644 | 64.53 | 15.47 | 584766 | 584.766 | 62.04 | 17.96 | 678888 | 678.888 | 59.55 | 20.45 | 773010 | 773.01 | 57.06 | 22.94 | 867132 | 867.132 | 54.57 | 25.43 | 961254 | 961.254 | 52.08 | 27.92 | 1055376 | 1055.376 | 49.59 | 30.41 | 1149498 | 1149.498 | 47.1 | 32.9 | 1243620 | 1243.62 | 45
11/17/20XX 10:00:00 AM | 0.41667 | 4 | 48.6 | 60.1 | 48.6 |  | 48.6 | 69.66 | 10.34 | 390852 | 390.852 | 67.32 | 12.68 | 479304 | 479.304 | 64.98 | 15.02 | 567756 | 567.756 | 62.64 | 17.36 | 656208 | 656.208 | 60.3 | 19.7 | 744660 | 744.66 | 57.96 | 22.04 | 833112 | 833.112 | 55.62 | 24.38 | 921564 | 921.564 | 53.28 | 26.72 | 1010016 | 1010.016 | 50.94 | 29.06 | 1098468 | 1098.468 | 48.6 | 31.4 | 1186920 | 1186.92 | 50
11/17/20XX 11:00:00 AM | 0.45833 | 4 | 50.3 | 55.8 | 50.3 |  | 50.3 | 69.83 | 10.17 | 384426 | 384.426 | 67.66 | 12.34 | 466452 | 466.452 | 65.49 | 14.51 | 548478 | 548.478 | 63.32 | 16.68 | 630504 | 630.504 | 61.15 | 18.85 | 712530 | 712.53 | 58.98 | 21.02 | 794556 | 794.556 | 56.81 | 23.19 | 876582 | 876.582 | 54.64 | 25.36 | 958608 | 958.608 | 52.47 | 27.53 | 1040634 | 1040.634 | 50.3 | 29.7 | 1122660 | 1122.66 | 50
11/17/20XX 12:00:00 PM | 0.5 | 4 | 50.6 | 56.6 | 50.6 |  | 50.6 | 69.86 | 10.14 | 383292 | 383.292 | 67.72 | 12.28 | 464184 | 464.184 | 65.58 | 14.42 | 545076 | 545.076 | 63.44 | 16.56 | 625968 | 625.968 | 61.3 | 18.7 | 706860 | 706.86 | 59.16 | 20.84 | 787752 | 787.752 | 57.02 | 22.98 | 868644 | 868.644 | 54.88 | 25.12 | 949536 | 949.536 | 52.74 | 27.26 | 1030428 | 1030.428 | 50.6 | 29.4 | 1111320 | 1111.32 | 50
11/17/20XX 1:00:00 PM | 0.54167 | 4 | 51.4 | 55.9 | 51.4 |  | 51.4 | 69.94 | 10.06 | 380268 | 380.268 | 67.88 | 12.12 | 458136 | 458.136 | 65.82 | 14.18 | 536004 | 536.004 | 63.76 | 16.24 | 613872 | 613.872 | 61.7 | 18.3 | 691740 | 691.74 | 59.64 | 20.36 | 769608 | 769.608 | 57.58 | 22.42 | 847476 | 847.476 | 55.52 | 24.48 | 925344 | 925.344 | 53.46 | 26.54 | 1003212 | 1003.212 | 51.4 | 28.6 | 1081080 | 1081.08 | 50
11/17/20XX 2:00:00 PM | 0.58333 | 4 | 51.3 | 56.5 | 51.3 |  | 51.3 | 69.93 | 10.07 | 380646 | 380.646 | 67.86 | 12.14 | 458892 | 458.892 | 65.79 | 14.21 | 537138 | 537.138 | 63.72 | 16.28 | 615384 | 615.384 | 61.65 | 18.35 | 693630 | 693.63 | 59.58 | 20.42 | 771876 | 771.876 | 57.51 | 22.49 | 850122 | 850.122 | 55.44 | 24.56 | 928368 | 928.368 | 53.37 | 26.63 | 1006614 | 1006.614 | 51.3 | 28.7 | 1084860 | 1084.86 | 50
11/17/20XX 3:00:00 PM | 0.625 | 4 | 51.3 | 55.2 | 51.3 |  | 51.3 | 69.93 | 10.07 | 380646 | 380.646 | 67.86 | 12.14 | 458892 | 458.892 | 65.79 | 14.21 | 537138 | 537.138 | 63.72 | 16.28 | 615384 | 615.384 | 61.65 | 18.35 | 693630 | 693.63 | 59.58 | 20.42 | 771876 | 771.876 | 57.51 | 22.49 | 850122 | 850.122 | 55.44 | 24.56 | 928368 | 928.368 | 53.37 | 26.63 | 1006614 | 1006.614 | 51.3 | 28.7 | 1084860 | 1084.86 | 50
11/17/20XX 4:00:00 PM | 0.66667 | 4 | 51.1 | 54.5 | 51.1 |  | 51.1 | 69.91 | 10.09 | 381402 | 381.402 | 67.82 | 12.18 | 460404 | 460.404 | 65.73 | 14.27 | 539406 | 539.406 | 63.64 | 16.36 | 618408 | 618.408 | 61.55 | 18.45 | 697410 | 697.41 | 59.46 | 20.54 | 776412 | 776.412 | 57.37 | 22.63 | 855414 | 855.414 | 55.28 | 24.72 | 934416 | 934.416 | 53.19 | 26.81 | 1013418 | 1013.418 | 51.1 | 28.9 | 1092420 | 1092.42 | 50
11/17/20XX 5:00:00 PM | 0.70833 | 4 | 50.1 | 56.5 | 50.1 |  | 50.1 | 69.81 | 10.19 | 385182 | 385.182 | 67.62 | 12.38 | 467964 | 467.964 | 65.43 | 14.57 | 550746 | 550.746 | 63.24 | 16.76 | 633528 | 633.528 | 61.05 | 18.95 | 716310 | 716.31 | 58.86 | 21.14 | 799092 | 799.092 | 56.67 | 23.33 | 881874 | 881.874 | 54.48 | 25.52 | 964656 | 964.656 | 52.29 | 27.71 | 1047438 | 1047.438 | 50.1 | 29.9 | 1130220 | 1130.22 | 50
11/17/20XX 6:00:00 PM | 0.75 | 4 | 49.8 | 57.4 | 49.8 |  | 49.8 | 69.78 | 10.22 | 386316 | 386.316 | 67.56 | 12.44 | 470232 | 470.232 | 65.34 | 14.66 | 554148 | 554.148 | 63.12 | 16.88 | 638064 | 638.064 | 60.9 | 19.1 | 721980 | 721.98 | 58.68 | 21.32 | 805896 | 805.896 | 56.46 | 23.54 | 889812 | 889.812 | 54.24 | 25.76 | 973728 | 973.728 | 52.02 | 27.98 | 1057644 | 1057.644 | 49.8 | 30.2 | 1141560 | 1141.56 | 50
11/17/20XX 7:00:00 PM | 0.79167 | 4 | 49.1 | 58 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/17/20XX 8:00:00 PM | 0.83333 | 4 | 48.3 | 57 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/17/20XX 9:00:00 PM | 0.875 | 4 | 47.5 | 58.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/17/20XX 10:00:00 PM | 0.91667 | 4 | 46.9 | 60.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/17/20XX 11:00:00 PM | 0.95833 | 4 | 46.5 | 59.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/17/20XX 12:00:00 AM | 0 | 5 | 46.1 | 61.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/18/20XX 1:00:00 AM | 0.041667 | 5 | 45.3 | 63.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/18/20XX 2:00:00 AM | 0.083333 | 5 | 44.8 | 62.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/18/20XX 3:00:00 AM | 0.125 | 5 | 43.7 | 63.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/18/20XX 4:00:00 AM | 0.16667 | 5 | 43.5 | 63.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/18/20XX 5:00:00 AM | 0.20833 | 5 | 43 | 63.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/18/20XX 6:00:00 AM | 0.25 | 5 | 42.3 | 63.5 | 42.3 |  | 42.3 | 69.03 | 10.97 | 414666 | 414.666 | 66.06 | 13.94 | 526932 | 526.932 | 63.09 | 16.91 | 639198 | 639.198 | 60.12 | 19.88 | 751464 | 751.464 | 57.15 | 22.85 | 863730 | 863.73 | 54.18 | 25.82 | 975996 | 975.996 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.27 | 34.73 | 1312794 | 1312.794 | 42.3 | 37.7 | 1425060 | 1425.06 | 40
11/18/20XX 7:00:00 AM | 0.29167 | 5 | 42 | 62.8 | 42 |  | 42 | 69 | 11 | 415800 | 415.8 | 66 | 14 | 529200 | 529.2 | 63 | 17 | 642600 | 642.6 | 60 | 20 | 756000 | 756 | 57 | 23 | 869400 | 869.4 | 54 | 26 | 982800 | 982.8 | 51 | 29 | 1096200 | 1096.2 | 48 | 32 | 1209600 | 1209.6 | 45 | 35 | 1323000 | 1323 | 42 | 38 | 1436400 | 1436.4 | 40
11/18/20XX 8:00:00 AM | 0.33333 | 5 | 42.6 | 61.9 | 42.6 |  | 42.6 | 69.06 | 10.94 | 413532 | 413.532 | 66.12 | 13.88 | 524664 | 524.664 | 63.18 | 16.82 | 635796 | 635.796 | 60.24 | 19.76 | 746928 | 746.928 | 57.3 | 22.7 | 858060 | 858.06 | 54.36 | 25.64 | 969192 | 969.192 | 51.42 | 28.58 | 1080324 | 1080.324 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.54 | 34.46 | 1302588 | 1302.588 | 42.6 | 37.4 | 1413720 | 1413.72 | 45
11/18/20XX 9:00:00 AM | 0.375 | 5 | 44.1 | 57.9 | 44.1 |  | 44.1 | 69.21 | 10.79 | 407862 | 407.862 | 66.42 | 13.58 | 513324 | 513.324 | 63.63 | 16.37 | 618786 | 618.786 | 60.84 | 19.16 | 724248 | 724.248 | 58.05 | 21.95 | 829710 | 829.71 | 55.26 | 24.74 | 935172 | 935.172 | 52.47 | 27.53 | 1040634 | 1040.634 | 49.68 | 30.32 | 1146096 | 1146.096 | 46.89 | 33.11 | 1251558 | 1251.558 | 44.1 | 35.9 | 1357020 | 1357.02 | 45
11/18/20XX 10:00:00 AM | 0.41667 | 5 | 46.2 | 53.9 | 46.2 |  | 46.2 | 69.42 | 10.58 | 399924 | 399.924 | 66.84 | 13.16 | 497448 | 497.448 | 64.26 | 15.74 | 594972 | 594.972 | 61.68 | 18.32 | 692496 | 692.496 | 59.1 | 20.9 | 790020 | 790.02 | 56.52 | 23.48 | 887544 | 887.544 | 53.94 | 26.06 | 985068 | 985.068 | 51.36 | 28.64 | 1082592 | 1082.592 | 48.78 | 31.22 | 1180116 | 1180.116 | 46.2 | 33.8 | 1277640 | 1277.64 | 45
11/18/20XX 11:00:00 AM | 0.45833 | 5 | 48.3 | 50.7 | 48.3 |  | 48.3 | 69.63 | 10.37 | 391986 | 391.986 | 67.26 | 12.74 | 481572 | 481.572 | 64.89 | 15.11 | 571158 | 571.158 | 62.52 | 17.48 | 660744 | 660.744 | 60.15 | 19.85 | 750330 | 750.33 | 57.78 | 22.22 | 839916 | 839.916 | 55.41 | 24.59 | 929502 | 929.502 | 53.04 | 26.96 | 1019088 | 1019.088 | 50.67 | 29.33 | 1108674 | 1108.674 | 48.3 | 31.7 | 1198260 | 1198.26 | 50
11/18/20XX 12:00:00 PM | 0.5 | 5 | 49.8 | 48.3 | 49.8 |  | 49.8 | 69.78 | 10.22 | 386316 | 386.316 | 67.56 | 12.44 | 470232 | 470.232 | 65.34 | 14.66 | 554148 | 554.148 | 63.12 | 16.88 | 638064 | 638.064 | 60.9 | 19.1 | 721980 | 721.98 | 58.68 | 21.32 | 805896 | 805.896 | 56.46 | 23.54 | 889812 | 889.812 | 54.24 | 25.76 | 973728 | 973.728 | 52.02 | 27.98 | 1057644 | 1057.644 | 49.8 | 30.2 | 1141560 | 1141.56 | 50
11/18/20XX 1:00:00 PM | 0.54167 | 5 | 50.8 | 47.1 | 50.8 |  | 50.8 | 69.88 | 10.12 | 382536 | 382.536 | 67.76 | 12.24 | 462672 | 462.672 | 65.64 | 14.36 | 542808 | 542.808 | 63.52 | 16.48 | 622944 | 622.944 | 61.4 | 18.6 | 703080 | 703.08 | 59.28 | 20.72 | 783216 | 783.216 | 57.16 | 22.84 | 863352 | 863.352 | 55.04 | 24.96 | 943488 | 943.488 | 52.92 | 27.08 | 1023624 | 1023.624 | 50.8 | 29.2 | 1103760 | 1103.76 | 50
11/18/20XX 2:00:00 PM | 0.58333 | 5 | 50.7 | 48.6 | 50.7 |  | 50.7 | 69.87 | 10.13 | 382914 | 382.914 | 67.74 | 12.26 | 463428 | 463.428 | 65.61 | 14.39 | 543942 | 543.942 | 63.48 | 16.52 | 624456 | 624.456 | 61.35 | 18.65 | 704970 | 704.97 | 59.22 | 20.78 | 785484 | 785.484 | 57.09 | 22.91 | 865998 | 865.998 | 54.96 | 25.04 | 946512 | 946.512 | 52.83 | 27.17 | 1027026 | 1027.026 | 50.7 | 29.3 | 1107540 | 1107.54 | 50
11/18/20XX 3:00:00 PM | 0.625 | 5 | 50.8 | 47.4 | 50.8 |  | 50.8 | 69.88 | 10.12 | 382536 | 382.536 | 67.76 | 12.24 | 462672 | 462.672 | 65.64 | 14.36 | 542808 | 542.808 | 63.52 | 16.48 | 622944 | 622.944 | 61.4 | 18.6 | 703080 | 703.08 | 59.28 | 20.72 | 783216 | 783.216 | 57.16 | 22.84 | 863352 | 863.352 | 55.04 | 24.96 | 943488 | 943.488 | 52.92 | 27.08 | 1023624 | 1023.624 | 50.8 | 29.2 | 1103760 | 1103.76 | 50
11/18/20XX 4:00:00 PM | 0.66667 | 5 | 50.5 | 48.6 | 50.5 |  | 50.5 | 69.85 | 10.15 | 383670 | 383.67 | 67.7 | 12.3 | 464940 | 464.94 | 65.55 | 14.45 | 546210 | 546.21 | 63.4 | 16.6 | 627480 | 627.48 | 61.25 | 18.75 | 708750 | 708.75 | 59.1 | 20.9 | 790020 | 790.02 | 56.95 | 23.05 | 871290 | 871.29 | 54.8 | 25.2 | 952560 | 952.56 | 52.65 | 27.35 | 1033830 | 1033.83 | 50.5 | 29.5 | 1115100 | 1115.1 | 50
11/18/20XX 5:00:00 PM | 0.70833 | 5 | 49 | 52.7 | 49 |  | 49 | 69.7 | 10.3 | 389340 | 389.34 | 67.4 | 12.6 | 476280 | 476.28 | 65.1 | 14.9 | 563220 | 563.22 | 62.8 | 17.2 | 650160 | 650.16 | 60.5 | 19.5 | 737100 | 737.1 | 58.2 | 21.8 | 824040 | 824.04 | 55.9 | 24.1 | 910980 | 910.98 | 53.6 | 26.4 | 997920 | 997.92 | 51.3 | 28.7 | 1084860 | 1084.86 | 49 | 31 | 1171800 | 1171.8 | 50
11/18/20XX 6:00:00 PM | 0.75 | 5 | 48.4 | 55 | 48.4 |  | 48.4 | 69.64 | 10.36 | 391608 | 391.608 | 67.28 | 12.72 | 480816 | 480.816 | 64.92 | 15.08 | 570024 | 570.024 | 62.56 | 17.44 | 659232 | 659.232 | 60.2 | 19.8 | 748440 | 748.44 | 57.84 | 22.16 | 837648 | 837.648 | 55.48 | 24.52 | 926856 | 926.856 | 53.12 | 26.88 | 1016064 | 1016.064 | 50.76 | 29.24 | 1105272 | 1105.272 | 48.4 | 31.6 | 1194480 | 1194.48 | 50
11/18/20XX 7:00:00 PM | 0.79167 | 5 | 48.4 | 56 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/18/20XX 8:00:00 PM | 0.83333 | 5 | 48.8 | 55 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/18/20XX 9:00:00 PM | 0.875 | 5 | 48 | 55.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/18/20XX 10:00:00 PM | 0.91667 | 5 | 47.1 | 58.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/18/20XX 11:00:00 PM | 0.95833 | 5 | 46.6 | 60.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/18/20XX 12:00:00 AM | 0 | 6 | 45.8 | 63.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/19/20XX 1:00:00 AM | 0.041667 | 6 | 45.7 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/19/20XX 2:00:00 AM | 0.083333 | 6 | 45.5 | 65 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/19/20XX 3:00:00 AM | 0.125 | 6 | 44.6 | 68.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/19/20XX 4:00:00 AM | 0.16667 | 6 | 44.5 | 68.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/19/20XX 5:00:00 AM | 0.20833 | 6 | 44 | 70.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/19/20XX 6:00:00 AM | 0.25 | 6 | 44.6 | 68.9 | 44.6 |  | 44.6 | 69.26 | 10.74 | 405972 | 405.972 | 66.52 | 13.48 | 509544 | 509.544 | 63.78 | 16.22 | 613116 | 613.116 | 61.04 | 18.96 | 716688 | 716.688 | 58.3 | 21.7 | 820260 | 820.26 | 55.56 | 24.44 | 923832 | 923.832 | 52.82 | 27.18 | 1027404 | 1027.404 | 50.08 | 29.92 | 1130976 | 1130.976 | 47.34 | 32.66 | 1234548 | 1234.548 | 44.6 | 35.4 | 1338120 | 1338.12 | 45
11/19/20XX 7:00:00 AM | 0.29167 | 6 | 44.3 | 69.2 | 44.3 |  | 44.3 | 69.23 | 10.77 | 407106 | 407.106 | 66.46 | 13.54 | 511812 | 511.812 | 63.69 | 16.31 | 616518 | 616.518 | 60.92 | 19.08 | 721224 | 721.224 | 58.15 | 21.85 | 825930 | 825.93 | 55.38 | 24.62 | 930636 | 930.636 | 52.61 | 27.39 | 1035342 | 1035.342 | 49.84 | 30.16 | 1140048 | 1140.048 | 47.07 | 32.93 | 1244754 | 1244.754 | 44.3 | 35.7 | 1349460 | 1349.46 | 45
11/19/20XX 8:00:00 AM | 0.33333 | 6 | 44.7 | 67.2 | 44.7 |  | 44.7 | 69.27 | 10.73 | 405594 | 405.594 | 66.54 | 13.46 | 508788 | 508.788 | 63.81 | 16.19 | 611982 | 611.982 | 61.08 | 18.92 | 715176 | 715.176 | 58.35 | 21.65 | 818370 | 818.37 | 55.62 | 24.38 | 921564 | 921.564 | 52.89 | 27.11 | 1024758 | 1024.758 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.43 | 32.57 | 1231146 | 1231.146 | 44.7 | 35.3 | 1334340 | 1334.34 | 45
11/19/20XX 9:00:00 AM | 0.375 | 6 | 45.6 | 64.4 | 45.6 |  | 45.6 | 69.36 | 10.64 | 402192 | 402.192 | 66.72 | 13.28 | 501984 | 501.984 | 64.08 | 15.92 | 601776 | 601.776 | 61.44 | 18.56 | 701568 | 701.568 | 58.8 | 21.2 | 801360 | 801.36 | 56.16 | 23.84 | 901152 | 901.152 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.88 | 29.12 | 1100736 | 1100.736 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.6 | 34.4 | 1300320 | 1300.32 | 45
11/19/20XX 10:00:00 AM | 0.41667 | 6 | 46.6 | 60.5 | 46.6 |  | 46.6 | 69.46 | 10.54 | 398412 | 398.412 | 66.92 | 13.08 | 494424 | 494.424 | 64.38 | 15.62 | 590436 | 590.436 | 61.84 | 18.16 | 686448 | 686.448 | 59.3 | 20.7 | 782460 | 782.46 | 56.76 | 23.24 | 878472 | 878.472 | 54.22 | 25.78 | 974484 | 974.484 | 51.68 | 28.32 | 1070496 | 1070.496 | 49.14 | 30.86 | 1166508 | 1166.508 | 46.6 | 33.4 | 1262520 | 1262.52 | 45
11/19/20XX 11:00:00 AM | 0.45833 | 6 | 48.1 | 57.3 | 48.1 |  | 48.1 | 69.61 | 10.39 | 392742 | 392.742 | 67.22 | 12.78 | 483084 | 483.084 | 64.83 | 15.17 | 573426 | 573.426 | 62.44 | 17.56 | 663768 | 663.768 | 60.05 | 19.95 | 754110 | 754.11 | 57.66 | 22.34 | 844452 | 844.452 | 55.27 | 24.73 | 934794 | 934.794 | 52.88 | 27.12 | 1025136 | 1025.136 | 50.49 | 29.51 | 1115478 | 1115.478 | 48.1 | 31.9 | 1205820 | 1205.82 | 50
11/19/20XX 12:00:00 PM | 0.5 | 6 | 49.1 | 55.9 | 49.1 |  | 49.1 | 69.71 | 10.29 | 388962 | 388.962 | 67.42 | 12.58 | 475524 | 475.524 | 65.13 | 14.87 | 562086 | 562.086 | 62.84 | 17.16 | 648648 | 648.648 | 60.55 | 19.45 | 735210 | 735.21 | 58.26 | 21.74 | 821772 | 821.772 | 55.97 | 24.03 | 908334 | 908.334 | 53.68 | 26.32 | 994896 | 994.896 | 51.39 | 28.61 | 1081458 | 1081.458 | 49.1 | 30.9 | 1168020 | 1168.02 | 50
11/19/20XX 1:00:00 PM | 0.54167 | 6 | 49.7 | 54.4 | 49.7 |  | 49.7 | 69.77 | 10.23 | 386694 | 386.694 | 67.54 | 12.46 | 470988 | 470.988 | 65.31 | 14.69 | 555282 | 555.282 | 63.08 | 16.92 | 639576 | 639.576 | 60.85 | 19.15 | 723870 | 723.87 | 58.62 | 21.38 | 808164 | 808.164 | 56.39 | 23.61 | 892458 | 892.458 | 54.16 | 25.84 | 976752 | 976.752 | 51.93 | 28.07 | 1061046 | 1061.046 | 49.7 | 30.3 | 1145340 | 1145.34 | 50
11/19/20XX 2:00:00 PM | 0.58333 | 6 | 49.3 | 57.4 | 49.3 |  | 49.3 | 69.73 | 10.27 | 388206 | 388.206 | 67.46 | 12.54 | 474012 | 474.012 | 65.19 | 14.81 | 559818 | 559.818 | 62.92 | 17.08 | 645624 | 645.624 | 60.65 | 19.35 | 731430 | 731.43 | 58.38 | 21.62 | 817236 | 817.236 | 56.11 | 23.89 | 903042 | 903.042 | 53.84 | 26.16 | 988848 | 988.848 | 51.57 | 28.43 | 1074654 | 1074.654 | 49.3 | 30.7 | 1160460 | 1160.46 | 50
11/19/20XX 3:00:00 PM | 0.625 | 6 | 49.2 | 57.9 | 49.2 |  | 49.2 | 69.72 | 10.28 | 388584 | 388.584 | 67.44 | 12.56 | 474768 | 474.768 | 65.16 | 14.84 | 560952 | 560.952 | 62.88 | 17.12 | 647136 | 647.136 | 60.6 | 19.4 | 733320 | 733.32 | 58.32 | 21.68 | 819504 | 819.504 | 56.04 | 23.96 | 905688 | 905.688 | 53.76 | 26.24 | 991872 | 991.872 | 51.48 | 28.52 | 1078056 | 1078.056 | 49.2 | 30.8 | 1164240 | 1164.24 | 50
11/19/20XX 4:00:00 PM | 0.66667 | 6 | 48.9 | 59.3 | 48.9 |  | 48.9 | 69.69 | 10.31 | 389718 | 389.718 | 67.38 | 12.62 | 477036 | 477.036 | 65.07 | 14.93 | 564354 | 564.354 | 62.76 | 17.24 | 651672 | 651.672 | 60.45 | 19.55 | 738990 | 738.99 | 58.14 | 21.86 | 826308 | 826.308 | 55.83 | 24.17 | 913626 | 913.626 | 53.52 | 26.48 | 1000944 | 1000.944 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.9 | 31.1 | 1175580 | 1175.58 | 50
11/19/20XX 5:00:00 PM | 0.70833 | 6 | 47.7 | 61.4 | 47.7 |  | 47.7 | 69.57 | 10.43 | 394254 | 394.254 | 67.14 | 12.86 | 486108 | 486.108 | 64.71 | 15.29 | 577962 | 577.962 | 62.28 | 17.72 | 669816 | 669.816 | 59.85 | 20.15 | 761670 | 761.67 | 57.42 | 22.58 | 853524 | 853.524 | 54.99 | 25.01 | 945378 | 945.378 | 52.56 | 27.44 | 1037232 | 1037.232 | 50.13 | 29.87 | 1129086 | 1129.086 | 47.7 | 32.3 | 1220940 | 1220.94 | 50
11/19/20XX 6:00:00 PM | 0.75 | 6 | 47.8 | 62.2 | 47.8 |  | 47.8 | 69.58 | 10.42 | 393876 | 393.876 | 67.16 | 12.84 | 485352 | 485.352 | 64.74 | 15.26 | 576828 | 576.828 | 62.32 | 17.68 | 668304 | 668.304 | 59.9 | 20.1 | 759780 | 759.78 | 57.48 | 22.52 | 851256 | 851.256 | 55.06 | 24.94 | 942732 | 942.732 | 52.64 | 27.36 | 1034208 | 1034.208 | 50.22 | 29.78 | 1125684 | 1125.684 | 47.8 | 32.2 | 1217160 | 1217.16 | 50
11/19/20XX 7:00:00 PM | 0.79167 | 6 | 47.5 | 62.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/19/20XX 8:00:00 PM | 0.83333 | 6 | 47.6 | 64.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/19/20XX 9:00:00 PM | 0.875 | 6 | 47.4 | 66.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/19/20XX 10:00:00 PM | 0.91667 | 6 | 46.8 | 68.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/19/20XX 11:00:00 PM | 0.95833 | 6 | 45.8 | 72.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/19/20XX 12:00:00 AM | 0 | 7 | 45.5 | 70.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/20/20XX 1:00:00 AM | 0.041667 | 7 | 45.1 | 70.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/20/20XX 2:00:00 AM | 0.083333 | 7 | 44.8 | 71.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/20/20XX 3:00:00 AM | 0.125 | 7 | 44.7 | 70.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/20/20XX 4:00:00 AM | 0.16667 | 7 | 44.4 | 70.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/20/20XX 5:00:00 AM | 0.20833 | 7 | 44.1 | 68.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/20/20XX 6:00:00 AM | 0.25 | 7 | 44.1 | 69.2 | 44.1 |  | 44.1 | 69.21 | 10.79 | 407862 | 407.862 | 66.42 | 13.58 | 513324 | 513.324 | 63.63 | 16.37 | 618786 | 618.786 | 60.84 | 19.16 | 724248 | 724.248 | 58.05 | 21.95 | 829710 | 829.71 | 55.26 | 24.74 | 935172 | 935.172 | 52.47 | 27.53 | 1040634 | 1040.634 | 49.68 | 30.32 | 1146096 | 1146.096 | 46.89 | 33.11 | 1251558 | 1251.558 | 44.1 | 35.9 | 1357020 | 1357.02 | 45
11/20/20XX 7:00:00 AM | 0.29167 | 7 | 43.5 | 67.1 | 43.5 |  | 43.5 | 69.15 | 10.85 | 410130 | 410.13 | 66.3 | 13.7 | 517860 | 517.86 | 63.45 | 16.55 | 625590 | 625.59 | 60.6 | 19.4 | 733320 | 733.32 | 57.75 | 22.25 | 841050 | 841.05 | 54.9 | 25.1 | 948780 | 948.78 | 52.05 | 27.95 | 1056510 | 1056.51 | 49.2 | 30.8 | 1164240 | 1164.24 | 46.35 | 33.65 | 1271970 | 1271.97 | 43.5 | 36.5 | 1379700 | 1379.7 | 45
11/20/20XX 8:00:00 AM | 0.33333 | 7 | 43.5 | 65.3 | 43.5 |  | 43.5 | 69.15 | 10.85 | 410130 | 410.13 | 66.3 | 13.7 | 517860 | 517.86 | 63.45 | 16.55 | 625590 | 625.59 | 60.6 | 19.4 | 733320 | 733.32 | 57.75 | 22.25 | 841050 | 841.05 | 54.9 | 25.1 | 948780 | 948.78 | 52.05 | 27.95 | 1056510 | 1056.51 | 49.2 | 30.8 | 1164240 | 1164.24 | 46.35 | 33.65 | 1271970 | 1271.97 | 43.5 | 36.5 | 1379700 | 1379.7 | 45
11/20/20XX 9:00:00 AM | 0.375 | 7 | 44.1 | 61.8 | 44.1 |  | 44.1 | 69.21 | 10.79 | 407862 | 407.862 | 66.42 | 13.58 | 513324 | 513.324 | 63.63 | 16.37 | 618786 | 618.786 | 60.84 | 19.16 | 724248 | 724.248 | 58.05 | 21.95 | 829710 | 829.71 | 55.26 | 24.74 | 935172 | 935.172 | 52.47 | 27.53 | 1040634 | 1040.634 | 49.68 | 30.32 | 1146096 | 1146.096 | 46.89 | 33.11 | 1251558 | 1251.558 | 44.1 | 35.9 | 1357020 | 1357.02 | 45
11/20/20XX 10:00:00 AM | 0.41667 | 7 | 45.2 | 58.2 | 45.2 |  | 45.2 | 69.32 | 10.68 | 403704 | 403.704 | 66.64 | 13.36 | 505008 | 505.008 | 63.96 | 16.04 | 606312 | 606.312 | 61.28 | 18.72 | 707616 | 707.616 | 58.6 | 21.4 | 808920 | 808.92 | 55.92 | 24.08 | 910224 | 910.224 | 53.24 | 26.76 | 1011528 | 1011.528 | 50.56 | 29.44 | 1112832 | 1112.832 | 47.88 | 32.12 | 1214136 | 1214.136 | 45.2 | 34.8 | 1315440 | 1315.44 | 45
11/20/20XX 11:00:00 AM | 0.45833 | 7 | 46.7 | 54.1 | 46.7 |  | 46.7 | 69.47 | 10.53 | 398034 | 398.034 | 66.94 | 13.06 | 493668 | 493.668 | 64.41 | 15.59 | 589302 | 589.302 | 61.88 | 18.12 | 684936 | 684.936 | 59.35 | 20.65 | 780570 | 780.57 | 56.82 | 23.18 | 876204 | 876.204 | 54.29 | 25.71 | 971838 | 971.838 | 51.76 | 28.24 | 1067472 | 1067.472 | 49.23 | 30.77 | 1163106 | 1163.106 | 46.7 | 33.3 | 1258740 | 1258.74 | 45
11/20/20XX 12:00:00 PM | 0.5 | 7 | 48.5 | 49.4 | 48.5 |  | 48.5 | 69.65 | 10.35 | 391230 | 391.23 | 67.3 | 12.7 | 480060 | 480.06 | 64.95 | 15.05 | 568890 | 568.89 | 62.6 | 17.4 | 657720 | 657.72 | 60.25 | 19.75 | 746550 | 746.55 | 57.9 | 22.1 | 835380 | 835.38 | 55.55 | 24.45 | 924210 | 924.21 | 53.2 | 26.8 | 1013040 | 1013.04 | 50.85 | 29.15 | 1101870 | 1101.87 | 48.5 | 31.5 | 1190700 | 1190.7 | 50
11/20/20XX 1:00:00 PM | 0.54167 | 7 | 49.8 | 46 | 49.8 |  | 49.8 | 69.78 | 10.22 | 386316 | 386.316 | 67.56 | 12.44 | 470232 | 470.232 | 65.34 | 14.66 | 554148 | 554.148 | 63.12 | 16.88 | 638064 | 638.064 | 60.9 | 19.1 | 721980 | 721.98 | 58.68 | 21.32 | 805896 | 805.896 | 56.46 | 23.54 | 889812 | 889.812 | 54.24 | 25.76 | 973728 | 973.728 | 52.02 | 27.98 | 1057644 | 1057.644 | 49.8 | 30.2 | 1141560 | 1141.56 | 50
11/20/20XX 2:00:00 PM | 0.58333 | 7 | 49.9 | 45.7 | 49.9 |  | 49.9 | 69.79 | 10.21 | 385938 | 385.938 | 67.58 | 12.42 | 469476 | 469.476 | 65.37 | 14.63 | 553014 | 553.014 | 63.16 | 16.84 | 636552 | 636.552 | 60.95 | 19.05 | 720090 | 720.09 | 58.74 | 21.26 | 803628 | 803.628 | 56.53 | 23.47 | 887166 | 887.166 | 54.32 | 25.68 | 970704 | 970.704 | 52.11 | 27.89 | 1054242 | 1054.242 | 49.9 | 30.1 | 1137780 | 1137.78 | 50
11/20/20XX 3:00:00 PM | 0.625 | 7 | 49.8 | 45.6 | 49.8 |  | 49.8 | 69.78 | 10.22 | 386316 | 386.316 | 67.56 | 12.44 | 470232 | 470.232 | 65.34 | 14.66 | 554148 | 554.148 | 63.12 | 16.88 | 638064 | 638.064 | 60.9 | 19.1 | 721980 | 721.98 | 58.68 | 21.32 | 805896 | 805.896 | 56.46 | 23.54 | 889812 | 889.812 | 54.24 | 25.76 | 973728 | 973.728 | 52.02 | 27.98 | 1057644 | 1057.644 | 49.8 | 30.2 | 1141560 | 1141.56 | 50
11/20/20XX 4:00:00 PM | 0.66667 | 7 | 49.4 | 43.9 | 49.4 |  | 49.4 | 69.74 | 10.26 | 387828 | 387.828 | 67.48 | 12.52 | 473256 | 473.256 | 65.22 | 14.78 | 558684 | 558.684 | 62.96 | 17.04 | 644112 | 644.112 | 60.7 | 19.3 | 729540 | 729.54 | 58.44 | 21.56 | 814968 | 814.968 | 56.18 | 23.82 | 900396 | 900.396 | 53.92 | 26.08 | 985824 | 985.824 | 51.66 | 28.34 | 1071252 | 1071.252 | 49.4 | 30.6 | 1156680 | 1156.68 | 50
11/20/20XX 5:00:00 PM | 0.70833 | 7 | 48.3 | 44.5 | 48.3 |  | 48.3 | 69.63 | 10.37 | 391986 | 391.986 | 67.26 | 12.74 | 481572 | 481.572 | 64.89 | 15.11 | 571158 | 571.158 | 62.52 | 17.48 | 660744 | 660.744 | 60.15 | 19.85 | 750330 | 750.33 | 57.78 | 22.22 | 839916 | 839.916 | 55.41 | 24.59 | 929502 | 929.502 | 53.04 | 26.96 | 1019088 | 1019.088 | 50.67 | 29.33 | 1108674 | 1108.674 | 48.3 | 31.7 | 1198260 | 1198.26 | 50
11/20/20XX 6:00:00 PM | 0.75 | 7 | 47.2 | 46.1 | 47.2 |  | 47.2 | 69.52 | 10.48 | 396144 | 396.144 | 67.04 | 12.96 | 489888 | 489.888 | 64.56 | 15.44 | 583632 | 583.632 | 62.08 | 17.92 | 677376 | 677.376 | 59.6 | 20.4 | 771120 | 771.12 | 57.12 | 22.88 | 864864 | 864.864 | 54.64 | 25.36 | 958608 | 958.608 | 52.16 | 27.84 | 1052352 | 1052.352 | 49.68 | 30.32 | 1146096 | 1146.096 | 47.2 | 32.8 | 1239840 | 1239.84 | 45
11/20/20XX 7:00:00 PM | 0.79167 | 7 | 46.9 | 46.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/20/20XX 8:00:00 PM | 0.83333 | 7 | 46.1 | 47.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/20/20XX 9:00:00 PM | 0.875 | 7 | 45.6 | 48.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/20/20XX 10:00:00 PM | 0.91667 | 7 | 44.1 | 51.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/20/20XX 11:00:00 PM | 0.95833 | 7 | 43.6 | 51.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/20/20XX 12:00:00 AM | 0 | 1 | 42.9 | 53 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/21/20XX 1:00:00 AM | 0.041667 | 1 | 42.5 | 53.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/21/20XX 2:00:00 AM | 0.083333 | 1 | 42.1 | 54.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/21/20XX 3:00:00 AM | 0.125 | 1 | 41.2 | 56.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/21/20XX 4:00:00 AM | 0.16667 | 1 | 40.6 | 58.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/21/20XX 5:00:00 AM | 0.20833 | 1 | 40.6 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/21/20XX 6:00:00 AM | 0.25 | 1 | 40.2 | 58 | 40.2 |  | 40.2 | 68.82 | 11.18 | 422604 | 422.604 | 65.64 | 14.36 | 542808 | 542.808 | 62.46 | 17.54 | 663012 | 663.012 | 59.28 | 20.72 | 783216 | 783.216 | 56.1 | 23.9 | 903420 | 903.42 | 52.92 | 27.08 | 1023624 | 1023.624 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.56 | 33.44 | 1264032 | 1264.032 | 43.38 | 36.62 | 1384236 | 1384.236 | 40.2 | 39.8 | 1504440 | 1504.44 | 40
11/21/20XX 7:00:00 AM | 0.29167 | 1 | 40.1 | 55.4 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
11/21/20XX 8:00:00 AM | 0.33333 | 1 | 40.6 | 55.4 | 40.6 |  | 40.6 | 68.86 | 11.14 | 421092 | 421.092 | 65.72 | 14.28 | 539784 | 539.784 | 62.58 | 17.42 | 658476 | 658.476 | 59.44 | 20.56 | 777168 | 777.168 | 56.3 | 23.7 | 895860 | 895.86 | 53.16 | 26.84 | 1014552 | 1014.552 | 50.02 | 29.98 | 1133244 | 1133.244 | 46.88 | 33.12 | 1251936 | 1251.936 | 43.74 | 36.26 | 1370628 | 1370.628 | 40.6 | 39.4 | 1489320 | 1489.32 | 40
11/21/20XX 9:00:00 AM | 0.375 | 1 | 41.9 | 53 | 41.9 |  | 41.9 | 68.99 | 11.01 | 416178 | 416.178 | 65.98 | 14.02 | 529956 | 529.956 | 62.97 | 17.03 | 643734 | 643.734 | 59.96 | 20.04 | 757512 | 757.512 | 56.95 | 23.05 | 871290 | 871.29 | 53.94 | 26.06 | 985068 | 985.068 | 50.93 | 29.07 | 1098846 | 1098.846 | 47.92 | 32.08 | 1212624 | 1212.624 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.9 | 38.1 | 1440180 | 1440.18 | 40
11/21/20XX 10:00:00 AM | 0.41667 | 1 | 43.7 | 50.1 | 43.7 |  | 43.7 | 69.17 | 10.83 | 409374 | 409.374 | 66.34 | 13.66 | 516348 | 516.348 | 63.51 | 16.49 | 623322 | 623.322 | 60.68 | 19.32 | 730296 | 730.296 | 57.85 | 22.15 | 837270 | 837.27 | 55.02 | 24.98 | 944244 | 944.244 | 52.19 | 27.81 | 1051218 | 1051.218 | 49.36 | 30.64 | 1158192 | 1158.192 | 46.53 | 33.47 | 1265166 | 1265.166 | 43.7 | 36.3 | 1372140 | 1372.14 | 45
11/21/20XX 11:00:00 AM | 0.45833 | 1 | 45.4 | 46.8 | 45.4 |  | 45.4 | 69.34 | 10.66 | 402948 | 402.948 | 66.68 | 13.32 | 503496 | 503.496 | 64.02 | 15.98 | 604044 | 604.044 | 61.36 | 18.64 | 704592 | 704.592 | 58.7 | 21.3 | 805140 | 805.14 | 56.04 | 23.96 | 905688 | 905.688 | 53.38 | 26.62 | 1006236 | 1006.236 | 50.72 | 29.28 | 1106784 | 1106.784 | 48.06 | 31.94 | 1207332 | 1207.332 | 45.4 | 34.6 | 1307880 | 1307.88 | 45
11/21/20XX 12:00:00 PM | 0.5 | 1 | 47.2 | 44.4 | 47.2 |  | 47.2 | 69.52 | 10.48 | 396144 | 396.144 | 67.04 | 12.96 | 489888 | 489.888 | 64.56 | 15.44 | 583632 | 583.632 | 62.08 | 17.92 | 677376 | 677.376 | 59.6 | 20.4 | 771120 | 771.12 | 57.12 | 22.88 | 864864 | 864.864 | 54.64 | 25.36 | 958608 | 958.608 | 52.16 | 27.84 | 1052352 | 1052.352 | 49.68 | 30.32 | 1146096 | 1146.096 | 47.2 | 32.8 | 1239840 | 1239.84 | 45
11/21/20XX 1:00:00 PM | 0.54167 | 1 | 48.3 | 43.5 | 48.3 |  | 48.3 | 69.63 | 10.37 | 391986 | 391.986 | 67.26 | 12.74 | 481572 | 481.572 | 64.89 | 15.11 | 571158 | 571.158 | 62.52 | 17.48 | 660744 | 660.744 | 60.15 | 19.85 | 750330 | 750.33 | 57.78 | 22.22 | 839916 | 839.916 | 55.41 | 24.59 | 929502 | 929.502 | 53.04 | 26.96 | 1019088 | 1019.088 | 50.67 | 29.33 | 1108674 | 1108.674 | 48.3 | 31.7 | 1198260 | 1198.26 | 50
11/21/20XX 2:00:00 PM | 0.58333 | 1 | 48.8 | 43.1 | 48.8 |  | 48.8 | 69.68 | 10.32 | 390096 | 390.096 | 67.36 | 12.64 | 477792 | 477.792 | 65.04 | 14.96 | 565488 | 565.488 | 62.72 | 17.28 | 653184 | 653.184 | 60.4 | 19.6 | 740880 | 740.88 | 58.08 | 21.92 | 828576 | 828.576 | 55.76 | 24.24 | 916272 | 916.272 | 53.44 | 26.56 | 1003968 | 1003.968 | 51.12 | 28.88 | 1091664 | 1091.664 | 48.8 | 31.2 | 1179360 | 1179.36 | 50
11/21/20XX 3:00:00 PM | 0.625 | 1 | 48.3 | 44.5 | 48.3 |  | 48.3 | 69.63 | 10.37 | 391986 | 391.986 | 67.26 | 12.74 | 481572 | 481.572 | 64.89 | 15.11 | 571158 | 571.158 | 62.52 | 17.48 | 660744 | 660.744 | 60.15 | 19.85 | 750330 | 750.33 | 57.78 | 22.22 | 839916 | 839.916 | 55.41 | 24.59 | 929502 | 929.502 | 53.04 | 26.96 | 1019088 | 1019.088 | 50.67 | 29.33 | 1108674 | 1108.674 | 48.3 | 31.7 | 1198260 | 1198.26 | 50
11/21/20XX 4:00:00 PM | 0.66667 | 1 | 47.8 | 46.1 | 47.8 |  | 47.8 | 69.58 | 10.42 | 393876 | 393.876 | 67.16 | 12.84 | 485352 | 485.352 | 64.74 | 15.26 | 576828 | 576.828 | 62.32 | 17.68 | 668304 | 668.304 | 59.9 | 20.1 | 759780 | 759.78 | 57.48 | 22.52 | 851256 | 851.256 | 55.06 | 24.94 | 942732 | 942.732 | 52.64 | 27.36 | 1034208 | 1034.208 | 50.22 | 29.78 | 1125684 | 1125.684 | 47.8 | 32.2 | 1217160 | 1217.16 | 50
11/21/20XX 5:00:00 PM | 0.70833 | 1 | 46.9 | 47.3 | 46.9 |  | 46.9 | 69.49 | 10.51 | 397278 | 397.278 | 66.98 | 13.02 | 492156 | 492.156 | 64.47 | 15.53 | 587034 | 587.034 | 61.96 | 18.04 | 681912 | 681.912 | 59.45 | 20.55 | 776790 | 776.79 | 56.94 | 23.06 | 871668 | 871.668 | 54.43 | 25.57 | 966546 | 966.546 | 51.92 | 28.08 | 1061424 | 1061.424 | 49.41 | 30.59 | 1156302 | 1156.302 | 46.9 | 33.1 | 1251180 | 1251.18 | 45
11/21/20XX 6:00:00 PM | 0.75 | 1 | 46.5 | 50.9 | 46.5 |  | 46.5 | 69.45 | 10.55 | 398790 | 398.79 | 66.9 | 13.1 | 495180 | 495.18 | 64.35 | 15.65 | 591570 | 591.57 | 61.8 | 18.2 | 687960 | 687.96 | 59.25 | 20.75 | 784350 | 784.35 | 56.7 | 23.3 | 880740 | 880.74 | 54.15 | 25.85 | 977130 | 977.13 | 51.6 | 28.4 | 1073520 | 1073.52 | 49.05 | 30.95 | 1169910 | 1169.91 | 46.5 | 33.5 | 1266300 | 1266.3 | 45
11/21/20XX 7:00:00 PM | 0.79167 | 1 | 45.5 | 55.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/21/20XX 8:00:00 PM | 0.83333 | 1 | 45.4 | 54.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/21/20XX 9:00:00 PM | 0.875 | 1 | 44.9 | 55.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/21/20XX 10:00:00 PM | 0.91667 | 1 | 44.8 | 56 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/21/20XX 11:00:00 PM | 0.95833 | 1 | 44.1 | 55.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/21/20XX 12:00:00 AM | 0 | 2 | 43.7 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/22/20XX 1:00:00 AM | 0.041667 | 2 | 43.7 | 60.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/22/20XX 2:00:00 AM | 0.083333 | 2 | 43.5 | 62.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/22/20XX 3:00:00 AM | 0.125 | 2 | 43.2 | 65.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/22/20XX 4:00:00 AM | 0.16667 | 2 | 42.9 | 68.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/22/20XX 5:00:00 AM | 0.20833 | 2 | 42.9 | 68.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/22/20XX 6:00:00 AM | 0.25 | 2 | 42.8 | 72 | 42.8 |  | 42.8 | 69.08 | 10.92 | 412776 | 412.776 | 66.16 | 13.84 | 523152 | 523.152 | 63.24 | 16.76 | 633528 | 633.528 | 60.32 | 19.68 | 743904 | 743.904 | 57.4 | 22.6 | 854280 | 854.28 | 54.48 | 25.52 | 964656 | 964.656 | 51.56 | 28.44 | 1075032 | 1075.032 | 48.64 | 31.36 | 1185408 | 1185.408 | 45.72 | 34.28 | 1295784 | 1295.784 | 42.8 | 37.2 | 1406160 | 1406.16 | 45
11/22/20XX 7:00:00 AM | 0.29167 | 2 | 43 | 72.3 | 43 |  | 43 | 69.1 | 10.9 | 412020 | 412.02 | 66.2 | 13.8 | 521640 | 521.64 | 63.3 | 16.7 | 631260 | 631.26 | 60.4 | 19.6 | 740880 | 740.88 | 57.5 | 22.5 | 850500 | 850.5 | 54.6 | 25.4 | 960120 | 960.12 | 51.7 | 28.3 | 1069740 | 1069.74 | 48.8 | 31.2 | 1179360 | 1179.36 | 45.9 | 34.1 | 1288980 | 1288.98 | 43 | 37 | 1398600 | 1398.6 | 45
11/22/20XX 8:00:00 AM | 0.33333 | 2 | 43.2 | 71.1 | 43.2 |  | 43.2 | 69.12 | 10.88 | 411264 | 411.264 | 66.24 | 13.76 | 520128 | 520.128 | 63.36 | 16.64 | 628992 | 628.992 | 60.48 | 19.52 | 737856 | 737.856 | 57.6 | 22.4 | 846720 | 846.72 | 54.72 | 25.28 | 955584 | 955.584 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.08 | 33.92 | 1282176 | 1282.176 | 43.2 | 36.8 | 1391040 | 1391.04 | 45
11/22/20XX 9:00:00 AM | 0.375 | 2 | 43.5 | 68.2 | 43.5 |  | 43.5 | 69.15 | 10.85 | 410130 | 410.13 | 66.3 | 13.7 | 517860 | 517.86 | 63.45 | 16.55 | 625590 | 625.59 | 60.6 | 19.4 | 733320 | 733.32 | 57.75 | 22.25 | 841050 | 841.05 | 54.9 | 25.1 | 948780 | 948.78 | 52.05 | 27.95 | 1056510 | 1056.51 | 49.2 | 30.8 | 1164240 | 1164.24 | 46.35 | 33.65 | 1271970 | 1271.97 | 43.5 | 36.5 | 1379700 | 1379.7 | 45
11/22/20XX 10:00:00 AM | 0.41667 | 2 | 44.7 | 64.2 | 44.7 |  | 44.7 | 69.27 | 10.73 | 405594 | 405.594 | 66.54 | 13.46 | 508788 | 508.788 | 63.81 | 16.19 | 611982 | 611.982 | 61.08 | 18.92 | 715176 | 715.176 | 58.35 | 21.65 | 818370 | 818.37 | 55.62 | 24.38 | 921564 | 921.564 | 52.89 | 27.11 | 1024758 | 1024.758 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.43 | 32.57 | 1231146 | 1231.146 | 44.7 | 35.3 | 1334340 | 1334.34 | 45
11/22/20XX 11:00:00 AM | 0.45833 | 2 | 45.8 | 60.6 | 45.8 |  | 45.8 | 69.38 | 10.62 | 401436 | 401.436 | 66.76 | 13.24 | 500472 | 500.472 | 64.14 | 15.86 | 599508 | 599.508 | 61.52 | 18.48 | 698544 | 698.544 | 58.9 | 21.1 | 797580 | 797.58 | 56.28 | 23.72 | 896616 | 896.616 | 53.66 | 26.34 | 995652 | 995.652 | 51.04 | 28.96 | 1094688 | 1094.688 | 48.42 | 31.58 | 1193724 | 1193.724 | 45.8 | 34.2 | 1292760 | 1292.76 | 45
11/22/20XX 12:00:00 PM | 0.5 | 2 | 47.2 | 57.6 | 47.2 |  | 47.2 | 69.52 | 10.48 | 396144 | 396.144 | 67.04 | 12.96 | 489888 | 489.888 | 64.56 | 15.44 | 583632 | 583.632 | 62.08 | 17.92 | 677376 | 677.376 | 59.6 | 20.4 | 771120 | 771.12 | 57.12 | 22.88 | 864864 | 864.864 | 54.64 | 25.36 | 958608 | 958.608 | 52.16 | 27.84 | 1052352 | 1052.352 | 49.68 | 30.32 | 1146096 | 1146.096 | 47.2 | 32.8 | 1239840 | 1239.84 | 45
11/22/20XX 1:00:00 PM | 0.54167 | 2 | 48.2 | 53.5 | 48.2 |  | 48.2 | 69.62 | 10.38 | 392364 | 392.364 | 67.24 | 12.76 | 482328 | 482.328 | 64.86 | 15.14 | 572292 | 572.292 | 62.48 | 17.52 | 662256 | 662.256 | 60.1 | 19.9 | 752220 | 752.22 | 57.72 | 22.28 | 842184 | 842.184 | 55.34 | 24.66 | 932148 | 932.148 | 52.96 | 27.04 | 1022112 | 1022.112 | 50.58 | 29.42 | 1112076 | 1112.076 | 48.2 | 31.8 | 1202040 | 1202.04 | 50
11/22/20XX 2:00:00 PM | 0.58333 | 2 | 48.4 | 51.5 | 48.4 |  | 48.4 | 69.64 | 10.36 | 391608 | 391.608 | 67.28 | 12.72 | 480816 | 480.816 | 64.92 | 15.08 | 570024 | 570.024 | 62.56 | 17.44 | 659232 | 659.232 | 60.2 | 19.8 | 748440 | 748.44 | 57.84 | 22.16 | 837648 | 837.648 | 55.48 | 24.52 | 926856 | 926.856 | 53.12 | 26.88 | 1016064 | 1016.064 | 50.76 | 29.24 | 1105272 | 1105.272 | 48.4 | 31.6 | 1194480 | 1194.48 | 50
11/22/20XX 3:00:00 PM | 0.625 | 2 | 48.6 | 50.8 | 48.6 |  | 48.6 | 69.66 | 10.34 | 390852 | 390.852 | 67.32 | 12.68 | 479304 | 479.304 | 64.98 | 15.02 | 567756 | 567.756 | 62.64 | 17.36 | 656208 | 656.208 | 60.3 | 19.7 | 744660 | 744.66 | 57.96 | 22.04 | 833112 | 833.112 | 55.62 | 24.38 | 921564 | 921.564 | 53.28 | 26.72 | 1010016 | 1010.016 | 50.94 | 29.06 | 1098468 | 1098.468 | 48.6 | 31.4 | 1186920 | 1186.92 | 50
11/22/20XX 4:00:00 PM | 0.66667 | 2 | 47.6 | 53.3 | 47.6 |  | 47.6 | 69.56 | 10.44 | 394632 | 394.632 | 67.12 | 12.88 | 486864 | 486.864 | 64.68 | 15.32 | 579096 | 579.096 | 62.24 | 17.76 | 671328 | 671.328 | 59.8 | 20.2 | 763560 | 763.56 | 57.36 | 22.64 | 855792 | 855.792 | 54.92 | 25.08 | 948024 | 948.024 | 52.48 | 27.52 | 1040256 | 1040.256 | 50.04 | 29.96 | 1132488 | 1132.488 | 47.6 | 32.4 | 1224720 | 1224.72 | 50
11/22/20XX 5:00:00 PM | 0.70833 | 2 | 46.6 | 54.6 | 46.6 |  | 46.6 | 69.46 | 10.54 | 398412 | 398.412 | 66.92 | 13.08 | 494424 | 494.424 | 64.38 | 15.62 | 590436 | 590.436 | 61.84 | 18.16 | 686448 | 686.448 | 59.3 | 20.7 | 782460 | 782.46 | 56.76 | 23.24 | 878472 | 878.472 | 54.22 | 25.78 | 974484 | 974.484 | 51.68 | 28.32 | 1070496 | 1070.496 | 49.14 | 30.86 | 1166508 | 1166.508 | 46.6 | 33.4 | 1262520 | 1262.52 | 45
11/22/20XX 6:00:00 PM | 0.75 | 2 | 46.5 | 53.2 | 46.5 |  | 46.5 | 69.45 | 10.55 | 398790 | 398.79 | 66.9 | 13.1 | 495180 | 495.18 | 64.35 | 15.65 | 591570 | 591.57 | 61.8 | 18.2 | 687960 | 687.96 | 59.25 | 20.75 | 784350 | 784.35 | 56.7 | 23.3 | 880740 | 880.74 | 54.15 | 25.85 | 977130 | 977.13 | 51.6 | 28.4 | 1073520 | 1073.52 | 49.05 | 30.95 | 1169910 | 1169.91 | 46.5 | 33.5 | 1266300 | 1266.3 | 45
11/22/20XX 7:00:00 PM | 0.79167 | 2 | 45.4 | 55.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/22/20XX 8:00:00 PM | 0.83333 | 2 | 44.9 | 57.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/22/20XX 9:00:00 PM | 0.875 | 2 | 44.3 | 59.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/22/20XX 10:00:00 PM | 0.91667 | 2 | 43.7 | 61 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/22/20XX 11:00:00 PM | 0.95833 | 2 | 43 | 62.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/22/20XX 12:00:00 AM | 0 | 3 | 42.8 | 63.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/23/20XX 1:00:00 AM | 0.041667 | 3 | 42.1 | 64.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/23/20XX 2:00:00 AM | 0.083333 | 3 | 41.5 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/23/20XX 3:00:00 AM | 0.125 | 3 | 41 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/23/20XX 4:00:00 AM | 0.16667 | 3 | 40.7 | 63.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/23/20XX 5:00:00 AM | 0.20833 | 3 | 40.2 | 63.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/23/20XX 6:00:00 AM | 0.25 | 3 | 39.5 | 64.7 | 39.5 |  | 39.5 | 68.75 | 11.25 | 425250 | 425.25 | 65.5 | 14.5 | 548100 | 548.1 | 62.25 | 17.75 | 670950 | 670.95 | 59 | 21 | 793800 | 793.8 | 55.75 | 24.25 | 916650 | 916.65 | 52.5 | 27.5 | 1039500 | 1039.5 | 49.25 | 30.75 | 1162350 | 1162.35 | 46 | 34 | 1285200 | 1285.2 | 42.75 | 37.25 | 1408050 | 1408.05 | 39.5 | 40.5 | 1530900 | 1530.9 | 40
11/23/20XX 7:00:00 AM | 0.29167 | 3 | 39.1 | 65.8 | 39.1 |  | 39.1 | 68.71 | 11.29 | 426762 | 426.762 | 65.42 | 14.58 | 551124 | 551.124 | 62.13 | 17.87 | 675486 | 675.486 | 58.84 | 21.16 | 799848 | 799.848 | 55.55 | 24.45 | 924210 | 924.21 | 52.26 | 27.74 | 1048572 | 1048.572 | 48.97 | 31.03 | 1172934 | 1172.934 | 45.68 | 34.32 | 1297296 | 1297.296 | 42.39 | 37.61 | 1421658 | 1421.658 | 39.1 | 40.9 | 1546020 | 1546.02 | 40
11/23/20XX 8:00:00 AM | 0.33333 | 3 | 39.4 | 63.7 | 39.4 |  | 39.4 | 68.74 | 11.26 | 425628 | 425.628 | 65.48 | 14.52 | 548856 | 548.856 | 62.22 | 17.78 | 672084 | 672.084 | 58.96 | 21.04 | 795312 | 795.312 | 55.7 | 24.3 | 918540 | 918.54 | 52.44 | 27.56 | 1041768 | 1041.768 | 49.18 | 30.82 | 1164996 | 1164.996 | 45.92 | 34.08 | 1288224 | 1288.224 | 42.66 | 37.34 | 1411452 | 1411.452 | 39.4 | 40.6 | 1534680 | 1534.68 | 40
11/23/20XX 9:00:00 AM | 0.375 | 3 | 40.5 | 61.7 | 40.5 |  | 40.5 | 68.85 | 11.15 | 421470 | 421.47 | 65.7 | 14.3 | 540540 | 540.54 | 62.55 | 17.45 | 659610 | 659.61 | 59.4 | 20.6 | 778680 | 778.68 | 56.25 | 23.75 | 897750 | 897.75 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.95 | 30.05 | 1135890 | 1135.89 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.65 | 36.35 | 1374030 | 1374.03 | 40.5 | 39.5 | 1493100 | 1493.1 | 40
11/23/20XX 10:00:00 AM | 0.41667 | 3 | 42.3 | 57.7 | 42.3 |  | 42.3 | 69.03 | 10.97 | 414666 | 414.666 | 66.06 | 13.94 | 526932 | 526.932 | 63.09 | 16.91 | 639198 | 639.198 | 60.12 | 19.88 | 751464 | 751.464 | 57.15 | 22.85 | 863730 | 863.73 | 54.18 | 25.82 | 975996 | 975.996 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.27 | 34.73 | 1312794 | 1312.794 | 42.3 | 37.7 | 1425060 | 1425.06 | 40
11/23/20XX 11:00:00 AM | 0.45833 | 3 | 44 | 54 | 44 |  | 44 | 69.2 | 10.8 | 408240 | 408.24 | 66.4 | 13.6 | 514080 | 514.08 | 63.6 | 16.4 | 619920 | 619.92 | 60.8 | 19.2 | 725760 | 725.76 | 58 | 22 | 831600 | 831.6 | 55.2 | 24.8 | 937440 | 937.44 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.6 | 30.4 | 1149120 | 1149.12 | 46.8 | 33.2 | 1254960 | 1254.96 | 44 | 36 | 1360800 | 1360.8 | 45
11/23/20XX 12:00:00 PM | 0.5 | 3 | 45.5 | 51.5 | 45.5 |  | 45.5 | 69.35 | 10.65 | 402570 | 402.57 | 66.7 | 13.3 | 502740 | 502.74 | 64.05 | 15.95 | 602910 | 602.91 | 61.4 | 18.6 | 703080 | 703.08 | 58.75 | 21.25 | 803250 | 803.25 | 56.1 | 23.9 | 903420 | 903.42 | 53.45 | 26.55 | 1003590 | 1003.59 | 50.8 | 29.2 | 1103760 | 1103.76 | 48.15 | 31.85 | 1203930 | 1203.93 | 45.5 | 34.5 | 1304100 | 1304.1 | 45
11/23/20XX 1:00:00 PM | 0.54167 | 3 | 46.2 | 49.1 | 46.2 |  | 46.2 | 69.42 | 10.58 | 399924 | 399.924 | 66.84 | 13.16 | 497448 | 497.448 | 64.26 | 15.74 | 594972 | 594.972 | 61.68 | 18.32 | 692496 | 692.496 | 59.1 | 20.9 | 790020 | 790.02 | 56.52 | 23.48 | 887544 | 887.544 | 53.94 | 26.06 | 985068 | 985.068 | 51.36 | 28.64 | 1082592 | 1082.592 | 48.78 | 31.22 | 1180116 | 1180.116 | 46.2 | 33.8 | 1277640 | 1277.64 | 45
11/23/20XX 2:00:00 PM | 0.58333 | 3 | 47.3 | 47.3 | 47.3 |  | 47.3 | 69.53 | 10.47 | 395766 | 395.766 | 67.06 | 12.94 | 489132 | 489.132 | 64.59 | 15.41 | 582498 | 582.498 | 62.12 | 17.88 | 675864 | 675.864 | 59.65 | 20.35 | 769230 | 769.23 | 57.18 | 22.82 | 862596 | 862.596 | 54.71 | 25.29 | 955962 | 955.962 | 52.24 | 27.76 | 1049328 | 1049.328 | 49.77 | 30.23 | 1142694 | 1142.694 | 47.3 | 32.7 | 1236060 | 1236.06 | 45
11/23/20XX 3:00:00 PM | 0.625 | 3 | 47 | 48.8 | 47 |  | 47 | 69.5 | 10.5 | 396900 | 396.9 | 67 | 13 | 491400 | 491.4 | 64.5 | 15.5 | 585900 | 585.9 | 62 | 18 | 680400 | 680.4 | 59.5 | 20.5 | 774900 | 774.9 | 57 | 23 | 869400 | 869.4 | 54.5 | 25.5 | 963900 | 963.9 | 52 | 28 | 1058400 | 1058.4 | 49.5 | 30.5 | 1152900 | 1152.9 | 47 | 33 | 1247400 | 1247.4 | 45
11/23/20XX 4:00:00 PM | 0.66667 | 3 | 46.3 | 49.4 | 46.3 |  | 46.3 | 69.43 | 10.57 | 399546 | 399.546 | 66.86 | 13.14 | 496692 | 496.692 | 64.29 | 15.71 | 593838 | 593.838 | 61.72 | 18.28 | 690984 | 690.984 | 59.15 | 20.85 | 788130 | 788.13 | 56.58 | 23.42 | 885276 | 885.276 | 54.01 | 25.99 | 982422 | 982.422 | 51.44 | 28.56 | 1079568 | 1079.568 | 48.87 | 31.13 | 1176714 | 1176.714 | 46.3 | 33.7 | 1273860 | 1273.86 | 45
11/23/20XX 5:00:00 PM | 0.70833 | 3 | 45 | 54.3 | 45 |  | 45 | 69.3 | 10.7 | 404460 | 404.46 | 66.6 | 13.4 | 506520 | 506.52 | 63.9 | 16.1 | 608580 | 608.58 | 61.2 | 18.8 | 710640 | 710.64 | 58.5 | 21.5 | 812700 | 812.7 | 55.8 | 24.2 | 914760 | 914.76 | 53.1 | 26.9 | 1016820 | 1016.82 | 50.4 | 29.6 | 1118880 | 1118.88 | 47.7 | 32.3 | 1220940 | 1220.94 | 45 | 35 | 1323000 | 1323 | 45
11/23/20XX 6:00:00 PM | 0.75 | 3 | 44.8 | 53.9 | 44.8 |  | 44.8 | 69.28 | 10.72 | 405216 | 405.216 | 66.56 | 13.44 | 508032 | 508.032 | 63.84 | 16.16 | 610848 | 610.848 | 61.12 | 18.88 | 713664 | 713.664 | 58.4 | 21.6 | 816480 | 816.48 | 55.68 | 24.32 | 919296 | 919.296 | 52.96 | 27.04 | 1022112 | 1022.112 | 50.24 | 29.76 | 1124928 | 1124.928 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.8 | 35.2 | 1330560 | 1330.56 | 45
11/23/20XX 7:00:00 PM | 0.79167 | 3 | 44.6 | 54.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/23/20XX 8:00:00 PM | 0.83333 | 3 | 43.8 | 56.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/23/20XX 9:00:00 PM | 0.875 | 3 | 43.2 | 57.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/23/20XX 10:00:00 PM | 0.91667 | 3 | 42.9 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/23/20XX 11:00:00 PM | 0.95833 | 3 | 42.2 | 59.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/23/20XX 12:00:00 AM | 0 | 4 | 41.4 | 61.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/24/20XX 1:00:00 AM | 0.041667 | 4 | 41 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/24/20XX 2:00:00 AM | 0.083333 | 4 | 40.3 | 61.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/24/20XX 3:00:00 AM | 0.125 | 4 | 40.4 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/24/20XX 4:00:00 AM | 0.16667 | 4 | 39.7 | 62.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/24/20XX 5:00:00 AM | 0.20833 | 4 | 39.6 | 61 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/24/20XX 6:00:00 AM | 0.25 | 4 | 39.5 | 60.8 | 39.5 |  | 39.5 | 68.75 | 11.25 | 425250 | 425.25 | 65.5 | 14.5 | 548100 | 548.1 | 62.25 | 17.75 | 670950 | 670.95 | 59 | 21 | 793800 | 793.8 | 55.75 | 24.25 | 916650 | 916.65 | 52.5 | 27.5 | 1039500 | 1039.5 | 49.25 | 30.75 | 1162350 | 1162.35 | 46 | 34 | 1285200 | 1285.2 | 42.75 | 37.25 | 1408050 | 1408.05 | 39.5 | 40.5 | 1530900 | 1530.9 | 40
11/24/20XX 7:00:00 AM | 0.29167 | 4 | 39.2 | 62.5 | 39.2 |  | 39.2 | 68.72 | 11.28 | 426384 | 426.384 | 65.44 | 14.56 | 550368 | 550.368 | 62.16 | 17.84 | 674352 | 674.352 | 58.88 | 21.12 | 798336 | 798.336 | 55.6 | 24.4 | 922320 | 922.32 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.04 | 30.96 | 1170288 | 1170.288 | 45.76 | 34.24 | 1294272 | 1294.272 | 42.48 | 37.52 | 1418256 | 1418.256 | 39.2 | 40.8 | 1542240 | 1542.24 | 40
11/24/20XX 8:00:00 AM | 0.33333 | 4 | 39.9 | 60.4 | 39.9 |  | 39.9 | 68.79 | 11.21 | 423738 | 423.738 | 65.58 | 14.42 | 545076 | 545.076 | 62.37 | 17.63 | 666414 | 666.414 | 59.16 | 20.84 | 787752 | 787.752 | 55.95 | 24.05 | 909090 | 909.09 | 52.74 | 27.26 | 1030428 | 1030.428 | 49.53 | 30.47 | 1151766 | 1151.766 | 46.32 | 33.68 | 1273104 | 1273.104 | 43.11 | 36.89 | 1394442 | 1394.442 | 39.9 | 40.1 | 1515780 | 1515.78 | 40
11/24/20XX 9:00:00 AM | 0.375 | 4 | 41.2 | 58.7 | 41.2 |  | 41.2 | 68.92 | 11.08 | 418824 | 418.824 | 65.84 | 14.16 | 535248 | 535.248 | 62.76 | 17.24 | 651672 | 651.672 | 59.68 | 20.32 | 768096 | 768.096 | 56.6 | 23.4 | 884520 | 884.52 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.44 | 29.56 | 1117368 | 1117.368 | 47.36 | 32.64 | 1233792 | 1233.792 | 44.28 | 35.72 | 1350216 | 1350.216 | 41.2 | 38.8 | 1466640 | 1466.64 | 40
11/24/20XX 10:00:00 AM | 0.41667 | 4 | 43.3 | 56.5 | 43.3 |  | 43.3 | 69.13 | 10.87 | 410886 | 410.886 | 66.26 | 13.74 | 519372 | 519.372 | 63.39 | 16.61 | 627858 | 627.858 | 60.52 | 19.48 | 736344 | 736.344 | 57.65 | 22.35 | 844830 | 844.83 | 54.78 | 25.22 | 953316 | 953.316 | 51.91 | 28.09 | 1061802 | 1061.802 | 49.04 | 30.96 | 1170288 | 1170.288 | 46.17 | 33.83 | 1278774 | 1278.774 | 43.3 | 36.7 | 1387260 | 1387.26 | 45
11/24/20XX 11:00:00 AM | 0.45833 | 4 | 44.7 | 54.1 | 44.7 |  | 44.7 | 69.27 | 10.73 | 405594 | 405.594 | 66.54 | 13.46 | 508788 | 508.788 | 63.81 | 16.19 | 611982 | 611.982 | 61.08 | 18.92 | 715176 | 715.176 | 58.35 | 21.65 | 818370 | 818.37 | 55.62 | 24.38 | 921564 | 921.564 | 52.89 | 27.11 | 1024758 | 1024.758 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.43 | 32.57 | 1231146 | 1231.146 | 44.7 | 35.3 | 1334340 | 1334.34 | 45
11/24/20XX 12:00:00 PM | 0.5 | 4 | 46.5 | 51.5 | 46.5 |  | 46.5 | 69.45 | 10.55 | 398790 | 398.79 | 66.9 | 13.1 | 495180 | 495.18 | 64.35 | 15.65 | 591570 | 591.57 | 61.8 | 18.2 | 687960 | 687.96 | 59.25 | 20.75 | 784350 | 784.35 | 56.7 | 23.3 | 880740 | 880.74 | 54.15 | 25.85 | 977130 | 977.13 | 51.6 | 28.4 | 1073520 | 1073.52 | 49.05 | 30.95 | 1169910 | 1169.91 | 46.5 | 33.5 | 1266300 | 1266.3 | 45
11/24/20XX 1:00:00 PM | 0.54167 | 4 | 47.4 | 49.9 | 47.4 |  | 47.4 | 69.54 | 10.46 | 395388 | 395.388 | 67.08 | 12.92 | 488376 | 488.376 | 64.62 | 15.38 | 581364 | 581.364 | 62.16 | 17.84 | 674352 | 674.352 | 59.7 | 20.3 | 767340 | 767.34 | 57.24 | 22.76 | 860328 | 860.328 | 54.78 | 25.22 | 953316 | 953.316 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.86 | 30.14 | 1139292 | 1139.292 | 47.4 | 32.6 | 1232280 | 1232.28 | 45
11/24/20XX 2:00:00 PM | 0.58333 | 4 | 48.2 | 48.5 | 48.2 |  | 48.2 | 69.62 | 10.38 | 392364 | 392.364 | 67.24 | 12.76 | 482328 | 482.328 | 64.86 | 15.14 | 572292 | 572.292 | 62.48 | 17.52 | 662256 | 662.256 | 60.1 | 19.9 | 752220 | 752.22 | 57.72 | 22.28 | 842184 | 842.184 | 55.34 | 24.66 | 932148 | 932.148 | 52.96 | 27.04 | 1022112 | 1022.112 | 50.58 | 29.42 | 1112076 | 1112.076 | 48.2 | 31.8 | 1202040 | 1202.04 | 50
11/24/20XX 3:00:00 PM | 0.625 | 4 | 48.1 | 49.1 | 48.1 |  | 48.1 | 69.61 | 10.39 | 392742 | 392.742 | 67.22 | 12.78 | 483084 | 483.084 | 64.83 | 15.17 | 573426 | 573.426 | 62.44 | 17.56 | 663768 | 663.768 | 60.05 | 19.95 | 754110 | 754.11 | 57.66 | 22.34 | 844452 | 844.452 | 55.27 | 24.73 | 934794 | 934.794 | 52.88 | 27.12 | 1025136 | 1025.136 | 50.49 | 29.51 | 1115478 | 1115.478 | 48.1 | 31.9 | 1205820 | 1205.82 | 50
11/24/20XX 4:00:00 PM | 0.66667 | 4 | 47.8 | 50.8 | 47.8 |  | 47.8 | 69.58 | 10.42 | 393876 | 393.876 | 67.16 | 12.84 | 485352 | 485.352 | 64.74 | 15.26 | 576828 | 576.828 | 62.32 | 17.68 | 668304 | 668.304 | 59.9 | 20.1 | 759780 | 759.78 | 57.48 | 22.52 | 851256 | 851.256 | 55.06 | 24.94 | 942732 | 942.732 | 52.64 | 27.36 | 1034208 | 1034.208 | 50.22 | 29.78 | 1125684 | 1125.684 | 47.8 | 32.2 | 1217160 | 1217.16 | 50
11/24/20XX 5:00:00 PM | 0.70833 | 4 | 47.1 | 52.8 | 47.1 |  | 47.1 | 69.51 | 10.49 | 396522 | 396.522 | 67.02 | 12.98 | 490644 | 490.644 | 64.53 | 15.47 | 584766 | 584.766 | 62.04 | 17.96 | 678888 | 678.888 | 59.55 | 20.45 | 773010 | 773.01 | 57.06 | 22.94 | 867132 | 867.132 | 54.57 | 25.43 | 961254 | 961.254 | 52.08 | 27.92 | 1055376 | 1055.376 | 49.59 | 30.41 | 1149498 | 1149.498 | 47.1 | 32.9 | 1243620 | 1243.62 | 45
11/24/20XX 6:00:00 PM | 0.75 | 4 | 46.7 | 55.5 | 46.7 |  | 46.7 | 69.47 | 10.53 | 398034 | 398.034 | 66.94 | 13.06 | 493668 | 493.668 | 64.41 | 15.59 | 589302 | 589.302 | 61.88 | 18.12 | 684936 | 684.936 | 59.35 | 20.65 | 780570 | 780.57 | 56.82 | 23.18 | 876204 | 876.204 | 54.29 | 25.71 | 971838 | 971.838 | 51.76 | 28.24 | 1067472 | 1067.472 | 49.23 | 30.77 | 1163106 | 1163.106 | 46.7 | 33.3 | 1258740 | 1258.74 | 45
11/24/20XX 7:00:00 PM | 0.79167 | 4 | 46.4 | 55.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/24/20XX 8:00:00 PM | 0.83333 | 4 | 45.9 | 56.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/24/20XX 9:00:00 PM | 0.875 | 4 | 45.6 | 58.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/24/20XX 10:00:00 PM | 0.91667 | 4 | 45.3 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/24/20XX 11:00:00 PM | 0.95833 | 4 | 44.7 | 62.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/24/20XX 12:00:00 AM | 0 | 5 | 44.4 | 61.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/25/20XX 1:00:00 AM | 0.041667 | 5 | 44 | 63 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/25/20XX 2:00:00 AM | 0.083333 | 5 | 43.9 | 63.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/25/20XX 3:00:00 AM | 0.125 | 5 | 43.7 | 63.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/25/20XX 4:00:00 AM | 0.16667 | 5 | 42.9 | 64.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/25/20XX 5:00:00 AM | 0.20833 | 5 | 42.8 | 63.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/25/20XX 6:00:00 AM | 0.25 | 5 | 42.4 | 62.5 | 42.4 |  | 42.4 | 69.04 | 10.96 | 414288 | 414.288 | 66.08 | 13.92 | 526176 | 526.176 | 63.12 | 16.88 | 638064 | 638.064 | 60.16 | 19.84 | 749952 | 749.952 | 57.2 | 22.8 | 861840 | 861.84 | 54.24 | 25.76 | 973728 | 973.728 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.32 | 31.68 | 1197504 | 1197.504 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.4 | 37.6 | 1421280 | 1421.28 | 40
11/25/20XX 7:00:00 AM | 0.29167 | 5 | 42.5 | 61.2 | 42.5 |  | 42.5 | 69.05 | 10.95 | 413910 | 413.91 | 66.1 | 13.9 | 525420 | 525.42 | 63.15 | 16.85 | 636930 | 636.93 | 60.2 | 19.8 | 748440 | 748.44 | 57.25 | 22.75 | 859950 | 859.95 | 54.3 | 25.7 | 971460 | 971.46 | 51.35 | 28.65 | 1082970 | 1082.97 | 48.4 | 31.6 | 1194480 | 1194.48 | 45.45 | 34.55 | 1305990 | 1305.99 | 42.5 | 37.5 | 1417500 | 1417.5 | 40
11/25/20XX 8:00:00 AM | 0.33333 | 5 | 42.8 | 61.4 | 42.8 |  | 42.8 | 69.08 | 10.92 | 412776 | 412.776 | 66.16 | 13.84 | 523152 | 523.152 | 63.24 | 16.76 | 633528 | 633.528 | 60.32 | 19.68 | 743904 | 743.904 | 57.4 | 22.6 | 854280 | 854.28 | 54.48 | 25.52 | 964656 | 964.656 | 51.56 | 28.44 | 1075032 | 1075.032 | 48.64 | 31.36 | 1185408 | 1185.408 | 45.72 | 34.28 | 1295784 | 1295.784 | 42.8 | 37.2 | 1406160 | 1406.16 | 45
11/25/20XX 9:00:00 AM | 0.375 | 5 | 44.3 | 58.1 | 44.3 |  | 44.3 | 69.23 | 10.77 | 407106 | 407.106 | 66.46 | 13.54 | 511812 | 511.812 | 63.69 | 16.31 | 616518 | 616.518 | 60.92 | 19.08 | 721224 | 721.224 | 58.15 | 21.85 | 825930 | 825.93 | 55.38 | 24.62 | 930636 | 930.636 | 52.61 | 27.39 | 1035342 | 1035.342 | 49.84 | 30.16 | 1140048 | 1140.048 | 47.07 | 32.93 | 1244754 | 1244.754 | 44.3 | 35.7 | 1349460 | 1349.46 | 45
11/25/20XX 10:00:00 AM | 0.41667 | 5 | 45.4 | 54.7 | 45.4 |  | 45.4 | 69.34 | 10.66 | 402948 | 402.948 | 66.68 | 13.32 | 503496 | 503.496 | 64.02 | 15.98 | 604044 | 604.044 | 61.36 | 18.64 | 704592 | 704.592 | 58.7 | 21.3 | 805140 | 805.14 | 56.04 | 23.96 | 905688 | 905.688 | 53.38 | 26.62 | 1006236 | 1006.236 | 50.72 | 29.28 | 1106784 | 1106.784 | 48.06 | 31.94 | 1207332 | 1207.332 | 45.4 | 34.6 | 1307880 | 1307.88 | 45
11/25/20XX 11:00:00 AM | 0.45833 | 5 | 46.9 | 52 | 46.9 |  | 46.9 | 69.49 | 10.51 | 397278 | 397.278 | 66.98 | 13.02 | 492156 | 492.156 | 64.47 | 15.53 | 587034 | 587.034 | 61.96 | 18.04 | 681912 | 681.912 | 59.45 | 20.55 | 776790 | 776.79 | 56.94 | 23.06 | 871668 | 871.668 | 54.43 | 25.57 | 966546 | 966.546 | 51.92 | 28.08 | 1061424 | 1061.424 | 49.41 | 30.59 | 1156302 | 1156.302 | 46.9 | 33.1 | 1251180 | 1251.18 | 45
11/25/20XX 12:00:00 PM | 0.5 | 5 | 47.9 | 50.4 | 47.9 |  | 47.9 | 69.59 | 10.41 | 393498 | 393.498 | 67.18 | 12.82 | 484596 | 484.596 | 64.77 | 15.23 | 575694 | 575.694 | 62.36 | 17.64 | 666792 | 666.792 | 59.95 | 20.05 | 757890 | 757.89 | 57.54 | 22.46 | 848988 | 848.988 | 55.13 | 24.87 | 940086 | 940.086 | 52.72 | 27.28 | 1031184 | 1031.184 | 50.31 | 29.69 | 1122282 | 1122.282 | 47.9 | 32.1 | 1213380 | 1213.38 | 50
11/25/20XX 1:00:00 PM | 0.54167 | 5 | 49 | 50.6 | 49 |  | 49 | 69.7 | 10.3 | 389340 | 389.34 | 67.4 | 12.6 | 476280 | 476.28 | 65.1 | 14.9 | 563220 | 563.22 | 62.8 | 17.2 | 650160 | 650.16 | 60.5 | 19.5 | 737100 | 737.1 | 58.2 | 21.8 | 824040 | 824.04 | 55.9 | 24.1 | 910980 | 910.98 | 53.6 | 26.4 | 997920 | 997.92 | 51.3 | 28.7 | 1084860 | 1084.86 | 49 | 31 | 1171800 | 1171.8 | 50
11/25/20XX 2:00:00 PM | 0.58333 | 5 | 48.8 | 53 | 48.8 |  | 48.8 | 69.68 | 10.32 | 390096 | 390.096 | 67.36 | 12.64 | 477792 | 477.792 | 65.04 | 14.96 | 565488 | 565.488 | 62.72 | 17.28 | 653184 | 653.184 | 60.4 | 19.6 | 740880 | 740.88 | 58.08 | 21.92 | 828576 | 828.576 | 55.76 | 24.24 | 916272 | 916.272 | 53.44 | 26.56 | 1003968 | 1003.968 | 51.12 | 28.88 | 1091664 | 1091.664 | 48.8 | 31.2 | 1179360 | 1179.36 | 50
11/25/20XX 3:00:00 PM | 0.625 | 5 | 49.2 | 54.3 | 49.2 |  | 49.2 | 69.72 | 10.28 | 388584 | 388.584 | 67.44 | 12.56 | 474768 | 474.768 | 65.16 | 14.84 | 560952 | 560.952 | 62.88 | 17.12 | 647136 | 647.136 | 60.6 | 19.4 | 733320 | 733.32 | 58.32 | 21.68 | 819504 | 819.504 | 56.04 | 23.96 | 905688 | 905.688 | 53.76 | 26.24 | 991872 | 991.872 | 51.48 | 28.52 | 1078056 | 1078.056 | 49.2 | 30.8 | 1164240 | 1164.24 | 50
11/25/20XX 4:00:00 PM | 0.66667 | 5 | 48.8 | 55.9 | 48.8 |  | 48.8 | 69.68 | 10.32 | 390096 | 390.096 | 67.36 | 12.64 | 477792 | 477.792 | 65.04 | 14.96 | 565488 | 565.488 | 62.72 | 17.28 | 653184 | 653.184 | 60.4 | 19.6 | 740880 | 740.88 | 58.08 | 21.92 | 828576 | 828.576 | 55.76 | 24.24 | 916272 | 916.272 | 53.44 | 26.56 | 1003968 | 1003.968 | 51.12 | 28.88 | 1091664 | 1091.664 | 48.8 | 31.2 | 1179360 | 1179.36 | 50
11/25/20XX 5:00:00 PM | 0.70833 | 5 | 47.9 | 59 | 47.9 |  | 47.9 | 69.59 | 10.41 | 393498 | 393.498 | 67.18 | 12.82 | 484596 | 484.596 | 64.77 | 15.23 | 575694 | 575.694 | 62.36 | 17.64 | 666792 | 666.792 | 59.95 | 20.05 | 757890 | 757.89 | 57.54 | 22.46 | 848988 | 848.988 | 55.13 | 24.87 | 940086 | 940.086 | 52.72 | 27.28 | 1031184 | 1031.184 | 50.31 | 29.69 | 1122282 | 1122.282 | 47.9 | 32.1 | 1213380 | 1213.38 | 50
11/25/20XX 6:00:00 PM | 0.75 | 5 | 47.5 | 60.9 | 47.5 |  | 47.5 | 69.55 | 10.45 | 395010 | 395.01 | 67.1 | 12.9 | 487620 | 487.62 | 64.65 | 15.35 | 580230 | 580.23 | 62.2 | 17.8 | 672840 | 672.84 | 59.75 | 20.25 | 765450 | 765.45 | 57.3 | 22.7 | 858060 | 858.06 | 54.85 | 25.15 | 950670 | 950.67 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.95 | 30.05 | 1135890 | 1135.89 | 47.5 | 32.5 | 1228500 | 1228.5 | 45
11/25/20XX 7:00:00 PM | 0.79167 | 5 | 47.6 | 59.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/25/20XX 8:00:00 PM | 0.83333 | 5 | 47.3 | 58.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/25/20XX 9:00:00 PM | 0.875 | 5 | 46.9 | 60.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/25/20XX 10:00:00 PM | 0.91667 | 5 | 47.1 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/25/20XX 11:00:00 PM | 0.95833 | 5 | 47 | 60.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/25/20XX 12:00:00 AM | 0 | 6 | 46.4 | 62.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/26/20XX 1:00:00 AM | 0.041667 | 6 | 46 | 62.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/26/20XX 2:00:00 AM | 0.083333 | 6 | 45.9 | 63 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/26/20XX 3:00:00 AM | 0.125 | 6 | 45.7 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/26/20XX 4:00:00 AM | 0.16667 | 6 | 45.5 | 64.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/26/20XX 5:00:00 AM | 0.20833 | 6 | 45.6 | 66.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/26/20XX 6:00:00 AM | 0.25 | 6 | 45.4 | 67.3 | 45.4 |  | 45.4 | 69.34 | 10.66 | 402948 | 402.948 | 66.68 | 13.32 | 503496 | 503.496 | 64.02 | 15.98 | 604044 | 604.044 | 61.36 | 18.64 | 704592 | 704.592 | 58.7 | 21.3 | 805140 | 805.14 | 56.04 | 23.96 | 905688 | 905.688 | 53.38 | 26.62 | 1006236 | 1006.236 | 50.72 | 29.28 | 1106784 | 1106.784 | 48.06 | 31.94 | 1207332 | 1207.332 | 45.4 | 34.6 | 1307880 | 1307.88 | 45
11/26/20XX 7:00:00 AM | 0.29167 | 6 | 44.7 | 68.4 | 44.7 |  | 44.7 | 69.27 | 10.73 | 405594 | 405.594 | 66.54 | 13.46 | 508788 | 508.788 | 63.81 | 16.19 | 611982 | 611.982 | 61.08 | 18.92 | 715176 | 715.176 | 58.35 | 21.65 | 818370 | 818.37 | 55.62 | 24.38 | 921564 | 921.564 | 52.89 | 27.11 | 1024758 | 1024.758 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.43 | 32.57 | 1231146 | 1231.146 | 44.7 | 35.3 | 1334340 | 1334.34 | 45
11/26/20XX 8:00:00 AM | 0.33333 | 6 | 45 | 68.6 | 45 |  | 45 | 69.3 | 10.7 | 404460 | 404.46 | 66.6 | 13.4 | 506520 | 506.52 | 63.9 | 16.1 | 608580 | 608.58 | 61.2 | 18.8 | 710640 | 710.64 | 58.5 | 21.5 | 812700 | 812.7 | 55.8 | 24.2 | 914760 | 914.76 | 53.1 | 26.9 | 1016820 | 1016.82 | 50.4 | 29.6 | 1118880 | 1118.88 | 47.7 | 32.3 | 1220940 | 1220.94 | 45 | 35 | 1323000 | 1323 | 45
11/26/20XX 9:00:00 AM | 0.375 | 6 | 45.9 | 67.9 | 45.9 |  | 45.9 | 69.39 | 10.61 | 401058 | 401.058 | 66.78 | 13.22 | 499716 | 499.716 | 64.17 | 15.83 | 598374 | 598.374 | 61.56 | 18.44 | 697032 | 697.032 | 58.95 | 21.05 | 795690 | 795.69 | 56.34 | 23.66 | 894348 | 894.348 | 53.73 | 26.27 | 993006 | 993.006 | 51.12 | 28.88 | 1091664 | 1091.664 | 48.51 | 31.49 | 1190322 | 1190.322 | 45.9 | 34.1 | 1288980 | 1288.98 | 45
11/26/20XX 10:00:00 AM | 0.41667 | 6 | 46.6 | 65.6 | 46.6 |  | 46.6 | 69.46 | 10.54 | 398412 | 398.412 | 66.92 | 13.08 | 494424 | 494.424 | 64.38 | 15.62 | 590436 | 590.436 | 61.84 | 18.16 | 686448 | 686.448 | 59.3 | 20.7 | 782460 | 782.46 | 56.76 | 23.24 | 878472 | 878.472 | 54.22 | 25.78 | 974484 | 974.484 | 51.68 | 28.32 | 1070496 | 1070.496 | 49.14 | 30.86 | 1166508 | 1166.508 | 46.6 | 33.4 | 1262520 | 1262.52 | 45
11/26/20XX 11:00:00 AM | 0.45833 | 6 | 48.2 | 59.4 | 48.2 |  | 48.2 | 69.62 | 10.38 | 392364 | 392.364 | 67.24 | 12.76 | 482328 | 482.328 | 64.86 | 15.14 | 572292 | 572.292 | 62.48 | 17.52 | 662256 | 662.256 | 60.1 | 19.9 | 752220 | 752.22 | 57.72 | 22.28 | 842184 | 842.184 | 55.34 | 24.66 | 932148 | 932.148 | 52.96 | 27.04 | 1022112 | 1022.112 | 50.58 | 29.42 | 1112076 | 1112.076 | 48.2 | 31.8 | 1202040 | 1202.04 | 50
11/26/20XX 12:00:00 PM | 0.5 | 6 | 49 | 56.7 | 49 |  | 49 | 69.7 | 10.3 | 389340 | 389.34 | 67.4 | 12.6 | 476280 | 476.28 | 65.1 | 14.9 | 563220 | 563.22 | 62.8 | 17.2 | 650160 | 650.16 | 60.5 | 19.5 | 737100 | 737.1 | 58.2 | 21.8 | 824040 | 824.04 | 55.9 | 24.1 | 910980 | 910.98 | 53.6 | 26.4 | 997920 | 997.92 | 51.3 | 28.7 | 1084860 | 1084.86 | 49 | 31 | 1171800 | 1171.8 | 50
11/26/20XX 1:00:00 PM | 0.54167 | 6 | 49.7 | 55 | 49.7 |  | 49.7 | 69.77 | 10.23 | 386694 | 386.694 | 67.54 | 12.46 | 470988 | 470.988 | 65.31 | 14.69 | 555282 | 555.282 | 63.08 | 16.92 | 639576 | 639.576 | 60.85 | 19.15 | 723870 | 723.87 | 58.62 | 21.38 | 808164 | 808.164 | 56.39 | 23.61 | 892458 | 892.458 | 54.16 | 25.84 | 976752 | 976.752 | 51.93 | 28.07 | 1061046 | 1061.046 | 49.7 | 30.3 | 1145340 | 1145.34 | 50
11/26/20XX 2:00:00 PM | 0.58333 | 6 | 49.9 | 56 | 49.9 |  | 49.9 | 69.79 | 10.21 | 385938 | 385.938 | 67.58 | 12.42 | 469476 | 469.476 | 65.37 | 14.63 | 553014 | 553.014 | 63.16 | 16.84 | 636552 | 636.552 | 60.95 | 19.05 | 720090 | 720.09 | 58.74 | 21.26 | 803628 | 803.628 | 56.53 | 23.47 | 887166 | 887.166 | 54.32 | 25.68 | 970704 | 970.704 | 52.11 | 27.89 | 1054242 | 1054.242 | 49.9 | 30.1 | 1137780 | 1137.78 | 50
11/26/20XX 3:00:00 PM | 0.625 | 6 | 49.4 | 58.4 | 49.4 |  | 49.4 | 69.74 | 10.26 | 387828 | 387.828 | 67.48 | 12.52 | 473256 | 473.256 | 65.22 | 14.78 | 558684 | 558.684 | 62.96 | 17.04 | 644112 | 644.112 | 60.7 | 19.3 | 729540 | 729.54 | 58.44 | 21.56 | 814968 | 814.968 | 56.18 | 23.82 | 900396 | 900.396 | 53.92 | 26.08 | 985824 | 985.824 | 51.66 | 28.34 | 1071252 | 1071.252 | 49.4 | 30.6 | 1156680 | 1156.68 | 50
11/26/20XX 4:00:00 PM | 0.66667 | 6 | 48.5 | 59.7 | 48.5 |  | 48.5 | 69.65 | 10.35 | 391230 | 391.23 | 67.3 | 12.7 | 480060 | 480.06 | 64.95 | 15.05 | 568890 | 568.89 | 62.6 | 17.4 | 657720 | 657.72 | 60.25 | 19.75 | 746550 | 746.55 | 57.9 | 22.1 | 835380 | 835.38 | 55.55 | 24.45 | 924210 | 924.21 | 53.2 | 26.8 | 1013040 | 1013.04 | 50.85 | 29.15 | 1101870 | 1101.87 | 48.5 | 31.5 | 1190700 | 1190.7 | 50
11/26/20XX 5:00:00 PM | 0.70833 | 6 | 47.3 | 63.5 | 47.3 |  | 47.3 | 69.53 | 10.47 | 395766 | 395.766 | 67.06 | 12.94 | 489132 | 489.132 | 64.59 | 15.41 | 582498 | 582.498 | 62.12 | 17.88 | 675864 | 675.864 | 59.65 | 20.35 | 769230 | 769.23 | 57.18 | 22.82 | 862596 | 862.596 | 54.71 | 25.29 | 955962 | 955.962 | 52.24 | 27.76 | 1049328 | 1049.328 | 49.77 | 30.23 | 1142694 | 1142.694 | 47.3 | 32.7 | 1236060 | 1236.06 | 45
11/26/20XX 6:00:00 PM | 0.75 | 6 | 46.8 | 64.8 | 46.8 |  | 46.8 | 69.48 | 10.52 | 397656 | 397.656 | 66.96 | 13.04 | 492912 | 492.912 | 64.44 | 15.56 | 588168 | 588.168 | 61.92 | 18.08 | 683424 | 683.424 | 59.4 | 20.6 | 778680 | 778.68 | 56.88 | 23.12 | 873936 | 873.936 | 54.36 | 25.64 | 969192 | 969.192 | 51.84 | 28.16 | 1064448 | 1064.448 | 49.32 | 30.68 | 1159704 | 1159.704 | 46.8 | 33.2 | 1254960 | 1254.96 | 45
11/26/20XX 7:00:00 PM | 0.79167 | 6 | 46.1 | 66.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/26/20XX 8:00:00 PM | 0.83333 | 6 | 46 | 67 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/26/20XX 9:00:00 PM | 0.875 | 6 | 45.5 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/26/20XX 10:00:00 PM | 0.91667 | 6 | 45.2 | 68.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/26/20XX 11:00:00 PM | 0.95833 | 6 | 45.1 | 68.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/26/20XX 12:00:00 AM | 0 | 7 | 44.8 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/27/20XX 1:00:00 AM | 0.041667 | 7 | 44.8 | 69.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/27/20XX 2:00:00 AM | 0.083333 | 7 | 44.8 | 70.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/27/20XX 3:00:00 AM | 0.125 | 7 | 44.5 | 71 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/27/20XX 4:00:00 AM | 0.16667 | 7 | 44.5 | 70.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/27/20XX 5:00:00 AM | 0.20833 | 7 | 43.9 | 72.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/27/20XX 6:00:00 AM | 0.25 | 7 | 44.3 | 70.5 | 44.3 |  | 44.3 | 69.23 | 10.77 | 407106 | 407.106 | 66.46 | 13.54 | 511812 | 511.812 | 63.69 | 16.31 | 616518 | 616.518 | 60.92 | 19.08 | 721224 | 721.224 | 58.15 | 21.85 | 825930 | 825.93 | 55.38 | 24.62 | 930636 | 930.636 | 52.61 | 27.39 | 1035342 | 1035.342 | 49.84 | 30.16 | 1140048 | 1140.048 | 47.07 | 32.93 | 1244754 | 1244.754 | 44.3 | 35.7 | 1349460 | 1349.46 | 45
11/27/20XX 7:00:00 AM | 0.29167 | 7 | 44 | 71.6 | 44 |  | 44 | 69.2 | 10.8 | 408240 | 408.24 | 66.4 | 13.6 | 514080 | 514.08 | 63.6 | 16.4 | 619920 | 619.92 | 60.8 | 19.2 | 725760 | 725.76 | 58 | 22 | 831600 | 831.6 | 55.2 | 24.8 | 937440 | 937.44 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.6 | 30.4 | 1149120 | 1149.12 | 46.8 | 33.2 | 1254960 | 1254.96 | 44 | 36 | 1360800 | 1360.8 | 45
11/27/20XX 8:00:00 AM | 0.33333 | 7 | 44.4 | 70.9 | 44.4 |  | 44.4 | 69.24 | 10.76 | 406728 | 406.728 | 66.48 | 13.52 | 511056 | 511.056 | 63.72 | 16.28 | 615384 | 615.384 | 60.96 | 19.04 | 719712 | 719.712 | 58.2 | 21.8 | 824040 | 824.04 | 55.44 | 24.56 | 928368 | 928.368 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.92 | 30.08 | 1137024 | 1137.024 | 47.16 | 32.84 | 1241352 | 1241.352 | 44.4 | 35.6 | 1345680 | 1345.68 | 45
11/27/20XX 9:00:00 AM | 0.375 | 7 | 45 | 71.6 | 45 |  | 45 | 69.3 | 10.7 | 404460 | 404.46 | 66.6 | 13.4 | 506520 | 506.52 | 63.9 | 16.1 | 608580 | 608.58 | 61.2 | 18.8 | 710640 | 710.64 | 58.5 | 21.5 | 812700 | 812.7 | 55.8 | 24.2 | 914760 | 914.76 | 53.1 | 26.9 | 1016820 | 1016.82 | 50.4 | 29.6 | 1118880 | 1118.88 | 47.7 | 32.3 | 1220940 | 1220.94 | 45 | 35 | 1323000 | 1323 | 45
11/27/20XX 10:00:00 AM | 0.41667 | 7 | 45.4 | 68.3 | 45.4 |  | 45.4 | 69.34 | 10.66 | 402948 | 402.948 | 66.68 | 13.32 | 503496 | 503.496 | 64.02 | 15.98 | 604044 | 604.044 | 61.36 | 18.64 | 704592 | 704.592 | 58.7 | 21.3 | 805140 | 805.14 | 56.04 | 23.96 | 905688 | 905.688 | 53.38 | 26.62 | 1006236 | 1006.236 | 50.72 | 29.28 | 1106784 | 1106.784 | 48.06 | 31.94 | 1207332 | 1207.332 | 45.4 | 34.6 | 1307880 | 1307.88 | 45
11/27/20XX 11:00:00 AM | 0.45833 | 7 | 46.1 | 65.8 | 46.1 |  | 46.1 | 69.41 | 10.59 | 400302 | 400.302 | 66.82 | 13.18 | 498204 | 498.204 | 64.23 | 15.77 | 596106 | 596.106 | 61.64 | 18.36 | 694008 | 694.008 | 59.05 | 20.95 | 791910 | 791.91 | 56.46 | 23.54 | 889812 | 889.812 | 53.87 | 26.13 | 987714 | 987.714 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.69 | 31.31 | 1183518 | 1183.518 | 46.1 | 33.9 | 1281420 | 1281.42 | 45
11/27/20XX 12:00:00 PM | 0.5 | 7 | 46.4 | 63.5 | 46.4 |  | 46.4 | 69.44 | 10.56 | 399168 | 399.168 | 66.88 | 13.12 | 495936 | 495.936 | 64.32 | 15.68 | 592704 | 592.704 | 61.76 | 18.24 | 689472 | 689.472 | 59.2 | 20.8 | 786240 | 786.24 | 56.64 | 23.36 | 883008 | 883.008 | 54.08 | 25.92 | 979776 | 979.776 | 51.52 | 28.48 | 1076544 | 1076.544 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.4 | 33.6 | 1270080 | 1270.08 | 45
11/27/20XX 1:00:00 PM | 0.54167 | 7 | 46.7 | 61.8 | 46.7 |  | 46.7 | 69.47 | 10.53 | 398034 | 398.034 | 66.94 | 13.06 | 493668 | 493.668 | 64.41 | 15.59 | 589302 | 589.302 | 61.88 | 18.12 | 684936 | 684.936 | 59.35 | 20.65 | 780570 | 780.57 | 56.82 | 23.18 | 876204 | 876.204 | 54.29 | 25.71 | 971838 | 971.838 | 51.76 | 28.24 | 1067472 | 1067.472 | 49.23 | 30.77 | 1163106 | 1163.106 | 46.7 | 33.3 | 1258740 | 1258.74 | 45
11/27/20XX 2:00:00 PM | 0.58333 | 7 | 47.1 | 60.3 | 47.1 |  | 47.1 | 69.51 | 10.49 | 396522 | 396.522 | 67.02 | 12.98 | 490644 | 490.644 | 64.53 | 15.47 | 584766 | 584.766 | 62.04 | 17.96 | 678888 | 678.888 | 59.55 | 20.45 | 773010 | 773.01 | 57.06 | 22.94 | 867132 | 867.132 | 54.57 | 25.43 | 961254 | 961.254 | 52.08 | 27.92 | 1055376 | 1055.376 | 49.59 | 30.41 | 1149498 | 1149.498 | 47.1 | 32.9 | 1243620 | 1243.62 | 45
11/27/20XX 3:00:00 PM | 0.625 | 7 | 46.9 | 59 | 46.9 |  | 46.9 | 69.49 | 10.51 | 397278 | 397.278 | 66.98 | 13.02 | 492156 | 492.156 | 64.47 | 15.53 | 587034 | 587.034 | 61.96 | 18.04 | 681912 | 681.912 | 59.45 | 20.55 | 776790 | 776.79 | 56.94 | 23.06 | 871668 | 871.668 | 54.43 | 25.57 | 966546 | 966.546 | 51.92 | 28.08 | 1061424 | 1061.424 | 49.41 | 30.59 | 1156302 | 1156.302 | 46.9 | 33.1 | 1251180 | 1251.18 | 45
11/27/20XX 4:00:00 PM | 0.66667 | 7 | 46.1 | 59.7 | 46.1 |  | 46.1 | 69.41 | 10.59 | 400302 | 400.302 | 66.82 | 13.18 | 498204 | 498.204 | 64.23 | 15.77 | 596106 | 596.106 | 61.64 | 18.36 | 694008 | 694.008 | 59.05 | 20.95 | 791910 | 791.91 | 56.46 | 23.54 | 889812 | 889.812 | 53.87 | 26.13 | 987714 | 987.714 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.69 | 31.31 | 1183518 | 1183.518 | 46.1 | 33.9 | 1281420 | 1281.42 | 45
11/27/20XX 5:00:00 PM | 0.70833 | 7 | 45.4 | 61.5 | 45.4 |  | 45.4 | 69.34 | 10.66 | 402948 | 402.948 | 66.68 | 13.32 | 503496 | 503.496 | 64.02 | 15.98 | 604044 | 604.044 | 61.36 | 18.64 | 704592 | 704.592 | 58.7 | 21.3 | 805140 | 805.14 | 56.04 | 23.96 | 905688 | 905.688 | 53.38 | 26.62 | 1006236 | 1006.236 | 50.72 | 29.28 | 1106784 | 1106.784 | 48.06 | 31.94 | 1207332 | 1207.332 | 45.4 | 34.6 | 1307880 | 1307.88 | 45
11/27/20XX 6:00:00 PM | 0.75 | 7 | 45.3 | 59.9 | 45.3 |  | 45.3 | 69.33 | 10.67 | 403326 | 403.326 | 66.66 | 13.34 | 504252 | 504.252 | 63.99 | 16.01 | 605178 | 605.178 | 61.32 | 18.68 | 706104 | 706.104 | 58.65 | 21.35 | 807030 | 807.03 | 55.98 | 24.02 | 907956 | 907.956 | 53.31 | 26.69 | 1008882 | 1008.882 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.97 | 32.03 | 1210734 | 1210.734 | 45.3 | 34.7 | 1311660 | 1311.66 | 45
11/27/20XX 7:00:00 PM | 0.79167 | 7 | 44.8 | 60.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/27/20XX 8:00:00 PM | 0.83333 | 7 | 44.7 | 59.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/27/20XX 9:00:00 PM | 0.875 | 7 | 43.7 | 60.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/27/20XX 10:00:00 PM | 0.91667 | 7 | 43.2 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/27/20XX 11:00:00 PM | 0.95833 | 7 | 43.1 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/27/20XX 12:00:00 AM | 0 | 1 | 42.1 | 60.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/28/20XX 1:00:00 AM | 0.041667 | 1 | 41.8 | 62 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/28/20XX 2:00:00 AM | 0.083333 | 1 | 41.2 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/28/20XX 3:00:00 AM | 0.125 | 1 | 40.8 | 62.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/28/20XX 4:00:00 AM | 0.16667 | 1 | 40.9 | 63.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/28/20XX 5:00:00 AM | 0.20833 | 1 | 40.7 | 63.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/28/20XX 6:00:00 AM | 0.25 | 1 | 40.3 | 65.8 | 40.3 |  | 40.3 | 68.83 | 11.17 | 422226 | 422.226 | 65.66 | 14.34 | 542052 | 542.052 | 62.49 | 17.51 | 661878 | 661.878 | 59.32 | 20.68 | 781704 | 781.704 | 56.15 | 23.85 | 901530 | 901.53 | 52.98 | 27.02 | 1021356 | 1021.356 | 49.81 | 30.19 | 1141182 | 1141.182 | 46.64 | 33.36 | 1261008 | 1261.008 | 43.47 | 36.53 | 1380834 | 1380.834 | 40.3 | 39.7 | 1500660 | 1500.66 | 40
11/28/20XX 7:00:00 AM | 0.29167 | 1 | 40.1 | 65.7 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
11/28/20XX 8:00:00 AM | 0.33333 | 1 | 41 | 62.4 | 41 |  | 41 | 68.9 | 11.1 | 419580 | 419.58 | 65.8 | 14.2 | 536760 | 536.76 | 62.7 | 17.3 | 653940 | 653.94 | 59.6 | 20.4 | 771120 | 771.12 | 56.5 | 23.5 | 888300 | 888.3 | 53.4 | 26.6 | 1005480 | 1005.48 | 50.3 | 29.7 | 1122660 | 1122.66 | 47.2 | 32.8 | 1239840 | 1239.84 | 44.1 | 35.9 | 1357020 | 1357.02 | 41 | 39 | 1474200 | 1474.2 | 40
11/28/20XX 9:00:00 AM | 0.375 | 1 | 42.7 | 58.4 | 42.7 |  | 42.7 | 69.07 | 10.93 | 413154 | 413.154 | 66.14 | 13.86 | 523908 | 523.908 | 63.21 | 16.79 | 634662 | 634.662 | 60.28 | 19.72 | 745416 | 745.416 | 57.35 | 22.65 | 856170 | 856.17 | 54.42 | 25.58 | 966924 | 966.924 | 51.49 | 28.51 | 1077678 | 1077.678 | 48.56 | 31.44 | 1188432 | 1188.432 | 45.63 | 34.37 | 1299186 | 1299.186 | 42.7 | 37.3 | 1409940 | 1409.94 | 45
11/28/20XX 10:00:00 AM | 0.41667 | 1 | 43.8 | 55.6 | 43.8 |  | 43.8 | 69.18 | 10.82 | 408996 | 408.996 | 66.36 | 13.64 | 515592 | 515.592 | 63.54 | 16.46 | 622188 | 622.188 | 60.72 | 19.28 | 728784 | 728.784 | 57.9 | 22.1 | 835380 | 835.38 | 55.08 | 24.92 | 941976 | 941.976 | 52.26 | 27.74 | 1048572 | 1048.572 | 49.44 | 30.56 | 1155168 | 1155.168 | 46.62 | 33.38 | 1261764 | 1261.764 | 43.8 | 36.2 | 1368360 | 1368.36 | 45
11/28/20XX 11:00:00 AM | 0.45833 | 1 | 45.5 | 52.3 | 45.5 |  | 45.5 | 69.35 | 10.65 | 402570 | 402.57 | 66.7 | 13.3 | 502740 | 502.74 | 64.05 | 15.95 | 602910 | 602.91 | 61.4 | 18.6 | 703080 | 703.08 | 58.75 | 21.25 | 803250 | 803.25 | 56.1 | 23.9 | 903420 | 903.42 | 53.45 | 26.55 | 1003590 | 1003.59 | 50.8 | 29.2 | 1103760 | 1103.76 | 48.15 | 31.85 | 1203930 | 1203.93 | 45.5 | 34.5 | 1304100 | 1304.1 | 45
11/28/20XX 12:00:00 PM | 0.5 | 1 | 46.9 | 49.7 | 46.9 |  | 46.9 | 69.49 | 10.51 | 397278 | 397.278 | 66.98 | 13.02 | 492156 | 492.156 | 64.47 | 15.53 | 587034 | 587.034 | 61.96 | 18.04 | 681912 | 681.912 | 59.45 | 20.55 | 776790 | 776.79 | 56.94 | 23.06 | 871668 | 871.668 | 54.43 | 25.57 | 966546 | 966.546 | 51.92 | 28.08 | 1061424 | 1061.424 | 49.41 | 30.59 | 1156302 | 1156.302 | 46.9 | 33.1 | 1251180 | 1251.18 | 45
11/28/20XX 1:00:00 PM | 0.54167 | 1 | 47.5 | 48.6 | 47.5 |  | 47.5 | 69.55 | 10.45 | 395010 | 395.01 | 67.1 | 12.9 | 487620 | 487.62 | 64.65 | 15.35 | 580230 | 580.23 | 62.2 | 17.8 | 672840 | 672.84 | 59.75 | 20.25 | 765450 | 765.45 | 57.3 | 22.7 | 858060 | 858.06 | 54.85 | 25.15 | 950670 | 950.67 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.95 | 30.05 | 1135890 | 1135.89 | 47.5 | 32.5 | 1228500 | 1228.5 | 45
11/28/20XX 2:00:00 PM | 0.58333 | 1 | 47.4 | 47.8 | 47.4 |  | 47.4 | 69.54 | 10.46 | 395388 | 395.388 | 67.08 | 12.92 | 488376 | 488.376 | 64.62 | 15.38 | 581364 | 581.364 | 62.16 | 17.84 | 674352 | 674.352 | 59.7 | 20.3 | 767340 | 767.34 | 57.24 | 22.76 | 860328 | 860.328 | 54.78 | 25.22 | 953316 | 953.316 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.86 | 30.14 | 1139292 | 1139.292 | 47.4 | 32.6 | 1232280 | 1232.28 | 45
11/28/20XX 3:00:00 PM | 0.625 | 1 | 47 | 49.9 | 47 |  | 47 | 69.5 | 10.5 | 396900 | 396.9 | 67 | 13 | 491400 | 491.4 | 64.5 | 15.5 | 585900 | 585.9 | 62 | 18 | 680400 | 680.4 | 59.5 | 20.5 | 774900 | 774.9 | 57 | 23 | 869400 | 869.4 | 54.5 | 25.5 | 963900 | 963.9 | 52 | 28 | 1058400 | 1058.4 | 49.5 | 30.5 | 1152900 | 1152.9 | 47 | 33 | 1247400 | 1247.4 | 45
11/28/20XX 4:00:00 PM | 0.66667 | 1 | 45.8 | 52.7 | 45.8 |  | 45.8 | 69.38 | 10.62 | 401436 | 401.436 | 66.76 | 13.24 | 500472 | 500.472 | 64.14 | 15.86 | 599508 | 599.508 | 61.52 | 18.48 | 698544 | 698.544 | 58.9 | 21.1 | 797580 | 797.58 | 56.28 | 23.72 | 896616 | 896.616 | 53.66 | 26.34 | 995652 | 995.652 | 51.04 | 28.96 | 1094688 | 1094.688 | 48.42 | 31.58 | 1193724 | 1193.724 | 45.8 | 34.2 | 1292760 | 1292.76 | 45
11/28/20XX 5:00:00 PM | 0.70833 | 1 | 44.6 | 55.1 | 44.6 |  | 44.6 | 69.26 | 10.74 | 405972 | 405.972 | 66.52 | 13.48 | 509544 | 509.544 | 63.78 | 16.22 | 613116 | 613.116 | 61.04 | 18.96 | 716688 | 716.688 | 58.3 | 21.7 | 820260 | 820.26 | 55.56 | 24.44 | 923832 | 923.832 | 52.82 | 27.18 | 1027404 | 1027.404 | 50.08 | 29.92 | 1130976 | 1130.976 | 47.34 | 32.66 | 1234548 | 1234.548 | 44.6 | 35.4 | 1338120 | 1338.12 | 45
11/28/20XX 6:00:00 PM | 0.75 | 1 | 44.3 | 57.4 | 44.3 |  | 44.3 | 69.23 | 10.77 | 407106 | 407.106 | 66.46 | 13.54 | 511812 | 511.812 | 63.69 | 16.31 | 616518 | 616.518 | 60.92 | 19.08 | 721224 | 721.224 | 58.15 | 21.85 | 825930 | 825.93 | 55.38 | 24.62 | 930636 | 930.636 | 52.61 | 27.39 | 1035342 | 1035.342 | 49.84 | 30.16 | 1140048 | 1140.048 | 47.07 | 32.93 | 1244754 | 1244.754 | 44.3 | 35.7 | 1349460 | 1349.46 | 45
11/28/20XX 7:00:00 PM | 0.79167 | 1 | 44.3 | 56.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/28/20XX 8:00:00 PM | 0.83333 | 1 | 43.4 | 56.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/28/20XX 9:00:00 PM | 0.875 | 1 | 43.4 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/28/20XX 10:00:00 PM | 0.91667 | 1 | 42.9 | 60.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/28/20XX 11:00:00 PM | 0.95833 | 1 | 42.5 | 61.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/28/20XX 12:00:00 AM | 0 | 2 | 42.3 | 62.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/29/20XX 1:00:00 AM | 0.041667 | 2 | 42 | 64.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/29/20XX 2:00:00 AM | 0.083333 | 2 | 41.7 | 65.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/29/20XX 3:00:00 AM | 0.125 | 2 | 41.5 | 66.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/29/20XX 4:00:00 AM | 0.16667 | 2 | 41.3 | 66 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/29/20XX 5:00:00 AM | 0.20833 | 2 | 41 | 66.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/29/20XX 6:00:00 AM | 0.25 | 2 | 41 | 66.9 | 41 |  | 41 | 68.9 | 11.1 | 419580 | 419.58 | 65.8 | 14.2 | 536760 | 536.76 | 62.7 | 17.3 | 653940 | 653.94 | 59.6 | 20.4 | 771120 | 771.12 | 56.5 | 23.5 | 888300 | 888.3 | 53.4 | 26.6 | 1005480 | 1005.48 | 50.3 | 29.7 | 1122660 | 1122.66 | 47.2 | 32.8 | 1239840 | 1239.84 | 44.1 | 35.9 | 1357020 | 1357.02 | 41 | 39 | 1474200 | 1474.2 | 40
11/29/20XX 7:00:00 AM | 0.29167 | 2 | 41.1 | 67.7 | 41.1 |  | 41.1 | 68.91 | 11.09 | 419202 | 419.202 | 65.82 | 14.18 | 536004 | 536.004 | 62.73 | 17.27 | 652806 | 652.806 | 59.64 | 20.36 | 769608 | 769.608 | 56.55 | 23.45 | 886410 | 886.41 | 53.46 | 26.54 | 1003212 | 1003.212 | 50.37 | 29.63 | 1120014 | 1120.014 | 47.28 | 32.72 | 1236816 | 1236.816 | 44.19 | 35.81 | 1353618 | 1353.618 | 41.1 | 38.9 | 1470420 | 1470.42 | 40
11/29/20XX 8:00:00 AM | 0.33333 | 2 | 41.8 | 65.6 | 41.8 |  | 41.8 | 68.98 | 11.02 | 416556 | 416.556 | 65.96 | 14.04 | 530712 | 530.712 | 62.94 | 17.06 | 644868 | 644.868 | 59.92 | 20.08 | 759024 | 759.024 | 56.9 | 23.1 | 873180 | 873.18 | 53.88 | 26.12 | 987336 | 987.336 | 50.86 | 29.14 | 1101492 | 1101.492 | 47.84 | 32.16 | 1215648 | 1215.648 | 44.82 | 35.18 | 1329804 | 1329.804 | 41.8 | 38.2 | 1443960 | 1443.96 | 40
11/29/20XX 9:00:00 AM | 0.375 | 2 | 43.4 | 63 | 43.4 |  | 43.4 | 69.14 | 10.86 | 410508 | 410.508 | 66.28 | 13.72 | 518616 | 518.616 | 63.42 | 16.58 | 626724 | 626.724 | 60.56 | 19.44 | 734832 | 734.832 | 57.7 | 22.3 | 842940 | 842.94 | 54.84 | 25.16 | 951048 | 951.048 | 51.98 | 28.02 | 1059156 | 1059.156 | 49.12 | 30.88 | 1167264 | 1167.264 | 46.26 | 33.74 | 1275372 | 1275.372 | 43.4 | 36.6 | 1383480 | 1383.48 | 45
11/29/20XX 10:00:00 AM | 0.41667 | 2 | 44.4 | 61.3 | 44.4 |  | 44.4 | 69.24 | 10.76 | 406728 | 406.728 | 66.48 | 13.52 | 511056 | 511.056 | 63.72 | 16.28 | 615384 | 615.384 | 60.96 | 19.04 | 719712 | 719.712 | 58.2 | 21.8 | 824040 | 824.04 | 55.44 | 24.56 | 928368 | 928.368 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.92 | 30.08 | 1137024 | 1137.024 | 47.16 | 32.84 | 1241352 | 1241.352 | 44.4 | 35.6 | 1345680 | 1345.68 | 45
11/29/20XX 11:00:00 AM | 0.45833 | 2 | 46 | 57.6 | 46 |  | 46 | 69.4 | 10.6 | 400680 | 400.68 | 66.8 | 13.2 | 498960 | 498.96 | 64.2 | 15.8 | 597240 | 597.24 | 61.6 | 18.4 | 695520 | 695.52 | 59 | 21 | 793800 | 793.8 | 56.4 | 23.6 | 892080 | 892.08 | 53.8 | 26.2 | 990360 | 990.36 | 51.2 | 28.8 | 1088640 | 1088.64 | 48.6 | 31.4 | 1186920 | 1186.92 | 46 | 34 | 1285200 | 1285.2 | 45
11/29/20XX 12:00:00 PM | 0.5 | 2 | 47.6 | 54 | 47.6 |  | 47.6 | 69.56 | 10.44 | 394632 | 394.632 | 67.12 | 12.88 | 486864 | 486.864 | 64.68 | 15.32 | 579096 | 579.096 | 62.24 | 17.76 | 671328 | 671.328 | 59.8 | 20.2 | 763560 | 763.56 | 57.36 | 22.64 | 855792 | 855.792 | 54.92 | 25.08 | 948024 | 948.024 | 52.48 | 27.52 | 1040256 | 1040.256 | 50.04 | 29.96 | 1132488 | 1132.488 | 47.6 | 32.4 | 1224720 | 1224.72 | 50
11/29/20XX 1:00:00 PM | 0.54167 | 2 | 48.9 | 50 | 48.9 |  | 48.9 | 69.69 | 10.31 | 389718 | 389.718 | 67.38 | 12.62 | 477036 | 477.036 | 65.07 | 14.93 | 564354 | 564.354 | 62.76 | 17.24 | 651672 | 651.672 | 60.45 | 19.55 | 738990 | 738.99 | 58.14 | 21.86 | 826308 | 826.308 | 55.83 | 24.17 | 913626 | 913.626 | 53.52 | 26.48 | 1000944 | 1000.944 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.9 | 31.1 | 1175580 | 1175.58 | 50
11/29/20XX 2:00:00 PM | 0.58333 | 2 | 49.2 | 49.7 | 49.2 |  | 49.2 | 69.72 | 10.28 | 388584 | 388.584 | 67.44 | 12.56 | 474768 | 474.768 | 65.16 | 14.84 | 560952 | 560.952 | 62.88 | 17.12 | 647136 | 647.136 | 60.6 | 19.4 | 733320 | 733.32 | 58.32 | 21.68 | 819504 | 819.504 | 56.04 | 23.96 | 905688 | 905.688 | 53.76 | 26.24 | 991872 | 991.872 | 51.48 | 28.52 | 1078056 | 1078.056 | 49.2 | 30.8 | 1164240 | 1164.24 | 50
11/29/20XX 3:00:00 PM | 0.625 | 2 | 49.4 | 49.7 | 49.4 |  | 49.4 | 69.74 | 10.26 | 387828 | 387.828 | 67.48 | 12.52 | 473256 | 473.256 | 65.22 | 14.78 | 558684 | 558.684 | 62.96 | 17.04 | 644112 | 644.112 | 60.7 | 19.3 | 729540 | 729.54 | 58.44 | 21.56 | 814968 | 814.968 | 56.18 | 23.82 | 900396 | 900.396 | 53.92 | 26.08 | 985824 | 985.824 | 51.66 | 28.34 | 1071252 | 1071.252 | 49.4 | 30.6 | 1156680 | 1156.68 | 50
11/29/20XX 4:00:00 PM | 0.66667 | 2 | 48.4 | 52.5 | 48.4 |  | 48.4 | 69.64 | 10.36 | 391608 | 391.608 | 67.28 | 12.72 | 480816 | 480.816 | 64.92 | 15.08 | 570024 | 570.024 | 62.56 | 17.44 | 659232 | 659.232 | 60.2 | 19.8 | 748440 | 748.44 | 57.84 | 22.16 | 837648 | 837.648 | 55.48 | 24.52 | 926856 | 926.856 | 53.12 | 26.88 | 1016064 | 1016.064 | 50.76 | 29.24 | 1105272 | 1105.272 | 48.4 | 31.6 | 1194480 | 1194.48 | 50
11/29/20XX 5:00:00 PM | 0.70833 | 2 | 47.5 | 54.6 | 47.5 |  | 47.5 | 69.55 | 10.45 | 395010 | 395.01 | 67.1 | 12.9 | 487620 | 487.62 | 64.65 | 15.35 | 580230 | 580.23 | 62.2 | 17.8 | 672840 | 672.84 | 59.75 | 20.25 | 765450 | 765.45 | 57.3 | 22.7 | 858060 | 858.06 | 54.85 | 25.15 | 950670 | 950.67 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.95 | 30.05 | 1135890 | 1135.89 | 47.5 | 32.5 | 1228500 | 1228.5 | 45
11/29/20XX 6:00:00 PM | 0.75 | 2 | 47.1 | 56.7 | 47.1 |  | 47.1 | 69.51 | 10.49 | 396522 | 396.522 | 67.02 | 12.98 | 490644 | 490.644 | 64.53 | 15.47 | 584766 | 584.766 | 62.04 | 17.96 | 678888 | 678.888 | 59.55 | 20.45 | 773010 | 773.01 | 57.06 | 22.94 | 867132 | 867.132 | 54.57 | 25.43 | 961254 | 961.254 | 52.08 | 27.92 | 1055376 | 1055.376 | 49.59 | 30.41 | 1149498 | 1149.498 | 47.1 | 32.9 | 1243620 | 1243.62 | 45
11/29/20XX 7:00:00 PM | 0.79167 | 2 | 46.5 | 58.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/29/20XX 8:00:00 PM | 0.83333 | 2 | 46.3 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/29/20XX 9:00:00 PM | 0.875 | 2 | 45.4 | 60.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/29/20XX 10:00:00 PM | 0.91667 | 2 | 44.8 | 62.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/29/20XX 11:00:00 PM | 0.95833 | 2 | 44.6 | 63.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/29/20XX 12:00:00 AM | 0 | 3 | 44.1 | 63.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/30/20XX 1:00:00 AM | 0.041667 | 3 | 43.7 | 62.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/30/20XX 2:00:00 AM | 0.083333 | 3 | 43.5 | 63.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/30/20XX 3:00:00 AM | 0.125 | 3 | 43.3 | 63.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/30/20XX 4:00:00 AM | 0.16667 | 3 | 43.2 | 63 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/30/20XX 5:00:00 AM | 0.20833 | 3 | 42.8 | 63.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/30/20XX 6:00:00 AM | 0.25 | 3 | 42.8 | 64.9 | 42.8 |  | 42.8 | 69.08 | 10.92 | 412776 | 412.776 | 66.16 | 13.84 | 523152 | 523.152 | 63.24 | 16.76 | 633528 | 633.528 | 60.32 | 19.68 | 743904 | 743.904 | 57.4 | 22.6 | 854280 | 854.28 | 54.48 | 25.52 | 964656 | 964.656 | 51.56 | 28.44 | 1075032 | 1075.032 | 48.64 | 31.36 | 1185408 | 1185.408 | 45.72 | 34.28 | 1295784 | 1295.784 | 42.8 | 37.2 | 1406160 | 1406.16 | 45
11/30/20XX 7:00:00 AM | 0.29167 | 3 | 42.7 | 65.2 | 42.7 |  | 42.7 | 69.07 | 10.93 | 413154 | 413.154 | 66.14 | 13.86 | 523908 | 523.908 | 63.21 | 16.79 | 634662 | 634.662 | 60.28 | 19.72 | 745416 | 745.416 | 57.35 | 22.65 | 856170 | 856.17 | 54.42 | 25.58 | 966924 | 966.924 | 51.49 | 28.51 | 1077678 | 1077.678 | 48.56 | 31.44 | 1188432 | 1188.432 | 45.63 | 34.37 | 1299186 | 1299.186 | 42.7 | 37.3 | 1409940 | 1409.94 | 45
11/30/20XX 8:00:00 AM | 0.33333 | 3 | 43.4 | 66.1 | 43.4 |  | 43.4 | 69.14 | 10.86 | 410508 | 410.508 | 66.28 | 13.72 | 518616 | 518.616 | 63.42 | 16.58 | 626724 | 626.724 | 60.56 | 19.44 | 734832 | 734.832 | 57.7 | 22.3 | 842940 | 842.94 | 54.84 | 25.16 | 951048 | 951.048 | 51.98 | 28.02 | 1059156 | 1059.156 | 49.12 | 30.88 | 1167264 | 1167.264 | 46.26 | 33.74 | 1275372 | 1275.372 | 43.4 | 36.6 | 1383480 | 1383.48 | 45
11/30/20XX 9:00:00 AM | 0.375 | 3 | 44.8 | 63.6 | 44.8 |  | 44.8 | 69.28 | 10.72 | 405216 | 405.216 | 66.56 | 13.44 | 508032 | 508.032 | 63.84 | 16.16 | 610848 | 610.848 | 61.12 | 18.88 | 713664 | 713.664 | 58.4 | 21.6 | 816480 | 816.48 | 55.68 | 24.32 | 919296 | 919.296 | 52.96 | 27.04 | 1022112 | 1022.112 | 50.24 | 29.76 | 1124928 | 1124.928 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.8 | 35.2 | 1330560 | 1330.56 | 45
11/30/20XX 10:00:00 AM | 0.41667 | 3 | 45.6 | 61.8 | 45.6 |  | 45.6 | 69.36 | 10.64 | 402192 | 402.192 | 66.72 | 13.28 | 501984 | 501.984 | 64.08 | 15.92 | 601776 | 601.776 | 61.44 | 18.56 | 701568 | 701.568 | 58.8 | 21.2 | 801360 | 801.36 | 56.16 | 23.84 | 901152 | 901.152 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.88 | 29.12 | 1100736 | 1100.736 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.6 | 34.4 | 1300320 | 1300.32 | 45
11/30/20XX 11:00:00 AM | 0.45833 | 3 | 46.9 | 59.2 | 46.9 |  | 46.9 | 69.49 | 10.51 | 397278 | 397.278 | 66.98 | 13.02 | 492156 | 492.156 | 64.47 | 15.53 | 587034 | 587.034 | 61.96 | 18.04 | 681912 | 681.912 | 59.45 | 20.55 | 776790 | 776.79 | 56.94 | 23.06 | 871668 | 871.668 | 54.43 | 25.57 | 966546 | 966.546 | 51.92 | 28.08 | 1061424 | 1061.424 | 49.41 | 30.59 | 1156302 | 1156.302 | 46.9 | 33.1 | 1251180 | 1251.18 | 45
11/30/20XX 12:00:00 PM | 0.5 | 3 | 46.9 | 61.5 | 46.9 |  | 46.9 | 69.49 | 10.51 | 397278 | 397.278 | 66.98 | 13.02 | 492156 | 492.156 | 64.47 | 15.53 | 587034 | 587.034 | 61.96 | 18.04 | 681912 | 681.912 | 59.45 | 20.55 | 776790 | 776.79 | 56.94 | 23.06 | 871668 | 871.668 | 54.43 | 25.57 | 966546 | 966.546 | 51.92 | 28.08 | 1061424 | 1061.424 | 49.41 | 30.59 | 1156302 | 1156.302 | 46.9 | 33.1 | 1251180 | 1251.18 | 45
11/30/20XX 1:00:00 PM | 0.54167 | 3 | 47.9 | 61.1 | 47.9 |  | 47.9 | 69.59 | 10.41 | 393498 | 393.498 | 67.18 | 12.82 | 484596 | 484.596 | 64.77 | 15.23 | 575694 | 575.694 | 62.36 | 17.64 | 666792 | 666.792 | 59.95 | 20.05 | 757890 | 757.89 | 57.54 | 22.46 | 848988 | 848.988 | 55.13 | 24.87 | 940086 | 940.086 | 52.72 | 27.28 | 1031184 | 1031.184 | 50.31 | 29.69 | 1122282 | 1122.282 | 47.9 | 32.1 | 1213380 | 1213.38 | 50
11/30/20XX 2:00:00 PM | 0.58333 | 3 | 47.2 | 63.4 | 47.2 |  | 47.2 | 69.52 | 10.48 | 396144 | 396.144 | 67.04 | 12.96 | 489888 | 489.888 | 64.56 | 15.44 | 583632 | 583.632 | 62.08 | 17.92 | 677376 | 677.376 | 59.6 | 20.4 | 771120 | 771.12 | 57.12 | 22.88 | 864864 | 864.864 | 54.64 | 25.36 | 958608 | 958.608 | 52.16 | 27.84 | 1052352 | 1052.352 | 49.68 | 30.32 | 1146096 | 1146.096 | 47.2 | 32.8 | 1239840 | 1239.84 | 45
11/30/20XX 3:00:00 PM | 0.625 | 3 | 46.7 | 64.7 | 46.7 |  | 46.7 | 69.47 | 10.53 | 398034 | 398.034 | 66.94 | 13.06 | 493668 | 493.668 | 64.41 | 15.59 | 589302 | 589.302 | 61.88 | 18.12 | 684936 | 684.936 | 59.35 | 20.65 | 780570 | 780.57 | 56.82 | 23.18 | 876204 | 876.204 | 54.29 | 25.71 | 971838 | 971.838 | 51.76 | 28.24 | 1067472 | 1067.472 | 49.23 | 30.77 | 1163106 | 1163.106 | 46.7 | 33.3 | 1258740 | 1258.74 | 45
11/30/20XX 4:00:00 PM | 0.66667 | 3 | 46.2 | 68.2 | 46.2 |  | 46.2 | 69.42 | 10.58 | 399924 | 399.924 | 66.84 | 13.16 | 497448 | 497.448 | 64.26 | 15.74 | 594972 | 594.972 | 61.68 | 18.32 | 692496 | 692.496 | 59.1 | 20.9 | 790020 | 790.02 | 56.52 | 23.48 | 887544 | 887.544 | 53.94 | 26.06 | 985068 | 985.068 | 51.36 | 28.64 | 1082592 | 1082.592 | 48.78 | 31.22 | 1180116 | 1180.116 | 46.2 | 33.8 | 1277640 | 1277.64 | 45
11/30/20XX 5:00:00 PM | 0.70833 | 3 | 45.9 | 71.8 | 45.9 |  | 45.9 | 69.39 | 10.61 | 401058 | 401.058 | 66.78 | 13.22 | 499716 | 499.716 | 64.17 | 15.83 | 598374 | 598.374 | 61.56 | 18.44 | 697032 | 697.032 | 58.95 | 21.05 | 795690 | 795.69 | 56.34 | 23.66 | 894348 | 894.348 | 53.73 | 26.27 | 993006 | 993.006 | 51.12 | 28.88 | 1091664 | 1091.664 | 48.51 | 31.49 | 1190322 | 1190.322 | 45.9 | 34.1 | 1288980 | 1288.98 | 45
11/30/20XX 6:00:00 PM | 0.75 | 3 | 46.1 | 72.3 | 46.1 |  | 46.1 | 69.41 | 10.59 | 400302 | 400.302 | 66.82 | 13.18 | 498204 | 498.204 | 64.23 | 15.77 | 596106 | 596.106 | 61.64 | 18.36 | 694008 | 694.008 | 59.05 | 20.95 | 791910 | 791.91 | 56.46 | 23.54 | 889812 | 889.812 | 53.87 | 26.13 | 987714 | 987.714 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.69 | 31.31 | 1183518 | 1183.518 | 46.1 | 33.9 | 1281420 | 1281.42 | 45
11/30/20XX 7:00:00 PM | 0.79167 | 3 | 46.2 | 72.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/30/20XX 8:00:00 PM | 0.83333 | 3 | 46.4 | 72.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/30/20XX 9:00:00 PM | 0.875 | 3 | 46.2 | 71.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/30/20XX 10:00:00 PM | 0.91667 | 3 | 46 | 71.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/30/20XX 11:00:00 PM | 0.95833 | 3 | 46.1 | 70.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11/30/20XX 12:00:00 AM | 0 | 4 | 45.8 | 72.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/1/20XX 1:00:00 AM | 0.041667 | 4 | 45.7 | 73.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/1/20XX 2:00:00 AM | 0.083333 | 4 | 45.1 | 73.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/1/20XX 3:00:00 AM | 0.125 | 4 | 44.5 | 73.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/1/20XX 4:00:00 AM | 0.16667 | 4 | 44.3 | 74.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/1/20XX 5:00:00 AM | 0.20833 | 4 | 44 | 75.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/1/20XX 6:00:00 AM | 0.25 | 4 | 43.7 | 75.4 | 43.7 |  | 43.7 | 69.17 | 10.83 | 409374 | 409.374 | 66.34 | 13.66 | 516348 | 516.348 | 63.51 | 16.49 | 623322 | 623.322 | 60.68 | 19.32 | 730296 | 730.296 | 57.85 | 22.15 | 837270 | 837.27 | 55.02 | 24.98 | 944244 | 944.244 | 52.19 | 27.81 | 1051218 | 1051.218 | 49.36 | 30.64 | 1158192 | 1158.192 | 46.53 | 33.47 | 1265166 | 1265.166 | 43.7 | 36.3 | 1372140 | 1372.14 | 45
12/1/20XX 7:00:00 AM | 0.29167 | 4 | 43.8 | 74.2 | 43.8 |  | 43.8 | 69.18 | 10.82 | 408996 | 408.996 | 66.36 | 13.64 | 515592 | 515.592 | 63.54 | 16.46 | 622188 | 622.188 | 60.72 | 19.28 | 728784 | 728.784 | 57.9 | 22.1 | 835380 | 835.38 | 55.08 | 24.92 | 941976 | 941.976 | 52.26 | 27.74 | 1048572 | 1048.572 | 49.44 | 30.56 | 1155168 | 1155.168 | 46.62 | 33.38 | 1261764 | 1261.764 | 43.8 | 36.2 | 1368360 | 1368.36 | 45
12/1/20XX 8:00:00 AM | 0.33333 | 4 | 44.3 | 72.7 | 44.3 |  | 44.3 | 69.23 | 10.77 | 407106 | 407.106 | 66.46 | 13.54 | 511812 | 511.812 | 63.69 | 16.31 | 616518 | 616.518 | 60.92 | 19.08 | 721224 | 721.224 | 58.15 | 21.85 | 825930 | 825.93 | 55.38 | 24.62 | 930636 | 930.636 | 52.61 | 27.39 | 1035342 | 1035.342 | 49.84 | 30.16 | 1140048 | 1140.048 | 47.07 | 32.93 | 1244754 | 1244.754 | 44.3 | 35.7 | 1349460 | 1349.46 | 45
12/1/20XX 9:00:00 AM | 0.375 | 4 | 45.5 | 69 | 45.5 |  | 45.5 | 69.35 | 10.65 | 402570 | 402.57 | 66.7 | 13.3 | 502740 | 502.74 | 64.05 | 15.95 | 602910 | 602.91 | 61.4 | 18.6 | 703080 | 703.08 | 58.75 | 21.25 | 803250 | 803.25 | 56.1 | 23.9 | 903420 | 903.42 | 53.45 | 26.55 | 1003590 | 1003.59 | 50.8 | 29.2 | 1103760 | 1103.76 | 48.15 | 31.85 | 1203930 | 1203.93 | 45.5 | 34.5 | 1304100 | 1304.1 | 45
12/1/20XX 10:00:00 AM | 0.41667 | 4 | 47 | 65.2 | 47 |  | 47 | 69.5 | 10.5 | 396900 | 396.9 | 67 | 13 | 491400 | 491.4 | 64.5 | 15.5 | 585900 | 585.9 | 62 | 18 | 680400 | 680.4 | 59.5 | 20.5 | 774900 | 774.9 | 57 | 23 | 869400 | 869.4 | 54.5 | 25.5 | 963900 | 963.9 | 52 | 28 | 1058400 | 1058.4 | 49.5 | 30.5 | 1152900 | 1152.9 | 47 | 33 | 1247400 | 1247.4 | 45
12/1/20XX 11:00:00 AM | 0.45833 | 4 | 48.2 | 63.5 | 48.2 |  | 48.2 | 69.62 | 10.38 | 392364 | 392.364 | 67.24 | 12.76 | 482328 | 482.328 | 64.86 | 15.14 | 572292 | 572.292 | 62.48 | 17.52 | 662256 | 662.256 | 60.1 | 19.9 | 752220 | 752.22 | 57.72 | 22.28 | 842184 | 842.184 | 55.34 | 24.66 | 932148 | 932.148 | 52.96 | 27.04 | 1022112 | 1022.112 | 50.58 | 29.42 | 1112076 | 1112.076 | 48.2 | 31.8 | 1202040 | 1202.04 | 50
12/1/20XX 12:00:00 PM | 0.5 | 4 | 49.2 | 61.2 | 49.2 |  | 49.2 | 69.72 | 10.28 | 388584 | 388.584 | 67.44 | 12.56 | 474768 | 474.768 | 65.16 | 14.84 | 560952 | 560.952 | 62.88 | 17.12 | 647136 | 647.136 | 60.6 | 19.4 | 733320 | 733.32 | 58.32 | 21.68 | 819504 | 819.504 | 56.04 | 23.96 | 905688 | 905.688 | 53.76 | 26.24 | 991872 | 991.872 | 51.48 | 28.52 | 1078056 | 1078.056 | 49.2 | 30.8 | 1164240 | 1164.24 | 50
12/1/20XX 1:00:00 PM | 0.54167 | 4 | 49.9 | 59.2 | 49.9 |  | 49.9 | 69.79 | 10.21 | 385938 | 385.938 | 67.58 | 12.42 | 469476 | 469.476 | 65.37 | 14.63 | 553014 | 553.014 | 63.16 | 16.84 | 636552 | 636.552 | 60.95 | 19.05 | 720090 | 720.09 | 58.74 | 21.26 | 803628 | 803.628 | 56.53 | 23.47 | 887166 | 887.166 | 54.32 | 25.68 | 970704 | 970.704 | 52.11 | 27.89 | 1054242 | 1054.242 | 49.9 | 30.1 | 1137780 | 1137.78 | 50
12/1/20XX 2:00:00 PM | 0.58333 | 4 | 50.3 | 57.9 | 50.3 |  | 50.3 | 69.83 | 10.17 | 384426 | 384.426 | 67.66 | 12.34 | 466452 | 466.452 | 65.49 | 14.51 | 548478 | 548.478 | 63.32 | 16.68 | 630504 | 630.504 | 61.15 | 18.85 | 712530 | 712.53 | 58.98 | 21.02 | 794556 | 794.556 | 56.81 | 23.19 | 876582 | 876.582 | 54.64 | 25.36 | 958608 | 958.608 | 52.47 | 27.53 | 1040634 | 1040.634 | 50.3 | 29.7 | 1122660 | 1122.66 | 50
12/1/20XX 3:00:00 PM | 0.625 | 4 | 49.5 | 59.5 | 49.5 |  | 49.5 | 69.75 | 10.25 | 387450 | 387.45 | 67.5 | 12.5 | 472500 | 472.5 | 65.25 | 14.75 | 557550 | 557.55 | 63 | 17 | 642600 | 642.6 | 60.75 | 19.25 | 727650 | 727.65 | 58.5 | 21.5 | 812700 | 812.7 | 56.25 | 23.75 | 897750 | 897.75 | 54 | 26 | 982800 | 982.8 | 51.75 | 28.25 | 1067850 | 1067.85 | 49.5 | 30.5 | 1152900 | 1152.9 | 50
12/1/20XX 4:00:00 PM | 0.66667 | 4 | 48 | 60.6 | 48 |  | 48 | 69.6 | 10.4 | 393120 | 393.12 | 67.2 | 12.8 | 483840 | 483.84 | 64.8 | 15.2 | 574560 | 574.56 | 62.4 | 17.6 | 665280 | 665.28 | 60 | 20 | 756000 | 756 | 57.6 | 22.4 | 846720 | 846.72 | 55.2 | 24.8 | 937440 | 937.44 | 52.8 | 27.2 | 1028160 | 1028.16 | 50.4 | 29.6 | 1118880 | 1118.88 | 48 | 32 | 1209600 | 1209.6 | 50
12/1/20XX 5:00:00 PM | 0.70833 | 4 | 47 | 61.4 | 47 |  | 47 | 69.5 | 10.5 | 396900 | 396.9 | 67 | 13 | 491400 | 491.4 | 64.5 | 15.5 | 585900 | 585.9 | 62 | 18 | 680400 | 680.4 | 59.5 | 20.5 | 774900 | 774.9 | 57 | 23 | 869400 | 869.4 | 54.5 | 25.5 | 963900 | 963.9 | 52 | 28 | 1058400 | 1058.4 | 49.5 | 30.5 | 1152900 | 1152.9 | 47 | 33 | 1247400 | 1247.4 | 45
12/1/20XX 6:00:00 PM | 0.75 | 4 | 46.3 | 63.1 | 46.3 |  | 46.3 | 69.43 | 10.57 | 399546 | 399.546 | 66.86 | 13.14 | 496692 | 496.692 | 64.29 | 15.71 | 593838 | 593.838 | 61.72 | 18.28 | 690984 | 690.984 | 59.15 | 20.85 | 788130 | 788.13 | 56.58 | 23.42 | 885276 | 885.276 | 54.01 | 25.99 | 982422 | 982.422 | 51.44 | 28.56 | 1079568 | 1079.568 | 48.87 | 31.13 | 1176714 | 1176.714 | 46.3 | 33.7 | 1273860 | 1273.86 | 45
12/1/20XX 7:00:00 PM | 0.79167 | 4 | 45.1 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/1/20XX 8:00:00 PM | 0.83333 | 4 | 44.5 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/1/20XX 9:00:00 PM | 0.875 | 4 | 44.1 | 67.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/1/20XX 10:00:00 PM | 0.91667 | 4 | 43.9 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/1/20XX 11:00:00 PM | 0.95833 | 4 | 43.4 | 65.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/1/20XX 12:00:00 AM | 0 | 5 | 42.7 | 66.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/2/20XX 1:00:00 AM | 0.041667 | 5 | 42.5 | 66.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/2/20XX 2:00:00 AM | 0.083333 | 5 | 41.8 | 66.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/2/20XX 3:00:00 AM | 0.125 | 5 | 41.6 | 68.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/2/20XX 4:00:00 AM | 0.16667 | 5 | 41.1 | 70.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/2/20XX 5:00:00 AM | 0.20833 | 5 | 41 | 70.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/2/20XX 6:00:00 AM | 0.25 | 5 | 40.8 | 72.3 | 40.8 |  | 40.8 | 68.88 | 11.12 | 420336 | 420.336 | 65.76 | 14.24 | 538272 | 538.272 | 62.64 | 17.36 | 656208 | 656.208 | 59.52 | 20.48 | 774144 | 774.144 | 56.4 | 23.6 | 892080 | 892.08 | 53.28 | 26.72 | 1010016 | 1010.016 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.04 | 32.96 | 1245888 | 1245.888 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.8 | 39.2 | 1481760 | 1481.76 | 40
12/2/20XX 7:00:00 AM | 0.29167 | 5 | 40.9 | 72.1 | 40.9 |  | 40.9 | 68.89 | 11.11 | 419958 | 419.958 | 65.78 | 14.22 | 537516 | 537.516 | 62.67 | 17.33 | 655074 | 655.074 | 59.56 | 20.44 | 772632 | 772.632 | 56.45 | 23.55 | 890190 | 890.19 | 53.34 | 26.66 | 1007748 | 1007.748 | 50.23 | 29.77 | 1125306 | 1125.306 | 47.12 | 32.88 | 1242864 | 1242.864 | 44.01 | 35.99 | 1360422 | 1360.422 | 40.9 | 39.1 | 1477980 | 1477.98 | 40
12/2/20XX 8:00:00 AM | 0.33333 | 5 | 41.5 | 71.9 | 41.5 |  | 41.5 | 68.95 | 11.05 | 417690 | 417.69 | 65.9 | 14.1 | 532980 | 532.98 | 62.85 | 17.15 | 648270 | 648.27 | 59.8 | 20.2 | 763560 | 763.56 | 56.75 | 23.25 | 878850 | 878.85 | 53.7 | 26.3 | 994140 | 994.14 | 50.65 | 29.35 | 1109430 | 1109.43 | 47.6 | 32.4 | 1224720 | 1224.72 | 44.55 | 35.45 | 1340010 | 1340.01 | 41.5 | 38.5 | 1455300 | 1455.3 | 40
12/2/20XX 9:00:00 AM | 0.375 | 5 | 43.1 | 70.5 | 43.1 |  | 43.1 | 69.11 | 10.89 | 411642 | 411.642 | 66.22 | 13.78 | 520884 | 520.884 | 63.33 | 16.67 | 630126 | 630.126 | 60.44 | 19.56 | 739368 | 739.368 | 57.55 | 22.45 | 848610 | 848.61 | 54.66 | 25.34 | 957852 | 957.852 | 51.77 | 28.23 | 1067094 | 1067.094 | 48.88 | 31.12 | 1176336 | 1176.336 | 45.99 | 34.01 | 1285578 | 1285.578 | 43.1 | 36.9 | 1394820 | 1394.82 | 45
12/2/20XX 10:00:00 AM | 0.41667 | 5 | 44.3 | 68.8 | 44.3 |  | 44.3 | 69.23 | 10.77 | 407106 | 407.106 | 66.46 | 13.54 | 511812 | 511.812 | 63.69 | 16.31 | 616518 | 616.518 | 60.92 | 19.08 | 721224 | 721.224 | 58.15 | 21.85 | 825930 | 825.93 | 55.38 | 24.62 | 930636 | 930.636 | 52.61 | 27.39 | 1035342 | 1035.342 | 49.84 | 30.16 | 1140048 | 1140.048 | 47.07 | 32.93 | 1244754 | 1244.754 | 44.3 | 35.7 | 1349460 | 1349.46 | 45
12/2/20XX 11:00:00 AM | 0.45833 | 5 | 45.8 | 67.8 | 45.8 |  | 45.8 | 69.38 | 10.62 | 401436 | 401.436 | 66.76 | 13.24 | 500472 | 500.472 | 64.14 | 15.86 | 599508 | 599.508 | 61.52 | 18.48 | 698544 | 698.544 | 58.9 | 21.1 | 797580 | 797.58 | 56.28 | 23.72 | 896616 | 896.616 | 53.66 | 26.34 | 995652 | 995.652 | 51.04 | 28.96 | 1094688 | 1094.688 | 48.42 | 31.58 | 1193724 | 1193.724 | 45.8 | 34.2 | 1292760 | 1292.76 | 45
12/2/20XX 12:00:00 PM | 0.5 | 5 | 47.7 | 63.2 | 47.7 |  | 47.7 | 69.57 | 10.43 | 394254 | 394.254 | 67.14 | 12.86 | 486108 | 486.108 | 64.71 | 15.29 | 577962 | 577.962 | 62.28 | 17.72 | 669816 | 669.816 | 59.85 | 20.15 | 761670 | 761.67 | 57.42 | 22.58 | 853524 | 853.524 | 54.99 | 25.01 | 945378 | 945.378 | 52.56 | 27.44 | 1037232 | 1037.232 | 50.13 | 29.87 | 1129086 | 1129.086 | 47.7 | 32.3 | 1220940 | 1220.94 | 50
12/2/20XX 1:00:00 PM | 0.54167 | 5 | 48.1 | 64 | 48.1 |  | 48.1 | 69.61 | 10.39 | 392742 | 392.742 | 67.22 | 12.78 | 483084 | 483.084 | 64.83 | 15.17 | 573426 | 573.426 | 62.44 | 17.56 | 663768 | 663.768 | 60.05 | 19.95 | 754110 | 754.11 | 57.66 | 22.34 | 844452 | 844.452 | 55.27 | 24.73 | 934794 | 934.794 | 52.88 | 27.12 | 1025136 | 1025.136 | 50.49 | 29.51 | 1115478 | 1115.478 | 48.1 | 31.9 | 1205820 | 1205.82 | 50
12/2/20XX 2:00:00 PM | 0.58333 | 5 | 48.4 | 64.9 | 48.4 |  | 48.4 | 69.64 | 10.36 | 391608 | 391.608 | 67.28 | 12.72 | 480816 | 480.816 | 64.92 | 15.08 | 570024 | 570.024 | 62.56 | 17.44 | 659232 | 659.232 | 60.2 | 19.8 | 748440 | 748.44 | 57.84 | 22.16 | 837648 | 837.648 | 55.48 | 24.52 | 926856 | 926.856 | 53.12 | 26.88 | 1016064 | 1016.064 | 50.76 | 29.24 | 1105272 | 1105.272 | 48.4 | 31.6 | 1194480 | 1194.48 | 50
12/2/20XX 3:00:00 PM | 0.625 | 5 | 48.6 | 64.6 | 48.6 |  | 48.6 | 69.66 | 10.34 | 390852 | 390.852 | 67.32 | 12.68 | 479304 | 479.304 | 64.98 | 15.02 | 567756 | 567.756 | 62.64 | 17.36 | 656208 | 656.208 | 60.3 | 19.7 | 744660 | 744.66 | 57.96 | 22.04 | 833112 | 833.112 | 55.62 | 24.38 | 921564 | 921.564 | 53.28 | 26.72 | 1010016 | 1010.016 | 50.94 | 29.06 | 1098468 | 1098.468 | 48.6 | 31.4 | 1186920 | 1186.92 | 50
12/2/20XX 4:00:00 PM | 0.66667 | 5 | 48.5 | 65.9 | 48.5 |  | 48.5 | 69.65 | 10.35 | 391230 | 391.23 | 67.3 | 12.7 | 480060 | 480.06 | 64.95 | 15.05 | 568890 | 568.89 | 62.6 | 17.4 | 657720 | 657.72 | 60.25 | 19.75 | 746550 | 746.55 | 57.9 | 22.1 | 835380 | 835.38 | 55.55 | 24.45 | 924210 | 924.21 | 53.2 | 26.8 | 1013040 | 1013.04 | 50.85 | 29.15 | 1101870 | 1101.87 | 48.5 | 31.5 | 1190700 | 1190.7 | 50
12/2/20XX 5:00:00 PM | 0.70833 | 5 | 48 | 67.8 | 48 |  | 48 | 69.6 | 10.4 | 393120 | 393.12 | 67.2 | 12.8 | 483840 | 483.84 | 64.8 | 15.2 | 574560 | 574.56 | 62.4 | 17.6 | 665280 | 665.28 | 60 | 20 | 756000 | 756 | 57.6 | 22.4 | 846720 | 846.72 | 55.2 | 24.8 | 937440 | 937.44 | 52.8 | 27.2 | 1028160 | 1028.16 | 50.4 | 29.6 | 1118880 | 1118.88 | 48 | 32 | 1209600 | 1209.6 | 50
12/2/20XX 6:00:00 PM | 0.75 | 5 | 47.9 | 70.3 | 47.9 |  | 47.9 | 69.59 | 10.41 | 393498 | 393.498 | 67.18 | 12.82 | 484596 | 484.596 | 64.77 | 15.23 | 575694 | 575.694 | 62.36 | 17.64 | 666792 | 666.792 | 59.95 | 20.05 | 757890 | 757.89 | 57.54 | 22.46 | 848988 | 848.988 | 55.13 | 24.87 | 940086 | 940.086 | 52.72 | 27.28 | 1031184 | 1031.184 | 50.31 | 29.69 | 1122282 | 1122.282 | 47.9 | 32.1 | 1213380 | 1213.38 | 50
12/2/20XX 7:00:00 PM | 0.79167 | 5 | 47.5 | 71 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/2/20XX 8:00:00 PM | 0.83333 | 5 | 47.3 | 73.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/2/20XX 9:00:00 PM | 0.875 | 5 | 47.4 | 73.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/2/20XX 10:00:00 PM | 0.91667 | 5 | 46.9 | 76.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/2/20XX 11:00:00 PM | 0.95833 | 5 | 46.5 | 76.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/2/20XX 12:00:00 AM | 0 | 6 | 46.6 | 77.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/3/20XX 1:00:00 AM | 0.041667 | 6 | 46.4 | 74.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/3/20XX 2:00:00 AM | 0.083333 | 6 | 46.2 | 75.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/3/20XX 3:00:00 AM | 0.125 | 6 | 45.9 | 76.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/3/20XX 4:00:00 AM | 0.16667 | 6 | 45.8 | 75.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/3/20XX 5:00:00 AM | 0.20833 | 6 | 45.7 | 76.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/3/20XX 6:00:00 AM | 0.25 | 6 | 45.7 | 75 | 45.7 |  | 45.7 | 69.37 | 10.63 | 401814 | 401.814 | 66.74 | 13.26 | 501228 | 501.228 | 64.11 | 15.89 | 600642 | 600.642 | 61.48 | 18.52 | 700056 | 700.056 | 58.85 | 21.15 | 799470 | 799.47 | 56.22 | 23.78 | 898884 | 898.884 | 53.59 | 26.41 | 998298 | 998.298 | 50.96 | 29.04 | 1097712 | 1097.712 | 48.33 | 31.67 | 1197126 | 1197.126 | 45.7 | 34.3 | 1296540 | 1296.54 | 45
12/3/20XX 7:00:00 AM | 0.29167 | 6 | 45.7 | 72.8 | 45.7 |  | 45.7 | 69.37 | 10.63 | 401814 | 401.814 | 66.74 | 13.26 | 501228 | 501.228 | 64.11 | 15.89 | 600642 | 600.642 | 61.48 | 18.52 | 700056 | 700.056 | 58.85 | 21.15 | 799470 | 799.47 | 56.22 | 23.78 | 898884 | 898.884 | 53.59 | 26.41 | 998298 | 998.298 | 50.96 | 29.04 | 1097712 | 1097.712 | 48.33 | 31.67 | 1197126 | 1197.126 | 45.7 | 34.3 | 1296540 | 1296.54 | 45
12/3/20XX 8:00:00 AM | 0.33333 | 6 | 45.6 | 69 | 45.6 |  | 45.6 | 69.36 | 10.64 | 402192 | 402.192 | 66.72 | 13.28 | 501984 | 501.984 | 64.08 | 15.92 | 601776 | 601.776 | 61.44 | 18.56 | 701568 | 701.568 | 58.8 | 21.2 | 801360 | 801.36 | 56.16 | 23.84 | 901152 | 901.152 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.88 | 29.12 | 1100736 | 1100.736 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.6 | 34.4 | 1300320 | 1300.32 | 45
12/3/20XX 9:00:00 AM | 0.375 | 6 | 46.2 | 67.6 | 46.2 |  | 46.2 | 69.42 | 10.58 | 399924 | 399.924 | 66.84 | 13.16 | 497448 | 497.448 | 64.26 | 15.74 | 594972 | 594.972 | 61.68 | 18.32 | 692496 | 692.496 | 59.1 | 20.9 | 790020 | 790.02 | 56.52 | 23.48 | 887544 | 887.544 | 53.94 | 26.06 | 985068 | 985.068 | 51.36 | 28.64 | 1082592 | 1082.592 | 48.78 | 31.22 | 1180116 | 1180.116 | 46.2 | 33.8 | 1277640 | 1277.64 | 45
12/3/20XX 10:00:00 AM | 0.41667 | 6 | 47.2 | 63.3 | 47.2 |  | 47.2 | 69.52 | 10.48 | 396144 | 396.144 | 67.04 | 12.96 | 489888 | 489.888 | 64.56 | 15.44 | 583632 | 583.632 | 62.08 | 17.92 | 677376 | 677.376 | 59.6 | 20.4 | 771120 | 771.12 | 57.12 | 22.88 | 864864 | 864.864 | 54.64 | 25.36 | 958608 | 958.608 | 52.16 | 27.84 | 1052352 | 1052.352 | 49.68 | 30.32 | 1146096 | 1146.096 | 47.2 | 32.8 | 1239840 | 1239.84 | 45
12/3/20XX 11:00:00 AM | 0.45833 | 6 | 48.5 | 59.7 | 48.5 |  | 48.5 | 69.65 | 10.35 | 391230 | 391.23 | 67.3 | 12.7 | 480060 | 480.06 | 64.95 | 15.05 | 568890 | 568.89 | 62.6 | 17.4 | 657720 | 657.72 | 60.25 | 19.75 | 746550 | 746.55 | 57.9 | 22.1 | 835380 | 835.38 | 55.55 | 24.45 | 924210 | 924.21 | 53.2 | 26.8 | 1013040 | 1013.04 | 50.85 | 29.15 | 1101870 | 1101.87 | 48.5 | 31.5 | 1190700 | 1190.7 | 50
12/3/20XX 12:00:00 PM | 0.5 | 6 | 49.3 | 57 | 49.3 |  | 49.3 | 69.73 | 10.27 | 388206 | 388.206 | 67.46 | 12.54 | 474012 | 474.012 | 65.19 | 14.81 | 559818 | 559.818 | 62.92 | 17.08 | 645624 | 645.624 | 60.65 | 19.35 | 731430 | 731.43 | 58.38 | 21.62 | 817236 | 817.236 | 56.11 | 23.89 | 903042 | 903.042 | 53.84 | 26.16 | 988848 | 988.848 | 51.57 | 28.43 | 1074654 | 1074.654 | 49.3 | 30.7 | 1160460 | 1160.46 | 50
12/3/20XX 1:00:00 PM | 0.54167 | 6 | 50 | 53.8 | 50 |  | 50 | 69.8 | 10.2 | 385560 | 385.56 | 67.6 | 12.4 | 468720 | 468.72 | 65.4 | 14.6 | 551880 | 551.88 | 63.2 | 16.8 | 635040 | 635.04 | 61 | 19 | 718200 | 718.2 | 58.8 | 21.2 | 801360 | 801.36 | 56.6 | 23.4 | 884520 | 884.52 | 54.4 | 25.6 | 967680 | 967.68 | 52.2 | 27.8 | 1050840 | 1050.84 | 50 | 30 | 1134000 | 1134 | 50
12/3/20XX 2:00:00 PM | 0.58333 | 6 | 50 | 52.4 | 50 |  | 50 | 69.8 | 10.2 | 385560 | 385.56 | 67.6 | 12.4 | 468720 | 468.72 | 65.4 | 14.6 | 551880 | 551.88 | 63.2 | 16.8 | 635040 | 635.04 | 61 | 19 | 718200 | 718.2 | 58.8 | 21.2 | 801360 | 801.36 | 56.6 | 23.4 | 884520 | 884.52 | 54.4 | 25.6 | 967680 | 967.68 | 52.2 | 27.8 | 1050840 | 1050.84 | 50 | 30 | 1134000 | 1134 | 50
12/3/20XX 3:00:00 PM | 0.625 | 6 | 49.8 | 54.4 | 49.8 |  | 49.8 | 69.78 | 10.22 | 386316 | 386.316 | 67.56 | 12.44 | 470232 | 470.232 | 65.34 | 14.66 | 554148 | 554.148 | 63.12 | 16.88 | 638064 | 638.064 | 60.9 | 19.1 | 721980 | 721.98 | 58.68 | 21.32 | 805896 | 805.896 | 56.46 | 23.54 | 889812 | 889.812 | 54.24 | 25.76 | 973728 | 973.728 | 52.02 | 27.98 | 1057644 | 1057.644 | 49.8 | 30.2 | 1141560 | 1141.56 | 50
12/3/20XX 4:00:00 PM | 0.66667 | 6 | 49.6 | 55.6 | 49.6 |  | 49.6 | 69.76 | 10.24 | 387072 | 387.072 | 67.52 | 12.48 | 471744 | 471.744 | 65.28 | 14.72 | 556416 | 556.416 | 63.04 | 16.96 | 641088 | 641.088 | 60.8 | 19.2 | 725760 | 725.76 | 58.56 | 21.44 | 810432 | 810.432 | 56.32 | 23.68 | 895104 | 895.104 | 54.08 | 25.92 | 979776 | 979.776 | 51.84 | 28.16 | 1064448 | 1064.448 | 49.6 | 30.4 | 1149120 | 1149.12 | 50
12/3/20XX 5:00:00 PM | 0.70833 | 6 | 48.7 | 57.1 | 48.7 |  | 48.7 | 69.67 | 10.33 | 390474 | 390.474 | 67.34 | 12.66 | 478548 | 478.548 | 65.01 | 14.99 | 566622 | 566.622 | 62.68 | 17.32 | 654696 | 654.696 | 60.35 | 19.65 | 742770 | 742.77 | 58.02 | 21.98 | 830844 | 830.844 | 55.69 | 24.31 | 918918 | 918.918 | 53.36 | 26.64 | 1006992 | 1006.992 | 51.03 | 28.97 | 1095066 | 1095.066 | 48.7 | 31.3 | 1183140 | 1183.14 | 50
12/3/20XX 6:00:00 PM | 0.75 | 6 | 48.2 | 57.9 | 48.2 |  | 48.2 | 69.62 | 10.38 | 392364 | 392.364 | 67.24 | 12.76 | 482328 | 482.328 | 64.86 | 15.14 | 572292 | 572.292 | 62.48 | 17.52 | 662256 | 662.256 | 60.1 | 19.9 | 752220 | 752.22 | 57.72 | 22.28 | 842184 | 842.184 | 55.34 | 24.66 | 932148 | 932.148 | 52.96 | 27.04 | 1022112 | 1022.112 | 50.58 | 29.42 | 1112076 | 1112.076 | 48.2 | 31.8 | 1202040 | 1202.04 | 50
12/3/20XX 7:00:00 PM | 0.79167 | 6 | 46.9 | 58.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/3/20XX 8:00:00 PM | 0.83333 | 6 | 46.2 | 61.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/3/20XX 9:00:00 PM | 0.875 | 6 | 45.6 | 61.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/3/20XX 10:00:00 PM | 0.91667 | 6 | 44.9 | 62.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/3/20XX 11:00:00 PM | 0.95833 | 6 | 44 | 63.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/3/20XX 12:00:00 AM | 0 | 7 | 43.6 | 63.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/4/20XX 1:00:00 AM | 0.041667 | 7 | 42.8 | 64.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/4/20XX 2:00:00 AM | 0.083333 | 7 | 42.6 | 64.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/4/20XX 3:00:00 AM | 0.125 | 7 | 41.7 | 67.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/4/20XX 4:00:00 AM | 0.16667 | 7 | 41.7 | 66.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/4/20XX 5:00:00 AM | 0.20833 | 7 | 41.5 | 67.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/4/20XX 6:00:00 AM | 0.25 | 7 | 41.2 | 68.2 | 41.2 |  | 41.2 | 68.92 | 11.08 | 418824 | 418.824 | 65.84 | 14.16 | 535248 | 535.248 | 62.76 | 17.24 | 651672 | 651.672 | 59.68 | 20.32 | 768096 | 768.096 | 56.6 | 23.4 | 884520 | 884.52 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.44 | 29.56 | 1117368 | 1117.368 | 47.36 | 32.64 | 1233792 | 1233.792 | 44.28 | 35.72 | 1350216 | 1350.216 | 41.2 | 38.8 | 1466640 | 1466.64 | 40
12/4/20XX 7:00:00 AM | 0.29167 | 7 | 40.7 | 69.1 | 40.7 |  | 40.7 | 68.87 | 11.13 | 420714 | 420.714 | 65.74 | 14.26 | 539028 | 539.028 | 62.61 | 17.39 | 657342 | 657.342 | 59.48 | 20.52 | 775656 | 775.656 | 56.35 | 23.65 | 893970 | 893.97 | 53.22 | 26.78 | 1012284 | 1012.284 | 50.09 | 29.91 | 1130598 | 1130.598 | 46.96 | 33.04 | 1248912 | 1248.912 | 43.83 | 36.17 | 1367226 | 1367.226 | 40.7 | 39.3 | 1485540 | 1485.54 | 40
12/4/20XX 8:00:00 AM | 0.33333 | 7 | 41.2 | 68.6 | 41.2 |  | 41.2 | 68.92 | 11.08 | 418824 | 418.824 | 65.84 | 14.16 | 535248 | 535.248 | 62.76 | 17.24 | 651672 | 651.672 | 59.68 | 20.32 | 768096 | 768.096 | 56.6 | 23.4 | 884520 | 884.52 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.44 | 29.56 | 1117368 | 1117.368 | 47.36 | 32.64 | 1233792 | 1233.792 | 44.28 | 35.72 | 1350216 | 1350.216 | 41.2 | 38.8 | 1466640 | 1466.64 | 40
12/4/20XX 9:00:00 AM | 0.375 | 7 | 42.4 | 65.1 | 42.4 |  | 42.4 | 69.04 | 10.96 | 414288 | 414.288 | 66.08 | 13.92 | 526176 | 526.176 | 63.12 | 16.88 | 638064 | 638.064 | 60.16 | 19.84 | 749952 | 749.952 | 57.2 | 22.8 | 861840 | 861.84 | 54.24 | 25.76 | 973728 | 973.728 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.32 | 31.68 | 1197504 | 1197.504 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.4 | 37.6 | 1421280 | 1421.28 | 40
12/4/20XX 10:00:00 AM | 0.41667 | 7 | 44.4 | 60.1 | 44.4 |  | 44.4 | 69.24 | 10.76 | 406728 | 406.728 | 66.48 | 13.52 | 511056 | 511.056 | 63.72 | 16.28 | 615384 | 615.384 | 60.96 | 19.04 | 719712 | 719.712 | 58.2 | 21.8 | 824040 | 824.04 | 55.44 | 24.56 | 928368 | 928.368 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.92 | 30.08 | 1137024 | 1137.024 | 47.16 | 32.84 | 1241352 | 1241.352 | 44.4 | 35.6 | 1345680 | 1345.68 | 45
12/4/20XX 11:00:00 AM | 0.45833 | 7 | 45.9 | 56.3 | 45.9 |  | 45.9 | 69.39 | 10.61 | 401058 | 401.058 | 66.78 | 13.22 | 499716 | 499.716 | 64.17 | 15.83 | 598374 | 598.374 | 61.56 | 18.44 | 697032 | 697.032 | 58.95 | 21.05 | 795690 | 795.69 | 56.34 | 23.66 | 894348 | 894.348 | 53.73 | 26.27 | 993006 | 993.006 | 51.12 | 28.88 | 1091664 | 1091.664 | 48.51 | 31.49 | 1190322 | 1190.322 | 45.9 | 34.1 | 1288980 | 1288.98 | 45
12/4/20XX 12:00:00 PM | 0.5 | 7 | 47.8 | 53 | 47.8 |  | 47.8 | 69.58 | 10.42 | 393876 | 393.876 | 67.16 | 12.84 | 485352 | 485.352 | 64.74 | 15.26 | 576828 | 576.828 | 62.32 | 17.68 | 668304 | 668.304 | 59.9 | 20.1 | 759780 | 759.78 | 57.48 | 22.52 | 851256 | 851.256 | 55.06 | 24.94 | 942732 | 942.732 | 52.64 | 27.36 | 1034208 | 1034.208 | 50.22 | 29.78 | 1125684 | 1125.684 | 47.8 | 32.2 | 1217160 | 1217.16 | 50
12/4/20XX 1:00:00 PM | 0.54167 | 7 | 48.3 | 50.9 | 48.3 |  | 48.3 | 69.63 | 10.37 | 391986 | 391.986 | 67.26 | 12.74 | 481572 | 481.572 | 64.89 | 15.11 | 571158 | 571.158 | 62.52 | 17.48 | 660744 | 660.744 | 60.15 | 19.85 | 750330 | 750.33 | 57.78 | 22.22 | 839916 | 839.916 | 55.41 | 24.59 | 929502 | 929.502 | 53.04 | 26.96 | 1019088 | 1019.088 | 50.67 | 29.33 | 1108674 | 1108.674 | 48.3 | 31.7 | 1198260 | 1198.26 | 50
12/4/20XX 2:00:00 PM | 0.58333 | 7 | 48.7 | 48.8 | 48.7 |  | 48.7 | 69.67 | 10.33 | 390474 | 390.474 | 67.34 | 12.66 | 478548 | 478.548 | 65.01 | 14.99 | 566622 | 566.622 | 62.68 | 17.32 | 654696 | 654.696 | 60.35 | 19.65 | 742770 | 742.77 | 58.02 | 21.98 | 830844 | 830.844 | 55.69 | 24.31 | 918918 | 918.918 | 53.36 | 26.64 | 1006992 | 1006.992 | 51.03 | 28.97 | 1095066 | 1095.066 | 48.7 | 31.3 | 1183140 | 1183.14 | 50
12/4/20XX 3:00:00 PM | 0.625 | 7 | 48.5 | 50.4 | 48.5 |  | 48.5 | 69.65 | 10.35 | 391230 | 391.23 | 67.3 | 12.7 | 480060 | 480.06 | 64.95 | 15.05 | 568890 | 568.89 | 62.6 | 17.4 | 657720 | 657.72 | 60.25 | 19.75 | 746550 | 746.55 | 57.9 | 22.1 | 835380 | 835.38 | 55.55 | 24.45 | 924210 | 924.21 | 53.2 | 26.8 | 1013040 | 1013.04 | 50.85 | 29.15 | 1101870 | 1101.87 | 48.5 | 31.5 | 1190700 | 1190.7 | 50
12/4/20XX 4:00:00 PM | 0.66667 | 7 | 47.7 | 52.4 | 47.7 |  | 47.7 | 69.57 | 10.43 | 394254 | 394.254 | 67.14 | 12.86 | 486108 | 486.108 | 64.71 | 15.29 | 577962 | 577.962 | 62.28 | 17.72 | 669816 | 669.816 | 59.85 | 20.15 | 761670 | 761.67 | 57.42 | 22.58 | 853524 | 853.524 | 54.99 | 25.01 | 945378 | 945.378 | 52.56 | 27.44 | 1037232 | 1037.232 | 50.13 | 29.87 | 1129086 | 1129.086 | 47.7 | 32.3 | 1220940 | 1220.94 | 50
12/4/20XX 5:00:00 PM | 0.70833 | 7 | 46.2 | 56 | 46.2 |  | 46.2 | 69.42 | 10.58 | 399924 | 399.924 | 66.84 | 13.16 | 497448 | 497.448 | 64.26 | 15.74 | 594972 | 594.972 | 61.68 | 18.32 | 692496 | 692.496 | 59.1 | 20.9 | 790020 | 790.02 | 56.52 | 23.48 | 887544 | 887.544 | 53.94 | 26.06 | 985068 | 985.068 | 51.36 | 28.64 | 1082592 | 1082.592 | 48.78 | 31.22 | 1180116 | 1180.116 | 46.2 | 33.8 | 1277640 | 1277.64 | 45
12/4/20XX 6:00:00 PM | 0.75 | 7 | 45.5 | 57.5 | 45.5 |  | 45.5 | 69.35 | 10.65 | 402570 | 402.57 | 66.7 | 13.3 | 502740 | 502.74 | 64.05 | 15.95 | 602910 | 602.91 | 61.4 | 18.6 | 703080 | 703.08 | 58.75 | 21.25 | 803250 | 803.25 | 56.1 | 23.9 | 903420 | 903.42 | 53.45 | 26.55 | 1003590 | 1003.59 | 50.8 | 29.2 | 1103760 | 1103.76 | 48.15 | 31.85 | 1203930 | 1203.93 | 45.5 | 34.5 | 1304100 | 1304.1 | 45
12/4/20XX 7:00:00 PM | 0.79167 | 7 | 45.3 | 59.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/4/20XX 8:00:00 PM | 0.83333 | 7 | 44.8 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/4/20XX 9:00:00 PM | 0.875 | 7 | 44.7 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/4/20XX 10:00:00 PM | 0.91667 | 7 | 44.1 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/4/20XX 11:00:00 PM | 0.95833 | 7 | 44.2 | 61.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/4/20XX 12:00:00 AM | 0 | 1 | 44.2 | 62.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/5/20XX 1:00:00 AM | 0.041667 | 1 | 44 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/5/20XX 2:00:00 AM | 0.083333 | 1 | 43.8 | 63.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/5/20XX 3:00:00 AM | 0.125 | 1 | 43.3 | 66.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/5/20XX 4:00:00 AM | 0.16667 | 1 | 42.9 | 70.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/5/20XX 5:00:00 AM | 0.20833 | 1 | 42.5 | 71.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/5/20XX 6:00:00 AM | 0.25 | 1 | 42.1 | 71.9 | 42.1 |  | 42.1 | 69.01 | 10.99 | 415422 | 415.422 | 66.02 | 13.98 | 528444 | 528.444 | 63.03 | 16.97 | 641466 | 641.466 | 60.04 | 19.96 | 754488 | 754.488 | 57.05 | 22.95 | 867510 | 867.51 | 54.06 | 25.94 | 980532 | 980.532 | 51.07 | 28.93 | 1093554 | 1093.554 | 48.08 | 31.92 | 1206576 | 1206.576 | 45.09 | 34.91 | 1319598 | 1319.598 | 42.1 | 37.9 | 1432620 | 1432.62 | 40
12/5/20XX 7:00:00 AM | 0.29167 | 1 | 42 | 72.8 | 42 |  | 42 | 69 | 11 | 415800 | 415.8 | 66 | 14 | 529200 | 529.2 | 63 | 17 | 642600 | 642.6 | 60 | 20 | 756000 | 756 | 57 | 23 | 869400 | 869.4 | 54 | 26 | 982800 | 982.8 | 51 | 29 | 1096200 | 1096.2 | 48 | 32 | 1209600 | 1209.6 | 45 | 35 | 1323000 | 1323 | 42 | 38 | 1436400 | 1436.4 | 40
12/5/20XX 8:00:00 AM | 0.33333 | 1 | 42.3 | 72 | 42.3 |  | 42.3 | 69.03 | 10.97 | 414666 | 414.666 | 66.06 | 13.94 | 526932 | 526.932 | 63.09 | 16.91 | 639198 | 639.198 | 60.12 | 19.88 | 751464 | 751.464 | 57.15 | 22.85 | 863730 | 863.73 | 54.18 | 25.82 | 975996 | 975.996 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.27 | 34.73 | 1312794 | 1312.794 | 42.3 | 37.7 | 1425060 | 1425.06 | 40
12/5/20XX 9:00:00 AM | 0.375 | 1 | 43.1 | 69.4 | 43.1 |  | 43.1 | 69.11 | 10.89 | 411642 | 411.642 | 66.22 | 13.78 | 520884 | 520.884 | 63.33 | 16.67 | 630126 | 630.126 | 60.44 | 19.56 | 739368 | 739.368 | 57.55 | 22.45 | 848610 | 848.61 | 54.66 | 25.34 | 957852 | 957.852 | 51.77 | 28.23 | 1067094 | 1067.094 | 48.88 | 31.12 | 1176336 | 1176.336 | 45.99 | 34.01 | 1285578 | 1285.578 | 43.1 | 36.9 | 1394820 | 1394.82 | 45
12/5/20XX 10:00:00 AM | 0.41667 | 1 | 44.7 | 67.7 | 44.7 |  | 44.7 | 69.27 | 10.73 | 405594 | 405.594 | 66.54 | 13.46 | 508788 | 508.788 | 63.81 | 16.19 | 611982 | 611.982 | 61.08 | 18.92 | 715176 | 715.176 | 58.35 | 21.65 | 818370 | 818.37 | 55.62 | 24.38 | 921564 | 921.564 | 52.89 | 27.11 | 1024758 | 1024.758 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.43 | 32.57 | 1231146 | 1231.146 | 44.7 | 35.3 | 1334340 | 1334.34 | 45
12/5/20XX 11:00:00 AM | 0.45833 | 1 | 45.6 | 68 | 45.6 |  | 45.6 | 69.36 | 10.64 | 402192 | 402.192 | 66.72 | 13.28 | 501984 | 501.984 | 64.08 | 15.92 | 601776 | 601.776 | 61.44 | 18.56 | 701568 | 701.568 | 58.8 | 21.2 | 801360 | 801.36 | 56.16 | 23.84 | 901152 | 901.152 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.88 | 29.12 | 1100736 | 1100.736 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.6 | 34.4 | 1300320 | 1300.32 | 45
12/5/20XX 12:00:00 PM | 0.5 | 1 | 46.4 | 66.6 | 46.4 |  | 46.4 | 69.44 | 10.56 | 399168 | 399.168 | 66.88 | 13.12 | 495936 | 495.936 | 64.32 | 15.68 | 592704 | 592.704 | 61.76 | 18.24 | 689472 | 689.472 | 59.2 | 20.8 | 786240 | 786.24 | 56.64 | 23.36 | 883008 | 883.008 | 54.08 | 25.92 | 979776 | 979.776 | 51.52 | 28.48 | 1076544 | 1076.544 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.4 | 33.6 | 1270080 | 1270.08 | 45
12/5/20XX 1:00:00 PM | 0.54167 | 1 | 47.1 | 65 | 47.1 |  | 47.1 | 69.51 | 10.49 | 396522 | 396.522 | 67.02 | 12.98 | 490644 | 490.644 | 64.53 | 15.47 | 584766 | 584.766 | 62.04 | 17.96 | 678888 | 678.888 | 59.55 | 20.45 | 773010 | 773.01 | 57.06 | 22.94 | 867132 | 867.132 | 54.57 | 25.43 | 961254 | 961.254 | 52.08 | 27.92 | 1055376 | 1055.376 | 49.59 | 30.41 | 1149498 | 1149.498 | 47.1 | 32.9 | 1243620 | 1243.62 | 45
12/5/20XX 2:00:00 PM | 0.58333 | 1 | 48.1 | 61.7 | 48.1 |  | 48.1 | 69.61 | 10.39 | 392742 | 392.742 | 67.22 | 12.78 | 483084 | 483.084 | 64.83 | 15.17 | 573426 | 573.426 | 62.44 | 17.56 | 663768 | 663.768 | 60.05 | 19.95 | 754110 | 754.11 | 57.66 | 22.34 | 844452 | 844.452 | 55.27 | 24.73 | 934794 | 934.794 | 52.88 | 27.12 | 1025136 | 1025.136 | 50.49 | 29.51 | 1115478 | 1115.478 | 48.1 | 31.9 | 1205820 | 1205.82 | 50
12/5/20XX 3:00:00 PM | 0.625 | 1 | 47.5 | 62.7 | 47.5 |  | 47.5 | 69.55 | 10.45 | 395010 | 395.01 | 67.1 | 12.9 | 487620 | 487.62 | 64.65 | 15.35 | 580230 | 580.23 | 62.2 | 17.8 | 672840 | 672.84 | 59.75 | 20.25 | 765450 | 765.45 | 57.3 | 22.7 | 858060 | 858.06 | 54.85 | 25.15 | 950670 | 950.67 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.95 | 30.05 | 1135890 | 1135.89 | 47.5 | 32.5 | 1228500 | 1228.5 | 45
12/5/20XX 4:00:00 PM | 0.66667 | 1 | 47.1 | 63.3 | 47.1 |  | 47.1 | 69.51 | 10.49 | 396522 | 396.522 | 67.02 | 12.98 | 490644 | 490.644 | 64.53 | 15.47 | 584766 | 584.766 | 62.04 | 17.96 | 678888 | 678.888 | 59.55 | 20.45 | 773010 | 773.01 | 57.06 | 22.94 | 867132 | 867.132 | 54.57 | 25.43 | 961254 | 961.254 | 52.08 | 27.92 | 1055376 | 1055.376 | 49.59 | 30.41 | 1149498 | 1149.498 | 47.1 | 32.9 | 1243620 | 1243.62 | 45
12/5/20XX 5:00:00 PM | 0.70833 | 1 | 46 | 65.7 | 46 |  | 46 | 69.4 | 10.6 | 400680 | 400.68 | 66.8 | 13.2 | 498960 | 498.96 | 64.2 | 15.8 | 597240 | 597.24 | 61.6 | 18.4 | 695520 | 695.52 | 59 | 21 | 793800 | 793.8 | 56.4 | 23.6 | 892080 | 892.08 | 53.8 | 26.2 | 990360 | 990.36 | 51.2 | 28.8 | 1088640 | 1088.64 | 48.6 | 31.4 | 1186920 | 1186.92 | 46 | 34 | 1285200 | 1285.2 | 45
12/5/20XX 6:00:00 PM | 0.75 | 1 | 45.4 | 67.1 | 45.4 |  | 45.4 | 69.34 | 10.66 | 402948 | 402.948 | 66.68 | 13.32 | 503496 | 503.496 | 64.02 | 15.98 | 604044 | 604.044 | 61.36 | 18.64 | 704592 | 704.592 | 58.7 | 21.3 | 805140 | 805.14 | 56.04 | 23.96 | 905688 | 905.688 | 53.38 | 26.62 | 1006236 | 1006.236 | 50.72 | 29.28 | 1106784 | 1106.784 | 48.06 | 31.94 | 1207332 | 1207.332 | 45.4 | 34.6 | 1307880 | 1307.88 | 45
12/5/20XX 7:00:00 PM | 0.79167 | 1 | 44.8 | 69.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/5/20XX 8:00:00 PM | 0.83333 | 1 | 44.8 | 71.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/5/20XX 9:00:00 PM | 0.875 | 1 | 44.8 | 72.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/5/20XX 10:00:00 PM | 0.91667 | 1 | 44.2 | 71.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/5/20XX 11:00:00 PM | 0.95833 | 1 | 43.9 | 71.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/5/20XX 12:00:00 AM | 0 | 2 | 43.9 | 70.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/6/20XX 1:00:00 AM | 0.041667 | 2 | 43.9 | 71 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/6/20XX 2:00:00 AM | 0.083333 | 2 | 43.2 | 72.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/6/20XX 3:00:00 AM | 0.125 | 2 | 42.7 | 72.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/6/20XX 4:00:00 AM | 0.16667 | 2 | 41.5 | 72.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/6/20XX 5:00:00 AM | 0.20833 | 2 | 41.5 | 70.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/6/20XX 6:00:00 AM | 0.25 | 2 | 41.2 | 70.1 | 41.2 |  | 41.2 | 68.92 | 11.08 | 418824 | 418.824 | 65.84 | 14.16 | 535248 | 535.248 | 62.76 | 17.24 | 651672 | 651.672 | 59.68 | 20.32 | 768096 | 768.096 | 56.6 | 23.4 | 884520 | 884.52 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.44 | 29.56 | 1117368 | 1117.368 | 47.36 | 32.64 | 1233792 | 1233.792 | 44.28 | 35.72 | 1350216 | 1350.216 | 41.2 | 38.8 | 1466640 | 1466.64 | 40
12/6/20XX 7:00:00 AM | 0.29167 | 2 | 40.2 | 70.3 | 40.2 |  | 40.2 | 68.82 | 11.18 | 422604 | 422.604 | 65.64 | 14.36 | 542808 | 542.808 | 62.46 | 17.54 | 663012 | 663.012 | 59.28 | 20.72 | 783216 | 783.216 | 56.1 | 23.9 | 903420 | 903.42 | 52.92 | 27.08 | 1023624 | 1023.624 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.56 | 33.44 | 1264032 | 1264.032 | 43.38 | 36.62 | 1384236 | 1384.236 | 40.2 | 39.8 | 1504440 | 1504.44 | 40
12/6/20XX 8:00:00 AM | 0.33333 | 2 | 40.1 | 70.5 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
12/6/20XX 9:00:00 AM | 0.375 | 2 | 40.7 | 67.5 | 40.7 |  | 40.7 | 68.87 | 11.13 | 420714 | 420.714 | 65.74 | 14.26 | 539028 | 539.028 | 62.61 | 17.39 | 657342 | 657.342 | 59.48 | 20.52 | 775656 | 775.656 | 56.35 | 23.65 | 893970 | 893.97 | 53.22 | 26.78 | 1012284 | 1012.284 | 50.09 | 29.91 | 1130598 | 1130.598 | 46.96 | 33.04 | 1248912 | 1248.912 | 43.83 | 36.17 | 1367226 | 1367.226 | 40.7 | 39.3 | 1485540 | 1485.54 | 40
12/6/20XX 10:00:00 AM | 0.41667 | 2 | 41.8 | 63.9 | 41.8 |  | 41.8 | 68.98 | 11.02 | 416556 | 416.556 | 65.96 | 14.04 | 530712 | 530.712 | 62.94 | 17.06 | 644868 | 644.868 | 59.92 | 20.08 | 759024 | 759.024 | 56.9 | 23.1 | 873180 | 873.18 | 53.88 | 26.12 | 987336 | 987.336 | 50.86 | 29.14 | 1101492 | 1101.492 | 47.84 | 32.16 | 1215648 | 1215.648 | 44.82 | 35.18 | 1329804 | 1329.804 | 41.8 | 38.2 | 1443960 | 1443.96 | 40
12/6/20XX 11:00:00 AM | 0.45833 | 2 | 43.1 | 61.9 | 43.1 |  | 43.1 | 69.11 | 10.89 | 411642 | 411.642 | 66.22 | 13.78 | 520884 | 520.884 | 63.33 | 16.67 | 630126 | 630.126 | 60.44 | 19.56 | 739368 | 739.368 | 57.55 | 22.45 | 848610 | 848.61 | 54.66 | 25.34 | 957852 | 957.852 | 51.77 | 28.23 | 1067094 | 1067.094 | 48.88 | 31.12 | 1176336 | 1176.336 | 45.99 | 34.01 | 1285578 | 1285.578 | 43.1 | 36.9 | 1394820 | 1394.82 | 45
12/6/20XX 12:00:00 PM | 0.5 | 2 | 43.4 | 60.8 | 43.4 |  | 43.4 | 69.14 | 10.86 | 410508 | 410.508 | 66.28 | 13.72 | 518616 | 518.616 | 63.42 | 16.58 | 626724 | 626.724 | 60.56 | 19.44 | 734832 | 734.832 | 57.7 | 22.3 | 842940 | 842.94 | 54.84 | 25.16 | 951048 | 951.048 | 51.98 | 28.02 | 1059156 | 1059.156 | 49.12 | 30.88 | 1167264 | 1167.264 | 46.26 | 33.74 | 1275372 | 1275.372 | 43.4 | 36.6 | 1383480 | 1383.48 | 45
12/6/20XX 1:00:00 PM | 0.54167 | 2 | 44.1 | 59.7 | 44.1 |  | 44.1 | 69.21 | 10.79 | 407862 | 407.862 | 66.42 | 13.58 | 513324 | 513.324 | 63.63 | 16.37 | 618786 | 618.786 | 60.84 | 19.16 | 724248 | 724.248 | 58.05 | 21.95 | 829710 | 829.71 | 55.26 | 24.74 | 935172 | 935.172 | 52.47 | 27.53 | 1040634 | 1040.634 | 49.68 | 30.32 | 1146096 | 1146.096 | 46.89 | 33.11 | 1251558 | 1251.558 | 44.1 | 35.9 | 1357020 | 1357.02 | 45
12/6/20XX 2:00:00 PM | 0.58333 | 2 | 44.3 | 58.3 | 44.3 |  | 44.3 | 69.23 | 10.77 | 407106 | 407.106 | 66.46 | 13.54 | 511812 | 511.812 | 63.69 | 16.31 | 616518 | 616.518 | 60.92 | 19.08 | 721224 | 721.224 | 58.15 | 21.85 | 825930 | 825.93 | 55.38 | 24.62 | 930636 | 930.636 | 52.61 | 27.39 | 1035342 | 1035.342 | 49.84 | 30.16 | 1140048 | 1140.048 | 47.07 | 32.93 | 1244754 | 1244.754 | 44.3 | 35.7 | 1349460 | 1349.46 | 45
12/6/20XX 3:00:00 PM | 0.625 | 2 | 44.4 | 58 | 44.4 |  | 44.4 | 69.24 | 10.76 | 406728 | 406.728 | 66.48 | 13.52 | 511056 | 511.056 | 63.72 | 16.28 | 615384 | 615.384 | 60.96 | 19.04 | 719712 | 719.712 | 58.2 | 21.8 | 824040 | 824.04 | 55.44 | 24.56 | 928368 | 928.368 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.92 | 30.08 | 1137024 | 1137.024 | 47.16 | 32.84 | 1241352 | 1241.352 | 44.4 | 35.6 | 1345680 | 1345.68 | 45
12/6/20XX 4:00:00 PM | 0.66667 | 2 | 44 | 59.2 | 44 |  | 44 | 69.2 | 10.8 | 408240 | 408.24 | 66.4 | 13.6 | 514080 | 514.08 | 63.6 | 16.4 | 619920 | 619.92 | 60.8 | 19.2 | 725760 | 725.76 | 58 | 22 | 831600 | 831.6 | 55.2 | 24.8 | 937440 | 937.44 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.6 | 30.4 | 1149120 | 1149.12 | 46.8 | 33.2 | 1254960 | 1254.96 | 44 | 36 | 1360800 | 1360.8 | 45
12/6/20XX 5:00:00 PM | 0.70833 | 2 | 43.7 | 59.2 | 43.7 |  | 43.7 | 69.17 | 10.83 | 409374 | 409.374 | 66.34 | 13.66 | 516348 | 516.348 | 63.51 | 16.49 | 623322 | 623.322 | 60.68 | 19.32 | 730296 | 730.296 | 57.85 | 22.15 | 837270 | 837.27 | 55.02 | 24.98 | 944244 | 944.244 | 52.19 | 27.81 | 1051218 | 1051.218 | 49.36 | 30.64 | 1158192 | 1158.192 | 46.53 | 33.47 | 1265166 | 1265.166 | 43.7 | 36.3 | 1372140 | 1372.14 | 45
12/6/20XX 6:00:00 PM | 0.75 | 2 | 43.2 | 60.4 | 43.2 |  | 43.2 | 69.12 | 10.88 | 411264 | 411.264 | 66.24 | 13.76 | 520128 | 520.128 | 63.36 | 16.64 | 628992 | 628.992 | 60.48 | 19.52 | 737856 | 737.856 | 57.6 | 22.4 | 846720 | 846.72 | 54.72 | 25.28 | 955584 | 955.584 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.08 | 33.92 | 1282176 | 1282.176 | 43.2 | 36.8 | 1391040 | 1391.04 | 45
12/6/20XX 7:00:00 PM | 0.79167 | 2 | 42.4 | 63 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/6/20XX 8:00:00 PM | 0.83333 | 2 | 41.8 | 64.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/6/20XX 9:00:00 PM | 0.875 | 2 | 41.3 | 66.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/6/20XX 10:00:00 PM | 0.91667 | 2 | 41.4 | 66.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/6/20XX 11:00:00 PM | 0.95833 | 2 | 40.6 | 67 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/6/20XX 12:00:00 AM | 0 | 3 | 40.5 | 68.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/7/20XX 1:00:00 AM | 0.041667 | 3 | 40 | 70.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/7/20XX 2:00:00 AM | 0.083333 | 3 | 40 | 71.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/7/20XX 3:00:00 AM | 0.125 | 3 | 39.7 | 71 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/7/20XX 4:00:00 AM | 0.16667 | 3 | 39.7 | 69.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/7/20XX 5:00:00 AM | 0.20833 | 3 | 39.4 | 69.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/7/20XX 6:00:00 AM | 0.25 | 3 | 39.5 | 69.8 | 39.5 |  | 39.5 | 68.75 | 11.25 | 425250 | 425.25 | 65.5 | 14.5 | 548100 | 548.1 | 62.25 | 17.75 | 670950 | 670.95 | 59 | 21 | 793800 | 793.8 | 55.75 | 24.25 | 916650 | 916.65 | 52.5 | 27.5 | 1039500 | 1039.5 | 49.25 | 30.75 | 1162350 | 1162.35 | 46 | 34 | 1285200 | 1285.2 | 42.75 | 37.25 | 1408050 | 1408.05 | 39.5 | 40.5 | 1530900 | 1530.9 | 40
12/7/20XX 7:00:00 AM | 0.29167 | 3 | 39.1 | 70.1 | 39.1 |  | 39.1 | 68.71 | 11.29 | 426762 | 426.762 | 65.42 | 14.58 | 551124 | 551.124 | 62.13 | 17.87 | 675486 | 675.486 | 58.84 | 21.16 | 799848 | 799.848 | 55.55 | 24.45 | 924210 | 924.21 | 52.26 | 27.74 | 1048572 | 1048.572 | 48.97 | 31.03 | 1172934 | 1172.934 | 45.68 | 34.32 | 1297296 | 1297.296 | 42.39 | 37.61 | 1421658 | 1421.658 | 39.1 | 40.9 | 1546020 | 1546.02 | 40
12/7/20XX 8:00:00 AM | 0.33333 | 3 | 38.9 | 69.2 | 38.9 |  | 38.9 | 68.69 | 11.31 | 427518 | 427.518 | 65.38 | 14.62 | 552636 | 552.636 | 62.07 | 17.93 | 677754 | 677.754 | 58.76 | 21.24 | 802872 | 802.872 | 55.45 | 24.55 | 927990 | 927.99 | 52.14 | 27.86 | 1053108 | 1053.108 | 48.83 | 31.17 | 1178226 | 1178.226 | 45.52 | 34.48 | 1303344 | 1303.344 | 42.21 | 37.79 | 1428462 | 1428.462 | 38.9 | 41.1 | 1553580 | 1553.58 | 40
12/7/20XX 9:00:00 AM | 0.375 | 3 | 39.3 | 67.5 | 39.3 |  | 39.3 | 68.73 | 11.27 | 426006 | 426.006 | 65.46 | 14.54 | 549612 | 549.612 | 62.19 | 17.81 | 673218 | 673.218 | 58.92 | 21.08 | 796824 | 796.824 | 55.65 | 24.35 | 920430 | 920.43 | 52.38 | 27.62 | 1044036 | 1044.036 | 49.11 | 30.89 | 1167642 | 1167.642 | 45.84 | 34.16 | 1291248 | 1291.248 | 42.57 | 37.43 | 1414854 | 1414.854 | 39.3 | 40.7 | 1538460 | 1538.46 | 40
12/7/20XX 10:00:00 AM | 0.41667 | 3 | 40.1 | 63.4 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
12/7/20XX 11:00:00 AM | 0.45833 | 3 | 40.9 | 58.9 | 40.9 |  | 40.9 | 68.89 | 11.11 | 419958 | 419.958 | 65.78 | 14.22 | 537516 | 537.516 | 62.67 | 17.33 | 655074 | 655.074 | 59.56 | 20.44 | 772632 | 772.632 | 56.45 | 23.55 | 890190 | 890.19 | 53.34 | 26.66 | 1007748 | 1007.748 | 50.23 | 29.77 | 1125306 | 1125.306 | 47.12 | 32.88 | 1242864 | 1242.864 | 44.01 | 35.99 | 1360422 | 1360.422 | 40.9 | 39.1 | 1477980 | 1477.98 | 40
12/7/20XX 12:00:00 PM | 0.5 | 3 | 41 | 58.6 | 41 |  | 41 | 68.9 | 11.1 | 419580 | 419.58 | 65.8 | 14.2 | 536760 | 536.76 | 62.7 | 17.3 | 653940 | 653.94 | 59.6 | 20.4 | 771120 | 771.12 | 56.5 | 23.5 | 888300 | 888.3 | 53.4 | 26.6 | 1005480 | 1005.48 | 50.3 | 29.7 | 1122660 | 1122.66 | 47.2 | 32.8 | 1239840 | 1239.84 | 44.1 | 35.9 | 1357020 | 1357.02 | 41 | 39 | 1474200 | 1474.2 | 40
12/7/20XX 1:00:00 PM | 0.54167 | 3 | 42.3 | 57.7 | 42.3 |  | 42.3 | 69.03 | 10.97 | 414666 | 414.666 | 66.06 | 13.94 | 526932 | 526.932 | 63.09 | 16.91 | 639198 | 639.198 | 60.12 | 19.88 | 751464 | 751.464 | 57.15 | 22.85 | 863730 | 863.73 | 54.18 | 25.82 | 975996 | 975.996 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.27 | 34.73 | 1312794 | 1312.794 | 42.3 | 37.7 | 1425060 | 1425.06 | 40
12/7/20XX 2:00:00 PM | 0.58333 | 3 | 42.4 | 55.7 | 42.4 |  | 42.4 | 69.04 | 10.96 | 414288 | 414.288 | 66.08 | 13.92 | 526176 | 526.176 | 63.12 | 16.88 | 638064 | 638.064 | 60.16 | 19.84 | 749952 | 749.952 | 57.2 | 22.8 | 861840 | 861.84 | 54.24 | 25.76 | 973728 | 973.728 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.32 | 31.68 | 1197504 | 1197.504 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.4 | 37.6 | 1421280 | 1421.28 | 40
12/7/20XX 3:00:00 PM | 0.625 | 3 | 42.6 | 54.1 | 42.6 |  | 42.6 | 69.06 | 10.94 | 413532 | 413.532 | 66.12 | 13.88 | 524664 | 524.664 | 63.18 | 16.82 | 635796 | 635.796 | 60.24 | 19.76 | 746928 | 746.928 | 57.3 | 22.7 | 858060 | 858.06 | 54.36 | 25.64 | 969192 | 969.192 | 51.42 | 28.58 | 1080324 | 1080.324 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.54 | 34.46 | 1302588 | 1302.588 | 42.6 | 37.4 | 1413720 | 1413.72 | 45
12/7/20XX 4:00:00 PM | 0.66667 | 3 | 41.8 | 54.4 | 41.8 |  | 41.8 | 68.98 | 11.02 | 416556 | 416.556 | 65.96 | 14.04 | 530712 | 530.712 | 62.94 | 17.06 | 644868 | 644.868 | 59.92 | 20.08 | 759024 | 759.024 | 56.9 | 23.1 | 873180 | 873.18 | 53.88 | 26.12 | 987336 | 987.336 | 50.86 | 29.14 | 1101492 | 1101.492 | 47.84 | 32.16 | 1215648 | 1215.648 | 44.82 | 35.18 | 1329804 | 1329.804 | 41.8 | 38.2 | 1443960 | 1443.96 | 40
12/7/20XX 5:00:00 PM | 0.70833 | 3 | 40.9 | 56 | 40.9 |  | 40.9 | 68.89 | 11.11 | 419958 | 419.958 | 65.78 | 14.22 | 537516 | 537.516 | 62.67 | 17.33 | 655074 | 655.074 | 59.56 | 20.44 | 772632 | 772.632 | 56.45 | 23.55 | 890190 | 890.19 | 53.34 | 26.66 | 1007748 | 1007.748 | 50.23 | 29.77 | 1125306 | 1125.306 | 47.12 | 32.88 | 1242864 | 1242.864 | 44.01 | 35.99 | 1360422 | 1360.422 | 40.9 | 39.1 | 1477980 | 1477.98 | 40
12/7/20XX 6:00:00 PM | 0.75 | 3 | 40.5 | 57.4 | 40.5 |  | 40.5 | 68.85 | 11.15 | 421470 | 421.47 | 65.7 | 14.3 | 540540 | 540.54 | 62.55 | 17.45 | 659610 | 659.61 | 59.4 | 20.6 | 778680 | 778.68 | 56.25 | 23.75 | 897750 | 897.75 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.95 | 30.05 | 1135890 | 1135.89 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.65 | 36.35 | 1374030 | 1374.03 | 40.5 | 39.5 | 1493100 | 1493.1 | 40
12/7/20XX 7:00:00 PM | 0.79167 | 3 | 40.6 | 56.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/7/20XX 8:00:00 PM | 0.83333 | 3 | 40 | 56.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/7/20XX 9:00:00 PM | 0.875 | 3 | 39.3 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/7/20XX 10:00:00 PM | 0.91667 | 3 | 38.6 | 60.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/7/20XX 11:00:00 PM | 0.95833 | 3 | 37.8 | 60.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/7/20XX 12:00:00 AM | 0 | 4 | 37.1 | 61.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/8/20XX 1:00:00 AM | 0.041667 | 4 | 36.3 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/8/20XX 2:00:00 AM | 0.083333 | 4 | 35.5 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/8/20XX 3:00:00 AM | 0.125 | 4 | 35.1 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/8/20XX 4:00:00 AM | 0.16667 | 4 | 34.9 | 60.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/8/20XX 5:00:00 AM | 0.20833 | 4 | 34.2 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/8/20XX 6:00:00 AM | 0.25 | 4 | 34.1 | 59.8 | 34.1 |  | 34.1 | 68.21 | 11.79 | 445662 | 445.662 | 64.42 | 15.58 | 588924 | 588.924 | 60.63 | 19.37 | 732186 | 732.186 | 56.84 | 23.16 | 875448 | 875.448 | 53.05 | 26.95 | 1018710 | 1018.71 | 49.26 | 30.74 | 1161972 | 1161.972 | 45.47 | 34.53 | 1305234 | 1305.234 | 41.68 | 38.32 | 1448496 | 1448.496 | 37.89 | 42.11 | 1591758 | 1591.758 | 34.1 | 45.9 | 1735020 | 1735.02 | 35
12/8/20XX 7:00:00 AM | 0.29167 | 4 | 33.8 | 59.9 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
12/8/20XX 8:00:00 AM | 0.33333 | 4 | 34.1 | 61.3 | 34.1 |  | 34.1 | 68.21 | 11.79 | 445662 | 445.662 | 64.42 | 15.58 | 588924 | 588.924 | 60.63 | 19.37 | 732186 | 732.186 | 56.84 | 23.16 | 875448 | 875.448 | 53.05 | 26.95 | 1018710 | 1018.71 | 49.26 | 30.74 | 1161972 | 1161.972 | 45.47 | 34.53 | 1305234 | 1305.234 | 41.68 | 38.32 | 1448496 | 1448.496 | 37.89 | 42.11 | 1591758 | 1591.758 | 34.1 | 45.9 | 1735020 | 1735.02 | 35
12/8/20XX 9:00:00 AM | 0.375 | 4 | 35.2 | 60.9 | 35.2 |  | 35.2 | 68.32 | 11.68 | 441504 | 441.504 | 64.64 | 15.36 | 580608 | 580.608 | 60.96 | 19.04 | 719712 | 719.712 | 57.28 | 22.72 | 858816 | 858.816 | 53.6 | 26.4 | 997920 | 997.92 | 49.92 | 30.08 | 1137024 | 1137.024 | 46.24 | 33.76 | 1276128 | 1276.128 | 42.56 | 37.44 | 1415232 | 1415.232 | 38.88 | 41.12 | 1554336 | 1554.336 | 35.2 | 44.8 | 1693440 | 1693.44 | 35
12/8/20XX 10:00:00 AM | 0.41667 | 4 | 36.2 | 57.5 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
12/8/20XX 11:00:00 AM | 0.45833 | 4 | 37.3 | 54.7 | 37.3 |  | 37.3 | 68.53 | 11.47 | 433566 | 433.566 | 65.06 | 14.94 | 564732 | 564.732 | 61.59 | 18.41 | 695898 | 695.898 | 58.12 | 21.88 | 827064 | 827.064 | 54.65 | 25.35 | 958230 | 958.23 | 51.18 | 28.82 | 1089396 | 1089.396 | 47.71 | 32.29 | 1220562 | 1220.562 | 44.24 | 35.76 | 1351728 | 1351.728 | 40.77 | 39.23 | 1482894 | 1482.894 | 37.3 | 42.7 | 1614060 | 1614.06 | 35
12/8/20XX 12:00:00 PM | 0.5 | 4 | 38.8 | 52.2 | 38.8 |  | 38.8 | 68.68 | 11.32 | 427896 | 427.896 | 65.36 | 14.64 | 553392 | 553.392 | 62.04 | 17.96 | 678888 | 678.888 | 58.72 | 21.28 | 804384 | 804.384 | 55.4 | 24.6 | 929880 | 929.88 | 52.08 | 27.92 | 1055376 | 1055.376 | 48.76 | 31.24 | 1180872 | 1180.872 | 45.44 | 34.56 | 1306368 | 1306.368 | 42.12 | 37.88 | 1431864 | 1431.864 | 38.8 | 41.2 | 1557360 | 1557.36 | 40
12/8/20XX 1:00:00 PM | 0.54167 | 4 | 39.7 | 51.5 | 39.7 |  | 39.7 | 68.77 | 11.23 | 424494 | 424.494 | 65.54 | 14.46 | 546588 | 546.588 | 62.31 | 17.69 | 668682 | 668.682 | 59.08 | 20.92 | 790776 | 790.776 | 55.85 | 24.15 | 912870 | 912.87 | 52.62 | 27.38 | 1034964 | 1034.964 | 49.39 | 30.61 | 1157058 | 1157.058 | 46.16 | 33.84 | 1279152 | 1279.152 | 42.93 | 37.07 | 1401246 | 1401.246 | 39.7 | 40.3 | 1523340 | 1523.34 | 40
12/8/20XX 2:00:00 PM | 0.58333 | 4 | 40.2 | 51.3 | 40.2 |  | 40.2 | 68.82 | 11.18 | 422604 | 422.604 | 65.64 | 14.36 | 542808 | 542.808 | 62.46 | 17.54 | 663012 | 663.012 | 59.28 | 20.72 | 783216 | 783.216 | 56.1 | 23.9 | 903420 | 903.42 | 52.92 | 27.08 | 1023624 | 1023.624 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.56 | 33.44 | 1264032 | 1264.032 | 43.38 | 36.62 | 1384236 | 1384.236 | 40.2 | 39.8 | 1504440 | 1504.44 | 40
12/8/20XX 3:00:00 PM | 0.625 | 4 | 40.1 | 51.9 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
12/8/20XX 4:00:00 PM | 0.66667 | 4 | 40.1 | 52.9 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
12/8/20XX 5:00:00 PM | 0.70833 | 4 | 38.9 | 56.7 | 38.9 |  | 38.9 | 68.69 | 11.31 | 427518 | 427.518 | 65.38 | 14.62 | 552636 | 552.636 | 62.07 | 17.93 | 677754 | 677.754 | 58.76 | 21.24 | 802872 | 802.872 | 55.45 | 24.55 | 927990 | 927.99 | 52.14 | 27.86 | 1053108 | 1053.108 | 48.83 | 31.17 | 1178226 | 1178.226 | 45.52 | 34.48 | 1303344 | 1303.344 | 42.21 | 37.79 | 1428462 | 1428.462 | 38.9 | 41.1 | 1553580 | 1553.58 | 40
12/8/20XX 6:00:00 PM | 0.75 | 4 | 38.4 | 57.7 | 38.4 |  | 38.4 | 68.64 | 11.36 | 429408 | 429.408 | 65.28 | 14.72 | 556416 | 556.416 | 61.92 | 18.08 | 683424 | 683.424 | 58.56 | 21.44 | 810432 | 810.432 | 55.2 | 24.8 | 937440 | 937.44 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.76 | 38.24 | 1445472 | 1445.472 | 38.4 | 41.6 | 1572480 | 1572.48 | 40
12/8/20XX 7:00:00 PM | 0.79167 | 4 | 38.1 | 58.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/8/20XX 8:00:00 PM | 0.83333 | 4 | 38.1 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/8/20XX 9:00:00 PM | 0.875 | 4 | 38 | 60.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/8/20XX 10:00:00 PM | 0.91667 | 4 | 37.6 | 62.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/8/20XX 11:00:00 PM | 0.95833 | 4 | 37.4 | 63.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/8/20XX 12:00:00 AM | 0 | 5 | 37.2 | 64.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/9/20XX 1:00:00 AM | 0.041667 | 5 | 36.5 | 67.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/9/20XX 2:00:00 AM | 0.083333 | 5 | 35.9 | 68.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/9/20XX 3:00:00 AM | 0.125 | 5 | 35.8 | 70.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/9/20XX 4:00:00 AM | 0.16667 | 5 | 36 | 70.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/9/20XX 5:00:00 AM | 0.20833 | 5 | 35.9 | 70.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/9/20XX 6:00:00 AM | 0.25 | 5 | 36.1 | 70 | 36.1 |  | 36.1 | 68.41 | 11.59 | 438102 | 438.102 | 64.82 | 15.18 | 573804 | 573.804 | 61.23 | 18.77 | 709506 | 709.506 | 57.64 | 22.36 | 845208 | 845.208 | 54.05 | 25.95 | 980910 | 980.91 | 50.46 | 29.54 | 1116612 | 1116.612 | 46.87 | 33.13 | 1252314 | 1252.314 | 43.28 | 36.72 | 1388016 | 1388.016 | 39.69 | 40.31 | 1523718 | 1523.718 | 36.1 | 43.9 | 1659420 | 1659.42 | 35
12/9/20XX 7:00:00 AM | 0.29167 | 5 | 36.3 | 69.6 | 36.3 |  | 36.3 | 68.43 | 11.57 | 437346 | 437.346 | 64.86 | 15.14 | 572292 | 572.292 | 61.29 | 18.71 | 707238 | 707.238 | 57.72 | 22.28 | 842184 | 842.184 | 54.15 | 25.85 | 977130 | 977.13 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.01 | 32.99 | 1247022 | 1247.022 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.87 | 40.13 | 1516914 | 1516.914 | 36.3 | 43.7 | 1651860 | 1651.86 | 35
12/9/20XX 8:00:00 AM | 0.33333 | 5 | 36.5 | 68.6 | 36.5 |  | 36.5 | 68.45 | 11.55 | 436590 | 436.59 | 64.9 | 15.1 | 570780 | 570.78 | 61.35 | 18.65 | 704970 | 704.97 | 57.8 | 22.2 | 839160 | 839.16 | 54.25 | 25.75 | 973350 | 973.35 | 50.7 | 29.3 | 1107540 | 1107.54 | 47.15 | 32.85 | 1241730 | 1241.73 | 43.6 | 36.4 | 1375920 | 1375.92 | 40.05 | 39.95 | 1510110 | 1510.11 | 36.5 | 43.5 | 1644300 | 1644.3 | 35
12/9/20XX 9:00:00 AM | 0.375 | 5 | 37.1 | 67.3 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
12/9/20XX 10:00:00 AM | 0.41667 | 5 | 37.8 | 68 | 37.8 |  | 37.8 | 68.58 | 11.42 | 431676 | 431.676 | 65.16 | 14.84 | 560952 | 560.952 | 61.74 | 18.26 | 690228 | 690.228 | 58.32 | 21.68 | 819504 | 819.504 | 54.9 | 25.1 | 948780 | 948.78 | 51.48 | 28.52 | 1078056 | 1078.056 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.22 | 38.78 | 1465884 | 1465.884 | 37.8 | 42.2 | 1595160 | 1595.16 | 40
12/9/20XX 11:00:00 AM | 0.45833 | 5 | 38.2 | 67.7 | 38.2 |  | 38.2 | 68.62 | 11.38 | 430164 | 430.164 | 65.24 | 14.76 | 557928 | 557.928 | 61.86 | 18.14 | 685692 | 685.692 | 58.48 | 21.52 | 813456 | 813.456 | 55.1 | 24.9 | 941220 | 941.22 | 51.72 | 28.28 | 1068984 | 1068.984 | 48.34 | 31.66 | 1196748 | 1196.748 | 44.96 | 35.04 | 1324512 | 1324.512 | 41.58 | 38.42 | 1452276 | 1452.276 | 38.2 | 41.8 | 1580040 | 1580.04 | 40
12/9/20XX 12:00:00 PM | 0.5 | 5 | 39.2 | 65.9 | 39.2 |  | 39.2 | 68.72 | 11.28 | 426384 | 426.384 | 65.44 | 14.56 | 550368 | 550.368 | 62.16 | 17.84 | 674352 | 674.352 | 58.88 | 21.12 | 798336 | 798.336 | 55.6 | 24.4 | 922320 | 922.32 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.04 | 30.96 | 1170288 | 1170.288 | 45.76 | 34.24 | 1294272 | 1294.272 | 42.48 | 37.52 | 1418256 | 1418.256 | 39.2 | 40.8 | 1542240 | 1542.24 | 40
12/9/20XX 1:00:00 PM | 0.54167 | 5 | 40.3 | 66.4 | 40.3 |  | 40.3 | 68.83 | 11.17 | 422226 | 422.226 | 65.66 | 14.34 | 542052 | 542.052 | 62.49 | 17.51 | 661878 | 661.878 | 59.32 | 20.68 | 781704 | 781.704 | 56.15 | 23.85 | 901530 | 901.53 | 52.98 | 27.02 | 1021356 | 1021.356 | 49.81 | 30.19 | 1141182 | 1141.182 | 46.64 | 33.36 | 1261008 | 1261.008 | 43.47 | 36.53 | 1380834 | 1380.834 | 40.3 | 39.7 | 1500660 | 1500.66 | 40
12/9/20XX 2:00:00 PM | 0.58333 | 5 | 40.9 | 66.3 | 40.9 |  | 40.9 | 68.89 | 11.11 | 419958 | 419.958 | 65.78 | 14.22 | 537516 | 537.516 | 62.67 | 17.33 | 655074 | 655.074 | 59.56 | 20.44 | 772632 | 772.632 | 56.45 | 23.55 | 890190 | 890.19 | 53.34 | 26.66 | 1007748 | 1007.748 | 50.23 | 29.77 | 1125306 | 1125.306 | 47.12 | 32.88 | 1242864 | 1242.864 | 44.01 | 35.99 | 1360422 | 1360.422 | 40.9 | 39.1 | 1477980 | 1477.98 | 40
12/9/20XX 3:00:00 PM | 0.625 | 5 | 40.9 | 66.7 | 40.9 |  | 40.9 | 68.89 | 11.11 | 419958 | 419.958 | 65.78 | 14.22 | 537516 | 537.516 | 62.67 | 17.33 | 655074 | 655.074 | 59.56 | 20.44 | 772632 | 772.632 | 56.45 | 23.55 | 890190 | 890.19 | 53.34 | 26.66 | 1007748 | 1007.748 | 50.23 | 29.77 | 1125306 | 1125.306 | 47.12 | 32.88 | 1242864 | 1242.864 | 44.01 | 35.99 | 1360422 | 1360.422 | 40.9 | 39.1 | 1477980 | 1477.98 | 40
12/9/20XX 4:00:00 PM | 0.66667 | 5 | 40.4 | 67.8 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
12/9/20XX 5:00:00 PM | 0.70833 | 5 | 40.4 | 69.7 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
12/9/20XX 6:00:00 PM | 0.75 | 5 | 40 | 70 | 40 |  | 40 | 68.8 | 11.2 | 423360 | 423.36 | 65.6 | 14.4 | 544320 | 544.32 | 62.4 | 17.6 | 665280 | 665.28 | 59.2 | 20.8 | 786240 | 786.24 | 56 | 24 | 907200 | 907.2 | 52.8 | 27.2 | 1028160 | 1028.16 | 49.6 | 30.4 | 1149120 | 1149.12 | 46.4 | 33.6 | 1270080 | 1270.08 | 43.2 | 36.8 | 1391040 | 1391.04 | 40 | 40 | 1512000 | 1512 | 40
12/9/20XX 7:00:00 PM | 0.79167 | 5 | 39.9 | 70.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/9/20XX 8:00:00 PM | 0.83333 | 5 | 38.1 | 79.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/9/20XX 9:00:00 PM | 0.875 | 5 | 40.2 | 68.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/9/20XX 10:00:00 PM | 0.91667 | 5 | 39.7 | 68.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/9/20XX 11:00:00 PM | 0.95833 | 5 | 38.9 | 70.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/9/20XX 12:00:00 AM | 0 | 6 | 38.2 | 71.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/10/20XX 1:00:00 AM | 0.041667 | 6 | 38.2 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/10/20XX 2:00:00 AM | 0.083333 | 6 | 37.9 | 69 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/10/20XX 3:00:00 AM | 0.125 | 6 | 37.8 | 68.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/10/20XX 4:00:00 AM | 0.16667 | 6 | 37.4 | 69 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/10/20XX 5:00:00 AM | 0.20833 | 6 | 36.9 | 70.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/10/20XX 6:00:00 AM | 0.25 | 6 | 37.1 | 67.8 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
12/10/20XX 7:00:00 AM | 0.29167 | 6 | 37.1 | 68.3 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
12/10/20XX 8:00:00 AM | 0.33333 | 6 | 36.7 | 69.6 | 36.7 |  | 36.7 | 68.47 | 11.53 | 435834 | 435.834 | 64.94 | 15.06 | 569268 | 569.268 | 61.41 | 18.59 | 702702 | 702.702 | 57.88 | 22.12 | 836136 | 836.136 | 54.35 | 25.65 | 969570 | 969.57 | 50.82 | 29.18 | 1103004 | 1103.004 | 47.29 | 32.71 | 1236438 | 1236.438 | 43.76 | 36.24 | 1369872 | 1369.872 | 40.23 | 39.77 | 1503306 | 1503.306 | 36.7 | 43.3 | 1636740 | 1636.74 | 35
12/10/20XX 9:00:00 AM | 0.375 | 6 | 37 | 69.5 | 37 |  | 37 | 68.5 | 11.5 | 434700 | 434.7 | 65 | 15 | 567000 | 567 | 61.5 | 18.5 | 699300 | 699.3 | 58 | 22 | 831600 | 831.6 | 54.5 | 25.5 | 963900 | 963.9 | 51 | 29 | 1096200 | 1096.2 | 47.5 | 32.5 | 1228500 | 1228.5 | 44 | 36 | 1360800 | 1360.8 | 40.5 | 39.5 | 1493100 | 1493.1 | 37 | 43 | 1625400 | 1625.4 | 35
12/10/20XX 10:00:00 AM | 0.41667 | 6 | 38.5 | 67.4 | 38.5 |  | 38.5 | 68.65 | 11.35 | 429030 | 429.03 | 65.3 | 14.7 | 555660 | 555.66 | 61.95 | 18.05 | 682290 | 682.29 | 58.6 | 21.4 | 808920 | 808.92 | 55.25 | 24.75 | 935550 | 935.55 | 51.9 | 28.1 | 1062180 | 1062.18 | 48.55 | 31.45 | 1188810 | 1188.81 | 45.2 | 34.8 | 1315440 | 1315.44 | 41.85 | 38.15 | 1442070 | 1442.07 | 38.5 | 41.5 | 1568700 | 1568.7 | 40
12/10/20XX 11:00:00 AM | 0.45833 | 6 | 39.7 | 66.4 | 39.7 |  | 39.7 | 68.77 | 11.23 | 424494 | 424.494 | 65.54 | 14.46 | 546588 | 546.588 | 62.31 | 17.69 | 668682 | 668.682 | 59.08 | 20.92 | 790776 | 790.776 | 55.85 | 24.15 | 912870 | 912.87 | 52.62 | 27.38 | 1034964 | 1034.964 | 49.39 | 30.61 | 1157058 | 1157.058 | 46.16 | 33.84 | 1279152 | 1279.152 | 42.93 | 37.07 | 1401246 | 1401.246 | 39.7 | 40.3 | 1523340 | 1523.34 | 40
12/10/20XX 12:00:00 PM | 0.5 | 6 | 39.8 | 64.6 | 39.8 |  | 39.8 | 68.78 | 11.22 | 424116 | 424.116 | 65.56 | 14.44 | 545832 | 545.832 | 62.34 | 17.66 | 667548 | 667.548 | 59.12 | 20.88 | 789264 | 789.264 | 55.9 | 24.1 | 910980 | 910.98 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.46 | 30.54 | 1154412 | 1154.412 | 46.24 | 33.76 | 1276128 | 1276.128 | 43.02 | 36.98 | 1397844 | 1397.844 | 39.8 | 40.2 | 1519560 | 1519.56 | 40
12/10/20XX 1:00:00 PM | 0.54167 | 6 | 40.4 | 63.3 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
12/10/20XX 2:00:00 PM | 0.58333 | 6 | 40.8 | 60.2 | 40.8 |  | 40.8 | 68.88 | 11.12 | 420336 | 420.336 | 65.76 | 14.24 | 538272 | 538.272 | 62.64 | 17.36 | 656208 | 656.208 | 59.52 | 20.48 | 774144 | 774.144 | 56.4 | 23.6 | 892080 | 892.08 | 53.28 | 26.72 | 1010016 | 1010.016 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.04 | 32.96 | 1245888 | 1245.888 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.8 | 39.2 | 1481760 | 1481.76 | 40
12/10/20XX 3:00:00 PM | 0.625 | 6 | 40.7 | 58.9 | 40.7 |  | 40.7 | 68.87 | 11.13 | 420714 | 420.714 | 65.74 | 14.26 | 539028 | 539.028 | 62.61 | 17.39 | 657342 | 657.342 | 59.48 | 20.52 | 775656 | 775.656 | 56.35 | 23.65 | 893970 | 893.97 | 53.22 | 26.78 | 1012284 | 1012.284 | 50.09 | 29.91 | 1130598 | 1130.598 | 46.96 | 33.04 | 1248912 | 1248.912 | 43.83 | 36.17 | 1367226 | 1367.226 | 40.7 | 39.3 | 1485540 | 1485.54 | 40
12/10/20XX 4:00:00 PM | 0.66667 | 6 | 40.4 | 58.4 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
12/10/20XX 5:00:00 PM | 0.70833 | 6 | 39.7 | 60 | 39.7 |  | 39.7 | 68.77 | 11.23 | 424494 | 424.494 | 65.54 | 14.46 | 546588 | 546.588 | 62.31 | 17.69 | 668682 | 668.682 | 59.08 | 20.92 | 790776 | 790.776 | 55.85 | 24.15 | 912870 | 912.87 | 52.62 | 27.38 | 1034964 | 1034.964 | 49.39 | 30.61 | 1157058 | 1157.058 | 46.16 | 33.84 | 1279152 | 1279.152 | 42.93 | 37.07 | 1401246 | 1401.246 | 39.7 | 40.3 | 1523340 | 1523.34 | 40
12/10/20XX 6:00:00 PM | 0.75 | 6 | 39.1 | 59.9 | 39.1 |  | 39.1 | 68.71 | 11.29 | 426762 | 426.762 | 65.42 | 14.58 | 551124 | 551.124 | 62.13 | 17.87 | 675486 | 675.486 | 58.84 | 21.16 | 799848 | 799.848 | 55.55 | 24.45 | 924210 | 924.21 | 52.26 | 27.74 | 1048572 | 1048.572 | 48.97 | 31.03 | 1172934 | 1172.934 | 45.68 | 34.32 | 1297296 | 1297.296 | 42.39 | 37.61 | 1421658 | 1421.658 | 39.1 | 40.9 | 1546020 | 1546.02 | 40
12/10/20XX 7:00:00 PM | 0.79167 | 6 | 38.9 | 60.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/10/20XX 8:00:00 PM | 0.83333 | 6 | 38.6 | 60.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/10/20XX 9:00:00 PM | 0.875 | 6 | 38.1 | 60.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/10/20XX 10:00:00 PM | 0.91667 | 6 | 37.6 | 60.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/10/20XX 11:00:00 PM | 0.95833 | 6 | 37.6 | 59.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/10/20XX 12:00:00 AM | 0 | 7 | 37 | 59.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/11/20XX 1:00:00 AM | 0.041667 | 7 | 35.7 | 58.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/11/20XX 2:00:00 AM | 0.083333 | 7 | 35.2 | 58.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/11/20XX 3:00:00 AM | 0.125 | 7 | 34.7 | 60.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/11/20XX 4:00:00 AM | 0.16667 | 7 | 34.3 | 60.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/11/20XX 5:00:00 AM | 0.20833 | 7 | 33.7 | 60.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/11/20XX 6:00:00 AM | 0.25 | 7 | 33.2 | 62.6 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
12/11/20XX 7:00:00 AM | 0.29167 | 7 | 33 | 63.8 | 33 |  | 33 | 68.1 | 11.9 | 449820 | 449.82 | 64.2 | 15.8 | 597240 | 597.24 | 60.3 | 19.7 | 744660 | 744.66 | 56.4 | 23.6 | 892080 | 892.08 | 52.5 | 27.5 | 1039500 | 1039.5 | 48.6 | 31.4 | 1186920 | 1186.92 | 44.7 | 35.3 | 1334340 | 1334.34 | 40.8 | 39.2 | 1481760 | 1481.76 | 36.9 | 43.1 | 1629180 | 1629.18 | 33 | 47 | 1776600 | 1776.6 | 35
12/11/20XX 8:00:00 AM | 0.33333 | 7 | 33.3 | 63.3 | 33.3 |  | 33.3 | 68.13 | 11.87 | 448686 | 448.686 | 64.26 | 15.74 | 594972 | 594.972 | 60.39 | 19.61 | 741258 | 741.258 | 56.52 | 23.48 | 887544 | 887.544 | 52.65 | 27.35 | 1033830 | 1033.83 | 48.78 | 31.22 | 1180116 | 1180.116 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.17 | 42.83 | 1618974 | 1618.974 | 33.3 | 46.7 | 1765260 | 1765.26 | 35
12/11/20XX 9:00:00 AM | 0.375 | 7 | 34.4 | 61.4 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
12/11/20XX 10:00:00 AM | 0.41667 | 7 | 36.2 | 56.7 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
12/11/20XX 11:00:00 AM | 0.45833 | 7 | 37.4 | 53 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
12/11/20XX 12:00:00 PM | 0.5 | 7 | 38.5 | 49.3 | 38.5 |  | 38.5 | 68.65 | 11.35 | 429030 | 429.03 | 65.3 | 14.7 | 555660 | 555.66 | 61.95 | 18.05 | 682290 | 682.29 | 58.6 | 21.4 | 808920 | 808.92 | 55.25 | 24.75 | 935550 | 935.55 | 51.9 | 28.1 | 1062180 | 1062.18 | 48.55 | 31.45 | 1188810 | 1188.81 | 45.2 | 34.8 | 1315440 | 1315.44 | 41.85 | 38.15 | 1442070 | 1442.07 | 38.5 | 41.5 | 1568700 | 1568.7 | 40
12/11/20XX 1:00:00 PM | 0.54167 | 7 | 39.6 | 47.8 | 39.6 |  | 39.6 | 68.76 | 11.24 | 424872 | 424.872 | 65.52 | 14.48 | 547344 | 547.344 | 62.28 | 17.72 | 669816 | 669.816 | 59.04 | 20.96 | 792288 | 792.288 | 55.8 | 24.2 | 914760 | 914.76 | 52.56 | 27.44 | 1037232 | 1037.232 | 49.32 | 30.68 | 1159704 | 1159.704 | 46.08 | 33.92 | 1282176 | 1282.176 | 42.84 | 37.16 | 1404648 | 1404.648 | 39.6 | 40.4 | 1527120 | 1527.12 | 40
12/11/20XX 2:00:00 PM | 0.58333 | 7 | 40.2 | 46.5 | 40.2 |  | 40.2 | 68.82 | 11.18 | 422604 | 422.604 | 65.64 | 14.36 | 542808 | 542.808 | 62.46 | 17.54 | 663012 | 663.012 | 59.28 | 20.72 | 783216 | 783.216 | 56.1 | 23.9 | 903420 | 903.42 | 52.92 | 27.08 | 1023624 | 1023.624 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.56 | 33.44 | 1264032 | 1264.032 | 43.38 | 36.62 | 1384236 | 1384.236 | 40.2 | 39.8 | 1504440 | 1504.44 | 40
12/11/20XX 3:00:00 PM | 0.625 | 7 | 40.3 | 45.5 | 40.3 |  | 40.3 | 68.83 | 11.17 | 422226 | 422.226 | 65.66 | 14.34 | 542052 | 542.052 | 62.49 | 17.51 | 661878 | 661.878 | 59.32 | 20.68 | 781704 | 781.704 | 56.15 | 23.85 | 901530 | 901.53 | 52.98 | 27.02 | 1021356 | 1021.356 | 49.81 | 30.19 | 1141182 | 1141.182 | 46.64 | 33.36 | 1261008 | 1261.008 | 43.47 | 36.53 | 1380834 | 1380.834 | 40.3 | 39.7 | 1500660 | 1500.66 | 40
12/11/20XX 4:00:00 PM | 0.66667 | 7 | 39.5 | 48.1 | 39.5 |  | 39.5 | 68.75 | 11.25 | 425250 | 425.25 | 65.5 | 14.5 | 548100 | 548.1 | 62.25 | 17.75 | 670950 | 670.95 | 59 | 21 | 793800 | 793.8 | 55.75 | 24.25 | 916650 | 916.65 | 52.5 | 27.5 | 1039500 | 1039.5 | 49.25 | 30.75 | 1162350 | 1162.35 | 46 | 34 | 1285200 | 1285.2 | 42.75 | 37.25 | 1408050 | 1408.05 | 39.5 | 40.5 | 1530900 | 1530.9 | 40
12/11/20XX 5:00:00 PM | 0.70833 | 7 | 39.3 | 51 | 39.3 |  | 39.3 | 68.73 | 11.27 | 426006 | 426.006 | 65.46 | 14.54 | 549612 | 549.612 | 62.19 | 17.81 | 673218 | 673.218 | 58.92 | 21.08 | 796824 | 796.824 | 55.65 | 24.35 | 920430 | 920.43 | 52.38 | 27.62 | 1044036 | 1044.036 | 49.11 | 30.89 | 1167642 | 1167.642 | 45.84 | 34.16 | 1291248 | 1291.248 | 42.57 | 37.43 | 1414854 | 1414.854 | 39.3 | 40.7 | 1538460 | 1538.46 | 40
12/11/20XX 6:00:00 PM | 0.75 | 7 | 38.5 | 54.6 | 38.5 |  | 38.5 | 68.65 | 11.35 | 429030 | 429.03 | 65.3 | 14.7 | 555660 | 555.66 | 61.95 | 18.05 | 682290 | 682.29 | 58.6 | 21.4 | 808920 | 808.92 | 55.25 | 24.75 | 935550 | 935.55 | 51.9 | 28.1 | 1062180 | 1062.18 | 48.55 | 31.45 | 1188810 | 1188.81 | 45.2 | 34.8 | 1315440 | 1315.44 | 41.85 | 38.15 | 1442070 | 1442.07 | 38.5 | 41.5 | 1568700 | 1568.7 | 40
12/11/20XX 7:00:00 PM | 0.79167 | 7 | 38.4 | 55 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/11/20XX 8:00:00 PM | 0.83333 | 7 | 37.9 | 55.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/11/20XX 9:00:00 PM | 0.875 | 7 | 37.7 | 57.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/11/20XX 10:00:00 PM | 0.91667 | 7 | 37.7 | 57.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/11/20XX 11:00:00 PM | 0.95833 | 7 | 37.5 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/11/20XX 12:00:00 AM | 0 | 1 | 37.3 | 58.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/12/20XX 1:00:00 AM | 0.041667 | 1 | 36.9 | 60.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/12/20XX 2:00:00 AM | 0.083333 | 1 | 36.8 | 63.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/12/20XX 3:00:00 AM | 0.125 | 1 | 36.6 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/12/20XX 4:00:00 AM | 0.16667 | 1 | 36.9 | 66 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/12/20XX 5:00:00 AM | 0.20833 | 1 | 37.4 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/12/20XX 6:00:00 AM | 0.25 | 1 | 37.7 | 64.2 | 37.7 |  | 37.7 | 68.57 | 11.43 | 432054 | 432.054 | 65.14 | 14.86 | 561708 | 561.708 | 61.71 | 18.29 | 691362 | 691.362 | 58.28 | 21.72 | 821016 | 821.016 | 54.85 | 25.15 | 950670 | 950.67 | 51.42 | 28.58 | 1080324 | 1080.324 | 47.99 | 32.01 | 1209978 | 1209.978 | 44.56 | 35.44 | 1339632 | 1339.632 | 41.13 | 38.87 | 1469286 | 1469.286 | 37.7 | 42.3 | 1598940 | 1598.94 | 40
12/12/20XX 7:00:00 AM | 0.29167 | 1 | 37.7 | 64.8 | 37.7 |  | 37.7 | 68.57 | 11.43 | 432054 | 432.054 | 65.14 | 14.86 | 561708 | 561.708 | 61.71 | 18.29 | 691362 | 691.362 | 58.28 | 21.72 | 821016 | 821.016 | 54.85 | 25.15 | 950670 | 950.67 | 51.42 | 28.58 | 1080324 | 1080.324 | 47.99 | 32.01 | 1209978 | 1209.978 | 44.56 | 35.44 | 1339632 | 1339.632 | 41.13 | 38.87 | 1469286 | 1469.286 | 37.7 | 42.3 | 1598940 | 1598.94 | 40
12/12/20XX 8:00:00 AM | 0.33333 | 1 | 38.1 | 64.5 | 38.1 |  | 38.1 | 68.61 | 11.39 | 430542 | 430.542 | 65.22 | 14.78 | 558684 | 558.684 | 61.83 | 18.17 | 686826 | 686.826 | 58.44 | 21.56 | 814968 | 814.968 | 55.05 | 24.95 | 943110 | 943.11 | 51.66 | 28.34 | 1071252 | 1071.252 | 48.27 | 31.73 | 1199394 | 1199.394 | 44.88 | 35.12 | 1327536 | 1327.536 | 41.49 | 38.51 | 1455678 | 1455.678 | 38.1 | 41.9 | 1583820 | 1583.82 | 40
12/12/20XX 9:00:00 AM | 0.375 | 1 | 39.4 | 62.9 | 39.4 |  | 39.4 | 68.74 | 11.26 | 425628 | 425.628 | 65.48 | 14.52 | 548856 | 548.856 | 62.22 | 17.78 | 672084 | 672.084 | 58.96 | 21.04 | 795312 | 795.312 | 55.7 | 24.3 | 918540 | 918.54 | 52.44 | 27.56 | 1041768 | 1041.768 | 49.18 | 30.82 | 1164996 | 1164.996 | 45.92 | 34.08 | 1288224 | 1288.224 | 42.66 | 37.34 | 1411452 | 1411.452 | 39.4 | 40.6 | 1534680 | 1534.68 | 40
12/12/20XX 10:00:00 AM | 0.41667 | 1 | 40.4 | 62.3 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
12/12/20XX 11:00:00 AM | 0.45833 | 1 | 41.7 | 59.1 | 41.7 |  | 41.7 | 68.97 | 11.03 | 416934 | 416.934 | 65.94 | 14.06 | 531468 | 531.468 | 62.91 | 17.09 | 646002 | 646.002 | 59.88 | 20.12 | 760536 | 760.536 | 56.85 | 23.15 | 875070 | 875.07 | 53.82 | 26.18 | 989604 | 989.604 | 50.79 | 29.21 | 1104138 | 1104.138 | 47.76 | 32.24 | 1218672 | 1218.672 | 44.73 | 35.27 | 1333206 | 1333.206 | 41.7 | 38.3 | 1447740 | 1447.74 | 40
12/12/20XX 12:00:00 PM | 0.5 | 1 | 42.8 | 56.7 | 42.8 |  | 42.8 | 69.08 | 10.92 | 412776 | 412.776 | 66.16 | 13.84 | 523152 | 523.152 | 63.24 | 16.76 | 633528 | 633.528 | 60.32 | 19.68 | 743904 | 743.904 | 57.4 | 22.6 | 854280 | 854.28 | 54.48 | 25.52 | 964656 | 964.656 | 51.56 | 28.44 | 1075032 | 1075.032 | 48.64 | 31.36 | 1185408 | 1185.408 | 45.72 | 34.28 | 1295784 | 1295.784 | 42.8 | 37.2 | 1406160 | 1406.16 | 45
12/12/20XX 1:00:00 PM | 0.54167 | 1 | 43.4 | 54.4 | 43.4 |  | 43.4 | 69.14 | 10.86 | 410508 | 410.508 | 66.28 | 13.72 | 518616 | 518.616 | 63.42 | 16.58 | 626724 | 626.724 | 60.56 | 19.44 | 734832 | 734.832 | 57.7 | 22.3 | 842940 | 842.94 | 54.84 | 25.16 | 951048 | 951.048 | 51.98 | 28.02 | 1059156 | 1059.156 | 49.12 | 30.88 | 1167264 | 1167.264 | 46.26 | 33.74 | 1275372 | 1275.372 | 43.4 | 36.6 | 1383480 | 1383.48 | 45
12/12/20XX 2:00:00 PM | 0.58333 | 1 | 43.2 | 54.3 | 43.2 |  | 43.2 | 69.12 | 10.88 | 411264 | 411.264 | 66.24 | 13.76 | 520128 | 520.128 | 63.36 | 16.64 | 628992 | 628.992 | 60.48 | 19.52 | 737856 | 737.856 | 57.6 | 22.4 | 846720 | 846.72 | 54.72 | 25.28 | 955584 | 955.584 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.08 | 33.92 | 1282176 | 1282.176 | 43.2 | 36.8 | 1391040 | 1391.04 | 45
12/12/20XX 3:00:00 PM | 0.625 | 1 | 43.4 | 52.8 | 43.4 |  | 43.4 | 69.14 | 10.86 | 410508 | 410.508 | 66.28 | 13.72 | 518616 | 518.616 | 63.42 | 16.58 | 626724 | 626.724 | 60.56 | 19.44 | 734832 | 734.832 | 57.7 | 22.3 | 842940 | 842.94 | 54.84 | 25.16 | 951048 | 951.048 | 51.98 | 28.02 | 1059156 | 1059.156 | 49.12 | 30.88 | 1167264 | 1167.264 | 46.26 | 33.74 | 1275372 | 1275.372 | 43.4 | 36.6 | 1383480 | 1383.48 | 45
12/12/20XX 4:00:00 PM | 0.66667 | 1 | 42.8 | 54.1 | 42.8 |  | 42.8 | 69.08 | 10.92 | 412776 | 412.776 | 66.16 | 13.84 | 523152 | 523.152 | 63.24 | 16.76 | 633528 | 633.528 | 60.32 | 19.68 | 743904 | 743.904 | 57.4 | 22.6 | 854280 | 854.28 | 54.48 | 25.52 | 964656 | 964.656 | 51.56 | 28.44 | 1075032 | 1075.032 | 48.64 | 31.36 | 1185408 | 1185.408 | 45.72 | 34.28 | 1295784 | 1295.784 | 42.8 | 37.2 | 1406160 | 1406.16 | 45
12/12/20XX 5:00:00 PM | 0.70833 | 1 | 41.9 | 54.5 | 41.9 |  | 41.9 | 68.99 | 11.01 | 416178 | 416.178 | 65.98 | 14.02 | 529956 | 529.956 | 62.97 | 17.03 | 643734 | 643.734 | 59.96 | 20.04 | 757512 | 757.512 | 56.95 | 23.05 | 871290 | 871.29 | 53.94 | 26.06 | 985068 | 985.068 | 50.93 | 29.07 | 1098846 | 1098.846 | 47.92 | 32.08 | 1212624 | 1212.624 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.9 | 38.1 | 1440180 | 1440.18 | 40
12/12/20XX 6:00:00 PM | 0.75 | 1 | 41.4 | 55.8 | 41.4 |  | 41.4 | 68.94 | 11.06 | 418068 | 418.068 | 65.88 | 14.12 | 533736 | 533.736 | 62.82 | 17.18 | 649404 | 649.404 | 59.76 | 20.24 | 765072 | 765.072 | 56.7 | 23.3 | 880740 | 880.74 | 53.64 | 26.36 | 996408 | 996.408 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.46 | 35.54 | 1343412 | 1343.412 | 41.4 | 38.6 | 1459080 | 1459.08 | 40
12/12/20XX 7:00:00 PM | 0.79167 | 1 | 40.5 | 57.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/12/20XX 8:00:00 PM | 0.83333 | 1 | 39.7 | 59.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/12/20XX 9:00:00 PM | 0.875 | 1 | 39.7 | 57 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/12/20XX 10:00:00 PM | 0.91667 | 1 | 39.4 | 56.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/12/20XX 11:00:00 PM | 0.95833 | 1 | 39.2 | 57.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/12/20XX 12:00:00 AM | 0 | 2 | 39 | 56.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/13/20XX 1:00:00 AM | 0.041667 | 2 | 38.3 | 56 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/13/20XX 2:00:00 AM | 0.083333 | 2 | 37.8 | 56.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/13/20XX 3:00:00 AM | 0.125 | 2 | 36.7 | 58.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/13/20XX 4:00:00 AM | 0.16667 | 2 | 36.7 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/13/20XX 5:00:00 AM | 0.20833 | 2 | 36.5 | 58.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/13/20XX 6:00:00 AM | 0.25 | 2 | 35.7 | 60.2 | 35.7 |  | 35.7 | 68.37 | 11.63 | 439614 | 439.614 | 64.74 | 15.26 | 576828 | 576.828 | 61.11 | 18.89 | 714042 | 714.042 | 57.48 | 22.52 | 851256 | 851.256 | 53.85 | 26.15 | 988470 | 988.47 | 50.22 | 29.78 | 1125684 | 1125.684 | 46.59 | 33.41 | 1262898 | 1262.898 | 42.96 | 37.04 | 1400112 | 1400.112 | 39.33 | 40.67 | 1537326 | 1537.326 | 35.7 | 44.3 | 1674540 | 1674.54 | 35
12/13/20XX 7:00:00 AM | 0.29167 | 2 | 36.1 | 60 | 36.1 |  | 36.1 | 68.41 | 11.59 | 438102 | 438.102 | 64.82 | 15.18 | 573804 | 573.804 | 61.23 | 18.77 | 709506 | 709.506 | 57.64 | 22.36 | 845208 | 845.208 | 54.05 | 25.95 | 980910 | 980.91 | 50.46 | 29.54 | 1116612 | 1116.612 | 46.87 | 33.13 | 1252314 | 1252.314 | 43.28 | 36.72 | 1388016 | 1388.016 | 39.69 | 40.31 | 1523718 | 1523.718 | 36.1 | 43.9 | 1659420 | 1659.42 | 35
12/13/20XX 8:00:00 AM | 0.33333 | 2 | 36.3 | 60 | 36.3 |  | 36.3 | 68.43 | 11.57 | 437346 | 437.346 | 64.86 | 15.14 | 572292 | 572.292 | 61.29 | 18.71 | 707238 | 707.238 | 57.72 | 22.28 | 842184 | 842.184 | 54.15 | 25.85 | 977130 | 977.13 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.01 | 32.99 | 1247022 | 1247.022 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.87 | 40.13 | 1516914 | 1516.914 | 36.3 | 43.7 | 1651860 | 1651.86 | 35
12/13/20XX 9:00:00 AM | 0.375 | 2 | 37.2 | 59.4 | 37.2 |  | 37.2 | 68.52 | 11.48 | 433944 | 433.944 | 65.04 | 14.96 | 565488 | 565.488 | 61.56 | 18.44 | 697032 | 697.032 | 58.08 | 21.92 | 828576 | 828.576 | 54.6 | 25.4 | 960120 | 960.12 | 51.12 | 28.88 | 1091664 | 1091.664 | 47.64 | 32.36 | 1223208 | 1223.208 | 44.16 | 35.84 | 1354752 | 1354.752 | 40.68 | 39.32 | 1486296 | 1486.296 | 37.2 | 42.8 | 1617840 | 1617.84 | 35
12/13/20XX 10:00:00 AM | 0.41667 | 2 | 38.6 | 57 | 38.6 |  | 38.6 | 68.66 | 11.34 | 428652 | 428.652 | 65.32 | 14.68 | 554904 | 554.904 | 61.98 | 18.02 | 681156 | 681.156 | 58.64 | 21.36 | 807408 | 807.408 | 55.3 | 24.7 | 933660 | 933.66 | 51.96 | 28.04 | 1059912 | 1059.912 | 48.62 | 31.38 | 1186164 | 1186.164 | 45.28 | 34.72 | 1312416 | 1312.416 | 41.94 | 38.06 | 1438668 | 1438.668 | 38.6 | 41.4 | 1564920 | 1564.92 | 40
12/13/20XX 11:00:00 AM | 0.45833 | 2 | 39.8 | 55.4 | 39.8 |  | 39.8 | 68.78 | 11.22 | 424116 | 424.116 | 65.56 | 14.44 | 545832 | 545.832 | 62.34 | 17.66 | 667548 | 667.548 | 59.12 | 20.88 | 789264 | 789.264 | 55.9 | 24.1 | 910980 | 910.98 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.46 | 30.54 | 1154412 | 1154.412 | 46.24 | 33.76 | 1276128 | 1276.128 | 43.02 | 36.98 | 1397844 | 1397.844 | 39.8 | 40.2 | 1519560 | 1519.56 | 40
12/13/20XX 12:00:00 PM | 0.5 | 2 | 40.8 | 56.6 | 40.8 |  | 40.8 | 68.88 | 11.12 | 420336 | 420.336 | 65.76 | 14.24 | 538272 | 538.272 | 62.64 | 17.36 | 656208 | 656.208 | 59.52 | 20.48 | 774144 | 774.144 | 56.4 | 23.6 | 892080 | 892.08 | 53.28 | 26.72 | 1010016 | 1010.016 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.04 | 32.96 | 1245888 | 1245.888 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.8 | 39.2 | 1481760 | 1481.76 | 40
12/13/20XX 1:00:00 PM | 0.54167 | 2 | 42.4 | 54.1 | 42.4 |  | 42.4 | 69.04 | 10.96 | 414288 | 414.288 | 66.08 | 13.92 | 526176 | 526.176 | 63.12 | 16.88 | 638064 | 638.064 | 60.16 | 19.84 | 749952 | 749.952 | 57.2 | 22.8 | 861840 | 861.84 | 54.24 | 25.76 | 973728 | 973.728 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.32 | 31.68 | 1197504 | 1197.504 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.4 | 37.6 | 1421280 | 1421.28 | 40
12/13/20XX 2:00:00 PM | 0.58333 | 2 | 43.1 | 53.2 | 43.1 |  | 43.1 | 69.11 | 10.89 | 411642 | 411.642 | 66.22 | 13.78 | 520884 | 520.884 | 63.33 | 16.67 | 630126 | 630.126 | 60.44 | 19.56 | 739368 | 739.368 | 57.55 | 22.45 | 848610 | 848.61 | 54.66 | 25.34 | 957852 | 957.852 | 51.77 | 28.23 | 1067094 | 1067.094 | 48.88 | 31.12 | 1176336 | 1176.336 | 45.99 | 34.01 | 1285578 | 1285.578 | 43.1 | 36.9 | 1394820 | 1394.82 | 45
12/13/20XX 3:00:00 PM | 0.625 | 2 | 42.4 | 54.1 | 42.4 |  | 42.4 | 69.04 | 10.96 | 414288 | 414.288 | 66.08 | 13.92 | 526176 | 526.176 | 63.12 | 16.88 | 638064 | 638.064 | 60.16 | 19.84 | 749952 | 749.952 | 57.2 | 22.8 | 861840 | 861.84 | 54.24 | 25.76 | 973728 | 973.728 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.32 | 31.68 | 1197504 | 1197.504 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.4 | 37.6 | 1421280 | 1421.28 | 40
12/13/20XX 4:00:00 PM | 0.66667 | 2 | 41.8 | 56 | 41.8 |  | 41.8 | 68.98 | 11.02 | 416556 | 416.556 | 65.96 | 14.04 | 530712 | 530.712 | 62.94 | 17.06 | 644868 | 644.868 | 59.92 | 20.08 | 759024 | 759.024 | 56.9 | 23.1 | 873180 | 873.18 | 53.88 | 26.12 | 987336 | 987.336 | 50.86 | 29.14 | 1101492 | 1101.492 | 47.84 | 32.16 | 1215648 | 1215.648 | 44.82 | 35.18 | 1329804 | 1329.804 | 41.8 | 38.2 | 1443960 | 1443.96 | 40
12/13/20XX 5:00:00 PM | 0.70833 | 2 | 41.2 | 58.5 | 41.2 |  | 41.2 | 68.92 | 11.08 | 418824 | 418.824 | 65.84 | 14.16 | 535248 | 535.248 | 62.76 | 17.24 | 651672 | 651.672 | 59.68 | 20.32 | 768096 | 768.096 | 56.6 | 23.4 | 884520 | 884.52 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.44 | 29.56 | 1117368 | 1117.368 | 47.36 | 32.64 | 1233792 | 1233.792 | 44.28 | 35.72 | 1350216 | 1350.216 | 41.2 | 38.8 | 1466640 | 1466.64 | 40
12/13/20XX 6:00:00 PM | 0.75 | 2 | 40.9 | 59 | 40.9 |  | 40.9 | 68.89 | 11.11 | 419958 | 419.958 | 65.78 | 14.22 | 537516 | 537.516 | 62.67 | 17.33 | 655074 | 655.074 | 59.56 | 20.44 | 772632 | 772.632 | 56.45 | 23.55 | 890190 | 890.19 | 53.34 | 26.66 | 1007748 | 1007.748 | 50.23 | 29.77 | 1125306 | 1125.306 | 47.12 | 32.88 | 1242864 | 1242.864 | 44.01 | 35.99 | 1360422 | 1360.422 | 40.9 | 39.1 | 1477980 | 1477.98 | 40
12/13/20XX 7:00:00 PM | 0.79167 | 2 | 39.9 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/13/20XX 8:00:00 PM | 0.83333 | 2 | 39.2 | 61.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/13/20XX 9:00:00 PM | 0.875 | 2 | 38.9 | 62.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/13/20XX 10:00:00 PM | 0.91667 | 2 | 38.5 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/13/20XX 11:00:00 PM | 0.95833 | 2 | 38.3 | 62.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/13/20XX 12:00:00 AM | 0 | 3 | 37.7 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/14/20XX 1:00:00 AM | 0.041667 | 3 | 37.1 | 69.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/14/20XX 2:00:00 AM | 0.083333 | 3 | 36.9 | 69.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/14/20XX 3:00:00 AM | 0.125 | 3 | 36.6 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/14/20XX 4:00:00 AM | 0.16667 | 3 | 36.4 | 70.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/14/20XX 5:00:00 AM | 0.20833 | 3 | 36 | 72.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/14/20XX 6:00:00 AM | 0.25 | 3 | 36 | 71.2 | 36 |  | 36 | 68.4 | 11.6 | 438480 | 438.48 | 64.8 | 15.2 | 574560 | 574.56 | 61.2 | 18.8 | 710640 | 710.64 | 57.6 | 22.4 | 846720 | 846.72 | 54 | 26 | 982800 | 982.8 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.2 | 36.8 | 1391040 | 1391.04 | 39.6 | 40.4 | 1527120 | 1527.12 | 36 | 44 | 1663200 | 1663.2 | 35
12/14/20XX 7:00:00 AM | 0.29167 | 3 | 36 | 72.3 | 36 |  | 36 | 68.4 | 11.6 | 438480 | 438.48 | 64.8 | 15.2 | 574560 | 574.56 | 61.2 | 18.8 | 710640 | 710.64 | 57.6 | 22.4 | 846720 | 846.72 | 54 | 26 | 982800 | 982.8 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.2 | 36.8 | 1391040 | 1391.04 | 39.6 | 40.4 | 1527120 | 1527.12 | 36 | 44 | 1663200 | 1663.2 | 35
12/14/20XX 8:00:00 AM | 0.33333 | 3 | 36.2 | 72.2 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
12/14/20XX 9:00:00 AM | 0.375 | 3 | 37.1 | 70.2 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
12/14/20XX 10:00:00 AM | 0.41667 | 3 | 38.1 | 67.4 | 38.1 |  | 38.1 | 68.61 | 11.39 | 430542 | 430.542 | 65.22 | 14.78 | 558684 | 558.684 | 61.83 | 18.17 | 686826 | 686.826 | 58.44 | 21.56 | 814968 | 814.968 | 55.05 | 24.95 | 943110 | 943.11 | 51.66 | 28.34 | 1071252 | 1071.252 | 48.27 | 31.73 | 1199394 | 1199.394 | 44.88 | 35.12 | 1327536 | 1327.536 | 41.49 | 38.51 | 1455678 | 1455.678 | 38.1 | 41.9 | 1583820 | 1583.82 | 40
12/14/20XX 11:00:00 AM | 0.45833 | 3 | 39.6 | 63.3 | 39.6 |  | 39.6 | 68.76 | 11.24 | 424872 | 424.872 | 65.52 | 14.48 | 547344 | 547.344 | 62.28 | 17.72 | 669816 | 669.816 | 59.04 | 20.96 | 792288 | 792.288 | 55.8 | 24.2 | 914760 | 914.76 | 52.56 | 27.44 | 1037232 | 1037.232 | 49.32 | 30.68 | 1159704 | 1159.704 | 46.08 | 33.92 | 1282176 | 1282.176 | 42.84 | 37.16 | 1404648 | 1404.648 | 39.6 | 40.4 | 1527120 | 1527.12 | 40
12/14/20XX 12:00:00 PM | 0.5 | 3 | 40.2 | 60.7 | 40.2 |  | 40.2 | 68.82 | 11.18 | 422604 | 422.604 | 65.64 | 14.36 | 542808 | 542.808 | 62.46 | 17.54 | 663012 | 663.012 | 59.28 | 20.72 | 783216 | 783.216 | 56.1 | 23.9 | 903420 | 903.42 | 52.92 | 27.08 | 1023624 | 1023.624 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.56 | 33.44 | 1264032 | 1264.032 | 43.38 | 36.62 | 1384236 | 1384.236 | 40.2 | 39.8 | 1504440 | 1504.44 | 40
12/14/20XX 1:00:00 PM | 0.54167 | 3 | 41.3 | 57.9 | 41.3 |  | 41.3 | 68.93 | 11.07 | 418446 | 418.446 | 65.86 | 14.14 | 534492 | 534.492 | 62.79 | 17.21 | 650538 | 650.538 | 59.72 | 20.28 | 766584 | 766.584 | 56.65 | 23.35 | 882630 | 882.63 | 53.58 | 26.42 | 998676 | 998.676 | 50.51 | 29.49 | 1114722 | 1114.722 | 47.44 | 32.56 | 1230768 | 1230.768 | 44.37 | 35.63 | 1346814 | 1346.814 | 41.3 | 38.7 | 1462860 | 1462.86 | 40
12/14/20XX 2:00:00 PM | 0.58333 | 3 | 41.5 | 57.2 | 41.5 |  | 41.5 | 68.95 | 11.05 | 417690 | 417.69 | 65.9 | 14.1 | 532980 | 532.98 | 62.85 | 17.15 | 648270 | 648.27 | 59.8 | 20.2 | 763560 | 763.56 | 56.75 | 23.25 | 878850 | 878.85 | 53.7 | 26.3 | 994140 | 994.14 | 50.65 | 29.35 | 1109430 | 1109.43 | 47.6 | 32.4 | 1224720 | 1224.72 | 44.55 | 35.45 | 1340010 | 1340.01 | 41.5 | 38.5 | 1455300 | 1455.3 | 40
12/14/20XX 3:00:00 PM | 0.625 | 3 | 42 | 56.4 | 42 |  | 42 | 69 | 11 | 415800 | 415.8 | 66 | 14 | 529200 | 529.2 | 63 | 17 | 642600 | 642.6 | 60 | 20 | 756000 | 756 | 57 | 23 | 869400 | 869.4 | 54 | 26 | 982800 | 982.8 | 51 | 29 | 1096200 | 1096.2 | 48 | 32 | 1209600 | 1209.6 | 45 | 35 | 1323000 | 1323 | 42 | 38 | 1436400 | 1436.4 | 40
12/14/20XX 4:00:00 PM | 0.66667 | 3 | 41.2 | 57.2 | 41.2 |  | 41.2 | 68.92 | 11.08 | 418824 | 418.824 | 65.84 | 14.16 | 535248 | 535.248 | 62.76 | 17.24 | 651672 | 651.672 | 59.68 | 20.32 | 768096 | 768.096 | 56.6 | 23.4 | 884520 | 884.52 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.44 | 29.56 | 1117368 | 1117.368 | 47.36 | 32.64 | 1233792 | 1233.792 | 44.28 | 35.72 | 1350216 | 1350.216 | 41.2 | 38.8 | 1466640 | 1466.64 | 40
12/14/20XX 5:00:00 PM | 0.70833 | 3 | 40.6 | 59 | 40.6 |  | 40.6 | 68.86 | 11.14 | 421092 | 421.092 | 65.72 | 14.28 | 539784 | 539.784 | 62.58 | 17.42 | 658476 | 658.476 | 59.44 | 20.56 | 777168 | 777.168 | 56.3 | 23.7 | 895860 | 895.86 | 53.16 | 26.84 | 1014552 | 1014.552 | 50.02 | 29.98 | 1133244 | 1133.244 | 46.88 | 33.12 | 1251936 | 1251.936 | 43.74 | 36.26 | 1370628 | 1370.628 | 40.6 | 39.4 | 1489320 | 1489.32 | 40
12/14/20XX 6:00:00 PM | 0.75 | 3 | 40.1 | 61 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
12/14/20XX 7:00:00 PM | 0.79167 | 3 | 39.9 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/14/20XX 8:00:00 PM | 0.83333 | 3 | 39.4 | 63.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/14/20XX 9:00:00 PM | 0.875 | 3 | 39.2 | 63.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/14/20XX 10:00:00 PM | 0.91667 | 3 | 39.5 | 64.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/14/20XX 11:00:00 PM | 0.95833 | 3 | 40 | 64.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/14/20XX 12:00:00 AM | 0 | 4 | 40.3 | 65.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/15/20XX 1:00:00 AM | 0.041667 | 4 | 40 | 68.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/15/20XX 2:00:00 AM | 0.083333 | 4 | 40 | 68.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/15/20XX 3:00:00 AM | 0.125 | 4 | 39.4 | 66.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/15/20XX 4:00:00 AM | 0.16667 | 4 | 39.5 | 67.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/15/20XX 5:00:00 AM | 0.20833 | 4 | 38.4 | 67.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/15/20XX 6:00:00 AM | 0.25 | 4 | 38.4 | 67.6 | 38.4 |  | 38.4 | 68.64 | 11.36 | 429408 | 429.408 | 65.28 | 14.72 | 556416 | 556.416 | 61.92 | 18.08 | 683424 | 683.424 | 58.56 | 21.44 | 810432 | 810.432 | 55.2 | 24.8 | 937440 | 937.44 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.76 | 38.24 | 1445472 | 1445.472 | 38.4 | 41.6 | 1572480 | 1572.48 | 40
12/15/20XX 7:00:00 AM | 0.29167 | 4 | 37.8 | 68.4 | 37.8 |  | 37.8 | 68.58 | 11.42 | 431676 | 431.676 | 65.16 | 14.84 | 560952 | 560.952 | 61.74 | 18.26 | 690228 | 690.228 | 58.32 | 21.68 | 819504 | 819.504 | 54.9 | 25.1 | 948780 | 948.78 | 51.48 | 28.52 | 1078056 | 1078.056 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.22 | 38.78 | 1465884 | 1465.884 | 37.8 | 42.2 | 1595160 | 1595.16 | 40
12/15/20XX 8:00:00 AM | 0.33333 | 4 | 37.7 | 67.5 | 37.7 |  | 37.7 | 68.57 | 11.43 | 432054 | 432.054 | 65.14 | 14.86 | 561708 | 561.708 | 61.71 | 18.29 | 691362 | 691.362 | 58.28 | 21.72 | 821016 | 821.016 | 54.85 | 25.15 | 950670 | 950.67 | 51.42 | 28.58 | 1080324 | 1080.324 | 47.99 | 32.01 | 1209978 | 1209.978 | 44.56 | 35.44 | 1339632 | 1339.632 | 41.13 | 38.87 | 1469286 | 1469.286 | 37.7 | 42.3 | 1598940 | 1598.94 | 40
12/15/20XX 9:00:00 AM | 0.375 | 4 | 38.5 | 65.3 | 38.5 |  | 38.5 | 68.65 | 11.35 | 429030 | 429.03 | 65.3 | 14.7 | 555660 | 555.66 | 61.95 | 18.05 | 682290 | 682.29 | 58.6 | 21.4 | 808920 | 808.92 | 55.25 | 24.75 | 935550 | 935.55 | 51.9 | 28.1 | 1062180 | 1062.18 | 48.55 | 31.45 | 1188810 | 1188.81 | 45.2 | 34.8 | 1315440 | 1315.44 | 41.85 | 38.15 | 1442070 | 1442.07 | 38.5 | 41.5 | 1568700 | 1568.7 | 40
12/15/20XX 10:00:00 AM | 0.41667 | 4 | 38.8 | 65.5 | 38.8 |  | 38.8 | 68.68 | 11.32 | 427896 | 427.896 | 65.36 | 14.64 | 553392 | 553.392 | 62.04 | 17.96 | 678888 | 678.888 | 58.72 | 21.28 | 804384 | 804.384 | 55.4 | 24.6 | 929880 | 929.88 | 52.08 | 27.92 | 1055376 | 1055.376 | 48.76 | 31.24 | 1180872 | 1180.872 | 45.44 | 34.56 | 1306368 | 1306.368 | 42.12 | 37.88 | 1431864 | 1431.864 | 38.8 | 41.2 | 1557360 | 1557.36 | 40
12/15/20XX 11:00:00 AM | 0.45833 | 4 | 40.2 | 61.3 | 40.2 |  | 40.2 | 68.82 | 11.18 | 422604 | 422.604 | 65.64 | 14.36 | 542808 | 542.808 | 62.46 | 17.54 | 663012 | 663.012 | 59.28 | 20.72 | 783216 | 783.216 | 56.1 | 23.9 | 903420 | 903.42 | 52.92 | 27.08 | 1023624 | 1023.624 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.56 | 33.44 | 1264032 | 1264.032 | 43.38 | 36.62 | 1384236 | 1384.236 | 40.2 | 39.8 | 1504440 | 1504.44 | 40
12/15/20XX 12:00:00 PM | 0.5 | 4 | 41.4 | 56.3 | 41.4 |  | 41.4 | 68.94 | 11.06 | 418068 | 418.068 | 65.88 | 14.12 | 533736 | 533.736 | 62.82 | 17.18 | 649404 | 649.404 | 59.76 | 20.24 | 765072 | 765.072 | 56.7 | 23.3 | 880740 | 880.74 | 53.64 | 26.36 | 996408 | 996.408 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.46 | 35.54 | 1343412 | 1343.412 | 41.4 | 38.6 | 1459080 | 1459.08 | 40
12/15/20XX 1:00:00 PM | 0.54167 | 4 | 42.3 | 56 | 42.3 |  | 42.3 | 69.03 | 10.97 | 414666 | 414.666 | 66.06 | 13.94 | 526932 | 526.932 | 63.09 | 16.91 | 639198 | 639.198 | 60.12 | 19.88 | 751464 | 751.464 | 57.15 | 22.85 | 863730 | 863.73 | 54.18 | 25.82 | 975996 | 975.996 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.27 | 34.73 | 1312794 | 1312.794 | 42.3 | 37.7 | 1425060 | 1425.06 | 40
12/15/20XX 2:00:00 PM | 0.58333 | 4 | 43 | 52.7 | 43 |  | 43 | 69.1 | 10.9 | 412020 | 412.02 | 66.2 | 13.8 | 521640 | 521.64 | 63.3 | 16.7 | 631260 | 631.26 | 60.4 | 19.6 | 740880 | 740.88 | 57.5 | 22.5 | 850500 | 850.5 | 54.6 | 25.4 | 960120 | 960.12 | 51.7 | 28.3 | 1069740 | 1069.74 | 48.8 | 31.2 | 1179360 | 1179.36 | 45.9 | 34.1 | 1288980 | 1288.98 | 43 | 37 | 1398600 | 1398.6 | 45
12/15/20XX 3:00:00 PM | 0.625 | 4 | 42.8 | 53.3 | 42.8 |  | 42.8 | 69.08 | 10.92 | 412776 | 412.776 | 66.16 | 13.84 | 523152 | 523.152 | 63.24 | 16.76 | 633528 | 633.528 | 60.32 | 19.68 | 743904 | 743.904 | 57.4 | 22.6 | 854280 | 854.28 | 54.48 | 25.52 | 964656 | 964.656 | 51.56 | 28.44 | 1075032 | 1075.032 | 48.64 | 31.36 | 1185408 | 1185.408 | 45.72 | 34.28 | 1295784 | 1295.784 | 42.8 | 37.2 | 1406160 | 1406.16 | 45
12/15/20XX 4:00:00 PM | 0.66667 | 4 | 42.2 | 55.5 | 42.2 |  | 42.2 | 69.02 | 10.98 | 415044 | 415.044 | 66.04 | 13.96 | 527688 | 527.688 | 63.06 | 16.94 | 640332 | 640.332 | 60.08 | 19.92 | 752976 | 752.976 | 57.1 | 22.9 | 865620 | 865.62 | 54.12 | 25.88 | 978264 | 978.264 | 51.14 | 28.86 | 1090908 | 1090.908 | 48.16 | 31.84 | 1203552 | 1203.552 | 45.18 | 34.82 | 1316196 | 1316.196 | 42.2 | 37.8 | 1428840 | 1428.84 | 40
12/15/20XX 5:00:00 PM | 0.70833 | 4 | 41.6 | 56 | 41.6 |  | 41.6 | 68.96 | 11.04 | 417312 | 417.312 | 65.92 | 14.08 | 532224 | 532.224 | 62.88 | 17.12 | 647136 | 647.136 | 59.84 | 20.16 | 762048 | 762.048 | 56.8 | 23.2 | 876960 | 876.96 | 53.76 | 26.24 | 991872 | 991.872 | 50.72 | 29.28 | 1106784 | 1106.784 | 47.68 | 32.32 | 1221696 | 1221.696 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.6 | 38.4 | 1451520 | 1451.52 | 40
12/15/20XX 6:00:00 PM | 0.75 | 4 | 41.2 | 56.1 | 41.2 |  | 41.2 | 68.92 | 11.08 | 418824 | 418.824 | 65.84 | 14.16 | 535248 | 535.248 | 62.76 | 17.24 | 651672 | 651.672 | 59.68 | 20.32 | 768096 | 768.096 | 56.6 | 23.4 | 884520 | 884.52 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.44 | 29.56 | 1117368 | 1117.368 | 47.36 | 32.64 | 1233792 | 1233.792 | 44.28 | 35.72 | 1350216 | 1350.216 | 41.2 | 38.8 | 1466640 | 1466.64 | 40
12/15/20XX 7:00:00 PM | 0.79167 | 4 | 40.9 | 57.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/15/20XX 8:00:00 PM | 0.83333 | 4 | 40.4 | 58.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/15/20XX 9:00:00 PM | 0.875 | 4 | 40 | 58.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/15/20XX 10:00:00 PM | 0.91667 | 4 | 39.6 | 59.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/15/20XX 11:00:00 PM | 0.95833 | 4 | 39.3 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/15/20XX 12:00:00 AM | 0 | 5 | 38.7 | 61.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/16/20XX 1:00:00 AM | 0.041667 | 5 | 37.9 | 64.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/16/20XX 2:00:00 AM | 0.083333 | 5 | 37.4 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/16/20XX 3:00:00 AM | 0.125 | 5 | 37.2 | 64 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/16/20XX 4:00:00 AM | 0.16667 | 5 | 36.7 | 63.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/16/20XX 5:00:00 AM | 0.20833 | 5 | 35.8 | 61.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/16/20XX 6:00:00 AM | 0.25 | 5 | 34.9 | 62.8 | 34.9 |  | 34.9 | 68.29 | 11.71 | 442638 | 442.638 | 64.58 | 15.42 | 582876 | 582.876 | 60.87 | 19.13 | 723114 | 723.114 | 57.16 | 22.84 | 863352 | 863.352 | 53.45 | 26.55 | 1003590 | 1003.59 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.03 | 33.97 | 1284066 | 1284.066 | 42.32 | 37.68 | 1424304 | 1424.304 | 38.61 | 41.39 | 1564542 | 1564.542 | 34.9 | 45.1 | 1704780 | 1704.78 | 35
12/16/20XX 7:00:00 AM | 0.29167 | 5 | 34.4 | 61.9 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
12/16/20XX 8:00:00 AM | 0.33333 | 5 | 34.3 | 62 | 34.3 |  | 34.3 | 68.23 | 11.77 | 444906 | 444.906 | 64.46 | 15.54 | 587412 | 587.412 | 60.69 | 19.31 | 729918 | 729.918 | 56.92 | 23.08 | 872424 | 872.424 | 53.15 | 26.85 | 1014930 | 1014.93 | 49.38 | 30.62 | 1157436 | 1157.436 | 45.61 | 34.39 | 1299942 | 1299.942 | 41.84 | 38.16 | 1442448 | 1442.448 | 38.07 | 41.93 | 1584954 | 1584.954 | 34.3 | 45.7 | 1727460 | 1727.46 | 35
12/16/20XX 9:00:00 AM | 0.375 | 5 | 34.4 | 61.8 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
12/16/20XX 10:00:00 AM | 0.41667 | 5 | 35.6 | 60 | 35.6 |  | 35.6 | 68.36 | 11.64 | 439992 | 439.992 | 64.72 | 15.28 | 577584 | 577.584 | 61.08 | 18.92 | 715176 | 715.176 | 57.44 | 22.56 | 852768 | 852.768 | 53.8 | 26.2 | 990360 | 990.36 | 50.16 | 29.84 | 1127952 | 1127.952 | 46.52 | 33.48 | 1265544 | 1265.544 | 42.88 | 37.12 | 1403136 | 1403.136 | 39.24 | 40.76 | 1540728 | 1540.728 | 35.6 | 44.4 | 1678320 | 1678.32 | 35
12/16/20XX 11:00:00 AM | 0.45833 | 5 | 36.6 | 59 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
12/16/20XX 12:00:00 PM | 0.5 | 5 | 37.8 | 55.9 | 37.8 |  | 37.8 | 68.58 | 11.42 | 431676 | 431.676 | 65.16 | 14.84 | 560952 | 560.952 | 61.74 | 18.26 | 690228 | 690.228 | 58.32 | 21.68 | 819504 | 819.504 | 54.9 | 25.1 | 948780 | 948.78 | 51.48 | 28.52 | 1078056 | 1078.056 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.22 | 38.78 | 1465884 | 1465.884 | 37.8 | 42.2 | 1595160 | 1595.16 | 40
12/16/20XX 1:00:00 PM | 0.54167 | 5 | 38.7 | 56.2 | 38.7 |  | 38.7 | 68.67 | 11.33 | 428274 | 428.274 | 65.34 | 14.66 | 554148 | 554.148 | 62.01 | 17.99 | 680022 | 680.022 | 58.68 | 21.32 | 805896 | 805.896 | 55.35 | 24.65 | 931770 | 931.77 | 52.02 | 27.98 | 1057644 | 1057.644 | 48.69 | 31.31 | 1183518 | 1183.518 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.03 | 37.97 | 1435266 | 1435.266 | 38.7 | 41.3 | 1561140 | 1561.14 | 40
12/16/20XX 2:00:00 PM | 0.58333 | 5 | 38.7 | 55.8 | 38.7 |  | 38.7 | 68.67 | 11.33 | 428274 | 428.274 | 65.34 | 14.66 | 554148 | 554.148 | 62.01 | 17.99 | 680022 | 680.022 | 58.68 | 21.32 | 805896 | 805.896 | 55.35 | 24.65 | 931770 | 931.77 | 52.02 | 27.98 | 1057644 | 1057.644 | 48.69 | 31.31 | 1183518 | 1183.518 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.03 | 37.97 | 1435266 | 1435.266 | 38.7 | 41.3 | 1561140 | 1561.14 | 40
12/16/20XX 3:00:00 PM | 0.625 | 5 | 38.5 | 56.6 | 38.5 |  | 38.5 | 68.65 | 11.35 | 429030 | 429.03 | 65.3 | 14.7 | 555660 | 555.66 | 61.95 | 18.05 | 682290 | 682.29 | 58.6 | 21.4 | 808920 | 808.92 | 55.25 | 24.75 | 935550 | 935.55 | 51.9 | 28.1 | 1062180 | 1062.18 | 48.55 | 31.45 | 1188810 | 1188.81 | 45.2 | 34.8 | 1315440 | 1315.44 | 41.85 | 38.15 | 1442070 | 1442.07 | 38.5 | 41.5 | 1568700 | 1568.7 | 40
12/16/20XX 4:00:00 PM | 0.66667 | 5 | 38.2 | 57.5 | 38.2 |  | 38.2 | 68.62 | 11.38 | 430164 | 430.164 | 65.24 | 14.76 | 557928 | 557.928 | 61.86 | 18.14 | 685692 | 685.692 | 58.48 | 21.52 | 813456 | 813.456 | 55.1 | 24.9 | 941220 | 941.22 | 51.72 | 28.28 | 1068984 | 1068.984 | 48.34 | 31.66 | 1196748 | 1196.748 | 44.96 | 35.04 | 1324512 | 1324.512 | 41.58 | 38.42 | 1452276 | 1452.276 | 38.2 | 41.8 | 1580040 | 1580.04 | 40
12/16/20XX 5:00:00 PM | 0.70833 | 5 | 37.9 | 58.3 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
12/16/20XX 6:00:00 PM | 0.75 | 5 | 37.3 | 61.7 | 37.3 |  | 37.3 | 68.53 | 11.47 | 433566 | 433.566 | 65.06 | 14.94 | 564732 | 564.732 | 61.59 | 18.41 | 695898 | 695.898 | 58.12 | 21.88 | 827064 | 827.064 | 54.65 | 25.35 | 958230 | 958.23 | 51.18 | 28.82 | 1089396 | 1089.396 | 47.71 | 32.29 | 1220562 | 1220.562 | 44.24 | 35.76 | 1351728 | 1351.728 | 40.77 | 39.23 | 1482894 | 1482.894 | 37.3 | 42.7 | 1614060 | 1614.06 | 35
12/16/20XX 7:00:00 PM | 0.79167 | 5 | 37.3 | 61.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/16/20XX 8:00:00 PM | 0.83333 | 5 | 36.7 | 62.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/16/20XX 9:00:00 PM | 0.875 | 5 | 35.8 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/16/20XX 10:00:00 PM | 0.91667 | 5 | 36.1 | 65.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/16/20XX 11:00:00 PM | 0.95833 | 5 | 35.9 | 65.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/16/20XX 12:00:00 AM | 0 | 6 | 35.5 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/17/20XX 1:00:00 AM | 0.041667 | 6 | 35.6 | 66.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/17/20XX 2:00:00 AM | 0.083333 | 6 | 35.6 | 64.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/17/20XX 3:00:00 AM | 0.125 | 6 | 35.6 | 66.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/17/20XX 4:00:00 AM | 0.16667 | 6 | 35 | 70.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/17/20XX 5:00:00 AM | 0.20833 | 6 | 35.3 | 70.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/17/20XX 6:00:00 AM | 0.25 | 6 | 35.2 | 72.4 | 35.2 |  | 35.2 | 68.32 | 11.68 | 441504 | 441.504 | 64.64 | 15.36 | 580608 | 580.608 | 60.96 | 19.04 | 719712 | 719.712 | 57.28 | 22.72 | 858816 | 858.816 | 53.6 | 26.4 | 997920 | 997.92 | 49.92 | 30.08 | 1137024 | 1137.024 | 46.24 | 33.76 | 1276128 | 1276.128 | 42.56 | 37.44 | 1415232 | 1415.232 | 38.88 | 41.12 | 1554336 | 1554.336 | 35.2 | 44.8 | 1693440 | 1693.44 | 35
12/17/20XX 7:00:00 AM | 0.29167 | 6 | 35.3 | 73.8 | 35.3 |  | 35.3 | 68.33 | 11.67 | 441126 | 441.126 | 64.66 | 15.34 | 579852 | 579.852 | 60.99 | 19.01 | 718578 | 718.578 | 57.32 | 22.68 | 857304 | 857.304 | 53.65 | 26.35 | 996030 | 996.03 | 49.98 | 30.02 | 1134756 | 1134.756 | 46.31 | 33.69 | 1273482 | 1273.482 | 42.64 | 37.36 | 1412208 | 1412.208 | 38.97 | 41.03 | 1550934 | 1550.934 | 35.3 | 44.7 | 1689660 | 1689.66 | 35
12/17/20XX 8:00:00 AM | 0.33333 | 6 | 35.4 | 73.3 | 35.4 |  | 35.4 | 68.34 | 11.66 | 440748 | 440.748 | 64.68 | 15.32 | 579096 | 579.096 | 61.02 | 18.98 | 717444 | 717.444 | 57.36 | 22.64 | 855792 | 855.792 | 53.7 | 26.3 | 994140 | 994.14 | 50.04 | 29.96 | 1132488 | 1132.488 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.72 | 37.28 | 1409184 | 1409.184 | 39.06 | 40.94 | 1547532 | 1547.532 | 35.4 | 44.6 | 1685880 | 1685.88 | 35
12/17/20XX 9:00:00 AM | 0.375 | 6 | 36.2 | 73.2 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
12/17/20XX 10:00:00 AM | 0.41667 | 6 | 37.8 | 72.2 | 37.8 |  | 37.8 | 68.58 | 11.42 | 431676 | 431.676 | 65.16 | 14.84 | 560952 | 560.952 | 61.74 | 18.26 | 690228 | 690.228 | 58.32 | 21.68 | 819504 | 819.504 | 54.9 | 25.1 | 948780 | 948.78 | 51.48 | 28.52 | 1078056 | 1078.056 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.22 | 38.78 | 1465884 | 1465.884 | 37.8 | 42.2 | 1595160 | 1595.16 | 40
12/17/20XX 11:00:00 AM | 0.45833 | 6 | 39.3 | 70 | 39.3 |  | 39.3 | 68.73 | 11.27 | 426006 | 426.006 | 65.46 | 14.54 | 549612 | 549.612 | 62.19 | 17.81 | 673218 | 673.218 | 58.92 | 21.08 | 796824 | 796.824 | 55.65 | 24.35 | 920430 | 920.43 | 52.38 | 27.62 | 1044036 | 1044.036 | 49.11 | 30.89 | 1167642 | 1167.642 | 45.84 | 34.16 | 1291248 | 1291.248 | 42.57 | 37.43 | 1414854 | 1414.854 | 39.3 | 40.7 | 1538460 | 1538.46 | 40
12/17/20XX 12:00:00 PM | 0.5 | 6 | 40.1 | 68.1 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
12/17/20XX 1:00:00 PM | 0.54167 | 6 | 40.7 | 67.7 | 40.7 |  | 40.7 | 68.87 | 11.13 | 420714 | 420.714 | 65.74 | 14.26 | 539028 | 539.028 | 62.61 | 17.39 | 657342 | 657.342 | 59.48 | 20.52 | 775656 | 775.656 | 56.35 | 23.65 | 893970 | 893.97 | 53.22 | 26.78 | 1012284 | 1012.284 | 50.09 | 29.91 | 1130598 | 1130.598 | 46.96 | 33.04 | 1248912 | 1248.912 | 43.83 | 36.17 | 1367226 | 1367.226 | 40.7 | 39.3 | 1485540 | 1485.54 | 40
12/17/20XX 2:00:00 PM | 0.58333 | 6 | 41 | 66 | 41 |  | 41 | 68.9 | 11.1 | 419580 | 419.58 | 65.8 | 14.2 | 536760 | 536.76 | 62.7 | 17.3 | 653940 | 653.94 | 59.6 | 20.4 | 771120 | 771.12 | 56.5 | 23.5 | 888300 | 888.3 | 53.4 | 26.6 | 1005480 | 1005.48 | 50.3 | 29.7 | 1122660 | 1122.66 | 47.2 | 32.8 | 1239840 | 1239.84 | 44.1 | 35.9 | 1357020 | 1357.02 | 41 | 39 | 1474200 | 1474.2 | 40
12/17/20XX 3:00:00 PM | 0.625 | 6 | 40.4 | 64.6 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
12/17/20XX 4:00:00 PM | 0.66667 | 6 | 40.1 | 65.4 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
12/17/20XX 5:00:00 PM | 0.70833 | 6 | 39.1 | 67.6 | 39.1 |  | 39.1 | 68.71 | 11.29 | 426762 | 426.762 | 65.42 | 14.58 | 551124 | 551.124 | 62.13 | 17.87 | 675486 | 675.486 | 58.84 | 21.16 | 799848 | 799.848 | 55.55 | 24.45 | 924210 | 924.21 | 52.26 | 27.74 | 1048572 | 1048.572 | 48.97 | 31.03 | 1172934 | 1172.934 | 45.68 | 34.32 | 1297296 | 1297.296 | 42.39 | 37.61 | 1421658 | 1421.658 | 39.1 | 40.9 | 1546020 | 1546.02 | 40
12/17/20XX 6:00:00 PM | 0.75 | 6 | 38.8 | 65.8 | 38.8 |  | 38.8 | 68.68 | 11.32 | 427896 | 427.896 | 65.36 | 14.64 | 553392 | 553.392 | 62.04 | 17.96 | 678888 | 678.888 | 58.72 | 21.28 | 804384 | 804.384 | 55.4 | 24.6 | 929880 | 929.88 | 52.08 | 27.92 | 1055376 | 1055.376 | 48.76 | 31.24 | 1180872 | 1180.872 | 45.44 | 34.56 | 1306368 | 1306.368 | 42.12 | 37.88 | 1431864 | 1431.864 | 38.8 | 41.2 | 1557360 | 1557.36 | 40
12/17/20XX 7:00:00 PM | 0.79167 | 6 | 38.5 | 65.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/17/20XX 8:00:00 PM | 0.83333 | 6 | 37.4444 | 69.6667 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/17/20XX 9:00:00 PM | 0.875 | 6 | 37.6 | 67.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/17/20XX 10:00:00 PM | 0.91667 | 6 | 37 | 68.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/17/20XX 11:00:00 PM | 0.95833 | 6 | 36.9 | 67.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/17/20XX 12:00:00 AM | 0 | 7 | 36.2 | 67.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/18/20XX 1:00:00 AM | 0.041667 | 7 | 35.7 | 68.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/18/20XX 2:00:00 AM | 0.083333 | 7 | 35.5 | 67.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/18/20XX 3:00:00 AM | 0.125 | 7 | 35.3 | 68.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/18/20XX 4:00:00 AM | 0.16667 | 7 | 35.1 | 70.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/18/20XX 5:00:00 AM | 0.20833 | 7 | 34.9 | 70.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/18/20XX 6:00:00 AM | 0.25 | 7 | 35.1 | 70.4 | 35.1 |  | 35.1 | 68.31 | 11.69 | 441882 | 441.882 | 64.62 | 15.38 | 581364 | 581.364 | 60.93 | 19.07 | 720846 | 720.846 | 57.24 | 22.76 | 860328 | 860.328 | 53.55 | 26.45 | 999810 | 999.81 | 49.86 | 30.14 | 1139292 | 1139.292 | 46.17 | 33.83 | 1278774 | 1278.774 | 42.48 | 37.52 | 1418256 | 1418.256 | 38.79 | 41.21 | 1557738 | 1557.738 | 35.1 | 44.9 | 1697220 | 1697.22 | 35
12/18/20XX 7:00:00 AM | 0.29167 | 7 | 34.5 | 70.1 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
12/18/20XX 8:00:00 AM | 0.33333 | 7 | 34.2 | 69.7 | 34.2 |  | 34.2 | 68.22 | 11.78 | 445284 | 445.284 | 64.44 | 15.56 | 588168 | 588.168 | 60.66 | 19.34 | 731052 | 731.052 | 56.88 | 23.12 | 873936 | 873.936 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.32 | 30.68 | 1159704 | 1159.704 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.98 | 42.02 | 1588356 | 1588.356 | 34.2 | 45.8 | 1731240 | 1731.24 | 35
12/18/20XX 9:00:00 AM | 0.375 | 7 | 35.1 | 67.6 | 35.1 |  | 35.1 | 68.31 | 11.69 | 441882 | 441.882 | 64.62 | 15.38 | 581364 | 581.364 | 60.93 | 19.07 | 720846 | 720.846 | 57.24 | 22.76 | 860328 | 860.328 | 53.55 | 26.45 | 999810 | 999.81 | 49.86 | 30.14 | 1139292 | 1139.292 | 46.17 | 33.83 | 1278774 | 1278.774 | 42.48 | 37.52 | 1418256 | 1418.256 | 38.79 | 41.21 | 1557738 | 1557.738 | 35.1 | 44.9 | 1697220 | 1697.22 | 35
12/18/20XX 10:00:00 AM | 0.41667 | 7 | 36.2 | 65.5 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
12/18/20XX 11:00:00 AM | 0.45833 | 7 | 37.6 | 61.5 | 37.6 |  | 37.6 | 68.56 | 11.44 | 432432 | 432.432 | 65.12 | 14.88 | 562464 | 562.464 | 61.68 | 18.32 | 692496 | 692.496 | 58.24 | 21.76 | 822528 | 822.528 | 54.8 | 25.2 | 952560 | 952.56 | 51.36 | 28.64 | 1082592 | 1082.592 | 47.92 | 32.08 | 1212624 | 1212.624 | 44.48 | 35.52 | 1342656 | 1342.656 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.6 | 42.4 | 1602720 | 1602.72 | 40
12/18/20XX 12:00:00 PM | 0.5 | 7 | 39 | 58.5 | 39 |  | 39 | 68.7 | 11.3 | 427140 | 427.14 | 65.4 | 14.6 | 551880 | 551.88 | 62.1 | 17.9 | 676620 | 676.62 | 58.8 | 21.2 | 801360 | 801.36 | 55.5 | 24.5 | 926100 | 926.1 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.6 | 34.4 | 1300320 | 1300.32 | 42.3 | 37.7 | 1425060 | 1425.06 | 39 | 41 | 1549800 | 1549.8 | 40
12/18/20XX 1:00:00 PM | 0.54167 | 7 | 40.1 | 55.2 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
12/18/20XX 2:00:00 PM | 0.58333 | 7 | 40.7 | 54.1 | 40.7 |  | 40.7 | 68.87 | 11.13 | 420714 | 420.714 | 65.74 | 14.26 | 539028 | 539.028 | 62.61 | 17.39 | 657342 | 657.342 | 59.48 | 20.52 | 775656 | 775.656 | 56.35 | 23.65 | 893970 | 893.97 | 53.22 | 26.78 | 1012284 | 1012.284 | 50.09 | 29.91 | 1130598 | 1130.598 | 46.96 | 33.04 | 1248912 | 1248.912 | 43.83 | 36.17 | 1367226 | 1367.226 | 40.7 | 39.3 | 1485540 | 1485.54 | 40
12/18/20XX 3:00:00 PM | 0.625 | 7 | 40 | 51.3 | 40 |  | 40 | 68.8 | 11.2 | 423360 | 423.36 | 65.6 | 14.4 | 544320 | 544.32 | 62.4 | 17.6 | 665280 | 665.28 | 59.2 | 20.8 | 786240 | 786.24 | 56 | 24 | 907200 | 907.2 | 52.8 | 27.2 | 1028160 | 1028.16 | 49.6 | 30.4 | 1149120 | 1149.12 | 46.4 | 33.6 | 1270080 | 1270.08 | 43.2 | 36.8 | 1391040 | 1391.04 | 40 | 40 | 1512000 | 1512 | 40
12/18/20XX 4:00:00 PM | 0.66667 | 7 | 39.5 | 49.7 | 39.5 |  | 39.5 | 68.75 | 11.25 | 425250 | 425.25 | 65.5 | 14.5 | 548100 | 548.1 | 62.25 | 17.75 | 670950 | 670.95 | 59 | 21 | 793800 | 793.8 | 55.75 | 24.25 | 916650 | 916.65 | 52.5 | 27.5 | 1039500 | 1039.5 | 49.25 | 30.75 | 1162350 | 1162.35 | 46 | 34 | 1285200 | 1285.2 | 42.75 | 37.25 | 1408050 | 1408.05 | 39.5 | 40.5 | 1530900 | 1530.9 | 40
12/18/20XX 5:00:00 PM | 0.70833 | 7 | 38.5 | 48.9 | 38.5 |  | 38.5 | 68.65 | 11.35 | 429030 | 429.03 | 65.3 | 14.7 | 555660 | 555.66 | 61.95 | 18.05 | 682290 | 682.29 | 58.6 | 21.4 | 808920 | 808.92 | 55.25 | 24.75 | 935550 | 935.55 | 51.9 | 28.1 | 1062180 | 1062.18 | 48.55 | 31.45 | 1188810 | 1188.81 | 45.2 | 34.8 | 1315440 | 1315.44 | 41.85 | 38.15 | 1442070 | 1442.07 | 38.5 | 41.5 | 1568700 | 1568.7 | 40
12/18/20XX 6:00:00 PM | 0.75 | 7 | 37.9 | 48.4 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
12/18/20XX 7:00:00 PM | 0.79167 | 7 | 37.2 | 47.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/18/20XX 8:00:00 PM | 0.83333 | 7 | 36.8 | 48.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/18/20XX 9:00:00 PM | 0.875 | 7 | 36.1 | 49.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/18/20XX 10:00:00 PM | 0.91667 | 7 | 35.3 | 50.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/18/20XX 11:00:00 PM | 0.95833 | 7 | 34.8 | 52.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/18/20XX 12:00:00 AM | 0 | 1 | 34.2 | 52.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/19/20XX 1:00:00 AM | 0.041667 | 1 | 34.1 | 53.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/19/20XX 2:00:00 AM | 0.083333 | 1 | 33.9 | 54.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/19/20XX 3:00:00 AM | 0.125 | 1 | 33.5 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/19/20XX 4:00:00 AM | 0.16667 | 1 | 33.6 | 55 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/19/20XX 5:00:00 AM | 0.20833 | 1 | 33.8 | 54.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/19/20XX 6:00:00 AM | 0.25 | 1 | 33.7 | 55.4 | 33.7 |  | 33.7 | 68.17 | 11.83 | 447174 | 447.174 | 64.34 | 15.66 | 591948 | 591.948 | 60.51 | 19.49 | 736722 | 736.722 | 56.68 | 23.32 | 881496 | 881.496 | 52.85 | 27.15 | 1026270 | 1026.27 | 49.02 | 30.98 | 1171044 | 1171.044 | 45.19 | 34.81 | 1315818 | 1315.818 | 41.36 | 38.64 | 1460592 | 1460.592 | 37.53 | 42.47 | 1605366 | 1605.366 | 33.7 | 46.3 | 1750140 | 1750.14 | 35
12/19/20XX 7:00:00 AM | 0.29167 | 1 | 33.6 | 55.8 | 33.6 |  | 33.6 | 68.16 | 11.84 | 447552 | 447.552 | 64.32 | 15.68 | 592704 | 592.704 | 60.48 | 19.52 | 737856 | 737.856 | 56.64 | 23.36 | 883008 | 883.008 | 52.8 | 27.2 | 1028160 | 1028.16 | 48.96 | 31.04 | 1173312 | 1173.312 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.28 | 38.72 | 1463616 | 1463.616 | 37.44 | 42.56 | 1608768 | 1608.768 | 33.6 | 46.4 | 1753920 | 1753.92 | 35
12/19/20XX 8:00:00 AM | 0.33333 | 1 | 33.4 | 56.2 | 33.4 |  | 33.4 | 68.14 | 11.86 | 448308 | 448.308 | 64.28 | 15.72 | 594216 | 594.216 | 60.42 | 19.58 | 740124 | 740.124 | 56.56 | 23.44 | 886032 | 886.032 | 52.7 | 27.3 | 1031940 | 1031.94 | 48.84 | 31.16 | 1177848 | 1177.848 | 44.98 | 35.02 | 1323756 | 1323.756 | 41.12 | 38.88 | 1469664 | 1469.664 | 37.26 | 42.74 | 1615572 | 1615.572 | 33.4 | 46.6 | 1761480 | 1761.48 | 35
12/19/20XX 9:00:00 AM | 0.375 | 1 | 34.2 | 54.1 | 34.2 |  | 34.2 | 68.22 | 11.78 | 445284 | 445.284 | 64.44 | 15.56 | 588168 | 588.168 | 60.66 | 19.34 | 731052 | 731.052 | 56.88 | 23.12 | 873936 | 873.936 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.32 | 30.68 | 1159704 | 1159.704 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.98 | 42.02 | 1588356 | 1588.356 | 34.2 | 45.8 | 1731240 | 1731.24 | 35
12/19/20XX 10:00:00 AM | 0.41667 | 1 | 35.5 | 51.3 | 35.5 |  | 35.5 | 68.35 | 11.65 | 440370 | 440.37 | 64.7 | 15.3 | 578340 | 578.34 | 61.05 | 18.95 | 716310 | 716.31 | 57.4 | 22.6 | 854280 | 854.28 | 53.75 | 26.25 | 992250 | 992.25 | 50.1 | 29.9 | 1130220 | 1130.22 | 46.45 | 33.55 | 1268190 | 1268.19 | 42.8 | 37.2 | 1406160 | 1406.16 | 39.15 | 40.85 | 1544130 | 1544.13 | 35.5 | 44.5 | 1682100 | 1682.1 | 35
12/19/20XX 11:00:00 AM | 0.45833 | 1 | 36.5 | 48.6 | 36.5 |  | 36.5 | 68.45 | 11.55 | 436590 | 436.59 | 64.9 | 15.1 | 570780 | 570.78 | 61.35 | 18.65 | 704970 | 704.97 | 57.8 | 22.2 | 839160 | 839.16 | 54.25 | 25.75 | 973350 | 973.35 | 50.7 | 29.3 | 1107540 | 1107.54 | 47.15 | 32.85 | 1241730 | 1241.73 | 43.6 | 36.4 | 1375920 | 1375.92 | 40.05 | 39.95 | 1510110 | 1510.11 | 36.5 | 43.5 | 1644300 | 1644.3 | 35
12/19/20XX 12:00:00 PM | 0.5 | 1 | 37.7 | 46.7 | 37.7 |  | 37.7 | 68.57 | 11.43 | 432054 | 432.054 | 65.14 | 14.86 | 561708 | 561.708 | 61.71 | 18.29 | 691362 | 691.362 | 58.28 | 21.72 | 821016 | 821.016 | 54.85 | 25.15 | 950670 | 950.67 | 51.42 | 28.58 | 1080324 | 1080.324 | 47.99 | 32.01 | 1209978 | 1209.978 | 44.56 | 35.44 | 1339632 | 1339.632 | 41.13 | 38.87 | 1469286 | 1469.286 | 37.7 | 42.3 | 1598940 | 1598.94 | 40
12/19/20XX 1:00:00 PM | 0.54167 | 1 | 38.7 | 44.4 | 38.7 |  | 38.7 | 68.67 | 11.33 | 428274 | 428.274 | 65.34 | 14.66 | 554148 | 554.148 | 62.01 | 17.99 | 680022 | 680.022 | 58.68 | 21.32 | 805896 | 805.896 | 55.35 | 24.65 | 931770 | 931.77 | 52.02 | 27.98 | 1057644 | 1057.644 | 48.69 | 31.31 | 1183518 | 1183.518 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.03 | 37.97 | 1435266 | 1435.266 | 38.7 | 41.3 | 1561140 | 1561.14 | 40
12/19/20XX 2:00:00 PM | 0.58333 | 1 | 39.8 | 45.3 | 39.8 |  | 39.8 | 68.78 | 11.22 | 424116 | 424.116 | 65.56 | 14.44 | 545832 | 545.832 | 62.34 | 17.66 | 667548 | 667.548 | 59.12 | 20.88 | 789264 | 789.264 | 55.9 | 24.1 | 910980 | 910.98 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.46 | 30.54 | 1154412 | 1154.412 | 46.24 | 33.76 | 1276128 | 1276.128 | 43.02 | 36.98 | 1397844 | 1397.844 | 39.8 | 40.2 | 1519560 | 1519.56 | 40
12/19/20XX 3:00:00 PM | 0.625 | 1 | 39.9 | 46.3 | 39.9 |  | 39.9 | 68.79 | 11.21 | 423738 | 423.738 | 65.58 | 14.42 | 545076 | 545.076 | 62.37 | 17.63 | 666414 | 666.414 | 59.16 | 20.84 | 787752 | 787.752 | 55.95 | 24.05 | 909090 | 909.09 | 52.74 | 27.26 | 1030428 | 1030.428 | 49.53 | 30.47 | 1151766 | 1151.766 | 46.32 | 33.68 | 1273104 | 1273.104 | 43.11 | 36.89 | 1394442 | 1394.442 | 39.9 | 40.1 | 1515780 | 1515.78 | 40
12/19/20XX 4:00:00 PM | 0.66667 | 1 | 39.8 | 47.4 | 39.8 |  | 39.8 | 68.78 | 11.22 | 424116 | 424.116 | 65.56 | 14.44 | 545832 | 545.832 | 62.34 | 17.66 | 667548 | 667.548 | 59.12 | 20.88 | 789264 | 789.264 | 55.9 | 24.1 | 910980 | 910.98 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.46 | 30.54 | 1154412 | 1154.412 | 46.24 | 33.76 | 1276128 | 1276.128 | 43.02 | 36.98 | 1397844 | 1397.844 | 39.8 | 40.2 | 1519560 | 1519.56 | 40
12/19/20XX 5:00:00 PM | 0.70833 | 1 | 39 | 49.1 | 39 |  | 39 | 68.7 | 11.3 | 427140 | 427.14 | 65.4 | 14.6 | 551880 | 551.88 | 62.1 | 17.9 | 676620 | 676.62 | 58.8 | 21.2 | 801360 | 801.36 | 55.5 | 24.5 | 926100 | 926.1 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.6 | 34.4 | 1300320 | 1300.32 | 42.3 | 37.7 | 1425060 | 1425.06 | 39 | 41 | 1549800 | 1549.8 | 40
12/19/20XX 6:00:00 PM | 0.75 | 1 | 38.6 | 50.7 | 38.6 |  | 38.6 | 68.66 | 11.34 | 428652 | 428.652 | 65.32 | 14.68 | 554904 | 554.904 | 61.98 | 18.02 | 681156 | 681.156 | 58.64 | 21.36 | 807408 | 807.408 | 55.3 | 24.7 | 933660 | 933.66 | 51.96 | 28.04 | 1059912 | 1059.912 | 48.62 | 31.38 | 1186164 | 1186.164 | 45.28 | 34.72 | 1312416 | 1312.416 | 41.94 | 38.06 | 1438668 | 1438.668 | 38.6 | 41.4 | 1564920 | 1564.92 | 40
12/19/20XX 7:00:00 PM | 0.79167 | 1 | 38 | 51.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/19/20XX 8:00:00 PM | 0.83333 | 1 | 37.6 | 53.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/19/20XX 9:00:00 PM | 0.875 | 1 | 37.4 | 54.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/19/20XX 10:00:00 PM | 0.91667 | 1 | 37.1 | 54.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/19/20XX 11:00:00 PM | 0.95833 | 1 | 37 | 54.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/19/20XX 12:00:00 AM | 0 | 2 | 36.8 | 54.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/20/20XX 1:00:00 AM | 0.041667 | 2 | 36.4 | 57.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/20/20XX 2:00:00 AM | 0.083333 | 2 | 36.4 | 58.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/20/20XX 3:00:00 AM | 0.125 | 2 | 35.8 | 59.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/20/20XX 4:00:00 AM | 0.16667 | 2 | 35.3 | 59.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/20/20XX 5:00:00 AM | 0.20833 | 2 | 35 | 63.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/20/20XX 6:00:00 AM | 0.25 | 2 | 34.4 | 63.3 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
12/20/20XX 7:00:00 AM | 0.29167 | 2 | 34.3 | 60.5 | 34.3 |  | 34.3 | 68.23 | 11.77 | 444906 | 444.906 | 64.46 | 15.54 | 587412 | 587.412 | 60.69 | 19.31 | 729918 | 729.918 | 56.92 | 23.08 | 872424 | 872.424 | 53.15 | 26.85 | 1014930 | 1014.93 | 49.38 | 30.62 | 1157436 | 1157.436 | 45.61 | 34.39 | 1299942 | 1299.942 | 41.84 | 38.16 | 1442448 | 1442.448 | 38.07 | 41.93 | 1584954 | 1584.954 | 34.3 | 45.7 | 1727460 | 1727.46 | 35
12/20/20XX 8:00:00 AM | 0.33333 | 2 | 34.2 | 59.4 | 34.2 |  | 34.2 | 68.22 | 11.78 | 445284 | 445.284 | 64.44 | 15.56 | 588168 | 588.168 | 60.66 | 19.34 | 731052 | 731.052 | 56.88 | 23.12 | 873936 | 873.936 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.32 | 30.68 | 1159704 | 1159.704 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.98 | 42.02 | 1588356 | 1588.356 | 34.2 | 45.8 | 1731240 | 1731.24 | 35
12/20/20XX 9:00:00 AM | 0.375 | 2 | 35.2 | 55.2 | 35.2 |  | 35.2 | 68.32 | 11.68 | 441504 | 441.504 | 64.64 | 15.36 | 580608 | 580.608 | 60.96 | 19.04 | 719712 | 719.712 | 57.28 | 22.72 | 858816 | 858.816 | 53.6 | 26.4 | 997920 | 997.92 | 49.92 | 30.08 | 1137024 | 1137.024 | 46.24 | 33.76 | 1276128 | 1276.128 | 42.56 | 37.44 | 1415232 | 1415.232 | 38.88 | 41.12 | 1554336 | 1554.336 | 35.2 | 44.8 | 1693440 | 1693.44 | 35
12/20/20XX 10:00:00 AM | 0.41667 | 2 | 36.2 | 52.6 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
12/20/20XX 11:00:00 AM | 0.45833 | 2 | 37.5 | 50.2 | 37.5 |  | 37.5 | 68.55 | 11.45 | 432810 | 432.81 | 65.1 | 14.9 | 563220 | 563.22 | 61.65 | 18.35 | 693630 | 693.63 | 58.2 | 21.8 | 824040 | 824.04 | 54.75 | 25.25 | 954450 | 954.45 | 51.3 | 28.7 | 1084860 | 1084.86 | 47.85 | 32.15 | 1215270 | 1215.27 | 44.4 | 35.6 | 1345680 | 1345.68 | 40.95 | 39.05 | 1476090 | 1476.09 | 37.5 | 42.5 | 1606500 | 1606.5 | 35
12/20/20XX 12:00:00 PM | 0.5 | 2 | 38.4 | 48.7 | 38.4 |  | 38.4 | 68.64 | 11.36 | 429408 | 429.408 | 65.28 | 14.72 | 556416 | 556.416 | 61.92 | 18.08 | 683424 | 683.424 | 58.56 | 21.44 | 810432 | 810.432 | 55.2 | 24.8 | 937440 | 937.44 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.76 | 38.24 | 1445472 | 1445.472 | 38.4 | 41.6 | 1572480 | 1572.48 | 40
12/20/20XX 1:00:00 PM | 0.54167 | 2 | 39.5 | 46.7 | 39.5 |  | 39.5 | 68.75 | 11.25 | 425250 | 425.25 | 65.5 | 14.5 | 548100 | 548.1 | 62.25 | 17.75 | 670950 | 670.95 | 59 | 21 | 793800 | 793.8 | 55.75 | 24.25 | 916650 | 916.65 | 52.5 | 27.5 | 1039500 | 1039.5 | 49.25 | 30.75 | 1162350 | 1162.35 | 46 | 34 | 1285200 | 1285.2 | 42.75 | 37.25 | 1408050 | 1408.05 | 39.5 | 40.5 | 1530900 | 1530.9 | 40
12/20/20XX 2:00:00 PM | 0.58333 | 2 | 40.4 | 45.6 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
12/20/20XX 3:00:00 PM | 0.625 | 2 | 40.2 | 45.9 | 40.2 |  | 40.2 | 68.82 | 11.18 | 422604 | 422.604 | 65.64 | 14.36 | 542808 | 542.808 | 62.46 | 17.54 | 663012 | 663.012 | 59.28 | 20.72 | 783216 | 783.216 | 56.1 | 23.9 | 903420 | 903.42 | 52.92 | 27.08 | 1023624 | 1023.624 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.56 | 33.44 | 1264032 | 1264.032 | 43.38 | 36.62 | 1384236 | 1384.236 | 40.2 | 39.8 | 1504440 | 1504.44 | 40
12/20/20XX 4:00:00 PM | 0.66667 | 2 | 40.2 | 47 | 40.2 |  | 40.2 | 68.82 | 11.18 | 422604 | 422.604 | 65.64 | 14.36 | 542808 | 542.808 | 62.46 | 17.54 | 663012 | 663.012 | 59.28 | 20.72 | 783216 | 783.216 | 56.1 | 23.9 | 903420 | 903.42 | 52.92 | 27.08 | 1023624 | 1023.624 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.56 | 33.44 | 1264032 | 1264.032 | 43.38 | 36.62 | 1384236 | 1384.236 | 40.2 | 39.8 | 1504440 | 1504.44 | 40
12/20/20XX 5:00:00 PM | 0.70833 | 2 | 39.4 | 51 | 39.4 |  | 39.4 | 68.74 | 11.26 | 425628 | 425.628 | 65.48 | 14.52 | 548856 | 548.856 | 62.22 | 17.78 | 672084 | 672.084 | 58.96 | 21.04 | 795312 | 795.312 | 55.7 | 24.3 | 918540 | 918.54 | 52.44 | 27.56 | 1041768 | 1041.768 | 49.18 | 30.82 | 1164996 | 1164.996 | 45.92 | 34.08 | 1288224 | 1288.224 | 42.66 | 37.34 | 1411452 | 1411.452 | 39.4 | 40.6 | 1534680 | 1534.68 | 40
12/20/20XX 6:00:00 PM | 0.75 | 2 | 39.3 | 52.1 | 39.3 |  | 39.3 | 68.73 | 11.27 | 426006 | 426.006 | 65.46 | 14.54 | 549612 | 549.612 | 62.19 | 17.81 | 673218 | 673.218 | 58.92 | 21.08 | 796824 | 796.824 | 55.65 | 24.35 | 920430 | 920.43 | 52.38 | 27.62 | 1044036 | 1044.036 | 49.11 | 30.89 | 1167642 | 1167.642 | 45.84 | 34.16 | 1291248 | 1291.248 | 42.57 | 37.43 | 1414854 | 1414.854 | 39.3 | 40.7 | 1538460 | 1538.46 | 40
12/20/20XX 7:00:00 PM | 0.79167 | 2 | 38.9 | 55.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/20/20XX 8:00:00 PM | 0.83333 | 2 | 38.4 | 59.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/20/20XX 9:00:00 PM | 0.875 | 2 | 38.2 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/20/20XX 10:00:00 PM | 0.91667 | 2 | 38.4 | 61.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/20/20XX 11:00:00 PM | 0.95833 | 2 | 38.3 | 63.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/20/20XX 12:00:00 AM | 0 | 3 | 38.3 | 65.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/21/20XX 1:00:00 AM | 0.041667 | 3 | 39.3 | 65.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/21/20XX 2:00:00 AM | 0.083333 | 3 | 39.5 | 66.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/21/20XX 3:00:00 AM | 0.125 | 3 | 39.5 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/21/20XX 4:00:00 AM | 0.16667 | 3 | 40.1 | 68.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/21/20XX 5:00:00 AM | 0.20833 | 3 | 40 | 70.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/21/20XX 6:00:00 AM | 0.25 | 3 | 40.4 | 71.3 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
12/21/20XX 7:00:00 AM | 0.29167 | 3 | 41 | 71.7 | 41 |  | 41 | 68.9 | 11.1 | 419580 | 419.58 | 65.8 | 14.2 | 536760 | 536.76 | 62.7 | 17.3 | 653940 | 653.94 | 59.6 | 20.4 | 771120 | 771.12 | 56.5 | 23.5 | 888300 | 888.3 | 53.4 | 26.6 | 1005480 | 1005.48 | 50.3 | 29.7 | 1122660 | 1122.66 | 47.2 | 32.8 | 1239840 | 1239.84 | 44.1 | 35.9 | 1357020 | 1357.02 | 41 | 39 | 1474200 | 1474.2 | 40
12/21/20XX 8:00:00 AM | 0.33333 | 3 | 41.6 | 71.8 | 41.6 |  | 41.6 | 68.96 | 11.04 | 417312 | 417.312 | 65.92 | 14.08 | 532224 | 532.224 | 62.88 | 17.12 | 647136 | 647.136 | 59.84 | 20.16 | 762048 | 762.048 | 56.8 | 23.2 | 876960 | 876.96 | 53.76 | 26.24 | 991872 | 991.872 | 50.72 | 29.28 | 1106784 | 1106.784 | 47.68 | 32.32 | 1221696 | 1221.696 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.6 | 38.4 | 1451520 | 1451.52 | 40
12/21/20XX 9:00:00 AM | 0.375 | 3 | 42.3 | 71.4 | 42.3 |  | 42.3 | 69.03 | 10.97 | 414666 | 414.666 | 66.06 | 13.94 | 526932 | 526.932 | 63.09 | 16.91 | 639198 | 639.198 | 60.12 | 19.88 | 751464 | 751.464 | 57.15 | 22.85 | 863730 | 863.73 | 54.18 | 25.82 | 975996 | 975.996 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.27 | 34.73 | 1312794 | 1312.794 | 42.3 | 37.7 | 1425060 | 1425.06 | 40
12/21/20XX 10:00:00 AM | 0.41667 | 3 | 42.9 | 68.8 | 42.9 |  | 42.9 | 69.09 | 10.91 | 412398 | 412.398 | 66.18 | 13.82 | 522396 | 522.396 | 63.27 | 16.73 | 632394 | 632.394 | 60.36 | 19.64 | 742392 | 742.392 | 57.45 | 22.55 | 852390 | 852.39 | 54.54 | 25.46 | 962388 | 962.388 | 51.63 | 28.37 | 1072386 | 1072.386 | 48.72 | 31.28 | 1182384 | 1182.384 | 45.81 | 34.19 | 1292382 | 1292.382 | 42.9 | 37.1 | 1402380 | 1402.38 | 45
12/21/20XX 11:00:00 AM | 0.45833 | 3 | 43.2 | 66.7 | 43.2 |  | 43.2 | 69.12 | 10.88 | 411264 | 411.264 | 66.24 | 13.76 | 520128 | 520.128 | 63.36 | 16.64 | 628992 | 628.992 | 60.48 | 19.52 | 737856 | 737.856 | 57.6 | 22.4 | 846720 | 846.72 | 54.72 | 25.28 | 955584 | 955.584 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.08 | 33.92 | 1282176 | 1282.176 | 43.2 | 36.8 | 1391040 | 1391.04 | 45
12/21/20XX 12:00:00 PM | 0.5 | 3 | 44.3 | 63 | 44.3 |  | 44.3 | 69.23 | 10.77 | 407106 | 407.106 | 66.46 | 13.54 | 511812 | 511.812 | 63.69 | 16.31 | 616518 | 616.518 | 60.92 | 19.08 | 721224 | 721.224 | 58.15 | 21.85 | 825930 | 825.93 | 55.38 | 24.62 | 930636 | 930.636 | 52.61 | 27.39 | 1035342 | 1035.342 | 49.84 | 30.16 | 1140048 | 1140.048 | 47.07 | 32.93 | 1244754 | 1244.754 | 44.3 | 35.7 | 1349460 | 1349.46 | 45
12/21/20XX 1:00:00 PM | 0.54167 | 3 | 44.8 | 61.1 | 44.8 |  | 44.8 | 69.28 | 10.72 | 405216 | 405.216 | 66.56 | 13.44 | 508032 | 508.032 | 63.84 | 16.16 | 610848 | 610.848 | 61.12 | 18.88 | 713664 | 713.664 | 58.4 | 21.6 | 816480 | 816.48 | 55.68 | 24.32 | 919296 | 919.296 | 52.96 | 27.04 | 1022112 | 1022.112 | 50.24 | 29.76 | 1124928 | 1124.928 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.8 | 35.2 | 1330560 | 1330.56 | 45
12/21/20XX 2:00:00 PM | 0.58333 | 3 | 45.1 | 60 | 45.1 |  | 45.1 | 69.31 | 10.69 | 404082 | 404.082 | 66.62 | 13.38 | 505764 | 505.764 | 63.93 | 16.07 | 607446 | 607.446 | 61.24 | 18.76 | 709128 | 709.128 | 58.55 | 21.45 | 810810 | 810.81 | 55.86 | 24.14 | 912492 | 912.492 | 53.17 | 26.83 | 1014174 | 1014.174 | 50.48 | 29.52 | 1115856 | 1115.856 | 47.79 | 32.21 | 1217538 | 1217.538 | 45.1 | 34.9 | 1319220 | 1319.22 | 45
12/21/20XX 3:00:00 PM | 0.625 | 3 | 45.6 | 58.7 | 45.6 |  | 45.6 | 69.36 | 10.64 | 402192 | 402.192 | 66.72 | 13.28 | 501984 | 501.984 | 64.08 | 15.92 | 601776 | 601.776 | 61.44 | 18.56 | 701568 | 701.568 | 58.8 | 21.2 | 801360 | 801.36 | 56.16 | 23.84 | 901152 | 901.152 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.88 | 29.12 | 1100736 | 1100.736 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.6 | 34.4 | 1300320 | 1300.32 | 45
12/21/20XX 4:00:00 PM | 0.66667 | 3 | 45.4 | 59.9 | 45.4 |  | 45.4 | 69.34 | 10.66 | 402948 | 402.948 | 66.68 | 13.32 | 503496 | 503.496 | 64.02 | 15.98 | 604044 | 604.044 | 61.36 | 18.64 | 704592 | 704.592 | 58.7 | 21.3 | 805140 | 805.14 | 56.04 | 23.96 | 905688 | 905.688 | 53.38 | 26.62 | 1006236 | 1006.236 | 50.72 | 29.28 | 1106784 | 1106.784 | 48.06 | 31.94 | 1207332 | 1207.332 | 45.4 | 34.6 | 1307880 | 1307.88 | 45
12/21/20XX 5:00:00 PM | 0.70833 | 3 | 44.9 | 60.5 | 44.9 |  | 44.9 | 69.29 | 10.71 | 404838 | 404.838 | 66.58 | 13.42 | 507276 | 507.276 | 63.87 | 16.13 | 609714 | 609.714 | 61.16 | 18.84 | 712152 | 712.152 | 58.45 | 21.55 | 814590 | 814.59 | 55.74 | 24.26 | 917028 | 917.028 | 53.03 | 26.97 | 1019466 | 1019.466 | 50.32 | 29.68 | 1121904 | 1121.904 | 47.61 | 32.39 | 1224342 | 1224.342 | 44.9 | 35.1 | 1326780 | 1326.78 | 45
12/21/20XX 6:00:00 PM | 0.75 | 3 | 44.8 | 62.1 | 44.8 |  | 44.8 | 69.28 | 10.72 | 405216 | 405.216 | 66.56 | 13.44 | 508032 | 508.032 | 63.84 | 16.16 | 610848 | 610.848 | 61.12 | 18.88 | 713664 | 713.664 | 58.4 | 21.6 | 816480 | 816.48 | 55.68 | 24.32 | 919296 | 919.296 | 52.96 | 27.04 | 1022112 | 1022.112 | 50.24 | 29.76 | 1124928 | 1124.928 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.8 | 35.2 | 1330560 | 1330.56 | 45
12/21/20XX 7:00:00 PM | 0.79167 | 3 | 44.9 | 63 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/21/20XX 8:00:00 PM | 0.83333 | 3 | 45 | 63.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/21/20XX 9:00:00 PM | 0.875 | 3 | 44.6 | 63.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/21/20XX 10:00:00 PM | 0.91667 | 3 | 44.3 | 65.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/21/20XX 11:00:00 PM | 0.95833 | 3 | 43.6 | 66.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/21/20XX 12:00:00 AM | 0 | 4 | 43.2 | 67.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/22/20XX 1:00:00 AM | 0.041667 | 4 | 43 | 68.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/22/20XX 2:00:00 AM | 0.083333 | 4 | 42.8 | 69.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/22/20XX 3:00:00 AM | 0.125 | 4 | 42.7 | 69.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/22/20XX 4:00:00 AM | 0.16667 | 4 | 42.9 | 68.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/22/20XX 5:00:00 AM | 0.20833 | 4 | 43.1 | 69 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/22/20XX 6:00:00 AM | 0.25 | 4 | 43.2 | 69.5 | 43.2 |  | 43.2 | 69.12 | 10.88 | 411264 | 411.264 | 66.24 | 13.76 | 520128 | 520.128 | 63.36 | 16.64 | 628992 | 628.992 | 60.48 | 19.52 | 737856 | 737.856 | 57.6 | 22.4 | 846720 | 846.72 | 54.72 | 25.28 | 955584 | 955.584 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.08 | 33.92 | 1282176 | 1282.176 | 43.2 | 36.8 | 1391040 | 1391.04 | 45
12/22/20XX 7:00:00 AM | 0.29167 | 4 | 42.5 | 67.6 | 42.5 |  | 42.5 | 69.05 | 10.95 | 413910 | 413.91 | 66.1 | 13.9 | 525420 | 525.42 | 63.15 | 16.85 | 636930 | 636.93 | 60.2 | 19.8 | 748440 | 748.44 | 57.25 | 22.75 | 859950 | 859.95 | 54.3 | 25.7 | 971460 | 971.46 | 51.35 | 28.65 | 1082970 | 1082.97 | 48.4 | 31.6 | 1194480 | 1194.48 | 45.45 | 34.55 | 1305990 | 1305.99 | 42.5 | 37.5 | 1417500 | 1417.5 | 40
12/22/20XX 8:00:00 AM | 0.33333 | 4 | 42.6 | 67.8 | 42.6 |  | 42.6 | 69.06 | 10.94 | 413532 | 413.532 | 66.12 | 13.88 | 524664 | 524.664 | 63.18 | 16.82 | 635796 | 635.796 | 60.24 | 19.76 | 746928 | 746.928 | 57.3 | 22.7 | 858060 | 858.06 | 54.36 | 25.64 | 969192 | 969.192 | 51.42 | 28.58 | 1080324 | 1080.324 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.54 | 34.46 | 1302588 | 1302.588 | 42.6 | 37.4 | 1413720 | 1413.72 | 45
12/22/20XX 9:00:00 AM | 0.375 | 4 | 43.5 | 64.6 | 43.5 |  | 43.5 | 69.15 | 10.85 | 410130 | 410.13 | 66.3 | 13.7 | 517860 | 517.86 | 63.45 | 16.55 | 625590 | 625.59 | 60.6 | 19.4 | 733320 | 733.32 | 57.75 | 22.25 | 841050 | 841.05 | 54.9 | 25.1 | 948780 | 948.78 | 52.05 | 27.95 | 1056510 | 1056.51 | 49.2 | 30.8 | 1164240 | 1164.24 | 46.35 | 33.65 | 1271970 | 1271.97 | 43.5 | 36.5 | 1379700 | 1379.7 | 45
12/22/20XX 10:00:00 AM | 0.41667 | 4 | 44.5 | 63 | 44.5 |  | 44.5 | 69.25 | 10.75 | 406350 | 406.35 | 66.5 | 13.5 | 510300 | 510.3 | 63.75 | 16.25 | 614250 | 614.25 | 61 | 19 | 718200 | 718.2 | 58.25 | 21.75 | 822150 | 822.15 | 55.5 | 24.5 | 926100 | 926.1 | 52.75 | 27.25 | 1030050 | 1030.05 | 50 | 30 | 1134000 | 1134 | 47.25 | 32.75 | 1237950 | 1237.95 | 44.5 | 35.5 | 1341900 | 1341.9 | 45
12/22/20XX 11:00:00 AM | 0.45833 | 4 | 45.3 | 61.3 | 45.3 |  | 45.3 | 69.33 | 10.67 | 403326 | 403.326 | 66.66 | 13.34 | 504252 | 504.252 | 63.99 | 16.01 | 605178 | 605.178 | 61.32 | 18.68 | 706104 | 706.104 | 58.65 | 21.35 | 807030 | 807.03 | 55.98 | 24.02 | 907956 | 907.956 | 53.31 | 26.69 | 1008882 | 1008.882 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.97 | 32.03 | 1210734 | 1210.734 | 45.3 | 34.7 | 1311660 | 1311.66 | 45
12/22/20XX 12:00:00 PM | 0.5 | 4 | 45.9 | 60.6 | 45.9 |  | 45.9 | 69.39 | 10.61 | 401058 | 401.058 | 66.78 | 13.22 | 499716 | 499.716 | 64.17 | 15.83 | 598374 | 598.374 | 61.56 | 18.44 | 697032 | 697.032 | 58.95 | 21.05 | 795690 | 795.69 | 56.34 | 23.66 | 894348 | 894.348 | 53.73 | 26.27 | 993006 | 993.006 | 51.12 | 28.88 | 1091664 | 1091.664 | 48.51 | 31.49 | 1190322 | 1190.322 | 45.9 | 34.1 | 1288980 | 1288.98 | 45
12/22/20XX 1:00:00 PM | 0.54167 | 4 | 46.5 | 59.2 | 46.5 |  | 46.5 | 69.45 | 10.55 | 398790 | 398.79 | 66.9 | 13.1 | 495180 | 495.18 | 64.35 | 15.65 | 591570 | 591.57 | 61.8 | 18.2 | 687960 | 687.96 | 59.25 | 20.75 | 784350 | 784.35 | 56.7 | 23.3 | 880740 | 880.74 | 54.15 | 25.85 | 977130 | 977.13 | 51.6 | 28.4 | 1073520 | 1073.52 | 49.05 | 30.95 | 1169910 | 1169.91 | 46.5 | 33.5 | 1266300 | 1266.3 | 45
12/22/20XX 2:00:00 PM | 0.58333 | 4 | 46.9 | 58.6 | 46.9 |  | 46.9 | 69.49 | 10.51 | 397278 | 397.278 | 66.98 | 13.02 | 492156 | 492.156 | 64.47 | 15.53 | 587034 | 587.034 | 61.96 | 18.04 | 681912 | 681.912 | 59.45 | 20.55 | 776790 | 776.79 | 56.94 | 23.06 | 871668 | 871.668 | 54.43 | 25.57 | 966546 | 966.546 | 51.92 | 28.08 | 1061424 | 1061.424 | 49.41 | 30.59 | 1156302 | 1156.302 | 46.9 | 33.1 | 1251180 | 1251.18 | 45
12/22/20XX 3:00:00 PM | 0.625 | 4 | 47.4 | 59.3 | 47.4 |  | 47.4 | 69.54 | 10.46 | 395388 | 395.388 | 67.08 | 12.92 | 488376 | 488.376 | 64.62 | 15.38 | 581364 | 581.364 | 62.16 | 17.84 | 674352 | 674.352 | 59.7 | 20.3 | 767340 | 767.34 | 57.24 | 22.76 | 860328 | 860.328 | 54.78 | 25.22 | 953316 | 953.316 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.86 | 30.14 | 1139292 | 1139.292 | 47.4 | 32.6 | 1232280 | 1232.28 | 45
12/22/20XX 4:00:00 PM | 0.66667 | 4 | 47.1 | 61.3 | 47.1 |  | 47.1 | 69.51 | 10.49 | 396522 | 396.522 | 67.02 | 12.98 | 490644 | 490.644 | 64.53 | 15.47 | 584766 | 584.766 | 62.04 | 17.96 | 678888 | 678.888 | 59.55 | 20.45 | 773010 | 773.01 | 57.06 | 22.94 | 867132 | 867.132 | 54.57 | 25.43 | 961254 | 961.254 | 52.08 | 27.92 | 1055376 | 1055.376 | 49.59 | 30.41 | 1149498 | 1149.498 | 47.1 | 32.9 | 1243620 | 1243.62 | 45
12/22/20XX 5:00:00 PM | 0.70833 | 4 | 46.7 | 61.9 | 46.7 |  | 46.7 | 69.47 | 10.53 | 398034 | 398.034 | 66.94 | 13.06 | 493668 | 493.668 | 64.41 | 15.59 | 589302 | 589.302 | 61.88 | 18.12 | 684936 | 684.936 | 59.35 | 20.65 | 780570 | 780.57 | 56.82 | 23.18 | 876204 | 876.204 | 54.29 | 25.71 | 971838 | 971.838 | 51.76 | 28.24 | 1067472 | 1067.472 | 49.23 | 30.77 | 1163106 | 1163.106 | 46.7 | 33.3 | 1258740 | 1258.74 | 45
12/22/20XX 6:00:00 PM | 0.75 | 4 | 46.2 | 62.1 | 46.2 |  | 46.2 | 69.42 | 10.58 | 399924 | 399.924 | 66.84 | 13.16 | 497448 | 497.448 | 64.26 | 15.74 | 594972 | 594.972 | 61.68 | 18.32 | 692496 | 692.496 | 59.1 | 20.9 | 790020 | 790.02 | 56.52 | 23.48 | 887544 | 887.544 | 53.94 | 26.06 | 985068 | 985.068 | 51.36 | 28.64 | 1082592 | 1082.592 | 48.78 | 31.22 | 1180116 | 1180.116 | 46.2 | 33.8 | 1277640 | 1277.64 | 45
12/22/20XX 7:00:00 PM | 0.79167 | 4 | 46 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/22/20XX 8:00:00 PM | 0.83333 | 4 | 45.3 | 61.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/22/20XX 9:00:00 PM | 0.875 | 4 | 44.6 | 61.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/22/20XX 10:00:00 PM | 0.91667 | 4 | 43.9 | 63.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/22/20XX 11:00:00 PM | 0.95833 | 4 | 43.4 | 64.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/22/20XX 12:00:00 AM | 0 | 5 | 42.5 | 68.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/23/20XX 1:00:00 AM | 0.041667 | 5 | 42.2 | 70.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/23/20XX 2:00:00 AM | 0.083333 | 5 | 42.1 | 71.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/23/20XX 3:00:00 AM | 0.125 | 5 | 41.9 | 70.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/23/20XX 4:00:00 AM | 0.16667 | 5 | 41.6 | 71.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/23/20XX 5:00:00 AM | 0.20833 | 5 | 40.8 | 73.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/23/20XX 6:00:00 AM | 0.25 | 5 | 40.6 | 74.4 | 40.6 |  | 40.6 | 68.86 | 11.14 | 421092 | 421.092 | 65.72 | 14.28 | 539784 | 539.784 | 62.58 | 17.42 | 658476 | 658.476 | 59.44 | 20.56 | 777168 | 777.168 | 56.3 | 23.7 | 895860 | 895.86 | 53.16 | 26.84 | 1014552 | 1014.552 | 50.02 | 29.98 | 1133244 | 1133.244 | 46.88 | 33.12 | 1251936 | 1251.936 | 43.74 | 36.26 | 1370628 | 1370.628 | 40.6 | 39.4 | 1489320 | 1489.32 | 40
12/23/20XX 7:00:00 AM | 0.29167 | 5 | 40.3 | 74.3 | 40.3 |  | 40.3 | 68.83 | 11.17 | 422226 | 422.226 | 65.66 | 14.34 | 542052 | 542.052 | 62.49 | 17.51 | 661878 | 661.878 | 59.32 | 20.68 | 781704 | 781.704 | 56.15 | 23.85 | 901530 | 901.53 | 52.98 | 27.02 | 1021356 | 1021.356 | 49.81 | 30.19 | 1141182 | 1141.182 | 46.64 | 33.36 | 1261008 | 1261.008 | 43.47 | 36.53 | 1380834 | 1380.834 | 40.3 | 39.7 | 1500660 | 1500.66 | 40
12/23/20XX 8:00:00 AM | 0.33333 | 5 | 40.4 | 74.2 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
12/23/20XX 9:00:00 AM | 0.375 | 5 | 40.9 | 73.2 | 40.9 |  | 40.9 | 68.89 | 11.11 | 419958 | 419.958 | 65.78 | 14.22 | 537516 | 537.516 | 62.67 | 17.33 | 655074 | 655.074 | 59.56 | 20.44 | 772632 | 772.632 | 56.45 | 23.55 | 890190 | 890.19 | 53.34 | 26.66 | 1007748 | 1007.748 | 50.23 | 29.77 | 1125306 | 1125.306 | 47.12 | 32.88 | 1242864 | 1242.864 | 44.01 | 35.99 | 1360422 | 1360.422 | 40.9 | 39.1 | 1477980 | 1477.98 | 40
12/23/20XX 10:00:00 AM | 0.41667 | 5 | 41.4 | 71.3 | 41.4 |  | 41.4 | 68.94 | 11.06 | 418068 | 418.068 | 65.88 | 14.12 | 533736 | 533.736 | 62.82 | 17.18 | 649404 | 649.404 | 59.76 | 20.24 | 765072 | 765.072 | 56.7 | 23.3 | 880740 | 880.74 | 53.64 | 26.36 | 996408 | 996.408 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.46 | 35.54 | 1343412 | 1343.412 | 41.4 | 38.6 | 1459080 | 1459.08 | 40
12/23/20XX 11:00:00 AM | 0.45833 | 5 | 42.4 | 68.7 | 42.4 |  | 42.4 | 69.04 | 10.96 | 414288 | 414.288 | 66.08 | 13.92 | 526176 | 526.176 | 63.12 | 16.88 | 638064 | 638.064 | 60.16 | 19.84 | 749952 | 749.952 | 57.2 | 22.8 | 861840 | 861.84 | 54.24 | 25.76 | 973728 | 973.728 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.32 | 31.68 | 1197504 | 1197.504 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.4 | 37.6 | 1421280 | 1421.28 | 40
12/23/20XX 12:00:00 PM | 0.5 | 5 | 43.2 | 68 | 43.2 |  | 43.2 | 69.12 | 10.88 | 411264 | 411.264 | 66.24 | 13.76 | 520128 | 520.128 | 63.36 | 16.64 | 628992 | 628.992 | 60.48 | 19.52 | 737856 | 737.856 | 57.6 | 22.4 | 846720 | 846.72 | 54.72 | 25.28 | 955584 | 955.584 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.08 | 33.92 | 1282176 | 1282.176 | 43.2 | 36.8 | 1391040 | 1391.04 | 45
12/23/20XX 1:00:00 PM | 0.54167 | 5 | 43.5 | 66.7 | 43.5 |  | 43.5 | 69.15 | 10.85 | 410130 | 410.13 | 66.3 | 13.7 | 517860 | 517.86 | 63.45 | 16.55 | 625590 | 625.59 | 60.6 | 19.4 | 733320 | 733.32 | 57.75 | 22.25 | 841050 | 841.05 | 54.9 | 25.1 | 948780 | 948.78 | 52.05 | 27.95 | 1056510 | 1056.51 | 49.2 | 30.8 | 1164240 | 1164.24 | 46.35 | 33.65 | 1271970 | 1271.97 | 43.5 | 36.5 | 1379700 | 1379.7 | 45
12/23/20XX 2:00:00 PM | 0.58333 | 5 | 43.8 | 63.8 | 43.8 |  | 43.8 | 69.18 | 10.82 | 408996 | 408.996 | 66.36 | 13.64 | 515592 | 515.592 | 63.54 | 16.46 | 622188 | 622.188 | 60.72 | 19.28 | 728784 | 728.784 | 57.9 | 22.1 | 835380 | 835.38 | 55.08 | 24.92 | 941976 | 941.976 | 52.26 | 27.74 | 1048572 | 1048.572 | 49.44 | 30.56 | 1155168 | 1155.168 | 46.62 | 33.38 | 1261764 | 1261.764 | 43.8 | 36.2 | 1368360 | 1368.36 | 45
12/23/20XX 3:00:00 PM | 0.625 | 5 | 43.9 | 64.8 | 43.9 |  | 43.9 | 69.19 | 10.81 | 408618 | 408.618 | 66.38 | 13.62 | 514836 | 514.836 | 63.57 | 16.43 | 621054 | 621.054 | 60.76 | 19.24 | 727272 | 727.272 | 57.95 | 22.05 | 833490 | 833.49 | 55.14 | 24.86 | 939708 | 939.708 | 52.33 | 27.67 | 1045926 | 1045.926 | 49.52 | 30.48 | 1152144 | 1152.144 | 46.71 | 33.29 | 1258362 | 1258.362 | 43.9 | 36.1 | 1364580 | 1364.58 | 45
12/23/20XX 4:00:00 PM | 0.66667 | 5 | 43.9 | 64.8 | 43.9 |  | 43.9 | 69.19 | 10.81 | 408618 | 408.618 | 66.38 | 13.62 | 514836 | 514.836 | 63.57 | 16.43 | 621054 | 621.054 | 60.76 | 19.24 | 727272 | 727.272 | 57.95 | 22.05 | 833490 | 833.49 | 55.14 | 24.86 | 939708 | 939.708 | 52.33 | 27.67 | 1045926 | 1045.926 | 49.52 | 30.48 | 1152144 | 1152.144 | 46.71 | 33.29 | 1258362 | 1258.362 | 43.9 | 36.1 | 1364580 | 1364.58 | 45
12/23/20XX 5:00:00 PM | 0.70833 | 5 | 43.7 | 65 | 43.7 |  | 43.7 | 69.17 | 10.83 | 409374 | 409.374 | 66.34 | 13.66 | 516348 | 516.348 | 63.51 | 16.49 | 623322 | 623.322 | 60.68 | 19.32 | 730296 | 730.296 | 57.85 | 22.15 | 837270 | 837.27 | 55.02 | 24.98 | 944244 | 944.244 | 52.19 | 27.81 | 1051218 | 1051.218 | 49.36 | 30.64 | 1158192 | 1158.192 | 46.53 | 33.47 | 1265166 | 1265.166 | 43.7 | 36.3 | 1372140 | 1372.14 | 45
12/23/20XX 6:00:00 PM | 0.75 | 5 | 43.3 | 65.4 | 43.3 |  | 43.3 | 69.13 | 10.87 | 410886 | 410.886 | 66.26 | 13.74 | 519372 | 519.372 | 63.39 | 16.61 | 627858 | 627.858 | 60.52 | 19.48 | 736344 | 736.344 | 57.65 | 22.35 | 844830 | 844.83 | 54.78 | 25.22 | 953316 | 953.316 | 51.91 | 28.09 | 1061802 | 1061.802 | 49.04 | 30.96 | 1170288 | 1170.288 | 46.17 | 33.83 | 1278774 | 1278.774 | 43.3 | 36.7 | 1387260 | 1387.26 | 45
12/23/20XX 7:00:00 PM | 0.79167 | 5 | 42.7 | 66.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/23/20XX 8:00:00 PM | 0.83333 | 5 | 42.6 | 67.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/23/20XX 9:00:00 PM | 0.875 | 5 | 41.5 | 66 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/23/20XX 10:00:00 PM | 0.91667 | 5 | 41.6 | 66.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/23/20XX 11:00:00 PM | 0.95833 | 5 | 41.2 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/23/20XX 12:00:00 AM | 0 | 6 | 40.2 | 65.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/24/20XX 1:00:00 AM | 0.041667 | 6 | 39.7 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/24/20XX 2:00:00 AM | 0.083333 | 6 | 39 | 69.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/24/20XX 3:00:00 AM | 0.125 | 6 | 38.6 | 69.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/24/20XX 4:00:00 AM | 0.16667 | 6 | 38.4 | 68.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/24/20XX 5:00:00 AM | 0.20833 | 6 | 37.9 | 69.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/24/20XX 6:00:00 AM | 0.25 | 6 | 37.9 | 69.4 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
12/24/20XX 7:00:00 AM | 0.29167 | 6 | 38.1 | 71.4 | 38.1 |  | 38.1 | 68.61 | 11.39 | 430542 | 430.542 | 65.22 | 14.78 | 558684 | 558.684 | 61.83 | 18.17 | 686826 | 686.826 | 58.44 | 21.56 | 814968 | 814.968 | 55.05 | 24.95 | 943110 | 943.11 | 51.66 | 28.34 | 1071252 | 1071.252 | 48.27 | 31.73 | 1199394 | 1199.394 | 44.88 | 35.12 | 1327536 | 1327.536 | 41.49 | 38.51 | 1455678 | 1455.678 | 38.1 | 41.9 | 1583820 | 1583.82 | 40
12/24/20XX 8:00:00 AM | 0.33333 | 6 | 38.2 | 71.9 | 38.2 |  | 38.2 | 68.62 | 11.38 | 430164 | 430.164 | 65.24 | 14.76 | 557928 | 557.928 | 61.86 | 18.14 | 685692 | 685.692 | 58.48 | 21.52 | 813456 | 813.456 | 55.1 | 24.9 | 941220 | 941.22 | 51.72 | 28.28 | 1068984 | 1068.984 | 48.34 | 31.66 | 1196748 | 1196.748 | 44.96 | 35.04 | 1324512 | 1324.512 | 41.58 | 38.42 | 1452276 | 1452.276 | 38.2 | 41.8 | 1580040 | 1580.04 | 40
12/24/20XX 9:00:00 AM | 0.375 | 6 | 38.9 | 71.5 | 38.9 |  | 38.9 | 68.69 | 11.31 | 427518 | 427.518 | 65.38 | 14.62 | 552636 | 552.636 | 62.07 | 17.93 | 677754 | 677.754 | 58.76 | 21.24 | 802872 | 802.872 | 55.45 | 24.55 | 927990 | 927.99 | 52.14 | 27.86 | 1053108 | 1053.108 | 48.83 | 31.17 | 1178226 | 1178.226 | 45.52 | 34.48 | 1303344 | 1303.344 | 42.21 | 37.79 | 1428462 | 1428.462 | 38.9 | 41.1 | 1553580 | 1553.58 | 40
12/24/20XX 10:00:00 AM | 0.41667 | 6 | 39.4 | 70.6 | 39.4 |  | 39.4 | 68.74 | 11.26 | 425628 | 425.628 | 65.48 | 14.52 | 548856 | 548.856 | 62.22 | 17.78 | 672084 | 672.084 | 58.96 | 21.04 | 795312 | 795.312 | 55.7 | 24.3 | 918540 | 918.54 | 52.44 | 27.56 | 1041768 | 1041.768 | 49.18 | 30.82 | 1164996 | 1164.996 | 45.92 | 34.08 | 1288224 | 1288.224 | 42.66 | 37.34 | 1411452 | 1411.452 | 39.4 | 40.6 | 1534680 | 1534.68 | 40
12/24/20XX 11:00:00 AM | 0.45833 | 6 | 40.6 | 67.9 | 40.6 |  | 40.6 | 68.86 | 11.14 | 421092 | 421.092 | 65.72 | 14.28 | 539784 | 539.784 | 62.58 | 17.42 | 658476 | 658.476 | 59.44 | 20.56 | 777168 | 777.168 | 56.3 | 23.7 | 895860 | 895.86 | 53.16 | 26.84 | 1014552 | 1014.552 | 50.02 | 29.98 | 1133244 | 1133.244 | 46.88 | 33.12 | 1251936 | 1251.936 | 43.74 | 36.26 | 1370628 | 1370.628 | 40.6 | 39.4 | 1489320 | 1489.32 | 40
12/24/20XX 12:00:00 PM | 0.5 | 6 | 41.5 | 64.5 | 41.5 |  | 41.5 | 68.95 | 11.05 | 417690 | 417.69 | 65.9 | 14.1 | 532980 | 532.98 | 62.85 | 17.15 | 648270 | 648.27 | 59.8 | 20.2 | 763560 | 763.56 | 56.75 | 23.25 | 878850 | 878.85 | 53.7 | 26.3 | 994140 | 994.14 | 50.65 | 29.35 | 1109430 | 1109.43 | 47.6 | 32.4 | 1224720 | 1224.72 | 44.55 | 35.45 | 1340010 | 1340.01 | 41.5 | 38.5 | 1455300 | 1455.3 | 40
12/24/20XX 1:00:00 PM | 0.54167 | 6 | 42.7 | 61.7 | 42.7 |  | 42.7 | 69.07 | 10.93 | 413154 | 413.154 | 66.14 | 13.86 | 523908 | 523.908 | 63.21 | 16.79 | 634662 | 634.662 | 60.28 | 19.72 | 745416 | 745.416 | 57.35 | 22.65 | 856170 | 856.17 | 54.42 | 25.58 | 966924 | 966.924 | 51.49 | 28.51 | 1077678 | 1077.678 | 48.56 | 31.44 | 1188432 | 1188.432 | 45.63 | 34.37 | 1299186 | 1299.186 | 42.7 | 37.3 | 1409940 | 1409.94 | 45
12/24/20XX 2:00:00 PM | 0.58333 | 6 | 43.2 | 60 | 43.2 |  | 43.2 | 69.12 | 10.88 | 411264 | 411.264 | 66.24 | 13.76 | 520128 | 520.128 | 63.36 | 16.64 | 628992 | 628.992 | 60.48 | 19.52 | 737856 | 737.856 | 57.6 | 22.4 | 846720 | 846.72 | 54.72 | 25.28 | 955584 | 955.584 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.08 | 33.92 | 1282176 | 1282.176 | 43.2 | 36.8 | 1391040 | 1391.04 | 45
12/24/20XX 3:00:00 PM | 0.625 | 6 | 43.5 | 59.5 | 43.5 |  | 43.5 | 69.15 | 10.85 | 410130 | 410.13 | 66.3 | 13.7 | 517860 | 517.86 | 63.45 | 16.55 | 625590 | 625.59 | 60.6 | 19.4 | 733320 | 733.32 | 57.75 | 22.25 | 841050 | 841.05 | 54.9 | 25.1 | 948780 | 948.78 | 52.05 | 27.95 | 1056510 | 1056.51 | 49.2 | 30.8 | 1164240 | 1164.24 | 46.35 | 33.65 | 1271970 | 1271.97 | 43.5 | 36.5 | 1379700 | 1379.7 | 45
12/24/20XX 4:00:00 PM | 0.66667 | 6 | 43.1 | 60.1 | 43.1 |  | 43.1 | 69.11 | 10.89 | 411642 | 411.642 | 66.22 | 13.78 | 520884 | 520.884 | 63.33 | 16.67 | 630126 | 630.126 | 60.44 | 19.56 | 739368 | 739.368 | 57.55 | 22.45 | 848610 | 848.61 | 54.66 | 25.34 | 957852 | 957.852 | 51.77 | 28.23 | 1067094 | 1067.094 | 48.88 | 31.12 | 1176336 | 1176.336 | 45.99 | 34.01 | 1285578 | 1285.578 | 43.1 | 36.9 | 1394820 | 1394.82 | 45
12/24/20XX 5:00:00 PM | 0.70833 | 6 | 42.4 | 61.9 | 42.4 |  | 42.4 | 69.04 | 10.96 | 414288 | 414.288 | 66.08 | 13.92 | 526176 | 526.176 | 63.12 | 16.88 | 638064 | 638.064 | 60.16 | 19.84 | 749952 | 749.952 | 57.2 | 22.8 | 861840 | 861.84 | 54.24 | 25.76 | 973728 | 973.728 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.32 | 31.68 | 1197504 | 1197.504 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.4 | 37.6 | 1421280 | 1421.28 | 40
12/24/20XX 6:00:00 PM | 0.75 | 6 | 42.3 | 62.7 | 42.3 |  | 42.3 | 69.03 | 10.97 | 414666 | 414.666 | 66.06 | 13.94 | 526932 | 526.932 | 63.09 | 16.91 | 639198 | 639.198 | 60.12 | 19.88 | 751464 | 751.464 | 57.15 | 22.85 | 863730 | 863.73 | 54.18 | 25.82 | 975996 | 975.996 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.27 | 34.73 | 1312794 | 1312.794 | 42.3 | 37.7 | 1425060 | 1425.06 | 40
12/24/20XX 7:00:00 PM | 0.79167 | 6 | 42 | 64.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/24/20XX 8:00:00 PM | 0.83333 | 6 | 41 | 68.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/24/20XX 9:00:00 PM | 0.875 | 6 | 41 | 66.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/24/20XX 10:00:00 PM | 0.91667 | 6 | 40.3 | 66.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/24/20XX 11:00:00 PM | 0.95833 | 6 | 39.7 | 68.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/24/20XX 12:00:00 AM | 0 | 7 | 38.9 | 69.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/25/20XX 1:00:00 AM | 0.041667 | 7 | 38.7 | 70.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/25/20XX 2:00:00 AM | 0.083333 | 7 | 38.5 | 70.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/25/20XX 3:00:00 AM | 0.125 | 7 | 38.9 | 71.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/25/20XX 4:00:00 AM | 0.16667 | 7 | 38.7 | 71.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/25/20XX 5:00:00 AM | 0.20833 | 7 | 38.1 | 71.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/25/20XX 6:00:00 AM | 0.25 | 7 | 37.1 | 71.5 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
12/25/20XX 7:00:00 AM | 0.29167 | 7 | 36.7 | 71.6 | 36.7 |  | 36.7 | 68.47 | 11.53 | 435834 | 435.834 | 64.94 | 15.06 | 569268 | 569.268 | 61.41 | 18.59 | 702702 | 702.702 | 57.88 | 22.12 | 836136 | 836.136 | 54.35 | 25.65 | 969570 | 969.57 | 50.82 | 29.18 | 1103004 | 1103.004 | 47.29 | 32.71 | 1236438 | 1236.438 | 43.76 | 36.24 | 1369872 | 1369.872 | 40.23 | 39.77 | 1503306 | 1503.306 | 36.7 | 43.3 | 1636740 | 1636.74 | 35
12/25/20XX 8:00:00 AM | 0.33333 | 7 | 36.8 | 72.1 | 36.8 |  | 36.8 | 68.48 | 11.52 | 435456 | 435.456 | 64.96 | 15.04 | 568512 | 568.512 | 61.44 | 18.56 | 701568 | 701.568 | 57.92 | 22.08 | 834624 | 834.624 | 54.4 | 25.6 | 967680 | 967.68 | 50.88 | 29.12 | 1100736 | 1100.736 | 47.36 | 32.64 | 1233792 | 1233.792 | 43.84 | 36.16 | 1366848 | 1366.848 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.8 | 43.2 | 1632960 | 1632.96 | 35
12/25/20XX 9:00:00 AM | 0.375 | 7 | 37.2 | 67 | 37.2 |  | 37.2 | 68.52 | 11.48 | 433944 | 433.944 | 65.04 | 14.96 | 565488 | 565.488 | 61.56 | 18.44 | 697032 | 697.032 | 58.08 | 21.92 | 828576 | 828.576 | 54.6 | 25.4 | 960120 | 960.12 | 51.12 | 28.88 | 1091664 | 1091.664 | 47.64 | 32.36 | 1223208 | 1223.208 | 44.16 | 35.84 | 1354752 | 1354.752 | 40.68 | 39.32 | 1486296 | 1486.296 | 37.2 | 42.8 | 1617840 | 1617.84 | 35
12/25/20XX 10:00:00 AM | 0.41667 | 7 | 38.5 | 60 | 38.5 |  | 38.5 | 68.65 | 11.35 | 429030 | 429.03 | 65.3 | 14.7 | 555660 | 555.66 | 61.95 | 18.05 | 682290 | 682.29 | 58.6 | 21.4 | 808920 | 808.92 | 55.25 | 24.75 | 935550 | 935.55 | 51.9 | 28.1 | 1062180 | 1062.18 | 48.55 | 31.45 | 1188810 | 1188.81 | 45.2 | 34.8 | 1315440 | 1315.44 | 41.85 | 38.15 | 1442070 | 1442.07 | 38.5 | 41.5 | 1568700 | 1568.7 | 40
12/25/20XX 11:00:00 AM | 0.45833 | 7 | 39.8 | 57.6 | 39.8 |  | 39.8 | 68.78 | 11.22 | 424116 | 424.116 | 65.56 | 14.44 | 545832 | 545.832 | 62.34 | 17.66 | 667548 | 667.548 | 59.12 | 20.88 | 789264 | 789.264 | 55.9 | 24.1 | 910980 | 910.98 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.46 | 30.54 | 1154412 | 1154.412 | 46.24 | 33.76 | 1276128 | 1276.128 | 43.02 | 36.98 | 1397844 | 1397.844 | 39.8 | 40.2 | 1519560 | 1519.56 | 40
12/25/20XX 12:00:00 PM | 0.5 | 7 | 40.7 | 55.8 | 40.7 |  | 40.7 | 68.87 | 11.13 | 420714 | 420.714 | 65.74 | 14.26 | 539028 | 539.028 | 62.61 | 17.39 | 657342 | 657.342 | 59.48 | 20.52 | 775656 | 775.656 | 56.35 | 23.65 | 893970 | 893.97 | 53.22 | 26.78 | 1012284 | 1012.284 | 50.09 | 29.91 | 1130598 | 1130.598 | 46.96 | 33.04 | 1248912 | 1248.912 | 43.83 | 36.17 | 1367226 | 1367.226 | 40.7 | 39.3 | 1485540 | 1485.54 | 40
12/25/20XX 1:00:00 PM | 0.54167 | 7 | 41.3 | 54.8 | 41.3 |  | 41.3 | 68.93 | 11.07 | 418446 | 418.446 | 65.86 | 14.14 | 534492 | 534.492 | 62.79 | 17.21 | 650538 | 650.538 | 59.72 | 20.28 | 766584 | 766.584 | 56.65 | 23.35 | 882630 | 882.63 | 53.58 | 26.42 | 998676 | 998.676 | 50.51 | 29.49 | 1114722 | 1114.722 | 47.44 | 32.56 | 1230768 | 1230.768 | 44.37 | 35.63 | 1346814 | 1346.814 | 41.3 | 38.7 | 1462860 | 1462.86 | 40
12/25/20XX 2:00:00 PM | 0.58333 | 7 | 41.4 | 53.3 | 41.4 |  | 41.4 | 68.94 | 11.06 | 418068 | 418.068 | 65.88 | 14.12 | 533736 | 533.736 | 62.82 | 17.18 | 649404 | 649.404 | 59.76 | 20.24 | 765072 | 765.072 | 56.7 | 23.3 | 880740 | 880.74 | 53.64 | 26.36 | 996408 | 996.408 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.46 | 35.54 | 1343412 | 1343.412 | 41.4 | 38.6 | 1459080 | 1459.08 | 40
12/25/20XX 3:00:00 PM | 0.625 | 7 | 42 | 52.4 | 42 |  | 42 | 69 | 11 | 415800 | 415.8 | 66 | 14 | 529200 | 529.2 | 63 | 17 | 642600 | 642.6 | 60 | 20 | 756000 | 756 | 57 | 23 | 869400 | 869.4 | 54 | 26 | 982800 | 982.8 | 51 | 29 | 1096200 | 1096.2 | 48 | 32 | 1209600 | 1209.6 | 45 | 35 | 1323000 | 1323 | 42 | 38 | 1436400 | 1436.4 | 40
12/25/20XX 4:00:00 PM | 0.66667 | 7 | 41.6 | 52.7 | 41.6 |  | 41.6 | 68.96 | 11.04 | 417312 | 417.312 | 65.92 | 14.08 | 532224 | 532.224 | 62.88 | 17.12 | 647136 | 647.136 | 59.84 | 20.16 | 762048 | 762.048 | 56.8 | 23.2 | 876960 | 876.96 | 53.76 | 26.24 | 991872 | 991.872 | 50.72 | 29.28 | 1106784 | 1106.784 | 47.68 | 32.32 | 1221696 | 1221.696 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.6 | 38.4 | 1451520 | 1451.52 | 40
12/25/20XX 5:00:00 PM | 0.70833 | 7 | 40.8 | 55.6 | 40.8 |  | 40.8 | 68.88 | 11.12 | 420336 | 420.336 | 65.76 | 14.24 | 538272 | 538.272 | 62.64 | 17.36 | 656208 | 656.208 | 59.52 | 20.48 | 774144 | 774.144 | 56.4 | 23.6 | 892080 | 892.08 | 53.28 | 26.72 | 1010016 | 1010.016 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.04 | 32.96 | 1245888 | 1245.888 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.8 | 39.2 | 1481760 | 1481.76 | 40
12/25/20XX 6:00:00 PM | 0.75 | 7 | 40.4 | 56.4 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
12/25/20XX 7:00:00 PM | 0.79167 | 7 | 40 | 57.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/25/20XX 8:00:00 PM | 0.83333 | 7 | 39.1 | 58.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/25/20XX 9:00:00 PM | 0.875 | 7 | 38.7 | 60.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/25/20XX 10:00:00 PM | 0.91667 | 7 | 38.3 | 60.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/25/20XX 11:00:00 PM | 0.95833 | 7 | 37.8 | 62.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/25/20XX 12:00:00 AM | 0 | 1 | 37.3 | 63.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/26/20XX 1:00:00 AM | 0.041667 | 1 | 36.6 | 60.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/26/20XX 2:00:00 AM | 0.083333 | 1 | 36.1 | 60.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/26/20XX 3:00:00 AM | 0.125 | 1 | 35.8 | 60.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/26/20XX 4:00:00 AM | 0.16667 | 1 | 35.6 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/26/20XX 5:00:00 AM | 0.20833 | 1 | 35.3 | 61.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/26/20XX 6:00:00 AM | 0.25 | 1 | 35.4 | 61 | 35.4 |  | 35.4 | 68.34 | 11.66 | 440748 | 440.748 | 64.68 | 15.32 | 579096 | 579.096 | 61.02 | 18.98 | 717444 | 717.444 | 57.36 | 22.64 | 855792 | 855.792 | 53.7 | 26.3 | 994140 | 994.14 | 50.04 | 29.96 | 1132488 | 1132.488 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.72 | 37.28 | 1409184 | 1409.184 | 39.06 | 40.94 | 1547532 | 1547.532 | 35.4 | 44.6 | 1685880 | 1685.88 | 35
12/26/20XX 7:00:00 AM | 0.29167 | 1 | 35.3 | 60.8 | 35.3 |  | 35.3 | 68.33 | 11.67 | 441126 | 441.126 | 64.66 | 15.34 | 579852 | 579.852 | 60.99 | 19.01 | 718578 | 718.578 | 57.32 | 22.68 | 857304 | 857.304 | 53.65 | 26.35 | 996030 | 996.03 | 49.98 | 30.02 | 1134756 | 1134.756 | 46.31 | 33.69 | 1273482 | 1273.482 | 42.64 | 37.36 | 1412208 | 1412.208 | 38.97 | 41.03 | 1550934 | 1550.934 | 35.3 | 44.7 | 1689660 | 1689.66 | 35
12/26/20XX 8:00:00 AM | 0.33333 | 1 | 35.1 | 60.6 | 35.1 |  | 35.1 | 68.31 | 11.69 | 441882 | 441.882 | 64.62 | 15.38 | 581364 | 581.364 | 60.93 | 19.07 | 720846 | 720.846 | 57.24 | 22.76 | 860328 | 860.328 | 53.55 | 26.45 | 999810 | 999.81 | 49.86 | 30.14 | 1139292 | 1139.292 | 46.17 | 33.83 | 1278774 | 1278.774 | 42.48 | 37.52 | 1418256 | 1418.256 | 38.79 | 41.21 | 1557738 | 1557.738 | 35.1 | 44.9 | 1697220 | 1697.22 | 35
12/26/20XX 9:00:00 AM | 0.375 | 1 | 35.5 | 60.1 | 35.5 |  | 35.5 | 68.35 | 11.65 | 440370 | 440.37 | 64.7 | 15.3 | 578340 | 578.34 | 61.05 | 18.95 | 716310 | 716.31 | 57.4 | 22.6 | 854280 | 854.28 | 53.75 | 26.25 | 992250 | 992.25 | 50.1 | 29.9 | 1130220 | 1130.22 | 46.45 | 33.55 | 1268190 | 1268.19 | 42.8 | 37.2 | 1406160 | 1406.16 | 39.15 | 40.85 | 1544130 | 1544.13 | 35.5 | 44.5 | 1682100 | 1682.1 | 35
12/26/20XX 10:00:00 AM | 0.41667 | 1 | 36.3 | 58.9 | 36.3 |  | 36.3 | 68.43 | 11.57 | 437346 | 437.346 | 64.86 | 15.14 | 572292 | 572.292 | 61.29 | 18.71 | 707238 | 707.238 | 57.72 | 22.28 | 842184 | 842.184 | 54.15 | 25.85 | 977130 | 977.13 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.01 | 32.99 | 1247022 | 1247.022 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.87 | 40.13 | 1516914 | 1516.914 | 36.3 | 43.7 | 1651860 | 1651.86 | 35
12/26/20XX 11:00:00 AM | 0.45833 | 1 | 37.2 | 58.6 | 37.2 |  | 37.2 | 68.52 | 11.48 | 433944 | 433.944 | 65.04 | 14.96 | 565488 | 565.488 | 61.56 | 18.44 | 697032 | 697.032 | 58.08 | 21.92 | 828576 | 828.576 | 54.6 | 25.4 | 960120 | 960.12 | 51.12 | 28.88 | 1091664 | 1091.664 | 47.64 | 32.36 | 1223208 | 1223.208 | 44.16 | 35.84 | 1354752 | 1354.752 | 40.68 | 39.32 | 1486296 | 1486.296 | 37.2 | 42.8 | 1617840 | 1617.84 | 35
12/26/20XX 12:00:00 PM | 0.5 | 1 | 37.8 | 59 | 37.8 |  | 37.8 | 68.58 | 11.42 | 431676 | 431.676 | 65.16 | 14.84 | 560952 | 560.952 | 61.74 | 18.26 | 690228 | 690.228 | 58.32 | 21.68 | 819504 | 819.504 | 54.9 | 25.1 | 948780 | 948.78 | 51.48 | 28.52 | 1078056 | 1078.056 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.22 | 38.78 | 1465884 | 1465.884 | 37.8 | 42.2 | 1595160 | 1595.16 | 40
12/26/20XX 1:00:00 PM | 0.54167 | 1 | 38.4 | 59.9 | 38.4 |  | 38.4 | 68.64 | 11.36 | 429408 | 429.408 | 65.28 | 14.72 | 556416 | 556.416 | 61.92 | 18.08 | 683424 | 683.424 | 58.56 | 21.44 | 810432 | 810.432 | 55.2 | 24.8 | 937440 | 937.44 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.76 | 38.24 | 1445472 | 1445.472 | 38.4 | 41.6 | 1572480 | 1572.48 | 40
12/26/20XX 2:00:00 PM | 0.58333 | 1 | 38.9 | 61.2 | 38.9 |  | 38.9 | 68.69 | 11.31 | 427518 | 427.518 | 65.38 | 14.62 | 552636 | 552.636 | 62.07 | 17.93 | 677754 | 677.754 | 58.76 | 21.24 | 802872 | 802.872 | 55.45 | 24.55 | 927990 | 927.99 | 52.14 | 27.86 | 1053108 | 1053.108 | 48.83 | 31.17 | 1178226 | 1178.226 | 45.52 | 34.48 | 1303344 | 1303.344 | 42.21 | 37.79 | 1428462 | 1428.462 | 38.9 | 41.1 | 1553580 | 1553.58 | 40
12/26/20XX 3:00:00 PM | 0.625 | 1 | 39 | 63.9 | 39 |  | 39 | 68.7 | 11.3 | 427140 | 427.14 | 65.4 | 14.6 | 551880 | 551.88 | 62.1 | 17.9 | 676620 | 676.62 | 58.8 | 21.2 | 801360 | 801.36 | 55.5 | 24.5 | 926100 | 926.1 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.6 | 34.4 | 1300320 | 1300.32 | 42.3 | 37.7 | 1425060 | 1425.06 | 39 | 41 | 1549800 | 1549.8 | 40
12/26/20XX 4:00:00 PM | 0.66667 | 1 | 38.6 | 65.7 | 38.6 |  | 38.6 | 68.66 | 11.34 | 428652 | 428.652 | 65.32 | 14.68 | 554904 | 554.904 | 61.98 | 18.02 | 681156 | 681.156 | 58.64 | 21.36 | 807408 | 807.408 | 55.3 | 24.7 | 933660 | 933.66 | 51.96 | 28.04 | 1059912 | 1059.912 | 48.62 | 31.38 | 1186164 | 1186.164 | 45.28 | 34.72 | 1312416 | 1312.416 | 41.94 | 38.06 | 1438668 | 1438.668 | 38.6 | 41.4 | 1564920 | 1564.92 | 40
12/26/20XX 5:00:00 PM | 0.70833 | 1 | 38.3 | 66.7 | 38.3 |  | 38.3 | 68.63 | 11.37 | 429786 | 429.786 | 65.26 | 14.74 | 557172 | 557.172 | 61.89 | 18.11 | 684558 | 684.558 | 58.52 | 21.48 | 811944 | 811.944 | 55.15 | 24.85 | 939330 | 939.33 | 51.78 | 28.22 | 1066716 | 1066.716 | 48.41 | 31.59 | 1194102 | 1194.102 | 45.04 | 34.96 | 1321488 | 1321.488 | 41.67 | 38.33 | 1448874 | 1448.874 | 38.3 | 41.7 | 1576260 | 1576.26 | 40
12/26/20XX 6:00:00 PM | 0.75 | 1 | 38.7 | 67.4 | 38.7 |  | 38.7 | 68.67 | 11.33 | 428274 | 428.274 | 65.34 | 14.66 | 554148 | 554.148 | 62.01 | 17.99 | 680022 | 680.022 | 58.68 | 21.32 | 805896 | 805.896 | 55.35 | 24.65 | 931770 | 931.77 | 52.02 | 27.98 | 1057644 | 1057.644 | 48.69 | 31.31 | 1183518 | 1183.518 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.03 | 37.97 | 1435266 | 1435.266 | 38.7 | 41.3 | 1561140 | 1561.14 | 40
12/26/20XX 7:00:00 PM | 0.79167 | 1 | 38.8 | 68.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/26/20XX 8:00:00 PM | 0.83333 | 1 | 38.7 | 70.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/26/20XX 9:00:00 PM | 0.875 | 1 | 38.8 | 70.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/26/20XX 10:00:00 PM | 0.91667 | 1 | 39.4 | 71.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/26/20XX 11:00:00 PM | 0.95833 | 1 | 39.3 | 72.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/26/20XX 12:00:00 AM | 0 | 2 | 39 | 73.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/27/20XX 1:00:00 AM | 0.041667 | 2 | 39.2 | 74.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/27/20XX 2:00:00 AM | 0.083333 | 2 | 38.9 | 75.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/27/20XX 3:00:00 AM | 0.125 | 2 | 39 | 74.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/27/20XX 4:00:00 AM | 0.16667 | 2 | 39.1 | 74.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/27/20XX 5:00:00 AM | 0.20833 | 2 | 39.6 | 71.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/27/20XX 6:00:00 AM | 0.25 | 2 | 39.2 | 71.7 | 39.2 |  | 39.2 | 68.72 | 11.28 | 426384 | 426.384 | 65.44 | 14.56 | 550368 | 550.368 | 62.16 | 17.84 | 674352 | 674.352 | 58.88 | 21.12 | 798336 | 798.336 | 55.6 | 24.4 | 922320 | 922.32 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.04 | 30.96 | 1170288 | 1170.288 | 45.76 | 34.24 | 1294272 | 1294.272 | 42.48 | 37.52 | 1418256 | 1418.256 | 39.2 | 40.8 | 1542240 | 1542.24 | 40
12/27/20XX 7:00:00 AM | 0.29167 | 2 | 39 | 69.7 | 39 |  | 39 | 68.7 | 11.3 | 427140 | 427.14 | 65.4 | 14.6 | 551880 | 551.88 | 62.1 | 17.9 | 676620 | 676.62 | 58.8 | 21.2 | 801360 | 801.36 | 55.5 | 24.5 | 926100 | 926.1 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.6 | 34.4 | 1300320 | 1300.32 | 42.3 | 37.7 | 1425060 | 1425.06 | 39 | 41 | 1549800 | 1549.8 | 40
12/27/20XX 8:00:00 AM | 0.33333 | 2 | 38.8 | 68.9 | 38.8 |  | 38.8 | 68.68 | 11.32 | 427896 | 427.896 | 65.36 | 14.64 | 553392 | 553.392 | 62.04 | 17.96 | 678888 | 678.888 | 58.72 | 21.28 | 804384 | 804.384 | 55.4 | 24.6 | 929880 | 929.88 | 52.08 | 27.92 | 1055376 | 1055.376 | 48.76 | 31.24 | 1180872 | 1180.872 | 45.44 | 34.56 | 1306368 | 1306.368 | 42.12 | 37.88 | 1431864 | 1431.864 | 38.8 | 41.2 | 1557360 | 1557.36 | 40
12/27/20XX 9:00:00 AM | 0.375 | 2 | 39.1 | 67.1 | 39.1 |  | 39.1 | 68.71 | 11.29 | 426762 | 426.762 | 65.42 | 14.58 | 551124 | 551.124 | 62.13 | 17.87 | 675486 | 675.486 | 58.84 | 21.16 | 799848 | 799.848 | 55.55 | 24.45 | 924210 | 924.21 | 52.26 | 27.74 | 1048572 | 1048.572 | 48.97 | 31.03 | 1172934 | 1172.934 | 45.68 | 34.32 | 1297296 | 1297.296 | 42.39 | 37.61 | 1421658 | 1421.658 | 39.1 | 40.9 | 1546020 | 1546.02 | 40
12/27/20XX 10:00:00 AM | 0.41667 | 2 | 40.1 | 64.6 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
12/27/20XX 11:00:00 AM | 0.45833 | 2 | 40.9 | 62.2 | 40.9 |  | 40.9 | 68.89 | 11.11 | 419958 | 419.958 | 65.78 | 14.22 | 537516 | 537.516 | 62.67 | 17.33 | 655074 | 655.074 | 59.56 | 20.44 | 772632 | 772.632 | 56.45 | 23.55 | 890190 | 890.19 | 53.34 | 26.66 | 1007748 | 1007.748 | 50.23 | 29.77 | 1125306 | 1125.306 | 47.12 | 32.88 | 1242864 | 1242.864 | 44.01 | 35.99 | 1360422 | 1360.422 | 40.9 | 39.1 | 1477980 | 1477.98 | 40
12/27/20XX 12:00:00 PM | 0.5 | 2 | 41.9 | 60 | 41.9 |  | 41.9 | 68.99 | 11.01 | 416178 | 416.178 | 65.98 | 14.02 | 529956 | 529.956 | 62.97 | 17.03 | 643734 | 643.734 | 59.96 | 20.04 | 757512 | 757.512 | 56.95 | 23.05 | 871290 | 871.29 | 53.94 | 26.06 | 985068 | 985.068 | 50.93 | 29.07 | 1098846 | 1098.846 | 47.92 | 32.08 | 1212624 | 1212.624 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.9 | 38.1 | 1440180 | 1440.18 | 40
12/27/20XX 1:00:00 PM | 0.54167 | 2 | 43.3 | 55 | 43.3 |  | 43.3 | 69.13 | 10.87 | 410886 | 410.886 | 66.26 | 13.74 | 519372 | 519.372 | 63.39 | 16.61 | 627858 | 627.858 | 60.52 | 19.48 | 736344 | 736.344 | 57.65 | 22.35 | 844830 | 844.83 | 54.78 | 25.22 | 953316 | 953.316 | 51.91 | 28.09 | 1061802 | 1061.802 | 49.04 | 30.96 | 1170288 | 1170.288 | 46.17 | 33.83 | 1278774 | 1278.774 | 43.3 | 36.7 | 1387260 | 1387.26 | 45
12/27/20XX 2:00:00 PM | 0.58333 | 2 | 43.8 | 52.7 | 43.8 |  | 43.8 | 69.18 | 10.82 | 408996 | 408.996 | 66.36 | 13.64 | 515592 | 515.592 | 63.54 | 16.46 | 622188 | 622.188 | 60.72 | 19.28 | 728784 | 728.784 | 57.9 | 22.1 | 835380 | 835.38 | 55.08 | 24.92 | 941976 | 941.976 | 52.26 | 27.74 | 1048572 | 1048.572 | 49.44 | 30.56 | 1155168 | 1155.168 | 46.62 | 33.38 | 1261764 | 1261.764 | 43.8 | 36.2 | 1368360 | 1368.36 | 45
12/27/20XX 3:00:00 PM | 0.625 | 2 | 44.4 | 52.4 | 44.4 |  | 44.4 | 69.24 | 10.76 | 406728 | 406.728 | 66.48 | 13.52 | 511056 | 511.056 | 63.72 | 16.28 | 615384 | 615.384 | 60.96 | 19.04 | 719712 | 719.712 | 58.2 | 21.8 | 824040 | 824.04 | 55.44 | 24.56 | 928368 | 928.368 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.92 | 30.08 | 1137024 | 1137.024 | 47.16 | 32.84 | 1241352 | 1241.352 | 44.4 | 35.6 | 1345680 | 1345.68 | 45
12/27/20XX 4:00:00 PM | 0.66667 | 2 | 44 | 54 | 44 |  | 44 | 69.2 | 10.8 | 408240 | 408.24 | 66.4 | 13.6 | 514080 | 514.08 | 63.6 | 16.4 | 619920 | 619.92 | 60.8 | 19.2 | 725760 | 725.76 | 58 | 22 | 831600 | 831.6 | 55.2 | 24.8 | 937440 | 937.44 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.6 | 30.4 | 1149120 | 1149.12 | 46.8 | 33.2 | 1254960 | 1254.96 | 44 | 36 | 1360800 | 1360.8 | 45
12/27/20XX 5:00:00 PM | 0.70833 | 2 | 43.1 | 56 | 43.1 |  | 43.1 | 69.11 | 10.89 | 411642 | 411.642 | 66.22 | 13.78 | 520884 | 520.884 | 63.33 | 16.67 | 630126 | 630.126 | 60.44 | 19.56 | 739368 | 739.368 | 57.55 | 22.45 | 848610 | 848.61 | 54.66 | 25.34 | 957852 | 957.852 | 51.77 | 28.23 | 1067094 | 1067.094 | 48.88 | 31.12 | 1176336 | 1176.336 | 45.99 | 34.01 | 1285578 | 1285.578 | 43.1 | 36.9 | 1394820 | 1394.82 | 45
12/27/20XX 6:00:00 PM | 0.75 | 2 | 42.6 | 57.5 | 42.6 |  | 42.6 | 69.06 | 10.94 | 413532 | 413.532 | 66.12 | 13.88 | 524664 | 524.664 | 63.18 | 16.82 | 635796 | 635.796 | 60.24 | 19.76 | 746928 | 746.928 | 57.3 | 22.7 | 858060 | 858.06 | 54.36 | 25.64 | 969192 | 969.192 | 51.42 | 28.58 | 1080324 | 1080.324 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.54 | 34.46 | 1302588 | 1302.588 | 42.6 | 37.4 | 1413720 | 1413.72 | 45
12/27/20XX 7:00:00 PM | 0.79167 | 2 | 41.9 | 59.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/27/20XX 8:00:00 PM | 0.83333 | 2 | 41.5 | 58.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/27/20XX 9:00:00 PM | 0.875 | 2 | 40.5 | 59.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/27/20XX 10:00:00 PM | 0.91667 | 2 | 39.6 | 58 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/27/20XX 11:00:00 PM | 0.95833 | 2 | 38.8 | 56.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/27/20XX 12:00:00 AM | 0 | 3 | 38 | 58.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/28/20XX 1:00:00 AM | 0.041667 | 3 | 37.6 | 57.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/28/20XX 2:00:00 AM | 0.083333 | 3 | 37 | 58.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/28/20XX 3:00:00 AM | 0.125 | 3 | 36.8 | 60.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/28/20XX 4:00:00 AM | 0.16667 | 3 | 36.6 | 61.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/28/20XX 5:00:00 AM | 0.20833 | 3 | 36.6 | 62.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/28/20XX 6:00:00 AM | 0.25 | 3 | 36.6 | 62.8 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
12/28/20XX 7:00:00 AM | 0.29167 | 3 | 36.6 | 63.8 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
12/28/20XX 8:00:00 AM | 0.33333 | 3 | 36.2 | 66.1 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
12/28/20XX 9:00:00 AM | 0.375 | 3 | 36.7 | 65.1 | 36.7 |  | 36.7 | 68.47 | 11.53 | 435834 | 435.834 | 64.94 | 15.06 | 569268 | 569.268 | 61.41 | 18.59 | 702702 | 702.702 | 57.88 | 22.12 | 836136 | 836.136 | 54.35 | 25.65 | 969570 | 969.57 | 50.82 | 29.18 | 1103004 | 1103.004 | 47.29 | 32.71 | 1236438 | 1236.438 | 43.76 | 36.24 | 1369872 | 1369.872 | 40.23 | 39.77 | 1503306 | 1503.306 | 36.7 | 43.3 | 1636740 | 1636.74 | 35
12/28/20XX 10:00:00 AM | 0.41667 | 3 | 38.1 | 59.4 | 38.1 |  | 38.1 | 68.61 | 11.39 | 430542 | 430.542 | 65.22 | 14.78 | 558684 | 558.684 | 61.83 | 18.17 | 686826 | 686.826 | 58.44 | 21.56 | 814968 | 814.968 | 55.05 | 24.95 | 943110 | 943.11 | 51.66 | 28.34 | 1071252 | 1071.252 | 48.27 | 31.73 | 1199394 | 1199.394 | 44.88 | 35.12 | 1327536 | 1327.536 | 41.49 | 38.51 | 1455678 | 1455.678 | 38.1 | 41.9 | 1583820 | 1583.82 | 40
12/28/20XX 11:00:00 AM | 0.45833 | 3 | 39.1 | 56.1 | 39.1 |  | 39.1 | 68.71 | 11.29 | 426762 | 426.762 | 65.42 | 14.58 | 551124 | 551.124 | 62.13 | 17.87 | 675486 | 675.486 | 58.84 | 21.16 | 799848 | 799.848 | 55.55 | 24.45 | 924210 | 924.21 | 52.26 | 27.74 | 1048572 | 1048.572 | 48.97 | 31.03 | 1172934 | 1172.934 | 45.68 | 34.32 | 1297296 | 1297.296 | 42.39 | 37.61 | 1421658 | 1421.658 | 39.1 | 40.9 | 1546020 | 1546.02 | 40
12/28/20XX 12:00:00 PM | 0.5 | 3 | 39.8 | 54 | 39.8 |  | 39.8 | 68.78 | 11.22 | 424116 | 424.116 | 65.56 | 14.44 | 545832 | 545.832 | 62.34 | 17.66 | 667548 | 667.548 | 59.12 | 20.88 | 789264 | 789.264 | 55.9 | 24.1 | 910980 | 910.98 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.46 | 30.54 | 1154412 | 1154.412 | 46.24 | 33.76 | 1276128 | 1276.128 | 43.02 | 36.98 | 1397844 | 1397.844 | 39.8 | 40.2 | 1519560 | 1519.56 | 40
12/28/20XX 1:00:00 PM | 0.54167 | 3 | 40.5 | 52.5 | 40.5 |  | 40.5 | 68.85 | 11.15 | 421470 | 421.47 | 65.7 | 14.3 | 540540 | 540.54 | 62.55 | 17.45 | 659610 | 659.61 | 59.4 | 20.6 | 778680 | 778.68 | 56.25 | 23.75 | 897750 | 897.75 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.95 | 30.05 | 1135890 | 1135.89 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.65 | 36.35 | 1374030 | 1374.03 | 40.5 | 39.5 | 1493100 | 1493.1 | 40
12/28/20XX 2:00:00 PM | 0.58333 | 3 | 40.9 | 51 | 40.9 |  | 40.9 | 68.89 | 11.11 | 419958 | 419.958 | 65.78 | 14.22 | 537516 | 537.516 | 62.67 | 17.33 | 655074 | 655.074 | 59.56 | 20.44 | 772632 | 772.632 | 56.45 | 23.55 | 890190 | 890.19 | 53.34 | 26.66 | 1007748 | 1007.748 | 50.23 | 29.77 | 1125306 | 1125.306 | 47.12 | 32.88 | 1242864 | 1242.864 | 44.01 | 35.99 | 1360422 | 1360.422 | 40.9 | 39.1 | 1477980 | 1477.98 | 40
12/28/20XX 3:00:00 PM | 0.625 | 3 | 41.2 | 51.7 | 41.2 |  | 41.2 | 68.92 | 11.08 | 418824 | 418.824 | 65.84 | 14.16 | 535248 | 535.248 | 62.76 | 17.24 | 651672 | 651.672 | 59.68 | 20.32 | 768096 | 768.096 | 56.6 | 23.4 | 884520 | 884.52 | 53.52 | 26.48 | 1000944 | 1000.944 | 50.44 | 29.56 | 1117368 | 1117.368 | 47.36 | 32.64 | 1233792 | 1233.792 | 44.28 | 35.72 | 1350216 | 1350.216 | 41.2 | 38.8 | 1466640 | 1466.64 | 40
12/28/20XX 4:00:00 PM | 0.66667 | 3 | 41.1 | 51.2 | 41.1 |  | 41.1 | 68.91 | 11.09 | 419202 | 419.202 | 65.82 | 14.18 | 536004 | 536.004 | 62.73 | 17.27 | 652806 | 652.806 | 59.64 | 20.36 | 769608 | 769.608 | 56.55 | 23.45 | 886410 | 886.41 | 53.46 | 26.54 | 1003212 | 1003.212 | 50.37 | 29.63 | 1120014 | 1120.014 | 47.28 | 32.72 | 1236816 | 1236.816 | 44.19 | 35.81 | 1353618 | 1353.618 | 41.1 | 38.9 | 1470420 | 1470.42 | 40
12/28/20XX 5:00:00 PM | 0.70833 | 3 | 40.2 | 52 | 40.2 |  | 40.2 | 68.82 | 11.18 | 422604 | 422.604 | 65.64 | 14.36 | 542808 | 542.808 | 62.46 | 17.54 | 663012 | 663.012 | 59.28 | 20.72 | 783216 | 783.216 | 56.1 | 23.9 | 903420 | 903.42 | 52.92 | 27.08 | 1023624 | 1023.624 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.56 | 33.44 | 1264032 | 1264.032 | 43.38 | 36.62 | 1384236 | 1384.236 | 40.2 | 39.8 | 1504440 | 1504.44 | 40
12/28/20XX 6:00:00 PM | 0.75 | 3 | 39.4 | 52.5 | 39.4 |  | 39.4 | 68.74 | 11.26 | 425628 | 425.628 | 65.48 | 14.52 | 548856 | 548.856 | 62.22 | 17.78 | 672084 | 672.084 | 58.96 | 21.04 | 795312 | 795.312 | 55.7 | 24.3 | 918540 | 918.54 | 52.44 | 27.56 | 1041768 | 1041.768 | 49.18 | 30.82 | 1164996 | 1164.996 | 45.92 | 34.08 | 1288224 | 1288.224 | 42.66 | 37.34 | 1411452 | 1411.452 | 39.4 | 40.6 | 1534680 | 1534.68 | 40
12/28/20XX 7:00:00 PM | 0.79167 | 3 | 38.6 | 53.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/28/20XX 8:00:00 PM | 0.83333 | 3 | 37.7 | 54.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/28/20XX 9:00:00 PM | 0.875 | 3 | 37 | 55.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/28/20XX 10:00:00 PM | 0.91667 | 3 | 36.5 | 56.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/28/20XX 11:00:00 PM | 0.95833 | 3 | 35.5 | 59.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/28/20XX 12:00:00 AM | 0 | 4 | 35.2 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/29/20XX 1:00:00 AM | 0.041667 | 4 | 34.6 | 61.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/29/20XX 2:00:00 AM | 0.083333 | 4 | 34.5 | 61.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/29/20XX 3:00:00 AM | 0.125 | 4 | 34.7 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/29/20XX 4:00:00 AM | 0.16667 | 4 | 34.7 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/29/20XX 5:00:00 AM | 0.20833 | 4 | 34.3 | 60.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/29/20XX 6:00:00 AM | 0.25 | 4 | 34.3 | 60.6 | 34.3 |  | 34.3 | 68.23 | 11.77 | 444906 | 444.906 | 64.46 | 15.54 | 587412 | 587.412 | 60.69 | 19.31 | 729918 | 729.918 | 56.92 | 23.08 | 872424 | 872.424 | 53.15 | 26.85 | 1014930 | 1014.93 | 49.38 | 30.62 | 1157436 | 1157.436 | 45.61 | 34.39 | 1299942 | 1299.942 | 41.84 | 38.16 | 1442448 | 1442.448 | 38.07 | 41.93 | 1584954 | 1584.954 | 34.3 | 45.7 | 1727460 | 1727.46 | 35
12/29/20XX 7:00:00 AM | 0.29167 | 4 | 34 | 61.2 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
12/29/20XX 8:00:00 AM | 0.33333 | 4 | 34 | 60 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
12/29/20XX 9:00:00 AM | 0.375 | 4 | 34.5 | 60 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
12/29/20XX 10:00:00 AM | 0.41667 | 4 | 34.8 | 59.7 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
12/29/20XX 11:00:00 AM | 0.45833 | 4 | 35.4 | 60.7 | 35.4 |  | 35.4 | 68.34 | 11.66 | 440748 | 440.748 | 64.68 | 15.32 | 579096 | 579.096 | 61.02 | 18.98 | 717444 | 717.444 | 57.36 | 22.64 | 855792 | 855.792 | 53.7 | 26.3 | 994140 | 994.14 | 50.04 | 29.96 | 1132488 | 1132.488 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.72 | 37.28 | 1409184 | 1409.184 | 39.06 | 40.94 | 1547532 | 1547.532 | 35.4 | 44.6 | 1685880 | 1685.88 | 35
12/29/20XX 12:00:00 PM | 0.5 | 4 | 36.4 | 60.8 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
12/29/20XX 1:00:00 PM | 0.54167 | 4 | 36.5 | 61.5 | 36.5 |  | 36.5 | 68.45 | 11.55 | 436590 | 436.59 | 64.9 | 15.1 | 570780 | 570.78 | 61.35 | 18.65 | 704970 | 704.97 | 57.8 | 22.2 | 839160 | 839.16 | 54.25 | 25.75 | 973350 | 973.35 | 50.7 | 29.3 | 1107540 | 1107.54 | 47.15 | 32.85 | 1241730 | 1241.73 | 43.6 | 36.4 | 1375920 | 1375.92 | 40.05 | 39.95 | 1510110 | 1510.11 | 36.5 | 43.5 | 1644300 | 1644.3 | 35
12/29/20XX 2:00:00 PM | 0.58333 | 4 | 36.4 | 62.4 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
12/29/20XX 3:00:00 PM | 0.625 | 4 | 36.5 | 63.4 | 36.5 |  | 36.5 | 68.45 | 11.55 | 436590 | 436.59 | 64.9 | 15.1 | 570780 | 570.78 | 61.35 | 18.65 | 704970 | 704.97 | 57.8 | 22.2 | 839160 | 839.16 | 54.25 | 25.75 | 973350 | 973.35 | 50.7 | 29.3 | 1107540 | 1107.54 | 47.15 | 32.85 | 1241730 | 1241.73 | 43.6 | 36.4 | 1375920 | 1375.92 | 40.05 | 39.95 | 1510110 | 1510.11 | 36.5 | 43.5 | 1644300 | 1644.3 | 35
12/29/20XX 4:00:00 PM | 0.66667 | 4 | 35.8 | 62.7 | 35.8 |  | 35.8 | 68.38 | 11.62 | 439236 | 439.236 | 64.76 | 15.24 | 576072 | 576.072 | 61.14 | 18.86 | 712908 | 712.908 | 57.52 | 22.48 | 849744 | 849.744 | 53.9 | 26.1 | 986580 | 986.58 | 50.28 | 29.72 | 1123416 | 1123.416 | 46.66 | 33.34 | 1260252 | 1260.252 | 43.04 | 36.96 | 1397088 | 1397.088 | 39.42 | 40.58 | 1533924 | 1533.924 | 35.8 | 44.2 | 1670760 | 1670.76 | 35
12/29/20XX 5:00:00 PM | 0.70833 | 4 | 35.3 | 63.3 | 35.3 |  | 35.3 | 68.33 | 11.67 | 441126 | 441.126 | 64.66 | 15.34 | 579852 | 579.852 | 60.99 | 19.01 | 718578 | 718.578 | 57.32 | 22.68 | 857304 | 857.304 | 53.65 | 26.35 | 996030 | 996.03 | 49.98 | 30.02 | 1134756 | 1134.756 | 46.31 | 33.69 | 1273482 | 1273.482 | 42.64 | 37.36 | 1412208 | 1412.208 | 38.97 | 41.03 | 1550934 | 1550.934 | 35.3 | 44.7 | 1689660 | 1689.66 | 35
12/29/20XX 6:00:00 PM | 0.75 | 4 | 34.8 | 63.4 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
12/29/20XX 7:00:00 PM | 0.79167 | 4 | 34.4 | 63 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/29/20XX 8:00:00 PM | 0.83333 | 4 | 33.7 | 64.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/29/20XX 9:00:00 PM | 0.875 | 4 | 33.5 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/29/20XX 10:00:00 PM | 0.91667 | 4 | 33.1 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/29/20XX 11:00:00 PM | 0.95833 | 4 | 33.3 | 63.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/29/20XX 12:00:00 AM | 0 | 5 | 33 | 64 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/30/20XX 1:00:00 AM | 0.041667 | 5 | 32.7 | 63.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/30/20XX 2:00:00 AM | 0.083333 | 5 | 32.7 | 64.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/30/20XX 3:00:00 AM | 0.125 | 5 | 32.5 | 64.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/30/20XX 4:00:00 AM | 0.16667 | 5 | 32.4 | 64.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/30/20XX 5:00:00 AM | 0.20833 | 5 | 32.4 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/30/20XX 6:00:00 AM | 0.25 | 5 | 32.2 | 65.1 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
12/30/20XX 7:00:00 AM | 0.29167 | 5 | 32.2 | 65.3 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
12/30/20XX 8:00:00 AM | 0.33333 | 5 | 32.2 | 65.3 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
12/30/20XX 9:00:00 AM | 0.375 | 5 | 33.3 | 64.9 | 33.3 |  | 33.3 | 68.13 | 11.87 | 448686 | 448.686 | 64.26 | 15.74 | 594972 | 594.972 | 60.39 | 19.61 | 741258 | 741.258 | 56.52 | 23.48 | 887544 | 887.544 | 52.65 | 27.35 | 1033830 | 1033.83 | 48.78 | 31.22 | 1180116 | 1180.116 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.17 | 42.83 | 1618974 | 1618.974 | 33.3 | 46.7 | 1765260 | 1765.26 | 35
12/30/20XX 10:00:00 AM | 0.41667 | 5 | 34.4 | 64.8 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
12/30/20XX 11:00:00 AM | 0.45833 | 5 | 35 | 61.9 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
12/30/20XX 12:00:00 PM | 0.5 | 5 | 35.4 | 59.4 | 35.4 |  | 35.4 | 68.34 | 11.66 | 440748 | 440.748 | 64.68 | 15.32 | 579096 | 579.096 | 61.02 | 18.98 | 717444 | 717.444 | 57.36 | 22.64 | 855792 | 855.792 | 53.7 | 26.3 | 994140 | 994.14 | 50.04 | 29.96 | 1132488 | 1132.488 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.72 | 37.28 | 1409184 | 1409.184 | 39.06 | 40.94 | 1547532 | 1547.532 | 35.4 | 44.6 | 1685880 | 1685.88 | 35
12/30/20XX 1:00:00 PM | 0.54167 | 5 | 36 | 58.3 | 36 |  | 36 | 68.4 | 11.6 | 438480 | 438.48 | 64.8 | 15.2 | 574560 | 574.56 | 61.2 | 18.8 | 710640 | 710.64 | 57.6 | 22.4 | 846720 | 846.72 | 54 | 26 | 982800 | 982.8 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.2 | 36.8 | 1391040 | 1391.04 | 39.6 | 40.4 | 1527120 | 1527.12 | 36 | 44 | 1663200 | 1663.2 | 35
12/30/20XX 2:00:00 PM | 0.58333 | 5 | 36.4 | 56.9 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
12/30/20XX 3:00:00 PM | 0.625 | 5 | 36.7 | 55.8 | 36.7 |  | 36.7 | 68.47 | 11.53 | 435834 | 435.834 | 64.94 | 15.06 | 569268 | 569.268 | 61.41 | 18.59 | 702702 | 702.702 | 57.88 | 22.12 | 836136 | 836.136 | 54.35 | 25.65 | 969570 | 969.57 | 50.82 | 29.18 | 1103004 | 1103.004 | 47.29 | 32.71 | 1236438 | 1236.438 | 43.76 | 36.24 | 1369872 | 1369.872 | 40.23 | 39.77 | 1503306 | 1503.306 | 36.7 | 43.3 | 1636740 | 1636.74 | 35
12/30/20XX 4:00:00 PM | 0.66667 | 5 | 36.4 | 55.3 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
12/30/20XX 5:00:00 PM | 0.70833 | 5 | 35.2 | 59.3 | 35.2 |  | 35.2 | 68.32 | 11.68 | 441504 | 441.504 | 64.64 | 15.36 | 580608 | 580.608 | 60.96 | 19.04 | 719712 | 719.712 | 57.28 | 22.72 | 858816 | 858.816 | 53.6 | 26.4 | 997920 | 997.92 | 49.92 | 30.08 | 1137024 | 1137.024 | 46.24 | 33.76 | 1276128 | 1276.128 | 42.56 | 37.44 | 1415232 | 1415.232 | 38.88 | 41.12 | 1554336 | 1554.336 | 35.2 | 44.8 | 1693440 | 1693.44 | 35
12/30/20XX 6:00:00 PM | 0.75 | 5 | 35 | 58.8 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
12/30/20XX 7:00:00 PM | 0.79167 | 5 | 34.6 | 60.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/30/20XX 8:00:00 PM | 0.83333 | 5 | 34.5 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/30/20XX 9:00:00 PM | 0.875 | 5 | 34.2 | 61.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/30/20XX 10:00:00 PM | 0.91667 | 5 | 34.4 | 61.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/30/20XX 11:00:00 PM | 0.95833 | 5 | 33.6 | 63.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/30/20XX 12:00:00 AM | 0 | 6 | 33.4 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/31/20XX 1:00:00 AM | 0.041667 | 6 | 33.4 | 63 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/31/20XX 2:00:00 AM | 0.083333 | 6 | 33.2 | 62.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/31/20XX 3:00:00 AM | 0.125 | 6 | 33.1 | 62.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/31/20XX 4:00:00 AM | 0.16667 | 6 | 33.5 | 61.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/31/20XX 5:00:00 AM | 0.20833 | 6 | 33.4 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/31/20XX 6:00:00 AM | 0.25 | 6 | 32.7 | 65.1 | 32.7 |  | 32.7 | 68.07 | 11.93 | 450954 | 450.954 | 64.14 | 15.86 | 599508 | 599.508 | 60.21 | 19.79 | 748062 | 748.062 | 56.28 | 23.72 | 896616 | 896.616 | 52.35 | 27.65 | 1045170 | 1045.17 | 48.42 | 31.58 | 1193724 | 1193.724 | 44.49 | 35.51 | 1342278 | 1342.278 | 40.56 | 39.44 | 1490832 | 1490.832 | 36.63 | 43.37 | 1639386 | 1639.386 | 32.7 | 47.3 | 1787940 | 1787.94 | 35
12/31/20XX 7:00:00 AM | 0.29167 | 6 | 33.2 | 62.5 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
12/31/20XX 8:00:00 AM | 0.33333 | 6 | 33.1 | 63.3 | 33.1 |  | 33.1 | 68.11 | 11.89 | 449442 | 449.442 | 64.22 | 15.78 | 596484 | 596.484 | 60.33 | 19.67 | 743526 | 743.526 | 56.44 | 23.56 | 890568 | 890.568 | 52.55 | 27.45 | 1037610 | 1037.61 | 48.66 | 31.34 | 1184652 | 1184.652 | 44.77 | 35.23 | 1331694 | 1331.694 | 40.88 | 39.12 | 1478736 | 1478.736 | 36.99 | 43.01 | 1625778 | 1625.778 | 33.1 | 46.9 | 1772820 | 1772.82 | 35
12/31/20XX 9:00:00 AM | 0.375 | 6 | 33.4 | 65 | 33.4 |  | 33.4 | 68.14 | 11.86 | 448308 | 448.308 | 64.28 | 15.72 | 594216 | 594.216 | 60.42 | 19.58 | 740124 | 740.124 | 56.56 | 23.44 | 886032 | 886.032 | 52.7 | 27.3 | 1031940 | 1031.94 | 48.84 | 31.16 | 1177848 | 1177.848 | 44.98 | 35.02 | 1323756 | 1323.756 | 41.12 | 38.88 | 1469664 | 1469.664 | 37.26 | 42.74 | 1615572 | 1615.572 | 33.4 | 46.6 | 1761480 | 1761.48 | 35
12/31/20XX 10:00:00 AM | 0.41667 | 6 | 34.3 | 60.8 | 34.3 |  | 34.3 | 68.23 | 11.77 | 444906 | 444.906 | 64.46 | 15.54 | 587412 | 587.412 | 60.69 | 19.31 | 729918 | 729.918 | 56.92 | 23.08 | 872424 | 872.424 | 53.15 | 26.85 | 1014930 | 1014.93 | 49.38 | 30.62 | 1157436 | 1157.436 | 45.61 | 34.39 | 1299942 | 1299.942 | 41.84 | 38.16 | 1442448 | 1442.448 | 38.07 | 41.93 | 1584954 | 1584.954 | 34.3 | 45.7 | 1727460 | 1727.46 | 35
12/31/20XX 11:00:00 AM | 0.45833 | 6 | 35.5 | 58.6 | 35.5 |  | 35.5 | 68.35 | 11.65 | 440370 | 440.37 | 64.7 | 15.3 | 578340 | 578.34 | 61.05 | 18.95 | 716310 | 716.31 | 57.4 | 22.6 | 854280 | 854.28 | 53.75 | 26.25 | 992250 | 992.25 | 50.1 | 29.9 | 1130220 | 1130.22 | 46.45 | 33.55 | 1268190 | 1268.19 | 42.8 | 37.2 | 1406160 | 1406.16 | 39.15 | 40.85 | 1544130 | 1544.13 | 35.5 | 44.5 | 1682100 | 1682.1 | 35
12/31/20XX 12:00:00 PM | 0.5 | 6 | 36.8 | 55.7 | 36.8 |  | 36.8 | 68.48 | 11.52 | 435456 | 435.456 | 64.96 | 15.04 | 568512 | 568.512 | 61.44 | 18.56 | 701568 | 701.568 | 57.92 | 22.08 | 834624 | 834.624 | 54.4 | 25.6 | 967680 | 967.68 | 50.88 | 29.12 | 1100736 | 1100.736 | 47.36 | 32.64 | 1233792 | 1233.792 | 43.84 | 36.16 | 1366848 | 1366.848 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.8 | 43.2 | 1632960 | 1632.96 | 35
12/31/20XX 1:00:00 PM | 0.54167 | 6 | 37.3 | 55.1 | 37.3 |  | 37.3 | 68.53 | 11.47 | 433566 | 433.566 | 65.06 | 14.94 | 564732 | 564.732 | 61.59 | 18.41 | 695898 | 695.898 | 58.12 | 21.88 | 827064 | 827.064 | 54.65 | 25.35 | 958230 | 958.23 | 51.18 | 28.82 | 1089396 | 1089.396 | 47.71 | 32.29 | 1220562 | 1220.562 | 44.24 | 35.76 | 1351728 | 1351.728 | 40.77 | 39.23 | 1482894 | 1482.894 | 37.3 | 42.7 | 1614060 | 1614.06 | 35
12/31/20XX 2:00:00 PM | 0.58333 | 6 | 37.7 | 55.5 | 37.7 |  | 37.7 | 68.57 | 11.43 | 432054 | 432.054 | 65.14 | 14.86 | 561708 | 561.708 | 61.71 | 18.29 | 691362 | 691.362 | 58.28 | 21.72 | 821016 | 821.016 | 54.85 | 25.15 | 950670 | 950.67 | 51.42 | 28.58 | 1080324 | 1080.324 | 47.99 | 32.01 | 1209978 | 1209.978 | 44.56 | 35.44 | 1339632 | 1339.632 | 41.13 | 38.87 | 1469286 | 1469.286 | 37.7 | 42.3 | 1598940 | 1598.94 | 40
12/31/20XX 3:00:00 PM | 0.625 | 6 | 38.3 | 54.8 | 38.3 |  | 38.3 | 68.63 | 11.37 | 429786 | 429.786 | 65.26 | 14.74 | 557172 | 557.172 | 61.89 | 18.11 | 684558 | 684.558 | 58.52 | 21.48 | 811944 | 811.944 | 55.15 | 24.85 | 939330 | 939.33 | 51.78 | 28.22 | 1066716 | 1066.716 | 48.41 | 31.59 | 1194102 | 1194.102 | 45.04 | 34.96 | 1321488 | 1321.488 | 41.67 | 38.33 | 1448874 | 1448.874 | 38.3 | 41.7 | 1576260 | 1576.26 | 40
12/31/20XX 4:00:00 PM | 0.66667 | 6 | 38 | 57 | 38 |  | 38 | 68.6 | 11.4 | 430920 | 430.92 | 65.2 | 14.8 | 559440 | 559.44 | 61.8 | 18.2 | 687960 | 687.96 | 58.4 | 21.6 | 816480 | 816.48 | 55 | 25 | 945000 | 945 | 51.6 | 28.4 | 1073520 | 1073.52 | 48.2 | 31.8 | 1202040 | 1202.04 | 44.8 | 35.2 | 1330560 | 1330.56 | 41.4 | 38.6 | 1459080 | 1459.08 | 38 | 42 | 1587600 | 1587.6 | 40
12/31/20XX 5:00:00 PM | 0.70833 | 6 | 37.3 | 58.6 | 37.3 |  | 37.3 | 68.53 | 11.47 | 433566 | 433.566 | 65.06 | 14.94 | 564732 | 564.732 | 61.59 | 18.41 | 695898 | 695.898 | 58.12 | 21.88 | 827064 | 827.064 | 54.65 | 25.35 | 958230 | 958.23 | 51.18 | 28.82 | 1089396 | 1089.396 | 47.71 | 32.29 | 1220562 | 1220.562 | 44.24 | 35.76 | 1351728 | 1351.728 | 40.77 | 39.23 | 1482894 | 1482.894 | 37.3 | 42.7 | 1614060 | 1614.06 | 35
12/31/20XX 6:00:00 PM | 0.75 | 6 | 37.4 | 58.9 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
12/31/20XX 7:00:00 PM | 0.79167 | 6 | 37.1 | 58.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/31/20XX 8:00:00 PM | 0.83333 | 6 | 36.8 | 57.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/31/20XX 9:00:00 PM | 0.875 | 6 | 36.5 | 58.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/31/20XX 10:00:00 PM | 0.91667 | 6 | 36 | 58.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/31/20XX 11:00:00 PM | 0.95833 | 6 | 35.9 | 60.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12/31/20XX 12:00:00 AM | 0 | 1 | 35.6 | 60.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/1/20XX 1:00:00 AM | 0.041667 | 1 | 32.8 | 57 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/1/20XX 2:00:00 AM | 0.083333 | 1 | 32.5 | 59.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/1/20XX 3:00:00 AM | 0.125 | 1 | 32.3 | 59.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/1/20XX 4:00:00 AM | 0.16667 | 1 | 32.1 | 59.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/1/20XX 5:00:00 AM | 0.20833 | 1 | 31.8 | 60.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/1/20XX 6:00:00 AM | 0.25 | 1 | 31.5 | 61.3 | 31.5 |  | 31.5 | 67.95 | 12.05 | 455490 | 455.49 | 63.9 | 16.1 | 608580 | 608.58 | 59.85 | 20.15 | 761670 | 761.67 | 55.8 | 24.2 | 914760 | 914.76 | 51.75 | 28.25 | 1067850 | 1067.85 | 47.7 | 32.3 | 1220940 | 1220.94 | 43.65 | 36.35 | 1374030 | 1374.03 | 39.6 | 40.4 | 1527120 | 1527.12 | 35.55 | 44.45 | 1680210 | 1680.21 | 31.5 | 48.5 | 1833300 | 1833.3 | 30
1/1/20XX 7:00:00 AM | 0.29167 | 1 | 31.7 | 60.2 | 31.7 |  | 31.7 | 67.97 | 12.03 | 454734 | 454.734 | 63.94 | 16.06 | 607068 | 607.068 | 59.91 | 20.09 | 759402 | 759.402 | 55.88 | 24.12 | 911736 | 911.736 | 51.85 | 28.15 | 1064070 | 1064.07 | 47.82 | 32.18 | 1216404 | 1216.404 | 43.79 | 36.21 | 1368738 | 1368.738 | 39.76 | 40.24 | 1521072 | 1521.072 | 35.73 | 44.27 | 1673406 | 1673.406 | 31.7 | 48.3 | 1825740 | 1825.74 | 30
1/1/20XX 8:00:00 AM | 0.33333 | 1 | 31.6 | 61.4 | 31.6 |  | 31.6 | 67.96 | 12.04 | 455112 | 455.112 | 63.92 | 16.08 | 607824 | 607.824 | 59.88 | 20.12 | 760536 | 760.536 | 55.84 | 24.16 | 913248 | 913.248 | 51.8 | 28.2 | 1065960 | 1065.96 | 47.76 | 32.24 | 1218672 | 1218.672 | 43.72 | 36.28 | 1371384 | 1371.384 | 39.68 | 40.32 | 1524096 | 1524.096 | 35.64 | 44.36 | 1676808 | 1676.808 | 31.6 | 48.4 | 1829520 | 1829.52 | 30
1/1/20XX 9:00:00 AM | 0.375 | 1 | 32.4 | 59 | 32.4 |  | 32.4 | 68.04 | 11.96 | 452088 | 452.088 | 64.08 | 15.92 | 601776 | 601.776 | 60.12 | 19.88 | 751464 | 751.464 | 56.16 | 23.84 | 901152 | 901.152 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.24 | 31.76 | 1200528 | 1200.528 | 44.28 | 35.72 | 1350216 | 1350.216 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.36 | 43.64 | 1649592 | 1649.592 | 32.4 | 47.6 | 1799280 | 1799.28 | 30
1/1/20XX 10:00:00 AM | 0.41667 | 1 | 33.8 | 56.7 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
1/1/20XX 11:00:00 AM | 0.45833 | 1 | 35 | 52.2 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
1/1/20XX 12:00:00 PM | 0.5 | 1 | 36.4 | 50.3 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
1/1/20XX 1:00:00 PM | 0.54167 | 1 | 36.8 | 50 | 36.8 |  | 36.8 | 68.48 | 11.52 | 435456 | 435.456 | 64.96 | 15.04 | 568512 | 568.512 | 61.44 | 18.56 | 701568 | 701.568 | 57.92 | 22.08 | 834624 | 834.624 | 54.4 | 25.6 | 967680 | 967.68 | 50.88 | 29.12 | 1100736 | 1100.736 | 47.36 | 32.64 | 1233792 | 1233.792 | 43.84 | 36.16 | 1366848 | 1366.848 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.8 | 43.2 | 1632960 | 1632.96 | 35
1/1/20XX 2:00:00 PM | 0.58333 | 1 | 37.7 | 49.3 | 37.7 |  | 37.7 | 68.57 | 11.43 | 432054 | 432.054 | 65.14 | 14.86 | 561708 | 561.708 | 61.71 | 18.29 | 691362 | 691.362 | 58.28 | 21.72 | 821016 | 821.016 | 54.85 | 25.15 | 950670 | 950.67 | 51.42 | 28.58 | 1080324 | 1080.324 | 47.99 | 32.01 | 1209978 | 1209.978 | 44.56 | 35.44 | 1339632 | 1339.632 | 41.13 | 38.87 | 1469286 | 1469.286 | 37.7 | 42.3 | 1598940 | 1598.94 | 40
1/1/20XX 3:00:00 PM | 0.625 | 1 | 37.9 | 48.4 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
1/1/20XX 4:00:00 PM | 0.66667 | 1 | 37.6 | 48.6 | 37.6 |  | 37.6 | 68.56 | 11.44 | 432432 | 432.432 | 65.12 | 14.88 | 562464 | 562.464 | 61.68 | 18.32 | 692496 | 692.496 | 58.24 | 21.76 | 822528 | 822.528 | 54.8 | 25.2 | 952560 | 952.56 | 51.36 | 28.64 | 1082592 | 1082.592 | 47.92 | 32.08 | 1212624 | 1212.624 | 44.48 | 35.52 | 1342656 | 1342.656 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.6 | 42.4 | 1602720 | 1602.72 | 40
1/1/20XX 5:00:00 PM | 0.70833 | 1 | 36.8 | 48.4 | 36.8 |  | 36.8 | 68.48 | 11.52 | 435456 | 435.456 | 64.96 | 15.04 | 568512 | 568.512 | 61.44 | 18.56 | 701568 | 701.568 | 57.92 | 22.08 | 834624 | 834.624 | 54.4 | 25.6 | 967680 | 967.68 | 50.88 | 29.12 | 1100736 | 1100.736 | 47.36 | 32.64 | 1233792 | 1233.792 | 43.84 | 36.16 | 1366848 | 1366.848 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.8 | 43.2 | 1632960 | 1632.96 | 35
1/1/20XX 6:00:00 PM | 0.75 | 1 | 36.7 | 49.4 | 36.7 |  | 36.7 | 68.47 | 11.53 | 435834 | 435.834 | 64.94 | 15.06 | 569268 | 569.268 | 61.41 | 18.59 | 702702 | 702.702 | 57.88 | 22.12 | 836136 | 836.136 | 54.35 | 25.65 | 969570 | 969.57 | 50.82 | 29.18 | 1103004 | 1103.004 | 47.29 | 32.71 | 1236438 | 1236.438 | 43.76 | 36.24 | 1369872 | 1369.872 | 40.23 | 39.77 | 1503306 | 1503.306 | 36.7 | 43.3 | 1636740 | 1636.74 | 35
1/1/20XX 7:00:00 PM | 0.79167 | 1 | 35.9 | 52.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/1/20XX 8:00:00 PM | 0.83333 | 1 | 35.5 | 54.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/1/20XX 9:00:00 PM | 0.875 | 1 | 35 | 56.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/1/20XX 10:00:00 PM | 0.91667 | 1 | 35.3 | 56.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/1/20XX 11:00:00 PM | 0.95833 | 1 | 34.9 | 57.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/1/20XX 12:00:00 AM | 0 | 2 | 34 | 57.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/2/20XX 1:00:00 AM | 0.041667 | 2 | 33.6 | 56.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/2/20XX 2:00:00 AM | 0.083333 | 2 | 33.2 | 57.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/2/20XX 3:00:00 AM | 0.125 | 2 | 32.5 | 58.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/2/20XX 4:00:00 AM | 0.16667 | 2 | 32.2 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/2/20XX 5:00:00 AM | 0.20833 | 2 | 31.8 | 61.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/2/20XX 6:00:00 AM | 0.25 | 2 | 31.3 | 62.6 | 31.3 |  | 31.3 | 67.93 | 12.07 | 456246 | 456.246 | 63.86 | 16.14 | 610092 | 610.092 | 59.79 | 20.21 | 763938 | 763.938 | 55.72 | 24.28 | 917784 | 917.784 | 51.65 | 28.35 | 1071630 | 1071.63 | 47.58 | 32.42 | 1225476 | 1225.476 | 43.51 | 36.49 | 1379322 | 1379.322 | 39.44 | 40.56 | 1533168 | 1533.168 | 35.37 | 44.63 | 1687014 | 1687.014 | 31.3 | 48.7 | 1840860 | 1840.86 | 30
1/2/20XX 7:00:00 AM | 0.29167 | 2 | 31.3 | 61.2 | 31.3 |  | 31.3 | 67.93 | 12.07 | 456246 | 456.246 | 63.86 | 16.14 | 610092 | 610.092 | 59.79 | 20.21 | 763938 | 763.938 | 55.72 | 24.28 | 917784 | 917.784 | 51.65 | 28.35 | 1071630 | 1071.63 | 47.58 | 32.42 | 1225476 | 1225.476 | 43.51 | 36.49 | 1379322 | 1379.322 | 39.44 | 40.56 | 1533168 | 1533.168 | 35.37 | 44.63 | 1687014 | 1687.014 | 31.3 | 48.7 | 1840860 | 1840.86 | 30
1/2/20XX 8:00:00 AM | 0.33333 | 2 | 31.4 | 62.2 | 31.4 |  | 31.4 | 67.94 | 12.06 | 455868 | 455.868 | 63.88 | 16.12 | 609336 | 609.336 | 59.82 | 20.18 | 762804 | 762.804 | 55.76 | 24.24 | 916272 | 916.272 | 51.7 | 28.3 | 1069740 | 1069.74 | 47.64 | 32.36 | 1223208 | 1223.208 | 43.58 | 36.42 | 1376676 | 1376.676 | 39.52 | 40.48 | 1530144 | 1530.144 | 35.46 | 44.54 | 1683612 | 1683.612 | 31.4 | 48.6 | 1837080 | 1837.08 | 30
1/2/20XX 9:00:00 AM | 0.375 | 2 | 32.1 | 60.9 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
1/2/20XX 10:00:00 AM | 0.41667 | 2 | 32.6 | 60.3 | 32.6 |  | 32.6 | 68.06 | 11.94 | 451332 | 451.332 | 64.12 | 15.88 | 600264 | 600.264 | 60.18 | 19.82 | 749196 | 749.196 | 56.24 | 23.76 | 898128 | 898.128 | 52.3 | 27.7 | 1047060 | 1047.06 | 48.36 | 31.64 | 1195992 | 1195.992 | 44.42 | 35.58 | 1344924 | 1344.924 | 40.48 | 39.52 | 1493856 | 1493.856 | 36.54 | 43.46 | 1642788 | 1642.788 | 32.6 | 47.4 | 1791720 | 1791.72 | 35
1/2/20XX 11:00:00 AM | 0.45833 | 2 | 33.4 | 57.8 | 33.4 |  | 33.4 | 68.14 | 11.86 | 448308 | 448.308 | 64.28 | 15.72 | 594216 | 594.216 | 60.42 | 19.58 | 740124 | 740.124 | 56.56 | 23.44 | 886032 | 886.032 | 52.7 | 27.3 | 1031940 | 1031.94 | 48.84 | 31.16 | 1177848 | 1177.848 | 44.98 | 35.02 | 1323756 | 1323.756 | 41.12 | 38.88 | 1469664 | 1469.664 | 37.26 | 42.74 | 1615572 | 1615.572 | 33.4 | 46.6 | 1761480 | 1761.48 | 35
1/2/20XX 12:00:00 PM | 0.5 | 2 | 34 | 57 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
1/2/20XX 1:00:00 PM | 0.54167 | 2 | 34.8 | 56.6 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
1/2/20XX 2:00:00 PM | 0.58333 | 2 | 35.1 | 56.3 | 35.1 |  | 35.1 | 68.31 | 11.69 | 441882 | 441.882 | 64.62 | 15.38 | 581364 | 581.364 | 60.93 | 19.07 | 720846 | 720.846 | 57.24 | 22.76 | 860328 | 860.328 | 53.55 | 26.45 | 999810 | 999.81 | 49.86 | 30.14 | 1139292 | 1139.292 | 46.17 | 33.83 | 1278774 | 1278.774 | 42.48 | 37.52 | 1418256 | 1418.256 | 38.79 | 41.21 | 1557738 | 1557.738 | 35.1 | 44.9 | 1697220 | 1697.22 | 35
1/2/20XX 3:00:00 PM | 0.625 | 2 | 35 | 56 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
1/2/20XX 4:00:00 PM | 0.66667 | 2 | 34.7 | 55.8 | 34.7 |  | 34.7 | 68.27 | 11.73 | 443394 | 443.394 | 64.54 | 15.46 | 584388 | 584.388 | 60.81 | 19.19 | 725382 | 725.382 | 57.08 | 22.92 | 866376 | 866.376 | 53.35 | 26.65 | 1007370 | 1007.37 | 49.62 | 30.38 | 1148364 | 1148.364 | 45.89 | 34.11 | 1289358 | 1289.358 | 42.16 | 37.84 | 1430352 | 1430.352 | 38.43 | 41.57 | 1571346 | 1571.346 | 34.7 | 45.3 | 1712340 | 1712.34 | 35
1/2/20XX 5:00:00 PM | 0.70833 | 2 | 34 | 57.6 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
1/2/20XX 6:00:00 PM | 0.75 | 2 | 33.4 | 58.6 | 33.4 |  | 33.4 | 68.14 | 11.86 | 448308 | 448.308 | 64.28 | 15.72 | 594216 | 594.216 | 60.42 | 19.58 | 740124 | 740.124 | 56.56 | 23.44 | 886032 | 886.032 | 52.7 | 27.3 | 1031940 | 1031.94 | 48.84 | 31.16 | 1177848 | 1177.848 | 44.98 | 35.02 | 1323756 | 1323.756 | 41.12 | 38.88 | 1469664 | 1469.664 | 37.26 | 42.74 | 1615572 | 1615.572 | 33.4 | 46.6 | 1761480 | 1761.48 | 35
1/2/20XX 7:00:00 PM | 0.79167 | 2 | 32.8 | 59.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/2/20XX 8:00:00 PM | 0.83333 | 2 | 32.1 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/2/20XX 9:00:00 PM | 0.875 | 2 | 31.5 | 61 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/2/20XX 10:00:00 PM | 0.91667 | 2 | 30.8 | 62.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/2/20XX 11:00:00 PM | 0.95833 | 2 | 30.1 | 62.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/2/20XX 12:00:00 AM | 0 | 3 | 29.7 | 62.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/3/20XX 1:00:00 AM | 0.041667 | 3 | 28.8 | 62.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/3/20XX 2:00:00 AM | 0.083333 | 3 | 28.1 | 61.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/3/20XX 3:00:00 AM | 0.125 | 3 | 27.7 | 62.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/3/20XX 4:00:00 AM | 0.16667 | 3 | 27.5 | 61 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/3/20XX 5:00:00 AM | 0.20833 | 3 | 27.1 | 61.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/3/20XX 6:00:00 AM | 0.25 | 3 | 26.8 | 60.7 | 26.8 |  | 26.8 | 67.48 | 12.52 | 473256 | 473.256 | 62.96 | 17.04 | 644112 | 644.112 | 58.44 | 21.56 | 814968 | 814.968 | 53.92 | 26.08 | 985824 | 985.824 | 49.4 | 30.6 | 1156680 | 1156.68 | 44.88 | 35.12 | 1327536 | 1327.536 | 40.36 | 39.64 | 1498392 | 1498.392 | 35.84 | 44.16 | 1669248 | 1669.248 | 31.32 | 48.68 | 1840104 | 1840.104 | 26.8 | 53.2 | 2010960 | 2010.96 | 25
1/3/20XX 7:00:00 AM | 0.29167 | 3 | 26.6 | 60.2 | 26.6 |  | 26.6 | 67.46 | 12.54 | 474012 | 474.012 | 62.92 | 17.08 | 645624 | 645.624 | 58.38 | 21.62 | 817236 | 817.236 | 53.84 | 26.16 | 988848 | 988.848 | 49.3 | 30.7 | 1160460 | 1160.46 | 44.76 | 35.24 | 1332072 | 1332.072 | 40.22 | 39.78 | 1503684 | 1503.684 | 35.68 | 44.32 | 1675296 | 1675.296 | 31.14 | 48.86 | 1846908 | 1846.908 | 26.6 | 53.4 | 2018520 | 2018.52 | 25
1/3/20XX 8:00:00 AM | 0.33333 | 3 | 26.5 | 59.8 | 26.5 |  | 26.5 | 67.45 | 12.55 | 474390 | 474.39 | 62.9 | 17.1 | 646380 | 646.38 | 58.35 | 21.65 | 818370 | 818.37 | 53.8 | 26.2 | 990360 | 990.36 | 49.25 | 30.75 | 1162350 | 1162.35 | 44.7 | 35.3 | 1334340 | 1334.34 | 40.15 | 39.85 | 1506330 | 1506.33 | 35.6 | 44.4 | 1678320 | 1678.32 | 31.05 | 48.95 | 1850310 | 1850.31 | 26.5 | 53.5 | 2022300 | 2022.3 | 25
1/3/20XX 9:00:00 AM | 0.375 | 3 | 27.3 | 58.6 | 27.3 |  | 27.3 | 67.53 | 12.47 | 471366 | 471.366 | 63.06 | 16.94 | 640332 | 640.332 | 58.59 | 21.41 | 809298 | 809.298 | 54.12 | 25.88 | 978264 | 978.264 | 49.65 | 30.35 | 1147230 | 1147.23 | 45.18 | 34.82 | 1316196 | 1316.196 | 40.71 | 39.29 | 1485162 | 1485.162 | 36.24 | 43.76 | 1654128 | 1654.128 | 31.77 | 48.23 | 1823094 | 1823.094 | 27.3 | 52.7 | 1992060 | 1992.06 | 25
1/3/20XX 10:00:00 AM | 0.41667 | 3 | 28.2 | 55.5 | 28.2 |  | 28.2 | 67.62 | 12.38 | 467964 | 467.964 | 63.24 | 16.76 | 633528 | 633.528 | 58.86 | 21.14 | 799092 | 799.092 | 54.48 | 25.52 | 964656 | 964.656 | 50.1 | 29.9 | 1130220 | 1130.22 | 45.72 | 34.28 | 1295784 | 1295.784 | 41.34 | 38.66 | 1461348 | 1461.348 | 36.96 | 43.04 | 1626912 | 1626.912 | 32.58 | 47.42 | 1792476 | 1792.476 | 28.2 | 51.8 | 1958040 | 1958.04 | 30
1/3/20XX 11:00:00 AM | 0.45833 | 3 | 29.5 | 54.1 | 29.5 |  | 29.5 | 67.75 | 12.25 | 463050 | 463.05 | 63.5 | 16.5 | 623700 | 623.7 | 59.25 | 20.75 | 784350 | 784.35 | 55 | 25 | 945000 | 945 | 50.75 | 29.25 | 1105650 | 1105.65 | 46.5 | 33.5 | 1266300 | 1266.3 | 42.25 | 37.75 | 1426950 | 1426.95 | 38 | 42 | 1587600 | 1587.6 | 33.75 | 46.25 | 1748250 | 1748.25 | 29.5 | 50.5 | 1908900 | 1908.9 | 30
1/3/20XX 12:00:00 PM | 0.5 | 3 | 31.1 | 49.2 | 31.1 |  | 31.1 | 67.91 | 12.09 | 457002 | 457.002 | 63.82 | 16.18 | 611604 | 611.604 | 59.73 | 20.27 | 766206 | 766.206 | 55.64 | 24.36 | 920808 | 920.808 | 51.55 | 28.45 | 1075410 | 1075.41 | 47.46 | 32.54 | 1230012 | 1230.012 | 43.37 | 36.63 | 1384614 | 1384.614 | 39.28 | 40.72 | 1539216 | 1539.216 | 35.19 | 44.81 | 1693818 | 1693.818 | 31.1 | 48.9 | 1848420 | 1848.42 | 30
1/3/20XX 1:00:00 PM | 0.54167 | 3 | 31.5 | 51.2 | 31.5 |  | 31.5 | 67.95 | 12.05 | 455490 | 455.49 | 63.9 | 16.1 | 608580 | 608.58 | 59.85 | 20.15 | 761670 | 761.67 | 55.8 | 24.2 | 914760 | 914.76 | 51.75 | 28.25 | 1067850 | 1067.85 | 47.7 | 32.3 | 1220940 | 1220.94 | 43.65 | 36.35 | 1374030 | 1374.03 | 39.6 | 40.4 | 1527120 | 1527.12 | 35.55 | 44.45 | 1680210 | 1680.21 | 31.5 | 48.5 | 1833300 | 1833.3 | 30
1/3/20XX 2:00:00 PM | 0.58333 | 3 | 31.5 | 52 | 31.5 |  | 31.5 | 67.95 | 12.05 | 455490 | 455.49 | 63.9 | 16.1 | 608580 | 608.58 | 59.85 | 20.15 | 761670 | 761.67 | 55.8 | 24.2 | 914760 | 914.76 | 51.75 | 28.25 | 1067850 | 1067.85 | 47.7 | 32.3 | 1220940 | 1220.94 | 43.65 | 36.35 | 1374030 | 1374.03 | 39.6 | 40.4 | 1527120 | 1527.12 | 35.55 | 44.45 | 1680210 | 1680.21 | 31.5 | 48.5 | 1833300 | 1833.3 | 30
1/3/20XX 3:00:00 PM | 0.625 | 3 | 31.3 | 52.3 | 31.3 |  | 31.3 | 67.93 | 12.07 | 456246 | 456.246 | 63.86 | 16.14 | 610092 | 610.092 | 59.79 | 20.21 | 763938 | 763.938 | 55.72 | 24.28 | 917784 | 917.784 | 51.65 | 28.35 | 1071630 | 1071.63 | 47.58 | 32.42 | 1225476 | 1225.476 | 43.51 | 36.49 | 1379322 | 1379.322 | 39.44 | 40.56 | 1533168 | 1533.168 | 35.37 | 44.63 | 1687014 | 1687.014 | 31.3 | 48.7 | 1840860 | 1840.86 | 30
1/3/20XX 4:00:00 PM | 0.66667 | 3 | 31.1 | 53.2 | 31.1 |  | 31.1 | 67.91 | 12.09 | 457002 | 457.002 | 63.82 | 16.18 | 611604 | 611.604 | 59.73 | 20.27 | 766206 | 766.206 | 55.64 | 24.36 | 920808 | 920.808 | 51.55 | 28.45 | 1075410 | 1075.41 | 47.46 | 32.54 | 1230012 | 1230.012 | 43.37 | 36.63 | 1384614 | 1384.614 | 39.28 | 40.72 | 1539216 | 1539.216 | 35.19 | 44.81 | 1693818 | 1693.818 | 31.1 | 48.9 | 1848420 | 1848.42 | 30
1/3/20XX 5:00:00 PM | 0.70833 | 3 | 30.8 | 54.4 | 30.8 |  | 30.8 | 67.88 | 12.12 | 458136 | 458.136 | 63.76 | 16.24 | 613872 | 613.872 | 59.64 | 20.36 | 769608 | 769.608 | 55.52 | 24.48 | 925344 | 925.344 | 51.4 | 28.6 | 1081080 | 1081.08 | 47.28 | 32.72 | 1236816 | 1236.816 | 43.16 | 36.84 | 1392552 | 1392.552 | 39.04 | 40.96 | 1548288 | 1548.288 | 34.92 | 45.08 | 1704024 | 1704.024 | 30.8 | 49.2 | 1859760 | 1859.76 | 30
1/3/20XX 6:00:00 PM | 0.75 | 3 | 30.4 | 55.2 | 30.4 |  | 30.4 | 67.84 | 12.16 | 459648 | 459.648 | 63.68 | 16.32 | 616896 | 616.896 | 59.52 | 20.48 | 774144 | 774.144 | 55.36 | 24.64 | 931392 | 931.392 | 51.2 | 28.8 | 1088640 | 1088.64 | 47.04 | 32.96 | 1245888 | 1245.888 | 42.88 | 37.12 | 1403136 | 1403.136 | 38.72 | 41.28 | 1560384 | 1560.384 | 34.56 | 45.44 | 1717632 | 1717.632 | 30.4 | 49.6 | 1874880 | 1874.88 | 30
1/3/20XX 7:00:00 PM | 0.79167 | 3 | 29.9 | 55.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/3/20XX 8:00:00 PM | 0.83333 | 3 | 29.8 | 54.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/3/20XX 9:00:00 PM | 0.875 | 3 | 29.6 | 56.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/3/20XX 10:00:00 PM | 0.91667 | 3 | 28.7 | 59.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/3/20XX 11:00:00 PM | 0.95833 | 3 | 28.6 | 59.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/3/20XX 12:00:00 AM | 0 | 4 | 28.3 | 59.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/4/20XX 1:00:00 AM | 0.041667 | 4 | 28.1 | 59.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/4/20XX 2:00:00 AM | 0.083333 | 4 | 28 | 61.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/4/20XX 3:00:00 AM | 0.125 | 4 | 27.7 | 59.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/4/20XX 4:00:00 AM | 0.16667 | 4 | 27.4 | 61.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/4/20XX 5:00:00 AM | 0.20833 | 4 | 27.7 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/4/20XX 6:00:00 AM | 0.25 | 4 | 27.3 | 65.5 | 27.3 |  | 27.3 | 67.53 | 12.47 | 471366 | 471.366 | 63.06 | 16.94 | 640332 | 640.332 | 58.59 | 21.41 | 809298 | 809.298 | 54.12 | 25.88 | 978264 | 978.264 | 49.65 | 30.35 | 1147230 | 1147.23 | 45.18 | 34.82 | 1316196 | 1316.196 | 40.71 | 39.29 | 1485162 | 1485.162 | 36.24 | 43.76 | 1654128 | 1654.128 | 31.77 | 48.23 | 1823094 | 1823.094 | 27.3 | 52.7 | 1992060 | 1992.06 | 25
1/4/20XX 7:00:00 AM | 0.29167 | 4 | 27.4 | 65.6 | 27.4 |  | 27.4 | 67.54 | 12.46 | 470988 | 470.988 | 63.08 | 16.92 | 639576 | 639.576 | 58.62 | 21.38 | 808164 | 808.164 | 54.16 | 25.84 | 976752 | 976.752 | 49.7 | 30.3 | 1145340 | 1145.34 | 45.24 | 34.76 | 1313928 | 1313.928 | 40.78 | 39.22 | 1482516 | 1482.516 | 36.32 | 43.68 | 1651104 | 1651.104 | 31.86 | 48.14 | 1819692 | 1819.692 | 27.4 | 52.6 | 1988280 | 1988.28 | 25
1/4/20XX 8:00:00 AM | 0.33333 | 4 | 27.2 | 67.2 | 27.2 |  | 27.2 | 67.52 | 12.48 | 471744 | 471.744 | 63.04 | 16.96 | 641088 | 641.088 | 58.56 | 21.44 | 810432 | 810.432 | 54.08 | 25.92 | 979776 | 979.776 | 49.6 | 30.4 | 1149120 | 1149.12 | 45.12 | 34.88 | 1318464 | 1318.464 | 40.64 | 39.36 | 1487808 | 1487.808 | 36.16 | 43.84 | 1657152 | 1657.152 | 31.68 | 48.32 | 1826496 | 1826.496 | 27.2 | 52.8 | 1995840 | 1995.84 | 25
1/4/20XX 9:00:00 AM | 0.375 | 4 | 28.2 | 64.5 | 28.2 |  | 28.2 | 67.62 | 12.38 | 467964 | 467.964 | 63.24 | 16.76 | 633528 | 633.528 | 58.86 | 21.14 | 799092 | 799.092 | 54.48 | 25.52 | 964656 | 964.656 | 50.1 | 29.9 | 1130220 | 1130.22 | 45.72 | 34.28 | 1295784 | 1295.784 | 41.34 | 38.66 | 1461348 | 1461.348 | 36.96 | 43.04 | 1626912 | 1626.912 | 32.58 | 47.42 | 1792476 | 1792.476 | 28.2 | 51.8 | 1958040 | 1958.04 | 30
1/4/20XX 10:00:00 AM | 0.41667 | 4 | 29.6 | 61.1 | 29.6 |  | 29.6 | 67.76 | 12.24 | 462672 | 462.672 | 63.52 | 16.48 | 622944 | 622.944 | 59.28 | 20.72 | 783216 | 783.216 | 55.04 | 24.96 | 943488 | 943.488 | 50.8 | 29.2 | 1103760 | 1103.76 | 46.56 | 33.44 | 1264032 | 1264.032 | 42.32 | 37.68 | 1424304 | 1424.304 | 38.08 | 41.92 | 1584576 | 1584.576 | 33.84 | 46.16 | 1744848 | 1744.848 | 29.6 | 50.4 | 1905120 | 1905.12 | 30
1/4/20XX 11:00:00 AM | 0.45833 | 4 | 31.2 | 58 | 31.2 |  | 31.2 | 67.92 | 12.08 | 456624 | 456.624 | 63.84 | 16.16 | 610848 | 610.848 | 59.76 | 20.24 | 765072 | 765.072 | 55.68 | 24.32 | 919296 | 919.296 | 51.6 | 28.4 | 1073520 | 1073.52 | 47.52 | 32.48 | 1227744 | 1227.744 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.36 | 40.64 | 1536192 | 1536.192 | 35.28 | 44.72 | 1690416 | 1690.416 | 31.2 | 48.8 | 1844640 | 1844.64 | 30
1/4/20XX 12:00:00 PM | 0.5 | 4 | 32.4 | 56.2 | 32.4 |  | 32.4 | 68.04 | 11.96 | 452088 | 452.088 | 64.08 | 15.92 | 601776 | 601.776 | 60.12 | 19.88 | 751464 | 751.464 | 56.16 | 23.84 | 901152 | 901.152 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.24 | 31.76 | 1200528 | 1200.528 | 44.28 | 35.72 | 1350216 | 1350.216 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.36 | 43.64 | 1649592 | 1649.592 | 32.4 | 47.6 | 1799280 | 1799.28 | 30
1/4/20XX 1:00:00 PM | 0.54167 | 4 | 33.7 | 52.8 | 33.7 |  | 33.7 | 68.17 | 11.83 | 447174 | 447.174 | 64.34 | 15.66 | 591948 | 591.948 | 60.51 | 19.49 | 736722 | 736.722 | 56.68 | 23.32 | 881496 | 881.496 | 52.85 | 27.15 | 1026270 | 1026.27 | 49.02 | 30.98 | 1171044 | 1171.044 | 45.19 | 34.81 | 1315818 | 1315.818 | 41.36 | 38.64 | 1460592 | 1460.592 | 37.53 | 42.47 | 1605366 | 1605.366 | 33.7 | 46.3 | 1750140 | 1750.14 | 35
1/4/20XX 2:00:00 PM | 0.58333 | 4 | 34.7 | 50.4 | 34.7 |  | 34.7 | 68.27 | 11.73 | 443394 | 443.394 | 64.54 | 15.46 | 584388 | 584.388 | 60.81 | 19.19 | 725382 | 725.382 | 57.08 | 22.92 | 866376 | 866.376 | 53.35 | 26.65 | 1007370 | 1007.37 | 49.62 | 30.38 | 1148364 | 1148.364 | 45.89 | 34.11 | 1289358 | 1289.358 | 42.16 | 37.84 | 1430352 | 1430.352 | 38.43 | 41.57 | 1571346 | 1571.346 | 34.7 | 45.3 | 1712340 | 1712.34 | 35
1/4/20XX 3:00:00 PM | 0.625 | 4 | 35.3 | 49.3 | 35.3 |  | 35.3 | 68.33 | 11.67 | 441126 | 441.126 | 64.66 | 15.34 | 579852 | 579.852 | 60.99 | 19.01 | 718578 | 718.578 | 57.32 | 22.68 | 857304 | 857.304 | 53.65 | 26.35 | 996030 | 996.03 | 49.98 | 30.02 | 1134756 | 1134.756 | 46.31 | 33.69 | 1273482 | 1273.482 | 42.64 | 37.36 | 1412208 | 1412.208 | 38.97 | 41.03 | 1550934 | 1550.934 | 35.3 | 44.7 | 1689660 | 1689.66 | 35
1/4/20XX 4:00:00 PM | 0.66667 | 4 | 34.9 | 48.9 | 34.9 |  | 34.9 | 68.29 | 11.71 | 442638 | 442.638 | 64.58 | 15.42 | 582876 | 582.876 | 60.87 | 19.13 | 723114 | 723.114 | 57.16 | 22.84 | 863352 | 863.352 | 53.45 | 26.55 | 1003590 | 1003.59 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.03 | 33.97 | 1284066 | 1284.066 | 42.32 | 37.68 | 1424304 | 1424.304 | 38.61 | 41.39 | 1564542 | 1564.542 | 34.9 | 45.1 | 1704780 | 1704.78 | 35
1/4/20XX 5:00:00 PM | 0.70833 | 4 | 34.3 | 50 | 34.3 |  | 34.3 | 68.23 | 11.77 | 444906 | 444.906 | 64.46 | 15.54 | 587412 | 587.412 | 60.69 | 19.31 | 729918 | 729.918 | 56.92 | 23.08 | 872424 | 872.424 | 53.15 | 26.85 | 1014930 | 1014.93 | 49.38 | 30.62 | 1157436 | 1157.436 | 45.61 | 34.39 | 1299942 | 1299.942 | 41.84 | 38.16 | 1442448 | 1442.448 | 38.07 | 41.93 | 1584954 | 1584.954 | 34.3 | 45.7 | 1727460 | 1727.46 | 35
1/4/20XX 6:00:00 PM | 0.75 | 4 | 33.9 | 50.8 | 33.9 |  | 33.9 | 68.19 | 11.81 | 446418 | 446.418 | 64.38 | 15.62 | 590436 | 590.436 | 60.57 | 19.43 | 734454 | 734.454 | 56.76 | 23.24 | 878472 | 878.472 | 52.95 | 27.05 | 1022490 | 1022.49 | 49.14 | 30.86 | 1166508 | 1166.508 | 45.33 | 34.67 | 1310526 | 1310.526 | 41.52 | 38.48 | 1454544 | 1454.544 | 37.71 | 42.29 | 1598562 | 1598.562 | 33.9 | 46.1 | 1742580 | 1742.58 | 35
1/4/20XX 7:00:00 PM | 0.79167 | 4 | 33.6 | 49.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/4/20XX 8:00:00 PM | 0.83333 | 4 | 32.8 | 49.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/4/20XX 9:00:00 PM | 0.875 | 4 | 32 | 49.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/4/20XX 10:00:00 PM | 0.91667 | 4 | 31.3 | 50.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/4/20XX 11:00:00 PM | 0.95833 | 4 | 30.8 | 49.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/4/20XX 12:00:00 AM | 0 | 5 | 30.3 | 49.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/5/20XX 1:00:00 AM | 0.041667 | 5 | 29.6 | 50.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/5/20XX 2:00:00 AM | 0.083333 | 5 | 29.1 | 53.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/5/20XX 3:00:00 AM | 0.125 | 5 | 28.3 | 54.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/5/20XX 4:00:00 AM | 0.16667 | 5 | 27.9 | 53.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/5/20XX 5:00:00 AM | 0.20833 | 5 | 27.7 | 53.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/5/20XX 6:00:00 AM | 0.25 | 5 | 27.4 | 54.3 | 27.4 |  | 27.4 | 67.54 | 12.46 | 470988 | 470.988 | 63.08 | 16.92 | 639576 | 639.576 | 58.62 | 21.38 | 808164 | 808.164 | 54.16 | 25.84 | 976752 | 976.752 | 49.7 | 30.3 | 1145340 | 1145.34 | 45.24 | 34.76 | 1313928 | 1313.928 | 40.78 | 39.22 | 1482516 | 1482.516 | 36.32 | 43.68 | 1651104 | 1651.104 | 31.86 | 48.14 | 1819692 | 1819.692 | 27.4 | 52.6 | 1988280 | 1988.28 | 25
1/5/20XX 7:00:00 AM | 0.29167 | 5 | 27.4 | 53.4 | 27.4 |  | 27.4 | 67.54 | 12.46 | 470988 | 470.988 | 63.08 | 16.92 | 639576 | 639.576 | 58.62 | 21.38 | 808164 | 808.164 | 54.16 | 25.84 | 976752 | 976.752 | 49.7 | 30.3 | 1145340 | 1145.34 | 45.24 | 34.76 | 1313928 | 1313.928 | 40.78 | 39.22 | 1482516 | 1482.516 | 36.32 | 43.68 | 1651104 | 1651.104 | 31.86 | 48.14 | 1819692 | 1819.692 | 27.4 | 52.6 | 1988280 | 1988.28 | 25
1/5/20XX 8:00:00 AM | 0.33333 | 5 | 27.5 | 54.2 | 27.5 |  | 27.5 | 67.55 | 12.45 | 470610 | 470.61 | 63.1 | 16.9 | 638820 | 638.82 | 58.65 | 21.35 | 807030 | 807.03 | 54.2 | 25.8 | 975240 | 975.24 | 49.75 | 30.25 | 1143450 | 1143.45 | 45.3 | 34.7 | 1311660 | 1311.66 | 40.85 | 39.15 | 1479870 | 1479.87 | 36.4 | 43.6 | 1648080 | 1648.08 | 31.95 | 48.05 | 1816290 | 1816.29 | 27.5 | 52.5 | 1984500 | 1984.5 | 25
1/5/20XX 9:00:00 AM | 0.375 | 5 | 28.3 | 53.6 | 28.3 |  | 28.3 | 67.63 | 12.37 | 467586 | 467.586 | 63.26 | 16.74 | 632772 | 632.772 | 58.89 | 21.11 | 797958 | 797.958 | 54.52 | 25.48 | 963144 | 963.144 | 50.15 | 29.85 | 1128330 | 1128.33 | 45.78 | 34.22 | 1293516 | 1293.516 | 41.41 | 38.59 | 1458702 | 1458.702 | 37.04 | 42.96 | 1623888 | 1623.888 | 32.67 | 47.33 | 1789074 | 1789.074 | 28.3 | 51.7 | 1954260 | 1954.26 | 30
1/5/20XX 10:00:00 AM | 0.41667 | 5 | 29.5 | 53.5 | 29.5 |  | 29.5 | 67.75 | 12.25 | 463050 | 463.05 | 63.5 | 16.5 | 623700 | 623.7 | 59.25 | 20.75 | 784350 | 784.35 | 55 | 25 | 945000 | 945 | 50.75 | 29.25 | 1105650 | 1105.65 | 46.5 | 33.5 | 1266300 | 1266.3 | 42.25 | 37.75 | 1426950 | 1426.95 | 38 | 42 | 1587600 | 1587.6 | 33.75 | 46.25 | 1748250 | 1748.25 | 29.5 | 50.5 | 1908900 | 1908.9 | 30
1/5/20XX 11:00:00 AM | 0.45833 | 5 | 30.5 | 50 | 30.5 |  | 30.5 | 67.85 | 12.15 | 459270 | 459.27 | 63.7 | 16.3 | 616140 | 616.14 | 59.55 | 20.45 | 773010 | 773.01 | 55.4 | 24.6 | 929880 | 929.88 | 51.25 | 28.75 | 1086750 | 1086.75 | 47.1 | 32.9 | 1243620 | 1243.62 | 42.95 | 37.05 | 1400490 | 1400.49 | 38.8 | 41.2 | 1557360 | 1557.36 | 34.65 | 45.35 | 1714230 | 1714.23 | 30.5 | 49.5 | 1871100 | 1871.1 | 30
1/5/20XX 12:00:00 PM | 0.5 | 5 | 31.5 | 48 | 31.5 |  | 31.5 | 67.95 | 12.05 | 455490 | 455.49 | 63.9 | 16.1 | 608580 | 608.58 | 59.85 | 20.15 | 761670 | 761.67 | 55.8 | 24.2 | 914760 | 914.76 | 51.75 | 28.25 | 1067850 | 1067.85 | 47.7 | 32.3 | 1220940 | 1220.94 | 43.65 | 36.35 | 1374030 | 1374.03 | 39.6 | 40.4 | 1527120 | 1527.12 | 35.55 | 44.45 | 1680210 | 1680.21 | 31.5 | 48.5 | 1833300 | 1833.3 | 30
1/5/20XX 1:00:00 PM | 0.54167 | 5 | 32.6 | 45.6 | 32.6 |  | 32.6 | 68.06 | 11.94 | 451332 | 451.332 | 64.12 | 15.88 | 600264 | 600.264 | 60.18 | 19.82 | 749196 | 749.196 | 56.24 | 23.76 | 898128 | 898.128 | 52.3 | 27.7 | 1047060 | 1047.06 | 48.36 | 31.64 | 1195992 | 1195.992 | 44.42 | 35.58 | 1344924 | 1344.924 | 40.48 | 39.52 | 1493856 | 1493.856 | 36.54 | 43.46 | 1642788 | 1642.788 | 32.6 | 47.4 | 1791720 | 1791.72 | 35
1/5/20XX 2:00:00 PM | 0.58333 | 5 | 32.9 | 43.5 | 32.9 |  | 32.9 | 68.09 | 11.91 | 450198 | 450.198 | 64.18 | 15.82 | 597996 | 597.996 | 60.27 | 19.73 | 745794 | 745.794 | 56.36 | 23.64 | 893592 | 893.592 | 52.45 | 27.55 | 1041390 | 1041.39 | 48.54 | 31.46 | 1189188 | 1189.188 | 44.63 | 35.37 | 1336986 | 1336.986 | 40.72 | 39.28 | 1484784 | 1484.784 | 36.81 | 43.19 | 1632582 | 1632.582 | 32.9 | 47.1 | 1780380 | 1780.38 | 35
1/5/20XX 3:00:00 PM | 0.625 | 5 | 33.3 | 43.5 | 33.3 |  | 33.3 | 68.13 | 11.87 | 448686 | 448.686 | 64.26 | 15.74 | 594972 | 594.972 | 60.39 | 19.61 | 741258 | 741.258 | 56.52 | 23.48 | 887544 | 887.544 | 52.65 | 27.35 | 1033830 | 1033.83 | 48.78 | 31.22 | 1180116 | 1180.116 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.17 | 42.83 | 1618974 | 1618.974 | 33.3 | 46.7 | 1765260 | 1765.26 | 35
1/5/20XX 4:00:00 PM | 0.66667 | 5 | 33.3 | 43.8 | 33.3 |  | 33.3 | 68.13 | 11.87 | 448686 | 448.686 | 64.26 | 15.74 | 594972 | 594.972 | 60.39 | 19.61 | 741258 | 741.258 | 56.52 | 23.48 | 887544 | 887.544 | 52.65 | 27.35 | 1033830 | 1033.83 | 48.78 | 31.22 | 1180116 | 1180.116 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.17 | 42.83 | 1618974 | 1618.974 | 33.3 | 46.7 | 1765260 | 1765.26 | 35
1/5/20XX 5:00:00 PM | 0.70833 | 5 | 32.5 | 44.6 | 32.5 |  | 32.5 | 68.05 | 11.95 | 451710 | 451.71 | 64.1 | 15.9 | 601020 | 601.02 | 60.15 | 19.85 | 750330 | 750.33 | 56.2 | 23.8 | 899640 | 899.64 | 52.25 | 27.75 | 1048950 | 1048.95 | 48.3 | 31.7 | 1198260 | 1198.26 | 44.35 | 35.65 | 1347570 | 1347.57 | 40.4 | 39.6 | 1496880 | 1496.88 | 36.45 | 43.55 | 1646190 | 1646.19 | 32.5 | 47.5 | 1795500 | 1795.5 | 30
1/5/20XX 6:00:00 PM | 0.75 | 5 | 32 | 46.7 | 32 |  | 32 | 68 | 12 | 453600 | 453.6 | 64 | 16 | 604800 | 604.8 | 60 | 20 | 756000 | 756 | 56 | 24 | 907200 | 907.2 | 52 | 28 | 1058400 | 1058.4 | 48 | 32 | 1209600 | 1209.6 | 44 | 36 | 1360800 | 1360.8 | 40 | 40 | 1512000 | 1512 | 36 | 44 | 1663200 | 1663.2 | 32 | 48 | 1814400 | 1814.4 | 30
1/5/20XX 7:00:00 PM | 0.79167 | 5 | 31.8 | 46.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/5/20XX 8:00:00 PM | 0.83333 | 5 | 31.3 | 47.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/5/20XX 9:00:00 PM | 0.875 | 5 | 30.9 | 48.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/5/20XX 10:00:00 PM | 0.91667 | 5 | 30.2 | 49.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/5/20XX 11:00:00 PM | 0.95833 | 5 | 30.1 | 49.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/5/20XX 12:00:00 AM | 0 | 6 | 30.4 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/6/20XX 1:00:00 AM | 0.041667 | 6 | 30.3 | 53.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/6/20XX 2:00:00 AM | 0.083333 | 6 | 30 | 54.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/6/20XX 3:00:00 AM | 0.125 | 6 | 29.9 | 55.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/6/20XX 4:00:00 AM | 0.16667 | 6 | 29.5 | 55.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/6/20XX 5:00:00 AM | 0.20833 | 6 | 29.5 | 58.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/6/20XX 6:00:00 AM | 0.25 | 6 | 28.9 | 60.9 | 28.9 |  | 28.9 | 67.69 | 12.31 | 465318 | 465.318 | 63.38 | 16.62 | 628236 | 628.236 | 59.07 | 20.93 | 791154 | 791.154 | 54.76 | 25.24 | 954072 | 954.072 | 50.45 | 29.55 | 1116990 | 1116.99 | 46.14 | 33.86 | 1279908 | 1279.908 | 41.83 | 38.17 | 1442826 | 1442.826 | 37.52 | 42.48 | 1605744 | 1605.744 | 33.21 | 46.79 | 1768662 | 1768.662 | 28.9 | 51.1 | 1931580 | 1931.58 | 30
1/6/20XX 7:00:00 AM | 0.29167 | 6 | 29.4 | 61.3 | 29.4 |  | 29.4 | 67.74 | 12.26 | 463428 | 463.428 | 63.48 | 16.52 | 624456 | 624.456 | 59.22 | 20.78 | 785484 | 785.484 | 54.96 | 25.04 | 946512 | 946.512 | 50.7 | 29.3 | 1107540 | 1107.54 | 46.44 | 33.56 | 1268568 | 1268.568 | 42.18 | 37.82 | 1429596 | 1429.596 | 37.92 | 42.08 | 1590624 | 1590.624 | 33.66 | 46.34 | 1751652 | 1751.652 | 29.4 | 50.6 | 1912680 | 1912.68 | 30
1/6/20XX 8:00:00 AM | 0.33333 | 6 | 29.6 | 60.7 | 29.6 |  | 29.6 | 67.76 | 12.24 | 462672 | 462.672 | 63.52 | 16.48 | 622944 | 622.944 | 59.28 | 20.72 | 783216 | 783.216 | 55.04 | 24.96 | 943488 | 943.488 | 50.8 | 29.2 | 1103760 | 1103.76 | 46.56 | 33.44 | 1264032 | 1264.032 | 42.32 | 37.68 | 1424304 | 1424.304 | 38.08 | 41.92 | 1584576 | 1584.576 | 33.84 | 46.16 | 1744848 | 1744.848 | 29.6 | 50.4 | 1905120 | 1905.12 | 30
1/6/20XX 9:00:00 AM | 0.375 | 6 | 30.3 | 59.1 | 30.3 |  | 30.3 | 67.83 | 12.17 | 460026 | 460.026 | 63.66 | 16.34 | 617652 | 617.652 | 59.49 | 20.51 | 775278 | 775.278 | 55.32 | 24.68 | 932904 | 932.904 | 51.15 | 28.85 | 1090530 | 1090.53 | 46.98 | 33.02 | 1248156 | 1248.156 | 42.81 | 37.19 | 1405782 | 1405.782 | 38.64 | 41.36 | 1563408 | 1563.408 | 34.47 | 45.53 | 1721034 | 1721.034 | 30.3 | 49.7 | 1878660 | 1878.66 | 30
1/6/20XX 10:00:00 AM | 0.41667 | 6 | 30.3 | 57.7 | 30.3 |  | 30.3 | 67.83 | 12.17 | 460026 | 460.026 | 63.66 | 16.34 | 617652 | 617.652 | 59.49 | 20.51 | 775278 | 775.278 | 55.32 | 24.68 | 932904 | 932.904 | 51.15 | 28.85 | 1090530 | 1090.53 | 46.98 | 33.02 | 1248156 | 1248.156 | 42.81 | 37.19 | 1405782 | 1405.782 | 38.64 | 41.36 | 1563408 | 1563.408 | 34.47 | 45.53 | 1721034 | 1721.034 | 30.3 | 49.7 | 1878660 | 1878.66 | 30
1/6/20XX 11:00:00 AM | 0.45833 | 6 | 31.6 | 54.5 | 31.6 |  | 31.6 | 67.96 | 12.04 | 455112 | 455.112 | 63.92 | 16.08 | 607824 | 607.824 | 59.88 | 20.12 | 760536 | 760.536 | 55.84 | 24.16 | 913248 | 913.248 | 51.8 | 28.2 | 1065960 | 1065.96 | 47.76 | 32.24 | 1218672 | 1218.672 | 43.72 | 36.28 | 1371384 | 1371.384 | 39.68 | 40.32 | 1524096 | 1524.096 | 35.64 | 44.36 | 1676808 | 1676.808 | 31.6 | 48.4 | 1829520 | 1829.52 | 30
1/6/20XX 12:00:00 PM | 0.5 | 6 | 32.4 | 50.7 | 32.4 |  | 32.4 | 68.04 | 11.96 | 452088 | 452.088 | 64.08 | 15.92 | 601776 | 601.776 | 60.12 | 19.88 | 751464 | 751.464 | 56.16 | 23.84 | 901152 | 901.152 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.24 | 31.76 | 1200528 | 1200.528 | 44.28 | 35.72 | 1350216 | 1350.216 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.36 | 43.64 | 1649592 | 1649.592 | 32.4 | 47.6 | 1799280 | 1799.28 | 30
1/6/20XX 1:00:00 PM | 0.54167 | 6 | 33.3 | 49.2 | 33.3 |  | 33.3 | 68.13 | 11.87 | 448686 | 448.686 | 64.26 | 15.74 | 594972 | 594.972 | 60.39 | 19.61 | 741258 | 741.258 | 56.52 | 23.48 | 887544 | 887.544 | 52.65 | 27.35 | 1033830 | 1033.83 | 48.78 | 31.22 | 1180116 | 1180.116 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.17 | 42.83 | 1618974 | 1618.974 | 33.3 | 46.7 | 1765260 | 1765.26 | 35
1/6/20XX 2:00:00 PM | 0.58333 | 6 | 33.9 | 44.7 | 33.9 |  | 33.9 | 68.19 | 11.81 | 446418 | 446.418 | 64.38 | 15.62 | 590436 | 590.436 | 60.57 | 19.43 | 734454 | 734.454 | 56.76 | 23.24 | 878472 | 878.472 | 52.95 | 27.05 | 1022490 | 1022.49 | 49.14 | 30.86 | 1166508 | 1166.508 | 45.33 | 34.67 | 1310526 | 1310.526 | 41.52 | 38.48 | 1454544 | 1454.544 | 37.71 | 42.29 | 1598562 | 1598.562 | 33.9 | 46.1 | 1742580 | 1742.58 | 35
1/6/20XX 3:00:00 PM | 0.625 | 6 | 34.4 | 44.8 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
1/6/20XX 4:00:00 PM | 0.66667 | 6 | 33.8 | 44.8 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
1/6/20XX 5:00:00 PM | 0.70833 | 6 | 33.2 | 45.4 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
1/6/20XX 6:00:00 PM | 0.75 | 6 | 32.6 | 47 | 32.6 |  | 32.6 | 68.06 | 11.94 | 451332 | 451.332 | 64.12 | 15.88 | 600264 | 600.264 | 60.18 | 19.82 | 749196 | 749.196 | 56.24 | 23.76 | 898128 | 898.128 | 52.3 | 27.7 | 1047060 | 1047.06 | 48.36 | 31.64 | 1195992 | 1195.992 | 44.42 | 35.58 | 1344924 | 1344.924 | 40.48 | 39.52 | 1493856 | 1493.856 | 36.54 | 43.46 | 1642788 | 1642.788 | 32.6 | 47.4 | 1791720 | 1791.72 | 35
1/6/20XX 7:00:00 PM | 0.79167 | 6 | 32.2 | 45.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/6/20XX 8:00:00 PM | 0.83333 | 6 | 31.4 | 49.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/6/20XX 9:00:00 PM | 0.875 | 6 | 30.9 | 51.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/6/20XX 10:00:00 PM | 0.91667 | 6 | 30.4 | 51.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/6/20XX 11:00:00 PM | 0.95833 | 6 | 29.4 | 54.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/6/20XX 12:00:00 AM | 0 | 7 | 29.1 | 54.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/7/20XX 1:00:00 AM | 0.041667 | 7 | 28.3 | 54 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/7/20XX 2:00:00 AM | 0.083333 | 7 | 27.9 | 55.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/7/20XX 3:00:00 AM | 0.125 | 7 | 27.7 | 55.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/7/20XX 4:00:00 AM | 0.16667 | 7 | 27.4 | 56.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/7/20XX 5:00:00 AM | 0.20833 | 7 | 27.2 | 57.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/7/20XX 6:00:00 AM | 0.25 | 7 | 26.8 | 58.1 | 26.8 |  | 26.8 | 67.48 | 12.52 | 473256 | 473.256 | 62.96 | 17.04 | 644112 | 644.112 | 58.44 | 21.56 | 814968 | 814.968 | 53.92 | 26.08 | 985824 | 985.824 | 49.4 | 30.6 | 1156680 | 1156.68 | 44.88 | 35.12 | 1327536 | 1327.536 | 40.36 | 39.64 | 1498392 | 1498.392 | 35.84 | 44.16 | 1669248 | 1669.248 | 31.32 | 48.68 | 1840104 | 1840.104 | 26.8 | 53.2 | 2010960 | 2010.96 | 25
1/7/20XX 7:00:00 AM | 0.29167 | 7 | 26.8 | 59.4 | 26.8 |  | 26.8 | 67.48 | 12.52 | 473256 | 473.256 | 62.96 | 17.04 | 644112 | 644.112 | 58.44 | 21.56 | 814968 | 814.968 | 53.92 | 26.08 | 985824 | 985.824 | 49.4 | 30.6 | 1156680 | 1156.68 | 44.88 | 35.12 | 1327536 | 1327.536 | 40.36 | 39.64 | 1498392 | 1498.392 | 35.84 | 44.16 | 1669248 | 1669.248 | 31.32 | 48.68 | 1840104 | 1840.104 | 26.8 | 53.2 | 2010960 | 2010.96 | 25
1/7/20XX 8:00:00 AM | 0.33333 | 7 | 26.7 | 60 | 26.7 |  | 26.7 | 67.47 | 12.53 | 473634 | 473.634 | 62.94 | 17.06 | 644868 | 644.868 | 58.41 | 21.59 | 816102 | 816.102 | 53.88 | 26.12 | 987336 | 987.336 | 49.35 | 30.65 | 1158570 | 1158.57 | 44.82 | 35.18 | 1329804 | 1329.804 | 40.29 | 39.71 | 1501038 | 1501.038 | 35.76 | 44.24 | 1672272 | 1672.272 | 31.23 | 48.77 | 1843506 | 1843.506 | 26.7 | 53.3 | 2014740 | 2014.74 | 25
1/7/20XX 9:00:00 AM | 0.375 | 7 | 27.5 | 58.7 | 27.5 |  | 27.5 | 67.55 | 12.45 | 470610 | 470.61 | 63.1 | 16.9 | 638820 | 638.82 | 58.65 | 21.35 | 807030 | 807.03 | 54.2 | 25.8 | 975240 | 975.24 | 49.75 | 30.25 | 1143450 | 1143.45 | 45.3 | 34.7 | 1311660 | 1311.66 | 40.85 | 39.15 | 1479870 | 1479.87 | 36.4 | 43.6 | 1648080 | 1648.08 | 31.95 | 48.05 | 1816290 | 1816.29 | 27.5 | 52.5 | 1984500 | 1984.5 | 25
1/7/20XX 10:00:00 AM | 0.41667 | 7 | 28.8 | 56.8 | 28.8 |  | 28.8 | 67.68 | 12.32 | 465696 | 465.696 | 63.36 | 16.64 | 628992 | 628.992 | 59.04 | 20.96 | 792288 | 792.288 | 54.72 | 25.28 | 955584 | 955.584 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.08 | 33.92 | 1282176 | 1282.176 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.44 | 42.56 | 1608768 | 1608.768 | 33.12 | 46.88 | 1772064 | 1772.064 | 28.8 | 51.2 | 1935360 | 1935.36 | 30
1/7/20XX 11:00:00 AM | 0.45833 | 7 | 29.9 | 56.4 | 29.9 |  | 29.9 | 67.79 | 12.21 | 461538 | 461.538 | 63.58 | 16.42 | 620676 | 620.676 | 59.37 | 20.63 | 779814 | 779.814 | 55.16 | 24.84 | 938952 | 938.952 | 50.95 | 29.05 | 1098090 | 1098.09 | 46.74 | 33.26 | 1257228 | 1257.228 | 42.53 | 37.47 | 1416366 | 1416.366 | 38.32 | 41.68 | 1575504 | 1575.504 | 34.11 | 45.89 | 1734642 | 1734.642 | 29.9 | 50.1 | 1893780 | 1893.78 | 30
1/7/20XX 12:00:00 PM | 0.5 | 7 | 30.9 | 53.7 | 30.9 |  | 30.9 | 67.89 | 12.11 | 457758 | 457.758 | 63.78 | 16.22 | 613116 | 613.116 | 59.67 | 20.33 | 768474 | 768.474 | 55.56 | 24.44 | 923832 | 923.832 | 51.45 | 28.55 | 1079190 | 1079.19 | 47.34 | 32.66 | 1234548 | 1234.548 | 43.23 | 36.77 | 1389906 | 1389.906 | 39.12 | 40.88 | 1545264 | 1545.264 | 35.01 | 44.99 | 1700622 | 1700.622 | 30.9 | 49.1 | 1855980 | 1855.98 | 30
1/7/20XX 1:00:00 PM | 0.54167 | 7 | 31.6 | 54.6 | 31.6 |  | 31.6 | 67.96 | 12.04 | 455112 | 455.112 | 63.92 | 16.08 | 607824 | 607.824 | 59.88 | 20.12 | 760536 | 760.536 | 55.84 | 24.16 | 913248 | 913.248 | 51.8 | 28.2 | 1065960 | 1065.96 | 47.76 | 32.24 | 1218672 | 1218.672 | 43.72 | 36.28 | 1371384 | 1371.384 | 39.68 | 40.32 | 1524096 | 1524.096 | 35.64 | 44.36 | 1676808 | 1676.808 | 31.6 | 48.4 | 1829520 | 1829.52 | 30
1/7/20XX 2:00:00 PM | 0.58333 | 7 | 32.3 | 54.4 | 32.3 |  | 32.3 | 68.03 | 11.97 | 452466 | 452.466 | 64.06 | 15.94 | 602532 | 602.532 | 60.09 | 19.91 | 752598 | 752.598 | 56.12 | 23.88 | 902664 | 902.664 | 52.15 | 27.85 | 1052730 | 1052.73 | 48.18 | 31.82 | 1202796 | 1202.796 | 44.21 | 35.79 | 1352862 | 1352.862 | 40.24 | 39.76 | 1502928 | 1502.928 | 36.27 | 43.73 | 1652994 | 1652.994 | 32.3 | 47.7 | 1803060 | 1803.06 | 30
1/7/20XX 3:00:00 PM | 0.625 | 7 | 32.5 | 53.9 | 32.5 |  | 32.5 | 68.05 | 11.95 | 451710 | 451.71 | 64.1 | 15.9 | 601020 | 601.02 | 60.15 | 19.85 | 750330 | 750.33 | 56.2 | 23.8 | 899640 | 899.64 | 52.25 | 27.75 | 1048950 | 1048.95 | 48.3 | 31.7 | 1198260 | 1198.26 | 44.35 | 35.65 | 1347570 | 1347.57 | 40.4 | 39.6 | 1496880 | 1496.88 | 36.45 | 43.55 | 1646190 | 1646.19 | 32.5 | 47.5 | 1795500 | 1795.5 | 30
1/7/20XX 4:00:00 PM | 0.66667 | 7 | 32.2 | 53.7 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
1/7/20XX 5:00:00 PM | 0.70833 | 7 | 31.5 | 54 | 31.5 |  | 31.5 | 67.95 | 12.05 | 455490 | 455.49 | 63.9 | 16.1 | 608580 | 608.58 | 59.85 | 20.15 | 761670 | 761.67 | 55.8 | 24.2 | 914760 | 914.76 | 51.75 | 28.25 | 1067850 | 1067.85 | 47.7 | 32.3 | 1220940 | 1220.94 | 43.65 | 36.35 | 1374030 | 1374.03 | 39.6 | 40.4 | 1527120 | 1527.12 | 35.55 | 44.45 | 1680210 | 1680.21 | 31.5 | 48.5 | 1833300 | 1833.3 | 30
1/7/20XX 6:00:00 PM | 0.75 | 7 | 30.9 | 55 | 30.9 |  | 30.9 | 67.89 | 12.11 | 457758 | 457.758 | 63.78 | 16.22 | 613116 | 613.116 | 59.67 | 20.33 | 768474 | 768.474 | 55.56 | 24.44 | 923832 | 923.832 | 51.45 | 28.55 | 1079190 | 1079.19 | 47.34 | 32.66 | 1234548 | 1234.548 | 43.23 | 36.77 | 1389906 | 1389.906 | 39.12 | 40.88 | 1545264 | 1545.264 | 35.01 | 44.99 | 1700622 | 1700.622 | 30.9 | 49.1 | 1855980 | 1855.98 | 30
1/7/20XX 7:00:00 PM | 0.79167 | 7 | 30.4 | 55.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/7/20XX 8:00:00 PM | 0.83333 | 7 | 29.6 | 54.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/7/20XX 9:00:00 PM | 0.875 | 7 | 29.3 | 56.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/7/20XX 10:00:00 PM | 0.91667 | 7 | 29.1 | 55.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/7/20XX 11:00:00 PM | 0.95833 | 7 | 28.1 | 56.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/7/20XX 12:00:00 AM | 0 | 1 | 27.6 | 55.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/8/20XX 1:00:00 AM | 0.041667 | 1 | 27.2 | 55.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/8/20XX 2:00:00 AM | 0.083333 | 1 | 26.8 | 55.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/8/20XX 3:00:00 AM | 0.125 | 1 | 26.7 | 55.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/8/20XX 4:00:00 AM | 0.16667 | 1 | 26.2 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/8/20XX 5:00:00 AM | 0.20833 | 1 | 25.7 | 60.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/8/20XX 6:00:00 AM | 0.25 | 1 | 25.6 | 60.9 | 25.6 |  | 25.6 | 67.36 | 12.64 | 477792 | 477.792 | 62.72 | 17.28 | 653184 | 653.184 | 58.08 | 21.92 | 828576 | 828.576 | 53.44 | 26.56 | 1003968 | 1003.968 | 48.8 | 31.2 | 1179360 | 1179.36 | 44.16 | 35.84 | 1354752 | 1354.752 | 39.52 | 40.48 | 1530144 | 1530.144 | 34.88 | 45.12 | 1705536 | 1705.536 | 30.24 | 49.76 | 1880928 | 1880.928 | 25.6 | 54.4 | 2056320 | 2056.32 | 25
1/8/20XX 7:00:00 AM | 0.29167 | 1 | 25.8 | 60.9 | 25.8 |  | 25.8 | 67.38 | 12.62 | 477036 | 477.036 | 62.76 | 17.24 | 651672 | 651.672 | 58.14 | 21.86 | 826308 | 826.308 | 53.52 | 26.48 | 1000944 | 1000.944 | 48.9 | 31.1 | 1175580 | 1175.58 | 44.28 | 35.72 | 1350216 | 1350.216 | 39.66 | 40.34 | 1524852 | 1524.852 | 35.04 | 44.96 | 1699488 | 1699.488 | 30.42 | 49.58 | 1874124 | 1874.124 | 25.8 | 54.2 | 2048760 | 2048.76 | 25
1/8/20XX 8:00:00 AM | 0.33333 | 1 | 25.9 | 61.7 | 25.9 |  | 25.9 | 67.39 | 12.61 | 476658 | 476.658 | 62.78 | 17.22 | 650916 | 650.916 | 58.17 | 21.83 | 825174 | 825.174 | 53.56 | 26.44 | 999432 | 999.432 | 48.95 | 31.05 | 1173690 | 1173.69 | 44.34 | 35.66 | 1347948 | 1347.948 | 39.73 | 40.27 | 1522206 | 1522.206 | 35.12 | 44.88 | 1696464 | 1696.464 | 30.51 | 49.49 | 1870722 | 1870.722 | 25.9 | 54.1 | 2044980 | 2044.98 | 25
1/8/20XX 9:00:00 AM | 0.375 | 1 | 27.2 | 60.1 | 27.2 |  | 27.2 | 67.52 | 12.48 | 471744 | 471.744 | 63.04 | 16.96 | 641088 | 641.088 | 58.56 | 21.44 | 810432 | 810.432 | 54.08 | 25.92 | 979776 | 979.776 | 49.6 | 30.4 | 1149120 | 1149.12 | 45.12 | 34.88 | 1318464 | 1318.464 | 40.64 | 39.36 | 1487808 | 1487.808 | 36.16 | 43.84 | 1657152 | 1657.152 | 31.68 | 48.32 | 1826496 | 1826.496 | 27.2 | 52.8 | 1995840 | 1995.84 | 25
1/8/20XX 10:00:00 AM | 0.41667 | 1 | 28.1 | 59.8 | 28.1 |  | 28.1 | 67.61 | 12.39 | 468342 | 468.342 | 63.22 | 16.78 | 634284 | 634.284 | 58.83 | 21.17 | 800226 | 800.226 | 54.44 | 25.56 | 966168 | 966.168 | 50.05 | 29.95 | 1132110 | 1132.11 | 45.66 | 34.34 | 1298052 | 1298.052 | 41.27 | 38.73 | 1463994 | 1463.994 | 36.88 | 43.12 | 1629936 | 1629.936 | 32.49 | 47.51 | 1795878 | 1795.878 | 28.1 | 51.9 | 1961820 | 1961.82 | 30
1/8/20XX 11:00:00 AM | 0.45833 | 1 | 29.3 | 56.3 | 29.3 |  | 29.3 | 67.73 | 12.27 | 463806 | 463.806 | 63.46 | 16.54 | 625212 | 625.212 | 59.19 | 20.81 | 786618 | 786.618 | 54.92 | 25.08 | 948024 | 948.024 | 50.65 | 29.35 | 1109430 | 1109.43 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.11 | 37.89 | 1432242 | 1432.242 | 37.84 | 42.16 | 1593648 | 1593.648 | 33.57 | 46.43 | 1755054 | 1755.054 | 29.3 | 50.7 | 1916460 | 1916.46 | 30
1/8/20XX 12:00:00 PM | 0.5 | 1 | 31 | 56.4 | 31 |  | 31 | 67.9 | 12.1 | 457380 | 457.38 | 63.8 | 16.2 | 612360 | 612.36 | 59.7 | 20.3 | 767340 | 767.34 | 55.6 | 24.4 | 922320 | 922.32 | 51.5 | 28.5 | 1077300 | 1077.3 | 47.4 | 32.6 | 1232280 | 1232.28 | 43.3 | 36.7 | 1387260 | 1387.26 | 39.2 | 40.8 | 1542240 | 1542.24 | 35.1 | 44.9 | 1697220 | 1697.22 | 31 | 49 | 1852200 | 1852.2 | 30
1/8/20XX 1:00:00 PM | 0.54167 | 1 | 31.6 | 53.2 | 31.6 |  | 31.6 | 67.96 | 12.04 | 455112 | 455.112 | 63.92 | 16.08 | 607824 | 607.824 | 59.88 | 20.12 | 760536 | 760.536 | 55.84 | 24.16 | 913248 | 913.248 | 51.8 | 28.2 | 1065960 | 1065.96 | 47.76 | 32.24 | 1218672 | 1218.672 | 43.72 | 36.28 | 1371384 | 1371.384 | 39.68 | 40.32 | 1524096 | 1524.096 | 35.64 | 44.36 | 1676808 | 1676.808 | 31.6 | 48.4 | 1829520 | 1829.52 | 30
1/8/20XX 2:00:00 PM | 0.58333 | 1 | 32.1 | 51.6 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
1/8/20XX 3:00:00 PM | 0.625 | 1 | 32.4 | 51 | 32.4 |  | 32.4 | 68.04 | 11.96 | 452088 | 452.088 | 64.08 | 15.92 | 601776 | 601.776 | 60.12 | 19.88 | 751464 | 751.464 | 56.16 | 23.84 | 901152 | 901.152 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.24 | 31.76 | 1200528 | 1200.528 | 44.28 | 35.72 | 1350216 | 1350.216 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.36 | 43.64 | 1649592 | 1649.592 | 32.4 | 47.6 | 1799280 | 1799.28 | 30
1/8/20XX 4:00:00 PM | 0.66667 | 1 | 32.5 | 52.4 | 32.5 |  | 32.5 | 68.05 | 11.95 | 451710 | 451.71 | 64.1 | 15.9 | 601020 | 601.02 | 60.15 | 19.85 | 750330 | 750.33 | 56.2 | 23.8 | 899640 | 899.64 | 52.25 | 27.75 | 1048950 | 1048.95 | 48.3 | 31.7 | 1198260 | 1198.26 | 44.35 | 35.65 | 1347570 | 1347.57 | 40.4 | 39.6 | 1496880 | 1496.88 | 36.45 | 43.55 | 1646190 | 1646.19 | 32.5 | 47.5 | 1795500 | 1795.5 | 30
1/8/20XX 5:00:00 PM | 0.70833 | 1 | 31.4 | 52 | 31.4 |  | 31.4 | 67.94 | 12.06 | 455868 | 455.868 | 63.88 | 16.12 | 609336 | 609.336 | 59.82 | 20.18 | 762804 | 762.804 | 55.76 | 24.24 | 916272 | 916.272 | 51.7 | 28.3 | 1069740 | 1069.74 | 47.64 | 32.36 | 1223208 | 1223.208 | 43.58 | 36.42 | 1376676 | 1376.676 | 39.52 | 40.48 | 1530144 | 1530.144 | 35.46 | 44.54 | 1683612 | 1683.612 | 31.4 | 48.6 | 1837080 | 1837.08 | 30
1/8/20XX 6:00:00 PM | 0.75 | 1 | 30.7 | 54.4 | 30.7 |  | 30.7 | 67.87 | 12.13 | 458514 | 458.514 | 63.74 | 16.26 | 614628 | 614.628 | 59.61 | 20.39 | 770742 | 770.742 | 55.48 | 24.52 | 926856 | 926.856 | 51.35 | 28.65 | 1082970 | 1082.97 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.09 | 36.91 | 1395198 | 1395.198 | 38.96 | 41.04 | 1551312 | 1551.312 | 34.83 | 45.17 | 1707426 | 1707.426 | 30.7 | 49.3 | 1863540 | 1863.54 | 30
1/8/20XX 7:00:00 PM | 0.79167 | 1 | 30.2 | 53.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/8/20XX 8:00:00 PM | 0.83333 | 1 | 29.8 | 54.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/8/20XX 9:00:00 PM | 0.875 | 1 | 29.2 | 55.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/8/20XX 10:00:00 PM | 0.91667 | 1 | 29 | 55.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/8/20XX 11:00:00 PM | 0.95833 | 1 | 28.8 | 56.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/8/20XX 12:00:00 AM | 0 | 2 | 28.3 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/9/20XX 1:00:00 AM | 0.041667 | 2 | 28 | 57.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/9/20XX 2:00:00 AM | 0.083333 | 2 | 28.2 | 56.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/9/20XX 3:00:00 AM | 0.125 | 2 | 28.1 | 58.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/9/20XX 4:00:00 AM | 0.16667 | 2 | 28.2 | 58.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/9/20XX 5:00:00 AM | 0.20833 | 2 | 28.4 | 57.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/9/20XX 6:00:00 AM | 0.25 | 2 | 28.2 | 59.3 | 28.2 |  | 28.2 | 67.62 | 12.38 | 467964 | 467.964 | 63.24 | 16.76 | 633528 | 633.528 | 58.86 | 21.14 | 799092 | 799.092 | 54.48 | 25.52 | 964656 | 964.656 | 50.1 | 29.9 | 1130220 | 1130.22 | 45.72 | 34.28 | 1295784 | 1295.784 | 41.34 | 38.66 | 1461348 | 1461.348 | 36.96 | 43.04 | 1626912 | 1626.912 | 32.58 | 47.42 | 1792476 | 1792.476 | 28.2 | 51.8 | 1958040 | 1958.04 | 30
1/9/20XX 7:00:00 AM | 0.29167 | 2 | 27.9 | 61 | 27.9 |  | 27.9 | 67.59 | 12.41 | 469098 | 469.098 | 63.18 | 16.82 | 635796 | 635.796 | 58.77 | 21.23 | 802494 | 802.494 | 54.36 | 25.64 | 969192 | 969.192 | 49.95 | 30.05 | 1135890 | 1135.89 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.13 | 38.87 | 1469286 | 1469.286 | 36.72 | 43.28 | 1635984 | 1635.984 | 32.31 | 47.69 | 1802682 | 1802.682 | 27.9 | 52.1 | 1969380 | 1969.38 | 30
1/9/20XX 8:00:00 AM | 0.33333 | 2 | 27.8 | 64 | 27.8 |  | 27.8 | 67.58 | 12.42 | 469476 | 469.476 | 63.16 | 16.84 | 636552 | 636.552 | 58.74 | 21.26 | 803628 | 803.628 | 54.32 | 25.68 | 970704 | 970.704 | 49.9 | 30.1 | 1137780 | 1137.78 | 45.48 | 34.52 | 1304856 | 1304.856 | 41.06 | 38.94 | 1471932 | 1471.932 | 36.64 | 43.36 | 1639008 | 1639.008 | 32.22 | 47.78 | 1806084 | 1806.084 | 27.8 | 52.2 | 1973160 | 1973.16 | 30
1/9/20XX 9:00:00 AM | 0.375 | 2 | 28.7 | 63.1 | 28.7 |  | 28.7 | 67.67 | 12.33 | 466074 | 466.074 | 63.34 | 16.66 | 629748 | 629.748 | 59.01 | 20.99 | 793422 | 793.422 | 54.68 | 25.32 | 957096 | 957.096 | 50.35 | 29.65 | 1120770 | 1120.77 | 46.02 | 33.98 | 1284444 | 1284.444 | 41.69 | 38.31 | 1448118 | 1448.118 | 37.36 | 42.64 | 1611792 | 1611.792 | 33.03 | 46.97 | 1775466 | 1775.466 | 28.7 | 51.3 | 1939140 | 1939.14 | 30
1/9/20XX 10:00:00 AM | 0.41667 | 2 | 30.4 | 57.9 | 30.4 |  | 30.4 | 67.84 | 12.16 | 459648 | 459.648 | 63.68 | 16.32 | 616896 | 616.896 | 59.52 | 20.48 | 774144 | 774.144 | 55.36 | 24.64 | 931392 | 931.392 | 51.2 | 28.8 | 1088640 | 1088.64 | 47.04 | 32.96 | 1245888 | 1245.888 | 42.88 | 37.12 | 1403136 | 1403.136 | 38.72 | 41.28 | 1560384 | 1560.384 | 34.56 | 45.44 | 1717632 | 1717.632 | 30.4 | 49.6 | 1874880 | 1874.88 | 30
1/9/20XX 11:00:00 AM | 0.45833 | 2 | 32.1 | 53.1 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
1/9/20XX 12:00:00 PM | 0.5 | 2 | 33.8 | 49.6 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
1/9/20XX 1:00:00 PM | 0.54167 | 2 | 34.7 | 46.9 | 34.7 |  | 34.7 | 68.27 | 11.73 | 443394 | 443.394 | 64.54 | 15.46 | 584388 | 584.388 | 60.81 | 19.19 | 725382 | 725.382 | 57.08 | 22.92 | 866376 | 866.376 | 53.35 | 26.65 | 1007370 | 1007.37 | 49.62 | 30.38 | 1148364 | 1148.364 | 45.89 | 34.11 | 1289358 | 1289.358 | 42.16 | 37.84 | 1430352 | 1430.352 | 38.43 | 41.57 | 1571346 | 1571.346 | 34.7 | 45.3 | 1712340 | 1712.34 | 35
1/9/20XX 2:00:00 PM | 0.58333 | 2 | 35.3 | 45.7 | 35.3 |  | 35.3 | 68.33 | 11.67 | 441126 | 441.126 | 64.66 | 15.34 | 579852 | 579.852 | 60.99 | 19.01 | 718578 | 718.578 | 57.32 | 22.68 | 857304 | 857.304 | 53.65 | 26.35 | 996030 | 996.03 | 49.98 | 30.02 | 1134756 | 1134.756 | 46.31 | 33.69 | 1273482 | 1273.482 | 42.64 | 37.36 | 1412208 | 1412.208 | 38.97 | 41.03 | 1550934 | 1550.934 | 35.3 | 44.7 | 1689660 | 1689.66 | 35
1/9/20XX 3:00:00 PM | 0.625 | 2 | 35.4 | 46.2 | 35.4 |  | 35.4 | 68.34 | 11.66 | 440748 | 440.748 | 64.68 | 15.32 | 579096 | 579.096 | 61.02 | 18.98 | 717444 | 717.444 | 57.36 | 22.64 | 855792 | 855.792 | 53.7 | 26.3 | 994140 | 994.14 | 50.04 | 29.96 | 1132488 | 1132.488 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.72 | 37.28 | 1409184 | 1409.184 | 39.06 | 40.94 | 1547532 | 1547.532 | 35.4 | 44.6 | 1685880 | 1685.88 | 35
1/9/20XX 4:00:00 PM | 0.66667 | 2 | 34.9 | 47.9 | 34.9 |  | 34.9 | 68.29 | 11.71 | 442638 | 442.638 | 64.58 | 15.42 | 582876 | 582.876 | 60.87 | 19.13 | 723114 | 723.114 | 57.16 | 22.84 | 863352 | 863.352 | 53.45 | 26.55 | 1003590 | 1003.59 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.03 | 33.97 | 1284066 | 1284.066 | 42.32 | 37.68 | 1424304 | 1424.304 | 38.61 | 41.39 | 1564542 | 1564.542 | 34.9 | 45.1 | 1704780 | 1704.78 | 35
1/9/20XX 5:00:00 PM | 0.70833 | 2 | 34.5 | 49.6 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
1/9/20XX 6:00:00 PM | 0.75 | 2 | 34.1 | 51 | 34.1 |  | 34.1 | 68.21 | 11.79 | 445662 | 445.662 | 64.42 | 15.58 | 588924 | 588.924 | 60.63 | 19.37 | 732186 | 732.186 | 56.84 | 23.16 | 875448 | 875.448 | 53.05 | 26.95 | 1018710 | 1018.71 | 49.26 | 30.74 | 1161972 | 1161.972 | 45.47 | 34.53 | 1305234 | 1305.234 | 41.68 | 38.32 | 1448496 | 1448.496 | 37.89 | 42.11 | 1591758 | 1591.758 | 34.1 | 45.9 | 1735020 | 1735.02 | 35
1/9/20XX 7:00:00 PM | 0.79167 | 2 | 33.6 | 51.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/9/20XX 8:00:00 PM | 0.83333 | 2 | 33.1 | 53.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/9/20XX 9:00:00 PM | 0.875 | 2 | 32.3 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/9/20XX 10:00:00 PM | 0.91667 | 2 | 31.9 | 54.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/9/20XX 11:00:00 PM | 0.95833 | 2 | 31.3 | 54.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/9/20XX 12:00:00 AM | 0 | 3 | 30.9 | 55 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/10/20XX 1:00:00 AM | 0.041667 | 3 | 30.8 | 54.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/10/20XX 2:00:00 AM | 0.083333 | 3 | 30.4 | 55.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/10/20XX 3:00:00 AM | 0.125 | 3 | 29.7 | 57.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/10/20XX 4:00:00 AM | 0.16667 | 3 | 29.1 | 58.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/10/20XX 5:00:00 AM | 0.20833 | 3 | 29 | 59.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/10/20XX 6:00:00 AM | 0.25 | 3 | 28.9 | 59.4 | 28.9 |  | 28.9 | 67.69 | 12.31 | 465318 | 465.318 | 63.38 | 16.62 | 628236 | 628.236 | 59.07 | 20.93 | 791154 | 791.154 | 54.76 | 25.24 | 954072 | 954.072 | 50.45 | 29.55 | 1116990 | 1116.99 | 46.14 | 33.86 | 1279908 | 1279.908 | 41.83 | 38.17 | 1442826 | 1442.826 | 37.52 | 42.48 | 1605744 | 1605.744 | 33.21 | 46.79 | 1768662 | 1768.662 | 28.9 | 51.1 | 1931580 | 1931.58 | 30
1/10/20XX 7:00:00 AM | 0.29167 | 3 | 28.8 | 60.7 | 28.8 |  | 28.8 | 67.68 | 12.32 | 465696 | 465.696 | 63.36 | 16.64 | 628992 | 628.992 | 59.04 | 20.96 | 792288 | 792.288 | 54.72 | 25.28 | 955584 | 955.584 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.08 | 33.92 | 1282176 | 1282.176 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.44 | 42.56 | 1608768 | 1608.768 | 33.12 | 46.88 | 1772064 | 1772.064 | 28.8 | 51.2 | 1935360 | 1935.36 | 30
1/10/20XX 8:00:00 AM | 0.33333 | 3 | 29.2 | 61.5 | 29.2 |  | 29.2 | 67.72 | 12.28 | 464184 | 464.184 | 63.44 | 16.56 | 625968 | 625.968 | 59.16 | 20.84 | 787752 | 787.752 | 54.88 | 25.12 | 949536 | 949.536 | 50.6 | 29.4 | 1111320 | 1111.32 | 46.32 | 33.68 | 1273104 | 1273.104 | 42.04 | 37.96 | 1434888 | 1434.888 | 37.76 | 42.24 | 1596672 | 1596.672 | 33.48 | 46.52 | 1758456 | 1758.456 | 29.2 | 50.8 | 1920240 | 1920.24 | 30
1/10/20XX 9:00:00 AM | 0.375 | 3 | 30.5 | 59.1 | 30.5 |  | 30.5 | 67.85 | 12.15 | 459270 | 459.27 | 63.7 | 16.3 | 616140 | 616.14 | 59.55 | 20.45 | 773010 | 773.01 | 55.4 | 24.6 | 929880 | 929.88 | 51.25 | 28.75 | 1086750 | 1086.75 | 47.1 | 32.9 | 1243620 | 1243.62 | 42.95 | 37.05 | 1400490 | 1400.49 | 38.8 | 41.2 | 1557360 | 1557.36 | 34.65 | 45.35 | 1714230 | 1714.23 | 30.5 | 49.5 | 1871100 | 1871.1 | 30
1/10/20XX 10:00:00 AM | 0.41667 | 3 | 32.2 | 58.1 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
1/10/20XX 11:00:00 AM | 0.45833 | 3 | 33.2 | 55.5 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
1/10/20XX 12:00:00 PM | 0.5 | 3 | 35 | 53.3 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
1/10/20XX 1:00:00 PM | 0.54167 | 3 | 36.5 | 54.1 | 36.5 |  | 36.5 | 68.45 | 11.55 | 436590 | 436.59 | 64.9 | 15.1 | 570780 | 570.78 | 61.35 | 18.65 | 704970 | 704.97 | 57.8 | 22.2 | 839160 | 839.16 | 54.25 | 25.75 | 973350 | 973.35 | 50.7 | 29.3 | 1107540 | 1107.54 | 47.15 | 32.85 | 1241730 | 1241.73 | 43.6 | 36.4 | 1375920 | 1375.92 | 40.05 | 39.95 | 1510110 | 1510.11 | 36.5 | 43.5 | 1644300 | 1644.3 | 35
1/10/20XX 2:00:00 PM | 0.58333 | 3 | 36.9 | 57.1 | 36.9 |  | 36.9 | 68.49 | 11.51 | 435078 | 435.078 | 64.98 | 15.02 | 567756 | 567.756 | 61.47 | 18.53 | 700434 | 700.434 | 57.96 | 22.04 | 833112 | 833.112 | 54.45 | 25.55 | 965790 | 965.79 | 50.94 | 29.06 | 1098468 | 1098.468 | 47.43 | 32.57 | 1231146 | 1231.146 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.41 | 39.59 | 1496502 | 1496.502 | 36.9 | 43.1 | 1629180 | 1629.18 | 35
1/10/20XX 3:00:00 PM | 0.625 | 3 | 37.1 | 57.3 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
1/10/20XX 4:00:00 PM | 0.66667 | 3 | 37 | 58.9 | 37 |  | 37 | 68.5 | 11.5 | 434700 | 434.7 | 65 | 15 | 567000 | 567 | 61.5 | 18.5 | 699300 | 699.3 | 58 | 22 | 831600 | 831.6 | 54.5 | 25.5 | 963900 | 963.9 | 51 | 29 | 1096200 | 1096.2 | 47.5 | 32.5 | 1228500 | 1228.5 | 44 | 36 | 1360800 | 1360.8 | 40.5 | 39.5 | 1493100 | 1493.1 | 37 | 43 | 1625400 | 1625.4 | 35
1/10/20XX 5:00:00 PM | 0.70833 | 3 | 36.6 | 58.1 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
1/10/20XX 6:00:00 PM | 0.75 | 3 | 36.1 | 59.9 | 36.1 |  | 36.1 | 68.41 | 11.59 | 438102 | 438.102 | 64.82 | 15.18 | 573804 | 573.804 | 61.23 | 18.77 | 709506 | 709.506 | 57.64 | 22.36 | 845208 | 845.208 | 54.05 | 25.95 | 980910 | 980.91 | 50.46 | 29.54 | 1116612 | 1116.612 | 46.87 | 33.13 | 1252314 | 1252.314 | 43.28 | 36.72 | 1388016 | 1388.016 | 39.69 | 40.31 | 1523718 | 1523.718 | 36.1 | 43.9 | 1659420 | 1659.42 | 35
1/10/20XX 7:00:00 PM | 0.79167 | 3 | 35.7 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/10/20XX 8:00:00 PM | 0.83333 | 3 | 35.9 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/10/20XX 9:00:00 PM | 0.875 | 3 | 35 | 61.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/10/20XX 10:00:00 PM | 0.91667 | 3 | 34.8 | 61.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/10/20XX 11:00:00 PM | 0.95833 | 3 | 34.3 | 63.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/10/20XX 12:00:00 AM | 0 | 4 | 34.6 | 62.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/11/20XX 1:00:00 AM | 0.041667 | 4 | 33.9 | 64 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/11/20XX 2:00:00 AM | 0.083333 | 4 | 33.9 | 66 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/11/20XX 3:00:00 AM | 0.125 | 4 | 33.6 | 66.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/11/20XX 4:00:00 AM | 0.16667 | 4 | 33.8 | 65.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/11/20XX 5:00:00 AM | 0.20833 | 4 | 33.8 | 67.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/11/20XX 6:00:00 AM | 0.25 | 4 | 33.8 | 67 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
1/11/20XX 7:00:00 AM | 0.29167 | 4 | 33.6 | 67.4 | 33.6 |  | 33.6 | 68.16 | 11.84 | 447552 | 447.552 | 64.32 | 15.68 | 592704 | 592.704 | 60.48 | 19.52 | 737856 | 737.856 | 56.64 | 23.36 | 883008 | 883.008 | 52.8 | 27.2 | 1028160 | 1028.16 | 48.96 | 31.04 | 1173312 | 1173.312 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.28 | 38.72 | 1463616 | 1463.616 | 37.44 | 42.56 | 1608768 | 1608.768 | 33.6 | 46.4 | 1753920 | 1753.92 | 35
1/11/20XX 8:00:00 AM | 0.33333 | 4 | 34 | 65.6 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
1/11/20XX 9:00:00 AM | 0.375 | 4 | 34.7 | 64.4 | 34.7 |  | 34.7 | 68.27 | 11.73 | 443394 | 443.394 | 64.54 | 15.46 | 584388 | 584.388 | 60.81 | 19.19 | 725382 | 725.382 | 57.08 | 22.92 | 866376 | 866.376 | 53.35 | 26.65 | 1007370 | 1007.37 | 49.62 | 30.38 | 1148364 | 1148.364 | 45.89 | 34.11 | 1289358 | 1289.358 | 42.16 | 37.84 | 1430352 | 1430.352 | 38.43 | 41.57 | 1571346 | 1571.346 | 34.7 | 45.3 | 1712340 | 1712.34 | 35
1/11/20XX 10:00:00 AM | 0.41667 | 4 | 36 | 62.6 | 36 |  | 36 | 68.4 | 11.6 | 438480 | 438.48 | 64.8 | 15.2 | 574560 | 574.56 | 61.2 | 18.8 | 710640 | 710.64 | 57.6 | 22.4 | 846720 | 846.72 | 54 | 26 | 982800 | 982.8 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.2 | 36.8 | 1391040 | 1391.04 | 39.6 | 40.4 | 1527120 | 1527.12 | 36 | 44 | 1663200 | 1663.2 | 35
1/11/20XX 11:00:00 AM | 0.45833 | 4 | 37.4 | 60.2 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
1/11/20XX 12:00:00 PM | 0.5 | 4 | 38.6 | 58.8 | 38.6 |  | 38.6 | 68.66 | 11.34 | 428652 | 428.652 | 65.32 | 14.68 | 554904 | 554.904 | 61.98 | 18.02 | 681156 | 681.156 | 58.64 | 21.36 | 807408 | 807.408 | 55.3 | 24.7 | 933660 | 933.66 | 51.96 | 28.04 | 1059912 | 1059.912 | 48.62 | 31.38 | 1186164 | 1186.164 | 45.28 | 34.72 | 1312416 | 1312.416 | 41.94 | 38.06 | 1438668 | 1438.668 | 38.6 | 41.4 | 1564920 | 1564.92 | 40
1/11/20XX 1:00:00 PM | 0.54167 | 4 | 39.7 | 57.9 | 39.7 |  | 39.7 | 68.77 | 11.23 | 424494 | 424.494 | 65.54 | 14.46 | 546588 | 546.588 | 62.31 | 17.69 | 668682 | 668.682 | 59.08 | 20.92 | 790776 | 790.776 | 55.85 | 24.15 | 912870 | 912.87 | 52.62 | 27.38 | 1034964 | 1034.964 | 49.39 | 30.61 | 1157058 | 1157.058 | 46.16 | 33.84 | 1279152 | 1279.152 | 42.93 | 37.07 | 1401246 | 1401.246 | 39.7 | 40.3 | 1523340 | 1523.34 | 40
1/11/20XX 2:00:00 PM | 0.58333 | 4 | 40.1 | 59.1 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
1/11/20XX 3:00:00 PM | 0.625 | 4 | 40.4 | 58 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
1/11/20XX 4:00:00 PM | 0.66667 | 4 | 40.4 | 58 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
1/11/20XX 5:00:00 PM | 0.70833 | 4 | 39.8 | 60.5 | 39.8 |  | 39.8 | 68.78 | 11.22 | 424116 | 424.116 | 65.56 | 14.44 | 545832 | 545.832 | 62.34 | 17.66 | 667548 | 667.548 | 59.12 | 20.88 | 789264 | 789.264 | 55.9 | 24.1 | 910980 | 910.98 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.46 | 30.54 | 1154412 | 1154.412 | 46.24 | 33.76 | 1276128 | 1276.128 | 43.02 | 36.98 | 1397844 | 1397.844 | 39.8 | 40.2 | 1519560 | 1519.56 | 40
1/11/20XX 6:00:00 PM | 0.75 | 4 | 39.5 | 63.7 | 39.5 |  | 39.5 | 68.75 | 11.25 | 425250 | 425.25 | 65.5 | 14.5 | 548100 | 548.1 | 62.25 | 17.75 | 670950 | 670.95 | 59 | 21 | 793800 | 793.8 | 55.75 | 24.25 | 916650 | 916.65 | 52.5 | 27.5 | 1039500 | 1039.5 | 49.25 | 30.75 | 1162350 | 1162.35 | 46 | 34 | 1285200 | 1285.2 | 42.75 | 37.25 | 1408050 | 1408.05 | 39.5 | 40.5 | 1530900 | 1530.9 | 40
1/11/20XX 7:00:00 PM | 0.79167 | 4 | 38.7 | 66 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/11/20XX 8:00:00 PM | 0.83333 | 4 | 39.4 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/11/20XX 9:00:00 PM | 0.875 | 4 | 39.3 | 66.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/11/20XX 10:00:00 PM | 0.91667 | 4 | 38.8 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/11/20XX 11:00:00 PM | 0.95833 | 4 | 38.5 | 73.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/11/20XX 12:00:00 AM | 0 | 5 | 38.3 | 73.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/12/20XX 1:00:00 AM | 0.041667 | 5 | 37.8 | 73.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/12/20XX 2:00:00 AM | 0.083333 | 5 | 37.5 | 73 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/12/20XX 3:00:00 AM | 0.125 | 5 | 37.1 | 73 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/12/20XX 4:00:00 AM | 0.16667 | 5 | 37.2 | 73.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/12/20XX 5:00:00 AM | 0.20833 | 5 | 37.4 | 75.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/12/20XX 6:00:00 AM | 0.25 | 5 | 37.9 | 75.1 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
1/12/20XX 7:00:00 AM | 0.29167 | 5 | 37.8 | 73.1 | 37.8 |  | 37.8 | 68.58 | 11.42 | 431676 | 431.676 | 65.16 | 14.84 | 560952 | 560.952 | 61.74 | 18.26 | 690228 | 690.228 | 58.32 | 21.68 | 819504 | 819.504 | 54.9 | 25.1 | 948780 | 948.78 | 51.48 | 28.52 | 1078056 | 1078.056 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.22 | 38.78 | 1465884 | 1465.884 | 37.8 | 42.2 | 1595160 | 1595.16 | 40
1/12/20XX 8:00:00 AM | 0.33333 | 5 | 37.9 | 73.7 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
1/12/20XX 9:00:00 AM | 0.375 | 5 | 38.2 | 74.2 | 38.2 |  | 38.2 | 68.62 | 11.38 | 430164 | 430.164 | 65.24 | 14.76 | 557928 | 557.928 | 61.86 | 18.14 | 685692 | 685.692 | 58.48 | 21.52 | 813456 | 813.456 | 55.1 | 24.9 | 941220 | 941.22 | 51.72 | 28.28 | 1068984 | 1068.984 | 48.34 | 31.66 | 1196748 | 1196.748 | 44.96 | 35.04 | 1324512 | 1324.512 | 41.58 | 38.42 | 1452276 | 1452.276 | 38.2 | 41.8 | 1580040 | 1580.04 | 40
1/12/20XX 10:00:00 AM | 0.41667 | 5 | 39.7 | 73.2 | 39.7 |  | 39.7 | 68.77 | 11.23 | 424494 | 424.494 | 65.54 | 14.46 | 546588 | 546.588 | 62.31 | 17.69 | 668682 | 668.682 | 59.08 | 20.92 | 790776 | 790.776 | 55.85 | 24.15 | 912870 | 912.87 | 52.62 | 27.38 | 1034964 | 1034.964 | 49.39 | 30.61 | 1157058 | 1157.058 | 46.16 | 33.84 | 1279152 | 1279.152 | 42.93 | 37.07 | 1401246 | 1401.246 | 39.7 | 40.3 | 1523340 | 1523.34 | 40
1/12/20XX 11:00:00 AM | 0.45833 | 5 | 41.1 | 71.2 | 41.1 |  | 41.1 | 68.91 | 11.09 | 419202 | 419.202 | 65.82 | 14.18 | 536004 | 536.004 | 62.73 | 17.27 | 652806 | 652.806 | 59.64 | 20.36 | 769608 | 769.608 | 56.55 | 23.45 | 886410 | 886.41 | 53.46 | 26.54 | 1003212 | 1003.212 | 50.37 | 29.63 | 1120014 | 1120.014 | 47.28 | 32.72 | 1236816 | 1236.816 | 44.19 | 35.81 | 1353618 | 1353.618 | 41.1 | 38.9 | 1470420 | 1470.42 | 40
1/12/20XX 12:00:00 PM | 0.5 | 5 | 42.2 | 68.7 | 42.2 |  | 42.2 | 69.02 | 10.98 | 415044 | 415.044 | 66.04 | 13.96 | 527688 | 527.688 | 63.06 | 16.94 | 640332 | 640.332 | 60.08 | 19.92 | 752976 | 752.976 | 57.1 | 22.9 | 865620 | 865.62 | 54.12 | 25.88 | 978264 | 978.264 | 51.14 | 28.86 | 1090908 | 1090.908 | 48.16 | 31.84 | 1203552 | 1203.552 | 45.18 | 34.82 | 1316196 | 1316.196 | 42.2 | 37.8 | 1428840 | 1428.84 | 40
1/12/20XX 1:00:00 PM | 0.54167 | 5 | 43 | 68.8 | 43 |  | 43 | 69.1 | 10.9 | 412020 | 412.02 | 66.2 | 13.8 | 521640 | 521.64 | 63.3 | 16.7 | 631260 | 631.26 | 60.4 | 19.6 | 740880 | 740.88 | 57.5 | 22.5 | 850500 | 850.5 | 54.6 | 25.4 | 960120 | 960.12 | 51.7 | 28.3 | 1069740 | 1069.74 | 48.8 | 31.2 | 1179360 | 1179.36 | 45.9 | 34.1 | 1288980 | 1288.98 | 43 | 37 | 1398600 | 1398.6 | 45
1/12/20XX 2:00:00 PM | 0.58333 | 5 | 43.6 | 66.9 | 43.6 |  | 43.6 | 69.16 | 10.84 | 409752 | 409.752 | 66.32 | 13.68 | 517104 | 517.104 | 63.48 | 16.52 | 624456 | 624.456 | 60.64 | 19.36 | 731808 | 731.808 | 57.8 | 22.2 | 839160 | 839.16 | 54.96 | 25.04 | 946512 | 946.512 | 52.12 | 27.88 | 1053864 | 1053.864 | 49.28 | 30.72 | 1161216 | 1161.216 | 46.44 | 33.56 | 1268568 | 1268.568 | 43.6 | 36.4 | 1375920 | 1375.92 | 45
1/12/20XX 3:00:00 PM | 0.625 | 5 | 43.7 | 65.3 | 43.7 |  | 43.7 | 69.17 | 10.83 | 409374 | 409.374 | 66.34 | 13.66 | 516348 | 516.348 | 63.51 | 16.49 | 623322 | 623.322 | 60.68 | 19.32 | 730296 | 730.296 | 57.85 | 22.15 | 837270 | 837.27 | 55.02 | 24.98 | 944244 | 944.244 | 52.19 | 27.81 | 1051218 | 1051.218 | 49.36 | 30.64 | 1158192 | 1158.192 | 46.53 | 33.47 | 1265166 | 1265.166 | 43.7 | 36.3 | 1372140 | 1372.14 | 45
1/12/20XX 4:00:00 PM | 0.66667 | 5 | 43.4 | 66.4 | 43.4 |  | 43.4 | 69.14 | 10.86 | 410508 | 410.508 | 66.28 | 13.72 | 518616 | 518.616 | 63.42 | 16.58 | 626724 | 626.724 | 60.56 | 19.44 | 734832 | 734.832 | 57.7 | 22.3 | 842940 | 842.94 | 54.84 | 25.16 | 951048 | 951.048 | 51.98 | 28.02 | 1059156 | 1059.156 | 49.12 | 30.88 | 1167264 | 1167.264 | 46.26 | 33.74 | 1275372 | 1275.372 | 43.4 | 36.6 | 1383480 | 1383.48 | 45
1/12/20XX 5:00:00 PM | 0.70833 | 5 | 42.3 | 70.6 | 42.3 |  | 42.3 | 69.03 | 10.97 | 414666 | 414.666 | 66.06 | 13.94 | 526932 | 526.932 | 63.09 | 16.91 | 639198 | 639.198 | 60.12 | 19.88 | 751464 | 751.464 | 57.15 | 22.85 | 863730 | 863.73 | 54.18 | 25.82 | 975996 | 975.996 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.27 | 34.73 | 1312794 | 1312.794 | 42.3 | 37.7 | 1425060 | 1425.06 | 40
1/12/20XX 6:00:00 PM | 0.75 | 5 | 41.3 | 72.4 | 41.3 |  | 41.3 | 68.93 | 11.07 | 418446 | 418.446 | 65.86 | 14.14 | 534492 | 534.492 | 62.79 | 17.21 | 650538 | 650.538 | 59.72 | 20.28 | 766584 | 766.584 | 56.65 | 23.35 | 882630 | 882.63 | 53.58 | 26.42 | 998676 | 998.676 | 50.51 | 29.49 | 1114722 | 1114.722 | 47.44 | 32.56 | 1230768 | 1230.768 | 44.37 | 35.63 | 1346814 | 1346.814 | 41.3 | 38.7 | 1462860 | 1462.86 | 40
1/12/20XX 7:00:00 PM | 0.79167 | 5 | 41.1 | 70.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/12/20XX 8:00:00 PM | 0.83333 | 5 | 40.5 | 71.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/12/20XX 9:00:00 PM | 0.875 | 5 | 40.4 | 70.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/12/20XX 10:00:00 PM | 0.91667 | 5 | 39.2 | 71.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/12/20XX 11:00:00 PM | 0.95833 | 5 | 39.2 | 71.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/12/20XX 12:00:00 AM | 0 | 6 | 38.9 | 69.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/13/20XX 1:00:00 AM | 0.041667 | 6 | 38.1 | 71.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/13/20XX 2:00:00 AM | 0.083333 | 6 | 38.2 | 70.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/13/20XX 3:00:00 AM | 0.125 | 6 | 37.7 | 71 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/13/20XX 4:00:00 AM | 0.16667 | 6 | 37.7 | 71.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/13/20XX 5:00:00 AM | 0.20833 | 6 | 37.5 | 71.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/13/20XX 6:00:00 AM | 0.25 | 6 | 37.4 | 69.3 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
1/13/20XX 7:00:00 AM | 0.29167 | 6 | 35.6 | 69.3 | 35.6 |  | 35.6 | 68.36 | 11.64 | 439992 | 439.992 | 64.72 | 15.28 | 577584 | 577.584 | 61.08 | 18.92 | 715176 | 715.176 | 57.44 | 22.56 | 852768 | 852.768 | 53.8 | 26.2 | 990360 | 990.36 | 50.16 | 29.84 | 1127952 | 1127.952 | 46.52 | 33.48 | 1265544 | 1265.544 | 42.88 | 37.12 | 1403136 | 1403.136 | 39.24 | 40.76 | 1540728 | 1540.728 | 35.6 | 44.4 | 1678320 | 1678.32 | 35
1/13/20XX 8:00:00 AM | 0.33333 | 6 | 34.2 | 66 | 34.2 |  | 34.2 | 68.22 | 11.78 | 445284 | 445.284 | 64.44 | 15.56 | 588168 | 588.168 | 60.66 | 19.34 | 731052 | 731.052 | 56.88 | 23.12 | 873936 | 873.936 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.32 | 30.68 | 1159704 | 1159.704 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.98 | 42.02 | 1588356 | 1588.356 | 34.2 | 45.8 | 1731240 | 1731.24 | 35
1/13/20XX 9:00:00 AM | 0.375 | 6 | 33.5 | 65.1 | 33.5 |  | 33.5 | 68.15 | 11.85 | 447930 | 447.93 | 64.3 | 15.7 | 593460 | 593.46 | 60.45 | 19.55 | 738990 | 738.99 | 56.6 | 23.4 | 884520 | 884.52 | 52.75 | 27.25 | 1030050 | 1030.05 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.05 | 34.95 | 1321110 | 1321.11 | 41.2 | 38.8 | 1466640 | 1466.64 | 37.35 | 42.65 | 1612170 | 1612.17 | 33.5 | 46.5 | 1757700 | 1757.7 | 35
1/13/20XX 10:00:00 AM | 0.41667 | 6 | 33.8 | 62.7 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
1/13/20XX 11:00:00 AM | 0.45833 | 6 | 34.5 | 57.6 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
1/13/20XX 12:00:00 PM | 0.5 | 6 | 35.3 | 54.7 | 35.3 |  | 35.3 | 68.33 | 11.67 | 441126 | 441.126 | 64.66 | 15.34 | 579852 | 579.852 | 60.99 | 19.01 | 718578 | 718.578 | 57.32 | 22.68 | 857304 | 857.304 | 53.65 | 26.35 | 996030 | 996.03 | 49.98 | 30.02 | 1134756 | 1134.756 | 46.31 | 33.69 | 1273482 | 1273.482 | 42.64 | 37.36 | 1412208 | 1412.208 | 38.97 | 41.03 | 1550934 | 1550.934 | 35.3 | 44.7 | 1689660 | 1689.66 | 35
1/13/20XX 1:00:00 PM | 0.54167 | 6 | 36.4 | 51.7 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
1/13/20XX 2:00:00 PM | 0.58333 | 6 | 36.1 | 52.2 | 36.1 |  | 36.1 | 68.41 | 11.59 | 438102 | 438.102 | 64.82 | 15.18 | 573804 | 573.804 | 61.23 | 18.77 | 709506 | 709.506 | 57.64 | 22.36 | 845208 | 845.208 | 54.05 | 25.95 | 980910 | 980.91 | 50.46 | 29.54 | 1116612 | 1116.612 | 46.87 | 33.13 | 1252314 | 1252.314 | 43.28 | 36.72 | 1388016 | 1388.016 | 39.69 | 40.31 | 1523718 | 1523.718 | 36.1 | 43.9 | 1659420 | 1659.42 | 35
1/13/20XX 3:00:00 PM | 0.625 | 6 | 36.3 | 50.7 | 36.3 |  | 36.3 | 68.43 | 11.57 | 437346 | 437.346 | 64.86 | 15.14 | 572292 | 572.292 | 61.29 | 18.71 | 707238 | 707.238 | 57.72 | 22.28 | 842184 | 842.184 | 54.15 | 25.85 | 977130 | 977.13 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.01 | 32.99 | 1247022 | 1247.022 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.87 | 40.13 | 1516914 | 1516.914 | 36.3 | 43.7 | 1651860 | 1651.86 | 35
1/13/20XX 4:00:00 PM | 0.66667 | 6 | 35.2 | 52.2 | 35.2 |  | 35.2 | 68.32 | 11.68 | 441504 | 441.504 | 64.64 | 15.36 | 580608 | 580.608 | 60.96 | 19.04 | 719712 | 719.712 | 57.28 | 22.72 | 858816 | 858.816 | 53.6 | 26.4 | 997920 | 997.92 | 49.92 | 30.08 | 1137024 | 1137.024 | 46.24 | 33.76 | 1276128 | 1276.128 | 42.56 | 37.44 | 1415232 | 1415.232 | 38.88 | 41.12 | 1554336 | 1554.336 | 35.2 | 44.8 | 1693440 | 1693.44 | 35
1/13/20XX 5:00:00 PM | 0.70833 | 6 | 34.2 | 53.3 | 34.2 |  | 34.2 | 68.22 | 11.78 | 445284 | 445.284 | 64.44 | 15.56 | 588168 | 588.168 | 60.66 | 19.34 | 731052 | 731.052 | 56.88 | 23.12 | 873936 | 873.936 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.32 | 30.68 | 1159704 | 1159.704 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.98 | 42.02 | 1588356 | 1588.356 | 34.2 | 45.8 | 1731240 | 1731.24 | 35
1/13/20XX 6:00:00 PM | 0.75 | 6 | 33.4 | 53.2 | 33.4 |  | 33.4 | 68.14 | 11.86 | 448308 | 448.308 | 64.28 | 15.72 | 594216 | 594.216 | 60.42 | 19.58 | 740124 | 740.124 | 56.56 | 23.44 | 886032 | 886.032 | 52.7 | 27.3 | 1031940 | 1031.94 | 48.84 | 31.16 | 1177848 | 1177.848 | 44.98 | 35.02 | 1323756 | 1323.756 | 41.12 | 38.88 | 1469664 | 1469.664 | 37.26 | 42.74 | 1615572 | 1615.572 | 33.4 | 46.6 | 1761480 | 1761.48 | 35
1/13/20XX 7:00:00 PM | 0.79167 | 6 | 32.4 | 55.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/13/20XX 8:00:00 PM | 0.83333 | 6 | 32.1 | 56.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/13/20XX 9:00:00 PM | 0.875 | 6 | 31.8 | 56.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/13/20XX 10:00:00 PM | 0.91667 | 6 | 31.1 | 57.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/13/20XX 11:00:00 PM | 0.95833 | 6 | 30.7 | 58 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/13/20XX 12:00:00 AM | 0 | 7 | 30.6 | 58.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/14/20XX 1:00:00 AM | 0.041667 | 7 | 30.3 | 59.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/14/20XX 2:00:00 AM | 0.083333 | 7 | 30 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/14/20XX 3:00:00 AM | 0.125 | 7 | 29.6 | 58.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/14/20XX 4:00:00 AM | 0.16667 | 7 | 29.1 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/14/20XX 5:00:00 AM | 0.20833 | 7 | 28.7 | 59.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/14/20XX 6:00:00 AM | 0.25 | 7 | 28.3 | 60.7 | 28.3 |  | 28.3 | 67.63 | 12.37 | 467586 | 467.586 | 63.26 | 16.74 | 632772 | 632.772 | 58.89 | 21.11 | 797958 | 797.958 | 54.52 | 25.48 | 963144 | 963.144 | 50.15 | 29.85 | 1128330 | 1128.33 | 45.78 | 34.22 | 1293516 | 1293.516 | 41.41 | 38.59 | 1458702 | 1458.702 | 37.04 | 42.96 | 1623888 | 1623.888 | 32.67 | 47.33 | 1789074 | 1789.074 | 28.3 | 51.7 | 1954260 | 1954.26 | 30
1/14/20XX 7:00:00 AM | 0.29167 | 7 | 28.7 | 59.9 | 28.7 |  | 28.7 | 67.67 | 12.33 | 466074 | 466.074 | 63.34 | 16.66 | 629748 | 629.748 | 59.01 | 20.99 | 793422 | 793.422 | 54.68 | 25.32 | 957096 | 957.096 | 50.35 | 29.65 | 1120770 | 1120.77 | 46.02 | 33.98 | 1284444 | 1284.444 | 41.69 | 38.31 | 1448118 | 1448.118 | 37.36 | 42.64 | 1611792 | 1611.792 | 33.03 | 46.97 | 1775466 | 1775.466 | 28.7 | 51.3 | 1939140 | 1939.14 | 30
1/14/20XX 8:00:00 AM | 0.33333 | 7 | 28.6 | 60.4 | 28.6 |  | 28.6 | 67.66 | 12.34 | 466452 | 466.452 | 63.32 | 16.68 | 630504 | 630.504 | 58.98 | 21.02 | 794556 | 794.556 | 54.64 | 25.36 | 958608 | 958.608 | 50.3 | 29.7 | 1122660 | 1122.66 | 45.96 | 34.04 | 1286712 | 1286.712 | 41.62 | 38.38 | 1450764 | 1450.764 | 37.28 | 42.72 | 1614816 | 1614.816 | 32.94 | 47.06 | 1778868 | 1778.868 | 28.6 | 51.4 | 1942920 | 1942.92 | 30
1/14/20XX 9:00:00 AM | 0.375 | 7 | 28.9 | 60.1 | 28.9 |  | 28.9 | 67.69 | 12.31 | 465318 | 465.318 | 63.38 | 16.62 | 628236 | 628.236 | 59.07 | 20.93 | 791154 | 791.154 | 54.76 | 25.24 | 954072 | 954.072 | 50.45 | 29.55 | 1116990 | 1116.99 | 46.14 | 33.86 | 1279908 | 1279.908 | 41.83 | 38.17 | 1442826 | 1442.826 | 37.52 | 42.48 | 1605744 | 1605.744 | 33.21 | 46.79 | 1768662 | 1768.662 | 28.9 | 51.1 | 1931580 | 1931.58 | 30
1/14/20XX 10:00:00 AM | 0.41667 | 7 | 29.9 | 59.5 | 29.9 |  | 29.9 | 67.79 | 12.21 | 461538 | 461.538 | 63.58 | 16.42 | 620676 | 620.676 | 59.37 | 20.63 | 779814 | 779.814 | 55.16 | 24.84 | 938952 | 938.952 | 50.95 | 29.05 | 1098090 | 1098.09 | 46.74 | 33.26 | 1257228 | 1257.228 | 42.53 | 37.47 | 1416366 | 1416.366 | 38.32 | 41.68 | 1575504 | 1575.504 | 34.11 | 45.89 | 1734642 | 1734.642 | 29.9 | 50.1 | 1893780 | 1893.78 | 30
1/14/20XX 11:00:00 AM | 0.45833 | 7 | 32.2 | 54.4 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
1/14/20XX 12:00:00 PM | 0.5 | 7 | 32.9 | 54 | 32.9 |  | 32.9 | 68.09 | 11.91 | 450198 | 450.198 | 64.18 | 15.82 | 597996 | 597.996 | 60.27 | 19.73 | 745794 | 745.794 | 56.36 | 23.64 | 893592 | 893.592 | 52.45 | 27.55 | 1041390 | 1041.39 | 48.54 | 31.46 | 1189188 | 1189.188 | 44.63 | 35.37 | 1336986 | 1336.986 | 40.72 | 39.28 | 1484784 | 1484.784 | 36.81 | 43.19 | 1632582 | 1632.582 | 32.9 | 47.1 | 1780380 | 1780.38 | 35
1/14/20XX 1:00:00 PM | 0.54167 | 7 | 34 | 51.7 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
1/14/20XX 2:00:00 PM | 0.58333 | 7 | 34.5 | 51.4 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
1/14/20XX 3:00:00 PM | 0.625 | 7 | 34.8 | 51.5 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
1/14/20XX 4:00:00 PM | 0.66667 | 7 | 34.3 | 53.8 | 34.3 |  | 34.3 | 68.23 | 11.77 | 444906 | 444.906 | 64.46 | 15.54 | 587412 | 587.412 | 60.69 | 19.31 | 729918 | 729.918 | 56.92 | 23.08 | 872424 | 872.424 | 53.15 | 26.85 | 1014930 | 1014.93 | 49.38 | 30.62 | 1157436 | 1157.436 | 45.61 | 34.39 | 1299942 | 1299.942 | 41.84 | 38.16 | 1442448 | 1442.448 | 38.07 | 41.93 | 1584954 | 1584.954 | 34.3 | 45.7 | 1727460 | 1727.46 | 35
1/14/20XX 5:00:00 PM | 0.70833 | 7 | 33.9 | 54.1 | 33.9 |  | 33.9 | 68.19 | 11.81 | 446418 | 446.418 | 64.38 | 15.62 | 590436 | 590.436 | 60.57 | 19.43 | 734454 | 734.454 | 56.76 | 23.24 | 878472 | 878.472 | 52.95 | 27.05 | 1022490 | 1022.49 | 49.14 | 30.86 | 1166508 | 1166.508 | 45.33 | 34.67 | 1310526 | 1310.526 | 41.52 | 38.48 | 1454544 | 1454.544 | 37.71 | 42.29 | 1598562 | 1598.562 | 33.9 | 46.1 | 1742580 | 1742.58 | 35
1/14/20XX 6:00:00 PM | 0.75 | 7 | 33.6 | 56.6 | 33.6 |  | 33.6 | 68.16 | 11.84 | 447552 | 447.552 | 64.32 | 15.68 | 592704 | 592.704 | 60.48 | 19.52 | 737856 | 737.856 | 56.64 | 23.36 | 883008 | 883.008 | 52.8 | 27.2 | 1028160 | 1028.16 | 48.96 | 31.04 | 1173312 | 1173.312 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.28 | 38.72 | 1463616 | 1463.616 | 37.44 | 42.56 | 1608768 | 1608.768 | 33.6 | 46.4 | 1753920 | 1753.92 | 35
1/14/20XX 7:00:00 PM | 0.79167 | 7 | 33.1 | 57.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/14/20XX 8:00:00 PM | 0.83333 | 7 | 32.9 | 58.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/14/20XX 9:00:00 PM | 0.875 | 7 | 32.5 | 57.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/14/20XX 10:00:00 PM | 0.91667 | 7 | 31.8 | 60.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/14/20XX 11:00:00 PM | 0.95833 | 7 | 31 | 62.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/14/20XX 12:00:00 AM | 0 | 1 | 30.6 | 62.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/15/20XX 1:00:00 AM | 0.041667 | 1 | 30.2 | 63.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/15/20XX 2:00:00 AM | 0.083333 | 1 | 29.8 | 62.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/15/20XX 3:00:00 AM | 0.125 | 1 | 29.3 | 65.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/15/20XX 4:00:00 AM | 0.16667 | 1 | 28.5 | 65.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/15/20XX 5:00:00 AM | 0.20833 | 1 | 28.3 | 66.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/15/20XX 6:00:00 AM | 0.25 | 1 | 28.4 | 64.9 | 28.4 |  | 28.4 | 67.64 | 12.36 | 467208 | 467.208 | 63.28 | 16.72 | 632016 | 632.016 | 58.92 | 21.08 | 796824 | 796.824 | 54.56 | 25.44 | 961632 | 961.632 | 50.2 | 29.8 | 1126440 | 1126.44 | 45.84 | 34.16 | 1291248 | 1291.248 | 41.48 | 38.52 | 1456056 | 1456.056 | 37.12 | 42.88 | 1620864 | 1620.864 | 32.76 | 47.24 | 1785672 | 1785.672 | 28.4 | 51.6 | 1950480 | 1950.48 | 30
1/15/20XX 7:00:00 AM | 0.29167 | 1 | 28.1 | 67.3 | 28.1 |  | 28.1 | 67.61 | 12.39 | 468342 | 468.342 | 63.22 | 16.78 | 634284 | 634.284 | 58.83 | 21.17 | 800226 | 800.226 | 54.44 | 25.56 | 966168 | 966.168 | 50.05 | 29.95 | 1132110 | 1132.11 | 45.66 | 34.34 | 1298052 | 1298.052 | 41.27 | 38.73 | 1463994 | 1463.994 | 36.88 | 43.12 | 1629936 | 1629.936 | 32.49 | 47.51 | 1795878 | 1795.878 | 28.1 | 51.9 | 1961820 | 1961.82 | 30
1/15/20XX 8:00:00 AM | 0.33333 | 1 | 28.1 | 66.6 | 28.1 |  | 28.1 | 67.61 | 12.39 | 468342 | 468.342 | 63.22 | 16.78 | 634284 | 634.284 | 58.83 | 21.17 | 800226 | 800.226 | 54.44 | 25.56 | 966168 | 966.168 | 50.05 | 29.95 | 1132110 | 1132.11 | 45.66 | 34.34 | 1298052 | 1298.052 | 41.27 | 38.73 | 1463994 | 1463.994 | 36.88 | 43.12 | 1629936 | 1629.936 | 32.49 | 47.51 | 1795878 | 1795.878 | 28.1 | 51.9 | 1961820 | 1961.82 | 30
1/15/20XX 9:00:00 AM | 0.375 | 1 | 29.3 | 63.7 | 29.3 |  | 29.3 | 67.73 | 12.27 | 463806 | 463.806 | 63.46 | 16.54 | 625212 | 625.212 | 59.19 | 20.81 | 786618 | 786.618 | 54.92 | 25.08 | 948024 | 948.024 | 50.65 | 29.35 | 1109430 | 1109.43 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.11 | 37.89 | 1432242 | 1432.242 | 37.84 | 42.16 | 1593648 | 1593.648 | 33.57 | 46.43 | 1755054 | 1755.054 | 29.3 | 50.7 | 1916460 | 1916.46 | 30
1/15/20XX 10:00:00 AM | 0.41667 | 1 | 30.7 | 60.2 | 30.7 |  | 30.7 | 67.87 | 12.13 | 458514 | 458.514 | 63.74 | 16.26 | 614628 | 614.628 | 59.61 | 20.39 | 770742 | 770.742 | 55.48 | 24.52 | 926856 | 926.856 | 51.35 | 28.65 | 1082970 | 1082.97 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.09 | 36.91 | 1395198 | 1395.198 | 38.96 | 41.04 | 1551312 | 1551.312 | 34.83 | 45.17 | 1707426 | 1707.426 | 30.7 | 49.3 | 1863540 | 1863.54 | 30
1/15/20XX 11:00:00 AM | 0.45833 | 1 | 31.8 | 58.1 | 31.8 |  | 31.8 | 67.98 | 12.02 | 454356 | 454.356 | 63.96 | 16.04 | 606312 | 606.312 | 59.94 | 20.06 | 758268 | 758.268 | 55.92 | 24.08 | 910224 | 910.224 | 51.9 | 28.1 | 1062180 | 1062.18 | 47.88 | 32.12 | 1214136 | 1214.136 | 43.86 | 36.14 | 1366092 | 1366.092 | 39.84 | 40.16 | 1518048 | 1518.048 | 35.82 | 44.18 | 1670004 | 1670.004 | 31.8 | 48.2 | 1821960 | 1821.96 | 30
1/15/20XX 12:00:00 PM | 0.5 | 1 | 33.3 | 55.1 | 33.3 |  | 33.3 | 68.13 | 11.87 | 448686 | 448.686 | 64.26 | 15.74 | 594972 | 594.972 | 60.39 | 19.61 | 741258 | 741.258 | 56.52 | 23.48 | 887544 | 887.544 | 52.65 | 27.35 | 1033830 | 1033.83 | 48.78 | 31.22 | 1180116 | 1180.116 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.17 | 42.83 | 1618974 | 1618.974 | 33.3 | 46.7 | 1765260 | 1765.26 | 35
1/15/20XX 1:00:00 PM | 0.54167 | 1 | 34.5 | 53.6 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
1/15/20XX 2:00:00 PM | 0.58333 | 1 | 35.7 | 51.5 | 35.7 |  | 35.7 | 68.37 | 11.63 | 439614 | 439.614 | 64.74 | 15.26 | 576828 | 576.828 | 61.11 | 18.89 | 714042 | 714.042 | 57.48 | 22.52 | 851256 | 851.256 | 53.85 | 26.15 | 988470 | 988.47 | 50.22 | 29.78 | 1125684 | 1125.684 | 46.59 | 33.41 | 1262898 | 1262.898 | 42.96 | 37.04 | 1400112 | 1400.112 | 39.33 | 40.67 | 1537326 | 1537.326 | 35.7 | 44.3 | 1674540 | 1674.54 | 35
1/15/20XX 3:00:00 PM | 0.625 | 1 | 36.2 | 50.9 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
1/15/20XX 4:00:00 PM | 0.66667 | 1 | 35.4 | 54.6 | 35.4 |  | 35.4 | 68.34 | 11.66 | 440748 | 440.748 | 64.68 | 15.32 | 579096 | 579.096 | 61.02 | 18.98 | 717444 | 717.444 | 57.36 | 22.64 | 855792 | 855.792 | 53.7 | 26.3 | 994140 | 994.14 | 50.04 | 29.96 | 1132488 | 1132.488 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.72 | 37.28 | 1409184 | 1409.184 | 39.06 | 40.94 | 1547532 | 1547.532 | 35.4 | 44.6 | 1685880 | 1685.88 | 35
1/15/20XX 5:00:00 PM | 0.70833 | 1 | 35 | 57.3 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
1/15/20XX 6:00:00 PM | 0.75 | 1 | 34.7 | 57.3 | 34.7 |  | 34.7 | 68.27 | 11.73 | 443394 | 443.394 | 64.54 | 15.46 | 584388 | 584.388 | 60.81 | 19.19 | 725382 | 725.382 | 57.08 | 22.92 | 866376 | 866.376 | 53.35 | 26.65 | 1007370 | 1007.37 | 49.62 | 30.38 | 1148364 | 1148.364 | 45.89 | 34.11 | 1289358 | 1289.358 | 42.16 | 37.84 | 1430352 | 1430.352 | 38.43 | 41.57 | 1571346 | 1571.346 | 34.7 | 45.3 | 1712340 | 1712.34 | 35
1/15/20XX 7:00:00 PM | 0.79167 | 1 | 34.3 | 57.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/15/20XX 8:00:00 PM | 0.83333 | 1 | 34.1 | 57.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/15/20XX 9:00:00 PM | 0.875 | 1 | 33.3 | 60.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/15/20XX 10:00:00 PM | 0.91667 | 1 | 32.7 | 61.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/15/20XX 11:00:00 PM | 0.95833 | 1 | 32.2 | 63.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/15/20XX 12:00:00 AM | 0 | 2 | 32 | 63.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/16/20XX 1:00:00 AM | 0.041667 | 2 | 31.5 | 66.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/16/20XX 2:00:00 AM | 0.083333 | 2 | 30.9 | 68.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/16/20XX 3:00:00 AM | 0.125 | 2 | 30.5 | 67.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/16/20XX 4:00:00 AM | 0.16667 | 2 | 30.5 | 66.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/16/20XX 5:00:00 AM | 0.20833 | 2 | 30.3 | 64.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/16/20XX 6:00:00 AM | 0.25 | 2 | 29.7 | 66.7 | 29.7 |  | 29.7 | 67.77 | 12.23 | 462294 | 462.294 | 63.54 | 16.46 | 622188 | 622.188 | 59.31 | 20.69 | 782082 | 782.082 | 55.08 | 24.92 | 941976 | 941.976 | 50.85 | 29.15 | 1101870 | 1101.87 | 46.62 | 33.38 | 1261764 | 1261.764 | 42.39 | 37.61 | 1421658 | 1421.658 | 38.16 | 41.84 | 1581552 | 1581.552 | 33.93 | 46.07 | 1741446 | 1741.446 | 29.7 | 50.3 | 1901340 | 1901.34 | 30
1/16/20XX 7:00:00 AM | 0.29167 | 2 | 29.7 | 68 | 29.7 |  | 29.7 | 67.77 | 12.23 | 462294 | 462.294 | 63.54 | 16.46 | 622188 | 622.188 | 59.31 | 20.69 | 782082 | 782.082 | 55.08 | 24.92 | 941976 | 941.976 | 50.85 | 29.15 | 1101870 | 1101.87 | 46.62 | 33.38 | 1261764 | 1261.764 | 42.39 | 37.61 | 1421658 | 1421.658 | 38.16 | 41.84 | 1581552 | 1581.552 | 33.93 | 46.07 | 1741446 | 1741.446 | 29.7 | 50.3 | 1901340 | 1901.34 | 30
1/16/20XX 8:00:00 AM | 0.33333 | 2 | 30.2 | 68.3 | 30.2 |  | 30.2 | 67.82 | 12.18 | 460404 | 460.404 | 63.64 | 16.36 | 618408 | 618.408 | 59.46 | 20.54 | 776412 | 776.412 | 55.28 | 24.72 | 934416 | 934.416 | 51.1 | 28.9 | 1092420 | 1092.42 | 46.92 | 33.08 | 1250424 | 1250.424 | 42.74 | 37.26 | 1408428 | 1408.428 | 38.56 | 41.44 | 1566432 | 1566.432 | 34.38 | 45.62 | 1724436 | 1724.436 | 30.2 | 49.8 | 1882440 | 1882.44 | 30
1/16/20XX 9:00:00 AM | 0.375 | 2 | 30.8 | 68 | 30.8 |  | 30.8 | 67.88 | 12.12 | 458136 | 458.136 | 63.76 | 16.24 | 613872 | 613.872 | 59.64 | 20.36 | 769608 | 769.608 | 55.52 | 24.48 | 925344 | 925.344 | 51.4 | 28.6 | 1081080 | 1081.08 | 47.28 | 32.72 | 1236816 | 1236.816 | 43.16 | 36.84 | 1392552 | 1392.552 | 39.04 | 40.96 | 1548288 | 1548.288 | 34.92 | 45.08 | 1704024 | 1704.024 | 30.8 | 49.2 | 1859760 | 1859.76 | 30
1/16/20XX 10:00:00 AM | 0.41667 | 2 | 32.1 | 63.9 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
1/16/20XX 11:00:00 AM | 0.45833 | 2 | 33.7 | 61.8 | 33.7 |  | 33.7 | 68.17 | 11.83 | 447174 | 447.174 | 64.34 | 15.66 | 591948 | 591.948 | 60.51 | 19.49 | 736722 | 736.722 | 56.68 | 23.32 | 881496 | 881.496 | 52.85 | 27.15 | 1026270 | 1026.27 | 49.02 | 30.98 | 1171044 | 1171.044 | 45.19 | 34.81 | 1315818 | 1315.818 | 41.36 | 38.64 | 1460592 | 1460.592 | 37.53 | 42.47 | 1605366 | 1605.366 | 33.7 | 46.3 | 1750140 | 1750.14 | 35
1/16/20XX 12:00:00 PM | 0.5 | 2 | 34.8 | 59.4 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
1/16/20XX 1:00:00 PM | 0.54167 | 2 | 36.4 | 55.8 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
1/16/20XX 2:00:00 PM | 0.58333 | 2 | 37.1 | 52.5 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
1/16/20XX 3:00:00 PM | 0.625 | 2 | 37.1 | 52.8 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
1/16/20XX 4:00:00 PM | 0.66667 | 2 | 36.8 | 53.1 | 36.8 |  | 36.8 | 68.48 | 11.52 | 435456 | 435.456 | 64.96 | 15.04 | 568512 | 568.512 | 61.44 | 18.56 | 701568 | 701.568 | 57.92 | 22.08 | 834624 | 834.624 | 54.4 | 25.6 | 967680 | 967.68 | 50.88 | 29.12 | 1100736 | 1100.736 | 47.36 | 32.64 | 1233792 | 1233.792 | 43.84 | 36.16 | 1366848 | 1366.848 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.8 | 43.2 | 1632960 | 1632.96 | 35
1/16/20XX 5:00:00 PM | 0.70833 | 2 | 35.9 | 54.3 | 35.9 |  | 35.9 | 68.39 | 11.61 | 438858 | 438.858 | 64.78 | 15.22 | 575316 | 575.316 | 61.17 | 18.83 | 711774 | 711.774 | 57.56 | 22.44 | 848232 | 848.232 | 53.95 | 26.05 | 984690 | 984.69 | 50.34 | 29.66 | 1121148 | 1121.148 | 46.73 | 33.27 | 1257606 | 1257.606 | 43.12 | 36.88 | 1394064 | 1394.064 | 39.51 | 40.49 | 1530522 | 1530.522 | 35.9 | 44.1 | 1666980 | 1666.98 | 35
1/16/20XX 6:00:00 PM | 0.75 | 2 | 34.7 | 56.4 | 34.7 |  | 34.7 | 68.27 | 11.73 | 443394 | 443.394 | 64.54 | 15.46 | 584388 | 584.388 | 60.81 | 19.19 | 725382 | 725.382 | 57.08 | 22.92 | 866376 | 866.376 | 53.35 | 26.65 | 1007370 | 1007.37 | 49.62 | 30.38 | 1148364 | 1148.364 | 45.89 | 34.11 | 1289358 | 1289.358 | 42.16 | 37.84 | 1430352 | 1430.352 | 38.43 | 41.57 | 1571346 | 1571.346 | 34.7 | 45.3 | 1712340 | 1712.34 | 35
1/16/20XX 7:00:00 PM | 0.79167 | 2 | 34.7 | 55.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/16/20XX 8:00:00 PM | 0.83333 | 2 | 34.2 | 57 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/16/20XX 9:00:00 PM | 0.875 | 2 | 33.7 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/16/20XX 10:00:00 PM | 0.91667 | 2 | 33.3 | 58.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/16/20XX 11:00:00 PM | 0.95833 | 2 | 33 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/16/20XX 12:00:00 AM | 0 | 3 | 32.4 | 63.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/17/20XX 1:00:00 AM | 0.041667 | 3 | 32.6 | 62.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/17/20XX 2:00:00 AM | 0.083333 | 3 | 32.1 | 64.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/17/20XX 3:00:00 AM | 0.125 | 3 | 31.8 | 64.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/17/20XX 4:00:00 AM | 0.16667 | 3 | 30.9 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/17/20XX 5:00:00 AM | 0.20833 | 3 | 30.6 | 63.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/17/20XX 6:00:00 AM | 0.25 | 3 | 30.4 | 62.5 | 30.4 |  | 30.4 | 67.84 | 12.16 | 459648 | 459.648 | 63.68 | 16.32 | 616896 | 616.896 | 59.52 | 20.48 | 774144 | 774.144 | 55.36 | 24.64 | 931392 | 931.392 | 51.2 | 28.8 | 1088640 | 1088.64 | 47.04 | 32.96 | 1245888 | 1245.888 | 42.88 | 37.12 | 1403136 | 1403.136 | 38.72 | 41.28 | 1560384 | 1560.384 | 34.56 | 45.44 | 1717632 | 1717.632 | 30.4 | 49.6 | 1874880 | 1874.88 | 30
1/17/20XX 7:00:00 AM | 0.29167 | 3 | 29.8 | 64.3 | 29.8 |  | 29.8 | 67.78 | 12.22 | 461916 | 461.916 | 63.56 | 16.44 | 621432 | 621.432 | 59.34 | 20.66 | 780948 | 780.948 | 55.12 | 24.88 | 940464 | 940.464 | 50.9 | 29.1 | 1099980 | 1099.98 | 46.68 | 33.32 | 1259496 | 1259.496 | 42.46 | 37.54 | 1419012 | 1419.012 | 38.24 | 41.76 | 1578528 | 1578.528 | 34.02 | 45.98 | 1738044 | 1738.044 | 29.8 | 50.2 | 1897560 | 1897.56 | 30
1/17/20XX 8:00:00 AM | 0.33333 | 3 | 29.7 | 62.9 | 29.7 |  | 29.7 | 67.77 | 12.23 | 462294 | 462.294 | 63.54 | 16.46 | 622188 | 622.188 | 59.31 | 20.69 | 782082 | 782.082 | 55.08 | 24.92 | 941976 | 941.976 | 50.85 | 29.15 | 1101870 | 1101.87 | 46.62 | 33.38 | 1261764 | 1261.764 | 42.39 | 37.61 | 1421658 | 1421.658 | 38.16 | 41.84 | 1581552 | 1581.552 | 33.93 | 46.07 | 1741446 | 1741.446 | 29.7 | 50.3 | 1901340 | 1901.34 | 30
1/17/20XX 9:00:00 AM | 0.375 | 3 | 30.4 | 62.8 | 30.4 |  | 30.4 | 67.84 | 12.16 | 459648 | 459.648 | 63.68 | 16.32 | 616896 | 616.896 | 59.52 | 20.48 | 774144 | 774.144 | 55.36 | 24.64 | 931392 | 931.392 | 51.2 | 28.8 | 1088640 | 1088.64 | 47.04 | 32.96 | 1245888 | 1245.888 | 42.88 | 37.12 | 1403136 | 1403.136 | 38.72 | 41.28 | 1560384 | 1560.384 | 34.56 | 45.44 | 1717632 | 1717.632 | 30.4 | 49.6 | 1874880 | 1874.88 | 30
1/17/20XX 10:00:00 AM | 0.41667 | 3 | 31.3 | 62.2 | 31.3 |  | 31.3 | 67.93 | 12.07 | 456246 | 456.246 | 63.86 | 16.14 | 610092 | 610.092 | 59.79 | 20.21 | 763938 | 763.938 | 55.72 | 24.28 | 917784 | 917.784 | 51.65 | 28.35 | 1071630 | 1071.63 | 47.58 | 32.42 | 1225476 | 1225.476 | 43.51 | 36.49 | 1379322 | 1379.322 | 39.44 | 40.56 | 1533168 | 1533.168 | 35.37 | 44.63 | 1687014 | 1687.014 | 31.3 | 48.7 | 1840860 | 1840.86 | 30
1/17/20XX 11:00:00 AM | 0.45833 | 3 | 32.2 | 63.7 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
1/17/20XX 12:00:00 PM | 0.5 | 3 | 33.2 | 63.3 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
1/17/20XX 1:00:00 PM | 0.54167 | 3 | 34.5 | 62.8 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
1/17/20XX 2:00:00 PM | 0.58333 | 3 | 34.4 | 62.7 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
1/17/20XX 3:00:00 PM | 0.625 | 3 | 34.5 | 62.8 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
1/17/20XX 4:00:00 PM | 0.66667 | 3 | 34.2 | 63.6 | 34.2 |  | 34.2 | 68.22 | 11.78 | 445284 | 445.284 | 64.44 | 15.56 | 588168 | 588.168 | 60.66 | 19.34 | 731052 | 731.052 | 56.88 | 23.12 | 873936 | 873.936 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.32 | 30.68 | 1159704 | 1159.704 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.98 | 42.02 | 1588356 | 1588.356 | 34.2 | 45.8 | 1731240 | 1731.24 | 35
1/17/20XX 5:00:00 PM | 0.70833 | 3 | 33.8 | 66 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
1/17/20XX 6:00:00 PM | 0.75 | 3 | 33.6 | 68.1 | 33.6 |  | 33.6 | 68.16 | 11.84 | 447552 | 447.552 | 64.32 | 15.68 | 592704 | 592.704 | 60.48 | 19.52 | 737856 | 737.856 | 56.64 | 23.36 | 883008 | 883.008 | 52.8 | 27.2 | 1028160 | 1028.16 | 48.96 | 31.04 | 1173312 | 1173.312 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.28 | 38.72 | 1463616 | 1463.616 | 37.44 | 42.56 | 1608768 | 1608.768 | 33.6 | 46.4 | 1753920 | 1753.92 | 35
1/17/20XX 7:00:00 PM | 0.79167 | 3 | 33.6 | 66.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/17/20XX 8:00:00 PM | 0.83333 | 3 | 33.7 | 66.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/17/20XX 9:00:00 PM | 0.875 | 3 | 33.6 | 67.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/17/20XX 10:00:00 PM | 0.91667 | 3 | 33.8 | 65.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/17/20XX 11:00:00 PM | 0.95833 | 3 | 33.6 | 67.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/17/20XX 12:00:00 AM | 0 | 4 | 33.8 | 68.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/18/20XX 1:00:00 AM | 0.041667 | 4 | 33.6 | 72 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/18/20XX 2:00:00 AM | 0.083333 | 4 | 33.7 | 72.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/18/20XX 3:00:00 AM | 0.125 | 4 | 33 | 71.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/18/20XX 4:00:00 AM | 0.16667 | 4 | 32.7 | 71.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/18/20XX 5:00:00 AM | 0.20833 | 4 | 32.8 | 69.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/18/20XX 6:00:00 AM | 0.25 | 4 | 32.3 | 70.7 | 32.3 |  | 32.3 | 68.03 | 11.97 | 452466 | 452.466 | 64.06 | 15.94 | 602532 | 602.532 | 60.09 | 19.91 | 752598 | 752.598 | 56.12 | 23.88 | 902664 | 902.664 | 52.15 | 27.85 | 1052730 | 1052.73 | 48.18 | 31.82 | 1202796 | 1202.796 | 44.21 | 35.79 | 1352862 | 1352.862 | 40.24 | 39.76 | 1502928 | 1502.928 | 36.27 | 43.73 | 1652994 | 1652.994 | 32.3 | 47.7 | 1803060 | 1803.06 | 30
1/18/20XX 7:00:00 AM | 0.29167 | 4 | 31.2 | 73.6 | 31.2 |  | 31.2 | 67.92 | 12.08 | 456624 | 456.624 | 63.84 | 16.16 | 610848 | 610.848 | 59.76 | 20.24 | 765072 | 765.072 | 55.68 | 24.32 | 919296 | 919.296 | 51.6 | 28.4 | 1073520 | 1073.52 | 47.52 | 32.48 | 1227744 | 1227.744 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.36 | 40.64 | 1536192 | 1536.192 | 35.28 | 44.72 | 1690416 | 1690.416 | 31.2 | 48.8 | 1844640 | 1844.64 | 30
1/18/20XX 8:00:00 AM | 0.33333 | 4 | 31.3 | 73.4 | 31.3 |  | 31.3 | 67.93 | 12.07 | 456246 | 456.246 | 63.86 | 16.14 | 610092 | 610.092 | 59.79 | 20.21 | 763938 | 763.938 | 55.72 | 24.28 | 917784 | 917.784 | 51.65 | 28.35 | 1071630 | 1071.63 | 47.58 | 32.42 | 1225476 | 1225.476 | 43.51 | 36.49 | 1379322 | 1379.322 | 39.44 | 40.56 | 1533168 | 1533.168 | 35.37 | 44.63 | 1687014 | 1687.014 | 31.3 | 48.7 | 1840860 | 1840.86 | 30
1/18/20XX 9:00:00 AM | 0.375 | 4 | 31.4 | 73.1 | 31.4 |  | 31.4 | 67.94 | 12.06 | 455868 | 455.868 | 63.88 | 16.12 | 609336 | 609.336 | 59.82 | 20.18 | 762804 | 762.804 | 55.76 | 24.24 | 916272 | 916.272 | 51.7 | 28.3 | 1069740 | 1069.74 | 47.64 | 32.36 | 1223208 | 1223.208 | 43.58 | 36.42 | 1376676 | 1376.676 | 39.52 | 40.48 | 1530144 | 1530.144 | 35.46 | 44.54 | 1683612 | 1683.612 | 31.4 | 48.6 | 1837080 | 1837.08 | 30
1/18/20XX 10:00:00 AM | 0.41667 | 4 | 32.3 | 70.8 | 32.3 |  | 32.3 | 68.03 | 11.97 | 452466 | 452.466 | 64.06 | 15.94 | 602532 | 602.532 | 60.09 | 19.91 | 752598 | 752.598 | 56.12 | 23.88 | 902664 | 902.664 | 52.15 | 27.85 | 1052730 | 1052.73 | 48.18 | 31.82 | 1202796 | 1202.796 | 44.21 | 35.79 | 1352862 | 1352.862 | 40.24 | 39.76 | 1502928 | 1502.928 | 36.27 | 43.73 | 1652994 | 1652.994 | 32.3 | 47.7 | 1803060 | 1803.06 | 30
1/18/20XX 11:00:00 AM | 0.45833 | 4 | 33.2 | 67.9 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
1/18/20XX 12:00:00 PM | 0.5 | 4 | 34.1 | 66.6 | 34.1 |  | 34.1 | 68.21 | 11.79 | 445662 | 445.662 | 64.42 | 15.58 | 588924 | 588.924 | 60.63 | 19.37 | 732186 | 732.186 | 56.84 | 23.16 | 875448 | 875.448 | 53.05 | 26.95 | 1018710 | 1018.71 | 49.26 | 30.74 | 1161972 | 1161.972 | 45.47 | 34.53 | 1305234 | 1305.234 | 41.68 | 38.32 | 1448496 | 1448.496 | 37.89 | 42.11 | 1591758 | 1591.758 | 34.1 | 45.9 | 1735020 | 1735.02 | 35
1/18/20XX 1:00:00 PM | 0.54167 | 4 | 35.3 | 62.1 | 35.3 |  | 35.3 | 68.33 | 11.67 | 441126 | 441.126 | 64.66 | 15.34 | 579852 | 579.852 | 60.99 | 19.01 | 718578 | 718.578 | 57.32 | 22.68 | 857304 | 857.304 | 53.65 | 26.35 | 996030 | 996.03 | 49.98 | 30.02 | 1134756 | 1134.756 | 46.31 | 33.69 | 1273482 | 1273.482 | 42.64 | 37.36 | 1412208 | 1412.208 | 38.97 | 41.03 | 1550934 | 1550.934 | 35.3 | 44.7 | 1689660 | 1689.66 | 35
1/18/20XX 2:00:00 PM | 0.58333 | 4 | 35.7 | 60.9 | 35.7 |  | 35.7 | 68.37 | 11.63 | 439614 | 439.614 | 64.74 | 15.26 | 576828 | 576.828 | 61.11 | 18.89 | 714042 | 714.042 | 57.48 | 22.52 | 851256 | 851.256 | 53.85 | 26.15 | 988470 | 988.47 | 50.22 | 29.78 | 1125684 | 1125.684 | 46.59 | 33.41 | 1262898 | 1262.898 | 42.96 | 37.04 | 1400112 | 1400.112 | 39.33 | 40.67 | 1537326 | 1537.326 | 35.7 | 44.3 | 1674540 | 1674.54 | 35
1/18/20XX 3:00:00 PM | 0.625 | 4 | 36 | 58.7 | 36 |  | 36 | 68.4 | 11.6 | 438480 | 438.48 | 64.8 | 15.2 | 574560 | 574.56 | 61.2 | 18.8 | 710640 | 710.64 | 57.6 | 22.4 | 846720 | 846.72 | 54 | 26 | 982800 | 982.8 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.2 | 36.8 | 1391040 | 1391.04 | 39.6 | 40.4 | 1527120 | 1527.12 | 36 | 44 | 1663200 | 1663.2 | 35
1/18/20XX 4:00:00 PM | 0.66667 | 4 | 35.7 | 58.6 | 35.7 |  | 35.7 | 68.37 | 11.63 | 439614 | 439.614 | 64.74 | 15.26 | 576828 | 576.828 | 61.11 | 18.89 | 714042 | 714.042 | 57.48 | 22.52 | 851256 | 851.256 | 53.85 | 26.15 | 988470 | 988.47 | 50.22 | 29.78 | 1125684 | 1125.684 | 46.59 | 33.41 | 1262898 | 1262.898 | 42.96 | 37.04 | 1400112 | 1400.112 | 39.33 | 40.67 | 1537326 | 1537.326 | 35.7 | 44.3 | 1674540 | 1674.54 | 35
1/18/20XX 5:00:00 PM | 0.70833 | 4 | 34.8 | 62.7 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
1/18/20XX 6:00:00 PM | 0.75 | 4 | 34.7 | 63.3 | 34.7 |  | 34.7 | 68.27 | 11.73 | 443394 | 443.394 | 64.54 | 15.46 | 584388 | 584.388 | 60.81 | 19.19 | 725382 | 725.382 | 57.08 | 22.92 | 866376 | 866.376 | 53.35 | 26.65 | 1007370 | 1007.37 | 49.62 | 30.38 | 1148364 | 1148.364 | 45.89 | 34.11 | 1289358 | 1289.358 | 42.16 | 37.84 | 1430352 | 1430.352 | 38.43 | 41.57 | 1571346 | 1571.346 | 34.7 | 45.3 | 1712340 | 1712.34 | 35
1/18/20XX 7:00:00 PM | 0.79167 | 4 | 33.6 | 64.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/18/20XX 8:00:00 PM | 0.83333 | 4 | 33 | 66.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/18/20XX 9:00:00 PM | 0.875 | 4 | 32.8 | 66.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/18/20XX 10:00:00 PM | 0.91667 | 4 | 32.5 | 66.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/18/20XX 11:00:00 PM | 0.95833 | 4 | 31.8 | 69.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/18/20XX 12:00:00 AM | 0 | 5 | 31.5 | 67.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/19/20XX 1:00:00 AM | 0.041667 | 5 | 30.9 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/19/20XX 2:00:00 AM | 0.083333 | 5 | 30.7 | 68.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/19/20XX 3:00:00 AM | 0.125 | 5 | 30.3 | 68.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/19/20XX 4:00:00 AM | 0.16667 | 5 | 30.4 | 68.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/19/20XX 5:00:00 AM | 0.20833 | 5 | 30.5 | 69.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/19/20XX 6:00:00 AM | 0.25 | 5 | 30.5 | 70.1 | 30.5 |  | 30.5 | 67.85 | 12.15 | 459270 | 459.27 | 63.7 | 16.3 | 616140 | 616.14 | 59.55 | 20.45 | 773010 | 773.01 | 55.4 | 24.6 | 929880 | 929.88 | 51.25 | 28.75 | 1086750 | 1086.75 | 47.1 | 32.9 | 1243620 | 1243.62 | 42.95 | 37.05 | 1400490 | 1400.49 | 38.8 | 41.2 | 1557360 | 1557.36 | 34.65 | 45.35 | 1714230 | 1714.23 | 30.5 | 49.5 | 1871100 | 1871.1 | 30
1/19/20XX 7:00:00 AM | 0.29167 | 5 | 30.3 | 70.7 | 30.3 |  | 30.3 | 67.83 | 12.17 | 460026 | 460.026 | 63.66 | 16.34 | 617652 | 617.652 | 59.49 | 20.51 | 775278 | 775.278 | 55.32 | 24.68 | 932904 | 932.904 | 51.15 | 28.85 | 1090530 | 1090.53 | 46.98 | 33.02 | 1248156 | 1248.156 | 42.81 | 37.19 | 1405782 | 1405.782 | 38.64 | 41.36 | 1563408 | 1563.408 | 34.47 | 45.53 | 1721034 | 1721.034 | 30.3 | 49.7 | 1878660 | 1878.66 | 30
1/19/20XX 8:00:00 AM | 0.33333 | 5 | 30.9 | 68.4 | 30.9 |  | 30.9 | 67.89 | 12.11 | 457758 | 457.758 | 63.78 | 16.22 | 613116 | 613.116 | 59.67 | 20.33 | 768474 | 768.474 | 55.56 | 24.44 | 923832 | 923.832 | 51.45 | 28.55 | 1079190 | 1079.19 | 47.34 | 32.66 | 1234548 | 1234.548 | 43.23 | 36.77 | 1389906 | 1389.906 | 39.12 | 40.88 | 1545264 | 1545.264 | 35.01 | 44.99 | 1700622 | 1700.622 | 30.9 | 49.1 | 1855980 | 1855.98 | 30
1/19/20XX 9:00:00 AM | 0.375 | 5 | 31.7 | 68 | 31.7 |  | 31.7 | 67.97 | 12.03 | 454734 | 454.734 | 63.94 | 16.06 | 607068 | 607.068 | 59.91 | 20.09 | 759402 | 759.402 | 55.88 | 24.12 | 911736 | 911.736 | 51.85 | 28.15 | 1064070 | 1064.07 | 47.82 | 32.18 | 1216404 | 1216.404 | 43.79 | 36.21 | 1368738 | 1368.738 | 39.76 | 40.24 | 1521072 | 1521.072 | 35.73 | 44.27 | 1673406 | 1673.406 | 31.7 | 48.3 | 1825740 | 1825.74 | 30
1/19/20XX 10:00:00 AM | 0.41667 | 5 | 33.3 | 63.3 | 33.3 |  | 33.3 | 68.13 | 11.87 | 448686 | 448.686 | 64.26 | 15.74 | 594972 | 594.972 | 60.39 | 19.61 | 741258 | 741.258 | 56.52 | 23.48 | 887544 | 887.544 | 52.65 | 27.35 | 1033830 | 1033.83 | 48.78 | 31.22 | 1180116 | 1180.116 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.17 | 42.83 | 1618974 | 1618.974 | 33.3 | 46.7 | 1765260 | 1765.26 | 35
1/19/20XX 11:00:00 AM | 0.45833 | 5 | 35.1 | 59 | 35.1 |  | 35.1 | 68.31 | 11.69 | 441882 | 441.882 | 64.62 | 15.38 | 581364 | 581.364 | 60.93 | 19.07 | 720846 | 720.846 | 57.24 | 22.76 | 860328 | 860.328 | 53.55 | 26.45 | 999810 | 999.81 | 49.86 | 30.14 | 1139292 | 1139.292 | 46.17 | 33.83 | 1278774 | 1278.774 | 42.48 | 37.52 | 1418256 | 1418.256 | 38.79 | 41.21 | 1557738 | 1557.738 | 35.1 | 44.9 | 1697220 | 1697.22 | 35
1/19/20XX 12:00:00 PM | 0.5 | 5 | 36.2 | 55.7 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
1/19/20XX 1:00:00 PM | 0.54167 | 5 | 37.6 | 54.3 | 37.6 |  | 37.6 | 68.56 | 11.44 | 432432 | 432.432 | 65.12 | 14.88 | 562464 | 562.464 | 61.68 | 18.32 | 692496 | 692.496 | 58.24 | 21.76 | 822528 | 822.528 | 54.8 | 25.2 | 952560 | 952.56 | 51.36 | 28.64 | 1082592 | 1082.592 | 47.92 | 32.08 | 1212624 | 1212.624 | 44.48 | 35.52 | 1342656 | 1342.656 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.6 | 42.4 | 1602720 | 1602.72 | 40
1/19/20XX 2:00:00 PM | 0.58333 | 5 | 37.4 | 57 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
1/19/20XX 3:00:00 PM | 0.625 | 5 | 38.5 | 56.5 | 38.5 |  | 38.5 | 68.65 | 11.35 | 429030 | 429.03 | 65.3 | 14.7 | 555660 | 555.66 | 61.95 | 18.05 | 682290 | 682.29 | 58.6 | 21.4 | 808920 | 808.92 | 55.25 | 24.75 | 935550 | 935.55 | 51.9 | 28.1 | 1062180 | 1062.18 | 48.55 | 31.45 | 1188810 | 1188.81 | 45.2 | 34.8 | 1315440 | 1315.44 | 41.85 | 38.15 | 1442070 | 1442.07 | 38.5 | 41.5 | 1568700 | 1568.7 | 40
1/19/20XX 4:00:00 PM | 0.66667 | 5 | 38.6 | 56.1 | 38.6 |  | 38.6 | 68.66 | 11.34 | 428652 | 428.652 | 65.32 | 14.68 | 554904 | 554.904 | 61.98 | 18.02 | 681156 | 681.156 | 58.64 | 21.36 | 807408 | 807.408 | 55.3 | 24.7 | 933660 | 933.66 | 51.96 | 28.04 | 1059912 | 1059.912 | 48.62 | 31.38 | 1186164 | 1186.164 | 45.28 | 34.72 | 1312416 | 1312.416 | 41.94 | 38.06 | 1438668 | 1438.668 | 38.6 | 41.4 | 1564920 | 1564.92 | 40
1/19/20XX 5:00:00 PM | 0.70833 | 5 | 38.4 | 56.6 | 38.4 |  | 38.4 | 68.64 | 11.36 | 429408 | 429.408 | 65.28 | 14.72 | 556416 | 556.416 | 61.92 | 18.08 | 683424 | 683.424 | 58.56 | 21.44 | 810432 | 810.432 | 55.2 | 24.8 | 937440 | 937.44 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.76 | 38.24 | 1445472 | 1445.472 | 38.4 | 41.6 | 1572480 | 1572.48 | 40
1/19/20XX 6:00:00 PM | 0.75 | 5 | 38.4 | 56.7 | 38.4 |  | 38.4 | 68.64 | 11.36 | 429408 | 429.408 | 65.28 | 14.72 | 556416 | 556.416 | 61.92 | 18.08 | 683424 | 683.424 | 58.56 | 21.44 | 810432 | 810.432 | 55.2 | 24.8 | 937440 | 937.44 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.76 | 38.24 | 1445472 | 1445.472 | 38.4 | 41.6 | 1572480 | 1572.48 | 40
1/19/20XX 7:00:00 PM | 0.79167 | 5 | 38.2 | 56.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/19/20XX 8:00:00 PM | 0.83333 | 5 | 37.8 | 59.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/19/20XX 9:00:00 PM | 0.875 | 5 | 37.3 | 58.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/19/20XX 10:00:00 PM | 0.91667 | 5 | 37.1 | 57.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/19/20XX 11:00:00 PM | 0.95833 | 5 | 37.3 | 58.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/19/20XX 12:00:00 AM | 0 | 6 | 36.7 | 58.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/20/20XX 1:00:00 AM | 0.041667 | 6 | 36.1 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/20/20XX 2:00:00 AM | 0.083333 | 6 | 35.6 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/20/20XX 3:00:00 AM | 0.125 | 6 | 35.1 | 59.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/20/20XX 4:00:00 AM | 0.16667 | 6 | 34.4 | 60.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/20/20XX 5:00:00 AM | 0.20833 | 6 | 34.2 | 60.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/20/20XX 6:00:00 AM | 0.25 | 6 | 34 | 59.6 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
1/20/20XX 7:00:00 AM | 0.29167 | 6 | 33.4 | 61 | 33.4 |  | 33.4 | 68.14 | 11.86 | 448308 | 448.308 | 64.28 | 15.72 | 594216 | 594.216 | 60.42 | 19.58 | 740124 | 740.124 | 56.56 | 23.44 | 886032 | 886.032 | 52.7 | 27.3 | 1031940 | 1031.94 | 48.84 | 31.16 | 1177848 | 1177.848 | 44.98 | 35.02 | 1323756 | 1323.756 | 41.12 | 38.88 | 1469664 | 1469.664 | 37.26 | 42.74 | 1615572 | 1615.572 | 33.4 | 46.6 | 1761480 | 1761.48 | 35
1/20/20XX 8:00:00 AM | 0.33333 | 6 | 33.5 | 59.1 | 33.5 |  | 33.5 | 68.15 | 11.85 | 447930 | 447.93 | 64.3 | 15.7 | 593460 | 593.46 | 60.45 | 19.55 | 738990 | 738.99 | 56.6 | 23.4 | 884520 | 884.52 | 52.75 | 27.25 | 1030050 | 1030.05 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.05 | 34.95 | 1321110 | 1321.11 | 41.2 | 38.8 | 1466640 | 1466.64 | 37.35 | 42.65 | 1612170 | 1612.17 | 33.5 | 46.5 | 1757700 | 1757.7 | 35
1/20/20XX 9:00:00 AM | 0.375 | 6 | 34.2 | 55.6 | 34.2 |  | 34.2 | 68.22 | 11.78 | 445284 | 445.284 | 64.44 | 15.56 | 588168 | 588.168 | 60.66 | 19.34 | 731052 | 731.052 | 56.88 | 23.12 | 873936 | 873.936 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.32 | 30.68 | 1159704 | 1159.704 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.98 | 42.02 | 1588356 | 1588.356 | 34.2 | 45.8 | 1731240 | 1731.24 | 35
1/20/20XX 10:00:00 AM | 0.41667 | 6 | 35 | 53 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
1/20/20XX 11:00:00 AM | 0.45833 | 6 | 36.9 | 50.1 | 36.9 |  | 36.9 | 68.49 | 11.51 | 435078 | 435.078 | 64.98 | 15.02 | 567756 | 567.756 | 61.47 | 18.53 | 700434 | 700.434 | 57.96 | 22.04 | 833112 | 833.112 | 54.45 | 25.55 | 965790 | 965.79 | 50.94 | 29.06 | 1098468 | 1098.468 | 47.43 | 32.57 | 1231146 | 1231.146 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.41 | 39.59 | 1496502 | 1496.502 | 36.9 | 43.1 | 1629180 | 1629.18 | 35
1/20/20XX 12:00:00 PM | 0.5 | 6 | 38.3 | 46.7 | 38.3 |  | 38.3 | 68.63 | 11.37 | 429786 | 429.786 | 65.26 | 14.74 | 557172 | 557.172 | 61.89 | 18.11 | 684558 | 684.558 | 58.52 | 21.48 | 811944 | 811.944 | 55.15 | 24.85 | 939330 | 939.33 | 51.78 | 28.22 | 1066716 | 1066.716 | 48.41 | 31.59 | 1194102 | 1194.102 | 45.04 | 34.96 | 1321488 | 1321.488 | 41.67 | 38.33 | 1448874 | 1448.874 | 38.3 | 41.7 | 1576260 | 1576.26 | 40
1/20/20XX 1:00:00 PM | 0.54167 | 6 | 39.8 | 44 | 39.8 |  | 39.8 | 68.78 | 11.22 | 424116 | 424.116 | 65.56 | 14.44 | 545832 | 545.832 | 62.34 | 17.66 | 667548 | 667.548 | 59.12 | 20.88 | 789264 | 789.264 | 55.9 | 24.1 | 910980 | 910.98 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.46 | 30.54 | 1154412 | 1154.412 | 46.24 | 33.76 | 1276128 | 1276.128 | 43.02 | 36.98 | 1397844 | 1397.844 | 39.8 | 40.2 | 1519560 | 1519.56 | 40
1/20/20XX 2:00:00 PM | 0.58333 | 6 | 39.8 | 42.5 | 39.8 |  | 39.8 | 68.78 | 11.22 | 424116 | 424.116 | 65.56 | 14.44 | 545832 | 545.832 | 62.34 | 17.66 | 667548 | 667.548 | 59.12 | 20.88 | 789264 | 789.264 | 55.9 | 24.1 | 910980 | 910.98 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.46 | 30.54 | 1154412 | 1154.412 | 46.24 | 33.76 | 1276128 | 1276.128 | 43.02 | 36.98 | 1397844 | 1397.844 | 39.8 | 40.2 | 1519560 | 1519.56 | 40
1/20/20XX 3:00:00 PM | 0.625 | 6 | 39.6 | 42.6 | 39.6 |  | 39.6 | 68.76 | 11.24 | 424872 | 424.872 | 65.52 | 14.48 | 547344 | 547.344 | 62.28 | 17.72 | 669816 | 669.816 | 59.04 | 20.96 | 792288 | 792.288 | 55.8 | 24.2 | 914760 | 914.76 | 52.56 | 27.44 | 1037232 | 1037.232 | 49.32 | 30.68 | 1159704 | 1159.704 | 46.08 | 33.92 | 1282176 | 1282.176 | 42.84 | 37.16 | 1404648 | 1404.648 | 39.6 | 40.4 | 1527120 | 1527.12 | 40
1/20/20XX 4:00:00 PM | 0.66667 | 6 | 38.8 | 44.2 | 38.8 |  | 38.8 | 68.68 | 11.32 | 427896 | 427.896 | 65.36 | 14.64 | 553392 | 553.392 | 62.04 | 17.96 | 678888 | 678.888 | 58.72 | 21.28 | 804384 | 804.384 | 55.4 | 24.6 | 929880 | 929.88 | 52.08 | 27.92 | 1055376 | 1055.376 | 48.76 | 31.24 | 1180872 | 1180.872 | 45.44 | 34.56 | 1306368 | 1306.368 | 42.12 | 37.88 | 1431864 | 1431.864 | 38.8 | 41.2 | 1557360 | 1557.36 | 40
1/20/20XX 5:00:00 PM | 0.70833 | 6 | 38.1 | 47 | 38.1 |  | 38.1 | 68.61 | 11.39 | 430542 | 430.542 | 65.22 | 14.78 | 558684 | 558.684 | 61.83 | 18.17 | 686826 | 686.826 | 58.44 | 21.56 | 814968 | 814.968 | 55.05 | 24.95 | 943110 | 943.11 | 51.66 | 28.34 | 1071252 | 1071.252 | 48.27 | 31.73 | 1199394 | 1199.394 | 44.88 | 35.12 | 1327536 | 1327.536 | 41.49 | 38.51 | 1455678 | 1455.678 | 38.1 | 41.9 | 1583820 | 1583.82 | 40
1/20/20XX 6:00:00 PM | 0.75 | 6 | 37 | 49.3 | 37 |  | 37 | 68.5 | 11.5 | 434700 | 434.7 | 65 | 15 | 567000 | 567 | 61.5 | 18.5 | 699300 | 699.3 | 58 | 22 | 831600 | 831.6 | 54.5 | 25.5 | 963900 | 963.9 | 51 | 29 | 1096200 | 1096.2 | 47.5 | 32.5 | 1228500 | 1228.5 | 44 | 36 | 1360800 | 1360.8 | 40.5 | 39.5 | 1493100 | 1493.1 | 37 | 43 | 1625400 | 1625.4 | 35
1/20/20XX 7:00:00 PM | 0.79167 | 6 | 36.3 | 52.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/20/20XX 8:00:00 PM | 0.83333 | 6 | 35.4 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/20/20XX 9:00:00 PM | 0.875 | 6 | 34.7 | 55.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/20/20XX 10:00:00 PM | 0.91667 | 6 | 33.8 | 55.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/20/20XX 11:00:00 PM | 0.95833 | 6 | 33 | 55.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/20/20XX 12:00:00 AM | 0 | 7 | 32.4 | 55.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/21/20XX 1:00:00 AM | 0.041667 | 7 | 32.2 | 55.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/21/20XX 2:00:00 AM | 0.083333 | 7 | 32 | 54.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/21/20XX 3:00:00 AM | 0.125 | 7 | 30.4 | 60.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/21/20XX 4:00:00 AM | 0.16667 | 7 | 29.8 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/21/20XX 5:00:00 AM | 0.20833 | 7 | 29.5 | 65.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/21/20XX 6:00:00 AM | 0.25 | 7 | 29.2 | 65.9 | 29.2 |  | 29.2 | 67.72 | 12.28 | 464184 | 464.184 | 63.44 | 16.56 | 625968 | 625.968 | 59.16 | 20.84 | 787752 | 787.752 | 54.88 | 25.12 | 949536 | 949.536 | 50.6 | 29.4 | 1111320 | 1111.32 | 46.32 | 33.68 | 1273104 | 1273.104 | 42.04 | 37.96 | 1434888 | 1434.888 | 37.76 | 42.24 | 1596672 | 1596.672 | 33.48 | 46.52 | 1758456 | 1758.456 | 29.2 | 50.8 | 1920240 | 1920.24 | 30
1/21/20XX 7:00:00 AM | 0.29167 | 7 | 28.9 | 66.3 | 28.9 |  | 28.9 | 67.69 | 12.31 | 465318 | 465.318 | 63.38 | 16.62 | 628236 | 628.236 | 59.07 | 20.93 | 791154 | 791.154 | 54.76 | 25.24 | 954072 | 954.072 | 50.45 | 29.55 | 1116990 | 1116.99 | 46.14 | 33.86 | 1279908 | 1279.908 | 41.83 | 38.17 | 1442826 | 1442.826 | 37.52 | 42.48 | 1605744 | 1605.744 | 33.21 | 46.79 | 1768662 | 1768.662 | 28.9 | 51.1 | 1931580 | 1931.58 | 30
1/21/20XX 8:00:00 AM | 0.33333 | 7 | 29 | 65.6 | 29 |  | 29 | 67.7 | 12.3 | 464940 | 464.94 | 63.4 | 16.6 | 627480 | 627.48 | 59.1 | 20.9 | 790020 | 790.02 | 54.8 | 25.2 | 952560 | 952.56 | 50.5 | 29.5 | 1115100 | 1115.1 | 46.2 | 33.8 | 1277640 | 1277.64 | 41.9 | 38.1 | 1440180 | 1440.18 | 37.6 | 42.4 | 1602720 | 1602.72 | 33.3 | 46.7 | 1765260 | 1765.26 | 29 | 51 | 1927800 | 1927.8 | 30
1/21/20XX 9:00:00 AM | 0.375 | 7 | 29.8 | 62.7 | 29.8 |  | 29.8 | 67.78 | 12.22 | 461916 | 461.916 | 63.56 | 16.44 | 621432 | 621.432 | 59.34 | 20.66 | 780948 | 780.948 | 55.12 | 24.88 | 940464 | 940.464 | 50.9 | 29.1 | 1099980 | 1099.98 | 46.68 | 33.32 | 1259496 | 1259.496 | 42.46 | 37.54 | 1419012 | 1419.012 | 38.24 | 41.76 | 1578528 | 1578.528 | 34.02 | 45.98 | 1738044 | 1738.044 | 29.8 | 50.2 | 1897560 | 1897.56 | 30
1/21/20XX 10:00:00 AM | 0.41667 | 7 | 30.2 | 61.5 | 30.2 |  | 30.2 | 67.82 | 12.18 | 460404 | 460.404 | 63.64 | 16.36 | 618408 | 618.408 | 59.46 | 20.54 | 776412 | 776.412 | 55.28 | 24.72 | 934416 | 934.416 | 51.1 | 28.9 | 1092420 | 1092.42 | 46.92 | 33.08 | 1250424 | 1250.424 | 42.74 | 37.26 | 1408428 | 1408.428 | 38.56 | 41.44 | 1566432 | 1566.432 | 34.38 | 45.62 | 1724436 | 1724.436 | 30.2 | 49.8 | 1882440 | 1882.44 | 30
1/21/20XX 11:00:00 AM | 0.45833 | 7 | 31.2 | 59.5 | 31.2 |  | 31.2 | 67.92 | 12.08 | 456624 | 456.624 | 63.84 | 16.16 | 610848 | 610.848 | 59.76 | 20.24 | 765072 | 765.072 | 55.68 | 24.32 | 919296 | 919.296 | 51.6 | 28.4 | 1073520 | 1073.52 | 47.52 | 32.48 | 1227744 | 1227.744 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.36 | 40.64 | 1536192 | 1536.192 | 35.28 | 44.72 | 1690416 | 1690.416 | 31.2 | 48.8 | 1844640 | 1844.64 | 30
1/21/20XX 12:00:00 PM | 0.5 | 7 | 32.1 | 57.8 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
1/21/20XX 1:00:00 PM | 0.54167 | 7 | 33.2 | 56.5 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
1/21/20XX 2:00:00 PM | 0.58333 | 7 | 33.7 | 55.1 | 33.7 |  | 33.7 | 68.17 | 11.83 | 447174 | 447.174 | 64.34 | 15.66 | 591948 | 591.948 | 60.51 | 19.49 | 736722 | 736.722 | 56.68 | 23.32 | 881496 | 881.496 | 52.85 | 27.15 | 1026270 | 1026.27 | 49.02 | 30.98 | 1171044 | 1171.044 | 45.19 | 34.81 | 1315818 | 1315.818 | 41.36 | 38.64 | 1460592 | 1460.592 | 37.53 | 42.47 | 1605366 | 1605.366 | 33.7 | 46.3 | 1750140 | 1750.14 | 35
1/21/20XX 3:00:00 PM | 0.625 | 7 | 33.7 | 53.6 | 33.7 |  | 33.7 | 68.17 | 11.83 | 447174 | 447.174 | 64.34 | 15.66 | 591948 | 591.948 | 60.51 | 19.49 | 736722 | 736.722 | 56.68 | 23.32 | 881496 | 881.496 | 52.85 | 27.15 | 1026270 | 1026.27 | 49.02 | 30.98 | 1171044 | 1171.044 | 45.19 | 34.81 | 1315818 | 1315.818 | 41.36 | 38.64 | 1460592 | 1460.592 | 37.53 | 42.47 | 1605366 | 1605.366 | 33.7 | 46.3 | 1750140 | 1750.14 | 35
1/21/20XX 4:00:00 PM | 0.66667 | 7 | 33.1 | 54.7 | 33.1 |  | 33.1 | 68.11 | 11.89 | 449442 | 449.442 | 64.22 | 15.78 | 596484 | 596.484 | 60.33 | 19.67 | 743526 | 743.526 | 56.44 | 23.56 | 890568 | 890.568 | 52.55 | 27.45 | 1037610 | 1037.61 | 48.66 | 31.34 | 1184652 | 1184.652 | 44.77 | 35.23 | 1331694 | 1331.694 | 40.88 | 39.12 | 1478736 | 1478.736 | 36.99 | 43.01 | 1625778 | 1625.778 | 33.1 | 46.9 | 1772820 | 1772.82 | 35
1/21/20XX 5:00:00 PM | 0.70833 | 7 | 32.4 | 55.1 | 32.4 |  | 32.4 | 68.04 | 11.96 | 452088 | 452.088 | 64.08 | 15.92 | 601776 | 601.776 | 60.12 | 19.88 | 751464 | 751.464 | 56.16 | 23.84 | 901152 | 901.152 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.24 | 31.76 | 1200528 | 1200.528 | 44.28 | 35.72 | 1350216 | 1350.216 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.36 | 43.64 | 1649592 | 1649.592 | 32.4 | 47.6 | 1799280 | 1799.28 | 30
1/21/20XX 6:00:00 PM | 0.75 | 7 | 32 | 55.4 | 32 |  | 32 | 68 | 12 | 453600 | 453.6 | 64 | 16 | 604800 | 604.8 | 60 | 20 | 756000 | 756 | 56 | 24 | 907200 | 907.2 | 52 | 28 | 1058400 | 1058.4 | 48 | 32 | 1209600 | 1209.6 | 44 | 36 | 1360800 | 1360.8 | 40 | 40 | 1512000 | 1512 | 36 | 44 | 1663200 | 1663.2 | 32 | 48 | 1814400 | 1814.4 | 30
1/21/20XX 7:00:00 PM | 0.79167 | 7 | 31.6 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/21/20XX 8:00:00 PM | 0.83333 | 7 | 31.1 | 58.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/21/20XX 9:00:00 PM | 0.875 | 7 | 30.5 | 61.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/21/20XX 10:00:00 PM | 0.91667 | 7 | 30.1 | 61.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/21/20XX 11:00:00 PM | 0.95833 | 7 | 29.5 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/21/20XX 12:00:00 AM | 0 | 1 | 29 | 62.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/22/20XX 1:00:00 AM | 0.041667 | 1 | 28.2 | 59.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/22/20XX 2:00:00 AM | 0.083333 | 1 | 27.9 | 60.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/22/20XX 3:00:00 AM | 0.125 | 1 | 27.1 | 61.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/22/20XX 4:00:00 AM | 0.16667 | 1 | 26.4 | 62.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/22/20XX 5:00:00 AM | 0.20833 | 1 | 26.1 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/22/20XX 6:00:00 AM | 0.25 | 1 | 25.7 | 64 | 25.7 |  | 25.7 | 67.37 | 12.63 | 477414 | 477.414 | 62.74 | 17.26 | 652428 | 652.428 | 58.11 | 21.89 | 827442 | 827.442 | 53.48 | 26.52 | 1002456 | 1002.456 | 48.85 | 31.15 | 1177470 | 1177.47 | 44.22 | 35.78 | 1352484 | 1352.484 | 39.59 | 40.41 | 1527498 | 1527.498 | 34.96 | 45.04 | 1702512 | 1702.512 | 30.33 | 49.67 | 1877526 | 1877.526 | 25.7 | 54.3 | 2052540 | 2052.54 | 25
1/22/20XX 7:00:00 AM | 0.29167 | 1 | 25.3 | 63.9 | 25.3 |  | 25.3 | 67.33 | 12.67 | 478926 | 478.926 | 62.66 | 17.34 | 655452 | 655.452 | 57.99 | 22.01 | 831978 | 831.978 | 53.32 | 26.68 | 1008504 | 1008.504 | 48.65 | 31.35 | 1185030 | 1185.03 | 43.98 | 36.02 | 1361556 | 1361.556 | 39.31 | 40.69 | 1538082 | 1538.082 | 34.64 | 45.36 | 1714608 | 1714.608 | 29.97 | 50.03 | 1891134 | 1891.134 | 25.3 | 54.7 | 2067660 | 2067.66 | 25
1/22/20XX 8:00:00 AM | 0.33333 | 1 | 25.3 | 64.1 | 25.3 |  | 25.3 | 67.33 | 12.67 | 478926 | 478.926 | 62.66 | 17.34 | 655452 | 655.452 | 57.99 | 22.01 | 831978 | 831.978 | 53.32 | 26.68 | 1008504 | 1008.504 | 48.65 | 31.35 | 1185030 | 1185.03 | 43.98 | 36.02 | 1361556 | 1361.556 | 39.31 | 40.69 | 1538082 | 1538.082 | 34.64 | 45.36 | 1714608 | 1714.608 | 29.97 | 50.03 | 1891134 | 1891.134 | 25.3 | 54.7 | 2067660 | 2067.66 | 25
1/22/20XX 9:00:00 AM | 0.375 | 1 | 25.9 | 64.5 | 25.9 |  | 25.9 | 67.39 | 12.61 | 476658 | 476.658 | 62.78 | 17.22 | 650916 | 650.916 | 58.17 | 21.83 | 825174 | 825.174 | 53.56 | 26.44 | 999432 | 999.432 | 48.95 | 31.05 | 1173690 | 1173.69 | 44.34 | 35.66 | 1347948 | 1347.948 | 39.73 | 40.27 | 1522206 | 1522.206 | 35.12 | 44.88 | 1696464 | 1696.464 | 30.51 | 49.49 | 1870722 | 1870.722 | 25.9 | 54.1 | 2044980 | 2044.98 | 25
1/22/20XX 10:00:00 AM | 0.41667 | 1 | 27.2 | 63.2 | 27.2 |  | 27.2 | 67.52 | 12.48 | 471744 | 471.744 | 63.04 | 16.96 | 641088 | 641.088 | 58.56 | 21.44 | 810432 | 810.432 | 54.08 | 25.92 | 979776 | 979.776 | 49.6 | 30.4 | 1149120 | 1149.12 | 45.12 | 34.88 | 1318464 | 1318.464 | 40.64 | 39.36 | 1487808 | 1487.808 | 36.16 | 43.84 | 1657152 | 1657.152 | 31.68 | 48.32 | 1826496 | 1826.496 | 27.2 | 52.8 | 1995840 | 1995.84 | 25
1/22/20XX 11:00:00 AM | 0.45833 | 1 | 29 | 58.5 | 29 |  | 29 | 67.7 | 12.3 | 464940 | 464.94 | 63.4 | 16.6 | 627480 | 627.48 | 59.1 | 20.9 | 790020 | 790.02 | 54.8 | 25.2 | 952560 | 952.56 | 50.5 | 29.5 | 1115100 | 1115.1 | 46.2 | 33.8 | 1277640 | 1277.64 | 41.9 | 38.1 | 1440180 | 1440.18 | 37.6 | 42.4 | 1602720 | 1602.72 | 33.3 | 46.7 | 1765260 | 1765.26 | 29 | 51 | 1927800 | 1927.8 | 30
1/22/20XX 12:00:00 PM | 0.5 | 1 | 30.6 | 55.4 | 30.6 |  | 30.6 | 67.86 | 12.14 | 458892 | 458.892 | 63.72 | 16.28 | 615384 | 615.384 | 59.58 | 20.42 | 771876 | 771.876 | 55.44 | 24.56 | 928368 | 928.368 | 51.3 | 28.7 | 1084860 | 1084.86 | 47.16 | 32.84 | 1241352 | 1241.352 | 43.02 | 36.98 | 1397844 | 1397.844 | 38.88 | 41.12 | 1554336 | 1554.336 | 34.74 | 45.26 | 1710828 | 1710.828 | 30.6 | 49.4 | 1867320 | 1867.32 | 30
1/22/20XX 1:00:00 PM | 0.54167 | 1 | 31.9 | 53.2 | 31.9 |  | 31.9 | 67.99 | 12.01 | 453978 | 453.978 | 63.98 | 16.02 | 605556 | 605.556 | 59.97 | 20.03 | 757134 | 757.134 | 55.96 | 24.04 | 908712 | 908.712 | 51.95 | 28.05 | 1060290 | 1060.29 | 47.94 | 32.06 | 1211868 | 1211.868 | 43.93 | 36.07 | 1363446 | 1363.446 | 39.92 | 40.08 | 1515024 | 1515.024 | 35.91 | 44.09 | 1666602 | 1666.602 | 31.9 | 48.1 | 1818180 | 1818.18 | 30
1/22/20XX 2:00:00 PM | 0.58333 | 1 | 32.9 | 51.1 | 32.9 |  | 32.9 | 68.09 | 11.91 | 450198 | 450.198 | 64.18 | 15.82 | 597996 | 597.996 | 60.27 | 19.73 | 745794 | 745.794 | 56.36 | 23.64 | 893592 | 893.592 | 52.45 | 27.55 | 1041390 | 1041.39 | 48.54 | 31.46 | 1189188 | 1189.188 | 44.63 | 35.37 | 1336986 | 1336.986 | 40.72 | 39.28 | 1484784 | 1484.784 | 36.81 | 43.19 | 1632582 | 1632.582 | 32.9 | 47.1 | 1780380 | 1780.38 | 35
1/22/20XX 3:00:00 PM | 0.625 | 1 | 33 | 52.7 | 33 |  | 33 | 68.1 | 11.9 | 449820 | 449.82 | 64.2 | 15.8 | 597240 | 597.24 | 60.3 | 19.7 | 744660 | 744.66 | 56.4 | 23.6 | 892080 | 892.08 | 52.5 | 27.5 | 1039500 | 1039.5 | 48.6 | 31.4 | 1186920 | 1186.92 | 44.7 | 35.3 | 1334340 | 1334.34 | 40.8 | 39.2 | 1481760 | 1481.76 | 36.9 | 43.1 | 1629180 | 1629.18 | 33 | 47 | 1776600 | 1776.6 | 35
1/22/20XX 4:00:00 PM | 0.66667 | 1 | 32.8 | 54.2 | 32.8 |  | 32.8 | 68.08 | 11.92 | 450576 | 450.576 | 64.16 | 15.84 | 598752 | 598.752 | 60.24 | 19.76 | 746928 | 746.928 | 56.32 | 23.68 | 895104 | 895.104 | 52.4 | 27.6 | 1043280 | 1043.28 | 48.48 | 31.52 | 1191456 | 1191.456 | 44.56 | 35.44 | 1339632 | 1339.632 | 40.64 | 39.36 | 1487808 | 1487.808 | 36.72 | 43.28 | 1635984 | 1635.984 | 32.8 | 47.2 | 1784160 | 1784.16 | 35
1/22/20XX 5:00:00 PM | 0.70833 | 1 | 32.2 | 57 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
1/22/20XX 6:00:00 PM | 0.75 | 1 | 31.8 | 57.9 | 31.8 |  | 31.8 | 67.98 | 12.02 | 454356 | 454.356 | 63.96 | 16.04 | 606312 | 606.312 | 59.94 | 20.06 | 758268 | 758.268 | 55.92 | 24.08 | 910224 | 910.224 | 51.9 | 28.1 | 1062180 | 1062.18 | 47.88 | 32.12 | 1214136 | 1214.136 | 43.86 | 36.14 | 1366092 | 1366.092 | 39.84 | 40.16 | 1518048 | 1518.048 | 35.82 | 44.18 | 1670004 | 1670.004 | 31.8 | 48.2 | 1821960 | 1821.96 | 30
1/22/20XX 7:00:00 PM | 0.79167 | 1 | 31.5 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/22/20XX 8:00:00 PM | 0.83333 | 1 | 30.8 | 58.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/22/20XX 9:00:00 PM | 0.875 | 1 | 30.5 | 58.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/22/20XX 10:00:00 PM | 0.91667 | 1 | 29.9 | 60.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/22/20XX 11:00:00 PM | 0.95833 | 1 | 28.9 | 60.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/22/20XX 12:00:00 AM | 0 | 2 | 28.3 | 61.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/23/20XX 1:00:00 AM | 0.041667 | 2 | 27.8 | 64.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/23/20XX 2:00:00 AM | 0.083333 | 2 | 27.6 | 65.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/23/20XX 3:00:00 AM | 0.125 | 2 | 27.5 | 65.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/23/20XX 4:00:00 AM | 0.16667 | 2 | 27.5 | 66.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/23/20XX 5:00:00 AM | 0.20833 | 2 | 26.8 | 69.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/23/20XX 6:00:00 AM | 0.25 | 2 | 26.7 | 69.3 | 26.7 |  | 26.7 | 67.47 | 12.53 | 473634 | 473.634 | 62.94 | 17.06 | 644868 | 644.868 | 58.41 | 21.59 | 816102 | 816.102 | 53.88 | 26.12 | 987336 | 987.336 | 49.35 | 30.65 | 1158570 | 1158.57 | 44.82 | 35.18 | 1329804 | 1329.804 | 40.29 | 39.71 | 1501038 | 1501.038 | 35.76 | 44.24 | 1672272 | 1672.272 | 31.23 | 48.77 | 1843506 | 1843.506 | 26.7 | 53.3 | 2014740 | 2014.74 | 25
1/23/20XX 7:00:00 AM | 0.29167 | 2 | 26.8 | 70.2 | 26.8 |  | 26.8 | 67.48 | 12.52 | 473256 | 473.256 | 62.96 | 17.04 | 644112 | 644.112 | 58.44 | 21.56 | 814968 | 814.968 | 53.92 | 26.08 | 985824 | 985.824 | 49.4 | 30.6 | 1156680 | 1156.68 | 44.88 | 35.12 | 1327536 | 1327.536 | 40.36 | 39.64 | 1498392 | 1498.392 | 35.84 | 44.16 | 1669248 | 1669.248 | 31.32 | 48.68 | 1840104 | 1840.104 | 26.8 | 53.2 | 2010960 | 2010.96 | 25
1/23/20XX 8:00:00 AM | 0.33333 | 2 | 27.5 | 71.8 | 27.5 |  | 27.5 | 67.55 | 12.45 | 470610 | 470.61 | 63.1 | 16.9 | 638820 | 638.82 | 58.65 | 21.35 | 807030 | 807.03 | 54.2 | 25.8 | 975240 | 975.24 | 49.75 | 30.25 | 1143450 | 1143.45 | 45.3 | 34.7 | 1311660 | 1311.66 | 40.85 | 39.15 | 1479870 | 1479.87 | 36.4 | 43.6 | 1648080 | 1648.08 | 31.95 | 48.05 | 1816290 | 1816.29 | 27.5 | 52.5 | 1984500 | 1984.5 | 25
1/23/20XX 9:00:00 AM | 0.375 | 2 | 28.7 | 69 | 28.7 |  | 28.7 | 67.67 | 12.33 | 466074 | 466.074 | 63.34 | 16.66 | 629748 | 629.748 | 59.01 | 20.99 | 793422 | 793.422 | 54.68 | 25.32 | 957096 | 957.096 | 50.35 | 29.65 | 1120770 | 1120.77 | 46.02 | 33.98 | 1284444 | 1284.444 | 41.69 | 38.31 | 1448118 | 1448.118 | 37.36 | 42.64 | 1611792 | 1611.792 | 33.03 | 46.97 | 1775466 | 1775.466 | 28.7 | 51.3 | 1939140 | 1939.14 | 30
1/23/20XX 10:00:00 AM | 0.41667 | 2 | 29.9 | 66.9 | 29.9 |  | 29.9 | 67.79 | 12.21 | 461538 | 461.538 | 63.58 | 16.42 | 620676 | 620.676 | 59.37 | 20.63 | 779814 | 779.814 | 55.16 | 24.84 | 938952 | 938.952 | 50.95 | 29.05 | 1098090 | 1098.09 | 46.74 | 33.26 | 1257228 | 1257.228 | 42.53 | 37.47 | 1416366 | 1416.366 | 38.32 | 41.68 | 1575504 | 1575.504 | 34.11 | 45.89 | 1734642 | 1734.642 | 29.9 | 50.1 | 1893780 | 1893.78 | 30
1/23/20XX 11:00:00 AM | 0.45833 | 2 | 31.7 | 62.4 | 31.7 |  | 31.7 | 67.97 | 12.03 | 454734 | 454.734 | 63.94 | 16.06 | 607068 | 607.068 | 59.91 | 20.09 | 759402 | 759.402 | 55.88 | 24.12 | 911736 | 911.736 | 51.85 | 28.15 | 1064070 | 1064.07 | 47.82 | 32.18 | 1216404 | 1216.404 | 43.79 | 36.21 | 1368738 | 1368.738 | 39.76 | 40.24 | 1521072 | 1521.072 | 35.73 | 44.27 | 1673406 | 1673.406 | 31.7 | 48.3 | 1825740 | 1825.74 | 30
1/23/20XX 12:00:00 PM | 0.5 | 2 | 33.1 | 61.2 | 33.1 |  | 33.1 | 68.11 | 11.89 | 449442 | 449.442 | 64.22 | 15.78 | 596484 | 596.484 | 60.33 | 19.67 | 743526 | 743.526 | 56.44 | 23.56 | 890568 | 890.568 | 52.55 | 27.45 | 1037610 | 1037.61 | 48.66 | 31.34 | 1184652 | 1184.652 | 44.77 | 35.23 | 1331694 | 1331.694 | 40.88 | 39.12 | 1478736 | 1478.736 | 36.99 | 43.01 | 1625778 | 1625.778 | 33.1 | 46.9 | 1772820 | 1772.82 | 35
1/23/20XX 1:00:00 PM | 0.54167 | 2 | 34.5 | 58.5 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
1/23/20XX 2:00:00 PM | 0.58333 | 2 | 35.1 | 56.6 | 35.1 |  | 35.1 | 68.31 | 11.69 | 441882 | 441.882 | 64.62 | 15.38 | 581364 | 581.364 | 60.93 | 19.07 | 720846 | 720.846 | 57.24 | 22.76 | 860328 | 860.328 | 53.55 | 26.45 | 999810 | 999.81 | 49.86 | 30.14 | 1139292 | 1139.292 | 46.17 | 33.83 | 1278774 | 1278.774 | 42.48 | 37.52 | 1418256 | 1418.256 | 38.79 | 41.21 | 1557738 | 1557.738 | 35.1 | 44.9 | 1697220 | 1697.22 | 35
1/23/20XX 3:00:00 PM | 0.625 | 2 | 35.5 | 55.6 | 35.5 |  | 35.5 | 68.35 | 11.65 | 440370 | 440.37 | 64.7 | 15.3 | 578340 | 578.34 | 61.05 | 18.95 | 716310 | 716.31 | 57.4 | 22.6 | 854280 | 854.28 | 53.75 | 26.25 | 992250 | 992.25 | 50.1 | 29.9 | 1130220 | 1130.22 | 46.45 | 33.55 | 1268190 | 1268.19 | 42.8 | 37.2 | 1406160 | 1406.16 | 39.15 | 40.85 | 1544130 | 1544.13 | 35.5 | 44.5 | 1682100 | 1682.1 | 35
1/23/20XX 4:00:00 PM | 0.66667 | 2 | 35.5 | 56.1 | 35.5 |  | 35.5 | 68.35 | 11.65 | 440370 | 440.37 | 64.7 | 15.3 | 578340 | 578.34 | 61.05 | 18.95 | 716310 | 716.31 | 57.4 | 22.6 | 854280 | 854.28 | 53.75 | 26.25 | 992250 | 992.25 | 50.1 | 29.9 | 1130220 | 1130.22 | 46.45 | 33.55 | 1268190 | 1268.19 | 42.8 | 37.2 | 1406160 | 1406.16 | 39.15 | 40.85 | 1544130 | 1544.13 | 35.5 | 44.5 | 1682100 | 1682.1 | 35
1/23/20XX 5:00:00 PM | 0.70833 | 2 | 34.4 | 59.5 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
1/23/20XX 6:00:00 PM | 0.75 | 2 | 34 | 60.4 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
1/23/20XX 7:00:00 PM | 0.79167 | 2 | 33.5 | 61 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/23/20XX 8:00:00 PM | 0.83333 | 2 | 33.1 | 61.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/23/20XX 9:00:00 PM | 0.875 | 2 | 32.6 | 61 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/23/20XX 10:00:00 PM | 0.91667 | 2 | 32.5 | 62.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/23/20XX 11:00:00 PM | 0.95833 | 2 | 32 | 62.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/23/20XX 12:00:00 AM | 0 | 3 | 31.7 | 62.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/24/20XX 1:00:00 AM | 0.041667 | 3 | 30.9 | 63.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/24/20XX 2:00:00 AM | 0.083333 | 3 | 30.6 | 65.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/24/20XX 3:00:00 AM | 0.125 | 3 | 30.4 | 65.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/24/20XX 4:00:00 AM | 0.16667 | 3 | 29.8 | 66.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/24/20XX 5:00:00 AM | 0.20833 | 3 | 29 | 67.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/24/20XX 6:00:00 AM | 0.25 | 3 | 28.6 | 68.3 | 28.6 |  | 28.6 | 67.66 | 12.34 | 466452 | 466.452 | 63.32 | 16.68 | 630504 | 630.504 | 58.98 | 21.02 | 794556 | 794.556 | 54.64 | 25.36 | 958608 | 958.608 | 50.3 | 29.7 | 1122660 | 1122.66 | 45.96 | 34.04 | 1286712 | 1286.712 | 41.62 | 38.38 | 1450764 | 1450.764 | 37.28 | 42.72 | 1614816 | 1614.816 | 32.94 | 47.06 | 1778868 | 1778.868 | 28.6 | 51.4 | 1942920 | 1942.92 | 30
1/24/20XX 7:00:00 AM | 0.29167 | 3 | 28 | 65.5 | 28 |  | 28 | 67.6 | 12.4 | 468720 | 468.72 | 63.2 | 16.8 | 635040 | 635.04 | 58.8 | 21.2 | 801360 | 801.36 | 54.4 | 25.6 | 967680 | 967.68 | 50 | 30 | 1134000 | 1134 | 45.6 | 34.4 | 1300320 | 1300.32 | 41.2 | 38.8 | 1466640 | 1466.64 | 36.8 | 43.2 | 1632960 | 1632.96 | 32.4 | 47.6 | 1799280 | 1799.28 | 28 | 52 | 1965600 | 1965.6 | 30
1/24/20XX 8:00:00 AM | 0.33333 | 3 | 27.5 | 66.9 | 27.5 |  | 27.5 | 67.55 | 12.45 | 470610 | 470.61 | 63.1 | 16.9 | 638820 | 638.82 | 58.65 | 21.35 | 807030 | 807.03 | 54.2 | 25.8 | 975240 | 975.24 | 49.75 | 30.25 | 1143450 | 1143.45 | 45.3 | 34.7 | 1311660 | 1311.66 | 40.85 | 39.15 | 1479870 | 1479.87 | 36.4 | 43.6 | 1648080 | 1648.08 | 31.95 | 48.05 | 1816290 | 1816.29 | 27.5 | 52.5 | 1984500 | 1984.5 | 25
1/24/20XX 9:00:00 AM | 0.375 | 3 | 27.8 | 65.5 | 27.8 |  | 27.8 | 67.58 | 12.42 | 469476 | 469.476 | 63.16 | 16.84 | 636552 | 636.552 | 58.74 | 21.26 | 803628 | 803.628 | 54.32 | 25.68 | 970704 | 970.704 | 49.9 | 30.1 | 1137780 | 1137.78 | 45.48 | 34.52 | 1304856 | 1304.856 | 41.06 | 38.94 | 1471932 | 1471.932 | 36.64 | 43.36 | 1639008 | 1639.008 | 32.22 | 47.78 | 1806084 | 1806.084 | 27.8 | 52.2 | 1973160 | 1973.16 | 30
1/24/20XX 10:00:00 AM | 0.41667 | 3 | 28.5 | 63.1 | 28.5 |  | 28.5 | 67.65 | 12.35 | 466830 | 466.83 | 63.3 | 16.7 | 631260 | 631.26 | 58.95 | 21.05 | 795690 | 795.69 | 54.6 | 25.4 | 960120 | 960.12 | 50.25 | 29.75 | 1124550 | 1124.55 | 45.9 | 34.1 | 1288980 | 1288.98 | 41.55 | 38.45 | 1453410 | 1453.41 | 37.2 | 42.8 | 1617840 | 1617.84 | 32.85 | 47.15 | 1782270 | 1782.27 | 28.5 | 51.5 | 1946700 | 1946.7 | 30
1/24/20XX 11:00:00 AM | 0.45833 | 3 | 29.5 | 61.6 | 29.5 |  | 29.5 | 67.75 | 12.25 | 463050 | 463.05 | 63.5 | 16.5 | 623700 | 623.7 | 59.25 | 20.75 | 784350 | 784.35 | 55 | 25 | 945000 | 945 | 50.75 | 29.25 | 1105650 | 1105.65 | 46.5 | 33.5 | 1266300 | 1266.3 | 42.25 | 37.75 | 1426950 | 1426.95 | 38 | 42 | 1587600 | 1587.6 | 33.75 | 46.25 | 1748250 | 1748.25 | 29.5 | 50.5 | 1908900 | 1908.9 | 30
1/24/20XX 12:00:00 PM | 0.5 | 3 | 30.8 | 59.3 | 30.8 |  | 30.8 | 67.88 | 12.12 | 458136 | 458.136 | 63.76 | 16.24 | 613872 | 613.872 | 59.64 | 20.36 | 769608 | 769.608 | 55.52 | 24.48 | 925344 | 925.344 | 51.4 | 28.6 | 1081080 | 1081.08 | 47.28 | 32.72 | 1236816 | 1236.816 | 43.16 | 36.84 | 1392552 | 1392.552 | 39.04 | 40.96 | 1548288 | 1548.288 | 34.92 | 45.08 | 1704024 | 1704.024 | 30.8 | 49.2 | 1859760 | 1859.76 | 30
1/24/20XX 1:00:00 PM | 0.54167 | 3 | 31.8 | 55.4 | 31.8 |  | 31.8 | 67.98 | 12.02 | 454356 | 454.356 | 63.96 | 16.04 | 606312 | 606.312 | 59.94 | 20.06 | 758268 | 758.268 | 55.92 | 24.08 | 910224 | 910.224 | 51.9 | 28.1 | 1062180 | 1062.18 | 47.88 | 32.12 | 1214136 | 1214.136 | 43.86 | 36.14 | 1366092 | 1366.092 | 39.84 | 40.16 | 1518048 | 1518.048 | 35.82 | 44.18 | 1670004 | 1670.004 | 31.8 | 48.2 | 1821960 | 1821.96 | 30
1/24/20XX 2:00:00 PM | 0.58333 | 3 | 32.1 | 54.7 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
1/24/20XX 3:00:00 PM | 0.625 | 3 | 32.3 | 55.1 | 32.3 |  | 32.3 | 68.03 | 11.97 | 452466 | 452.466 | 64.06 | 15.94 | 602532 | 602.532 | 60.09 | 19.91 | 752598 | 752.598 | 56.12 | 23.88 | 902664 | 902.664 | 52.15 | 27.85 | 1052730 | 1052.73 | 48.18 | 31.82 | 1202796 | 1202.796 | 44.21 | 35.79 | 1352862 | 1352.862 | 40.24 | 39.76 | 1502928 | 1502.928 | 36.27 | 43.73 | 1652994 | 1652.994 | 32.3 | 47.7 | 1803060 | 1803.06 | 30
1/24/20XX 4:00:00 PM | 0.66667 | 3 | 32.2 | 54.4 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
1/24/20XX 5:00:00 PM | 0.70833 | 3 | 32 | 54.7 | 32 |  | 32 | 68 | 12 | 453600 | 453.6 | 64 | 16 | 604800 | 604.8 | 60 | 20 | 756000 | 756 | 56 | 24 | 907200 | 907.2 | 52 | 28 | 1058400 | 1058.4 | 48 | 32 | 1209600 | 1209.6 | 44 | 36 | 1360800 | 1360.8 | 40 | 40 | 1512000 | 1512 | 36 | 44 | 1663200 | 1663.2 | 32 | 48 | 1814400 | 1814.4 | 30
1/24/20XX 6:00:00 PM | 0.75 | 3 | 31.7 | 55 | 31.7 |  | 31.7 | 67.97 | 12.03 | 454734 | 454.734 | 63.94 | 16.06 | 607068 | 607.068 | 59.91 | 20.09 | 759402 | 759.402 | 55.88 | 24.12 | 911736 | 911.736 | 51.85 | 28.15 | 1064070 | 1064.07 | 47.82 | 32.18 | 1216404 | 1216.404 | 43.79 | 36.21 | 1368738 | 1368.738 | 39.76 | 40.24 | 1521072 | 1521.072 | 35.73 | 44.27 | 1673406 | 1673.406 | 31.7 | 48.3 | 1825740 | 1825.74 | 30
1/24/20XX 7:00:00 PM | 0.79167 | 3 | 31.4 | 54.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/24/20XX 8:00:00 PM | 0.83333 | 3 | 30.6 | 54.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/24/20XX 9:00:00 PM | 0.875 | 3 | 30.2 | 55.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/24/20XX 10:00:00 PM | 0.91667 | 3 | 30.1 | 56.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/24/20XX 11:00:00 PM | 0.95833 | 3 | 30.1 | 56.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/24/20XX 12:00:00 AM | 0 | 4 | 30 | 56.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/25/20XX 1:00:00 AM | 0.041667 | 4 | 29.7 | 57.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/25/20XX 2:00:00 AM | 0.083333 | 4 | 29.9 | 58.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/25/20XX 3:00:00 AM | 0.125 | 4 | 29.4 | 58.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/25/20XX 4:00:00 AM | 0.16667 | 4 | 29.2 | 59.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/25/20XX 5:00:00 AM | 0.20833 | 4 | 29.2 | 61 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/25/20XX 6:00:00 AM | 0.25 | 4 | 29.4 | 62.2 | 29.4 |  | 29.4 | 67.74 | 12.26 | 463428 | 463.428 | 63.48 | 16.52 | 624456 | 624.456 | 59.22 | 20.78 | 785484 | 785.484 | 54.96 | 25.04 | 946512 | 946.512 | 50.7 | 29.3 | 1107540 | 1107.54 | 46.44 | 33.56 | 1268568 | 1268.568 | 42.18 | 37.82 | 1429596 | 1429.596 | 37.92 | 42.08 | 1590624 | 1590.624 | 33.66 | 46.34 | 1751652 | 1751.652 | 29.4 | 50.6 | 1912680 | 1912.68 | 30
1/25/20XX 7:00:00 AM | 0.29167 | 4 | 29.5 | 61.9 | 29.5 |  | 29.5 | 67.75 | 12.25 | 463050 | 463.05 | 63.5 | 16.5 | 623700 | 623.7 | 59.25 | 20.75 | 784350 | 784.35 | 55 | 25 | 945000 | 945 | 50.75 | 29.25 | 1105650 | 1105.65 | 46.5 | 33.5 | 1266300 | 1266.3 | 42.25 | 37.75 | 1426950 | 1426.95 | 38 | 42 | 1587600 | 1587.6 | 33.75 | 46.25 | 1748250 | 1748.25 | 29.5 | 50.5 | 1908900 | 1908.9 | 30
1/25/20XX 8:00:00 AM | 0.33333 | 4 | 29.7 | 63.5 | 29.7 |  | 29.7 | 67.77 | 12.23 | 462294 | 462.294 | 63.54 | 16.46 | 622188 | 622.188 | 59.31 | 20.69 | 782082 | 782.082 | 55.08 | 24.92 | 941976 | 941.976 | 50.85 | 29.15 | 1101870 | 1101.87 | 46.62 | 33.38 | 1261764 | 1261.764 | 42.39 | 37.61 | 1421658 | 1421.658 | 38.16 | 41.84 | 1581552 | 1581.552 | 33.93 | 46.07 | 1741446 | 1741.446 | 29.7 | 50.3 | 1901340 | 1901.34 | 30
1/25/20XX 9:00:00 AM | 0.375 | 4 | 30.9 | 62.7 | 30.9 |  | 30.9 | 67.89 | 12.11 | 457758 | 457.758 | 63.78 | 16.22 | 613116 | 613.116 | 59.67 | 20.33 | 768474 | 768.474 | 55.56 | 24.44 | 923832 | 923.832 | 51.45 | 28.55 | 1079190 | 1079.19 | 47.34 | 32.66 | 1234548 | 1234.548 | 43.23 | 36.77 | 1389906 | 1389.906 | 39.12 | 40.88 | 1545264 | 1545.264 | 35.01 | 44.99 | 1700622 | 1700.622 | 30.9 | 49.1 | 1855980 | 1855.98 | 30
1/25/20XX 10:00:00 AM | 0.41667 | 4 | 32.1 | 59.1 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
1/25/20XX 11:00:00 AM | 0.45833 | 4 | 33.5 | 57.6 | 33.5 |  | 33.5 | 68.15 | 11.85 | 447930 | 447.93 | 64.3 | 15.7 | 593460 | 593.46 | 60.45 | 19.55 | 738990 | 738.99 | 56.6 | 23.4 | 884520 | 884.52 | 52.75 | 27.25 | 1030050 | 1030.05 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.05 | 34.95 | 1321110 | 1321.11 | 41.2 | 38.8 | 1466640 | 1466.64 | 37.35 | 42.65 | 1612170 | 1612.17 | 33.5 | 46.5 | 1757700 | 1757.7 | 35
1/25/20XX 12:00:00 PM | 0.5 | 4 | 34.5 | 53.9 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
1/25/20XX 1:00:00 PM | 0.54167 | 4 | 35.6 | 51.7 | 35.6 |  | 35.6 | 68.36 | 11.64 | 439992 | 439.992 | 64.72 | 15.28 | 577584 | 577.584 | 61.08 | 18.92 | 715176 | 715.176 | 57.44 | 22.56 | 852768 | 852.768 | 53.8 | 26.2 | 990360 | 990.36 | 50.16 | 29.84 | 1127952 | 1127.952 | 46.52 | 33.48 | 1265544 | 1265.544 | 42.88 | 37.12 | 1403136 | 1403.136 | 39.24 | 40.76 | 1540728 | 1540.728 | 35.6 | 44.4 | 1678320 | 1678.32 | 35
1/25/20XX 2:00:00 PM | 0.58333 | 4 | 36.3 | 52.9 | 36.3 |  | 36.3 | 68.43 | 11.57 | 437346 | 437.346 | 64.86 | 15.14 | 572292 | 572.292 | 61.29 | 18.71 | 707238 | 707.238 | 57.72 | 22.28 | 842184 | 842.184 | 54.15 | 25.85 | 977130 | 977.13 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.01 | 32.99 | 1247022 | 1247.022 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.87 | 40.13 | 1516914 | 1516.914 | 36.3 | 43.7 | 1651860 | 1651.86 | 35
1/25/20XX 3:00:00 PM | 0.625 | 4 | 36.8 | 51 | 36.8 |  | 36.8 | 68.48 | 11.52 | 435456 | 435.456 | 64.96 | 15.04 | 568512 | 568.512 | 61.44 | 18.56 | 701568 | 701.568 | 57.92 | 22.08 | 834624 | 834.624 | 54.4 | 25.6 | 967680 | 967.68 | 50.88 | 29.12 | 1100736 | 1100.736 | 47.36 | 32.64 | 1233792 | 1233.792 | 43.84 | 36.16 | 1366848 | 1366.848 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.8 | 43.2 | 1632960 | 1632.96 | 35
1/25/20XX 4:00:00 PM | 0.66667 | 4 | 37 | 50.4 | 37 |  | 37 | 68.5 | 11.5 | 434700 | 434.7 | 65 | 15 | 567000 | 567 | 61.5 | 18.5 | 699300 | 699.3 | 58 | 22 | 831600 | 831.6 | 54.5 | 25.5 | 963900 | 963.9 | 51 | 29 | 1096200 | 1096.2 | 47.5 | 32.5 | 1228500 | 1228.5 | 44 | 36 | 1360800 | 1360.8 | 40.5 | 39.5 | 1493100 | 1493.1 | 37 | 43 | 1625400 | 1625.4 | 35
1/25/20XX 5:00:00 PM | 0.70833 | 4 | 36.1 | 51.5 | 36.1 |  | 36.1 | 68.41 | 11.59 | 438102 | 438.102 | 64.82 | 15.18 | 573804 | 573.804 | 61.23 | 18.77 | 709506 | 709.506 | 57.64 | 22.36 | 845208 | 845.208 | 54.05 | 25.95 | 980910 | 980.91 | 50.46 | 29.54 | 1116612 | 1116.612 | 46.87 | 33.13 | 1252314 | 1252.314 | 43.28 | 36.72 | 1388016 | 1388.016 | 39.69 | 40.31 | 1523718 | 1523.718 | 36.1 | 43.9 | 1659420 | 1659.42 | 35
1/25/20XX 6:00:00 PM | 0.75 | 4 | 35.5 | 57.1 | 35.5 |  | 35.5 | 68.35 | 11.65 | 440370 | 440.37 | 64.7 | 15.3 | 578340 | 578.34 | 61.05 | 18.95 | 716310 | 716.31 | 57.4 | 22.6 | 854280 | 854.28 | 53.75 | 26.25 | 992250 | 992.25 | 50.1 | 29.9 | 1130220 | 1130.22 | 46.45 | 33.55 | 1268190 | 1268.19 | 42.8 | 37.2 | 1406160 | 1406.16 | 39.15 | 40.85 | 1544130 | 1544.13 | 35.5 | 44.5 | 1682100 | 1682.1 | 35
1/25/20XX 7:00:00 PM | 0.79167 | 4 | 34.9 | 57.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/25/20XX 8:00:00 PM | 0.83333 | 4 | 34.5 | 57.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/25/20XX 9:00:00 PM | 0.875 | 4 | 34.4 | 56.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/25/20XX 10:00:00 PM | 0.91667 | 4 | 33.6 | 56.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/25/20XX 11:00:00 PM | 0.95833 | 4 | 33.7 | 55 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/25/20XX 12:00:00 AM | 0 | 5 | 33.3 | 57.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/26/20XX 1:00:00 AM | 0.041667 | 5 | 32.6 | 57.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/26/20XX 2:00:00 AM | 0.083333 | 5 | 31.9 | 57.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/26/20XX 3:00:00 AM | 0.125 | 5 | 31.2 | 57.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/26/20XX 4:00:00 AM | 0.16667 | 5 | 30.3 | 59.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/26/20XX 5:00:00 AM | 0.20833 | 5 | 30 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/26/20XX 6:00:00 AM | 0.25 | 5 | 29.8 | 59.5 | 29.8 |  | 29.8 | 67.78 | 12.22 | 461916 | 461.916 | 63.56 | 16.44 | 621432 | 621.432 | 59.34 | 20.66 | 780948 | 780.948 | 55.12 | 24.88 | 940464 | 940.464 | 50.9 | 29.1 | 1099980 | 1099.98 | 46.68 | 33.32 | 1259496 | 1259.496 | 42.46 | 37.54 | 1419012 | 1419.012 | 38.24 | 41.76 | 1578528 | 1578.528 | 34.02 | 45.98 | 1738044 | 1738.044 | 29.8 | 50.2 | 1897560 | 1897.56 | 30
1/26/20XX 7:00:00 AM | 0.29167 | 5 | 29.7 | 59.6 | 29.7 |  | 29.7 | 67.77 | 12.23 | 462294 | 462.294 | 63.54 | 16.46 | 622188 | 622.188 | 59.31 | 20.69 | 782082 | 782.082 | 55.08 | 24.92 | 941976 | 941.976 | 50.85 | 29.15 | 1101870 | 1101.87 | 46.62 | 33.38 | 1261764 | 1261.764 | 42.39 | 37.61 | 1421658 | 1421.658 | 38.16 | 41.84 | 1581552 | 1581.552 | 33.93 | 46.07 | 1741446 | 1741.446 | 29.7 | 50.3 | 1901340 | 1901.34 | 30
1/26/20XX 8:00:00 AM | 0.33333 | 5 | 30 | 59.5 | 30 |  | 30 | 67.8 | 12.2 | 461160 | 461.16 | 63.6 | 16.4 | 619920 | 619.92 | 59.4 | 20.6 | 778680 | 778.68 | 55.2 | 24.8 | 937440 | 937.44 | 51 | 29 | 1096200 | 1096.2 | 46.8 | 33.2 | 1254960 | 1254.96 | 42.6 | 37.4 | 1413720 | 1413.72 | 38.4 | 41.6 | 1572480 | 1572.48 | 34.2 | 45.8 | 1731240 | 1731.24 | 30 | 50 | 1890000 | 1890 | 30
1/26/20XX 9:00:00 AM | 0.375 | 5 | 30.2 | 63.5 | 30.2 |  | 30.2 | 67.82 | 12.18 | 460404 | 460.404 | 63.64 | 16.36 | 618408 | 618.408 | 59.46 | 20.54 | 776412 | 776.412 | 55.28 | 24.72 | 934416 | 934.416 | 51.1 | 28.9 | 1092420 | 1092.42 | 46.92 | 33.08 | 1250424 | 1250.424 | 42.74 | 37.26 | 1408428 | 1408.428 | 38.56 | 41.44 | 1566432 | 1566.432 | 34.38 | 45.62 | 1724436 | 1724.436 | 30.2 | 49.8 | 1882440 | 1882.44 | 30
1/26/20XX 10:00:00 AM | 0.41667 | 5 | 31 | 62.1 | 31 |  | 31 | 67.9 | 12.1 | 457380 | 457.38 | 63.8 | 16.2 | 612360 | 612.36 | 59.7 | 20.3 | 767340 | 767.34 | 55.6 | 24.4 | 922320 | 922.32 | 51.5 | 28.5 | 1077300 | 1077.3 | 47.4 | 32.6 | 1232280 | 1232.28 | 43.3 | 36.7 | 1387260 | 1387.26 | 39.2 | 40.8 | 1542240 | 1542.24 | 35.1 | 44.9 | 1697220 | 1697.22 | 31 | 49 | 1852200 | 1852.2 | 30
1/26/20XX 11:00:00 AM | 0.45833 | 5 | 32.1 | 59.8 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
1/26/20XX 12:00:00 PM | 0.5 | 5 | 32.9 | 56.5 | 32.9 |  | 32.9 | 68.09 | 11.91 | 450198 | 450.198 | 64.18 | 15.82 | 597996 | 597.996 | 60.27 | 19.73 | 745794 | 745.794 | 56.36 | 23.64 | 893592 | 893.592 | 52.45 | 27.55 | 1041390 | 1041.39 | 48.54 | 31.46 | 1189188 | 1189.188 | 44.63 | 35.37 | 1336986 | 1336.986 | 40.72 | 39.28 | 1484784 | 1484.784 | 36.81 | 43.19 | 1632582 | 1632.582 | 32.9 | 47.1 | 1780380 | 1780.38 | 35
1/26/20XX 1:00:00 PM | 0.54167 | 5 | 34.1 | 55.3 | 34.1 |  | 34.1 | 68.21 | 11.79 | 445662 | 445.662 | 64.42 | 15.58 | 588924 | 588.924 | 60.63 | 19.37 | 732186 | 732.186 | 56.84 | 23.16 | 875448 | 875.448 | 53.05 | 26.95 | 1018710 | 1018.71 | 49.26 | 30.74 | 1161972 | 1161.972 | 45.47 | 34.53 | 1305234 | 1305.234 | 41.68 | 38.32 | 1448496 | 1448.496 | 37.89 | 42.11 | 1591758 | 1591.758 | 34.1 | 45.9 | 1735020 | 1735.02 | 35
1/26/20XX 2:00:00 PM | 0.58333 | 5 | 34.3 | 54.1 | 34.3 |  | 34.3 | 68.23 | 11.77 | 444906 | 444.906 | 64.46 | 15.54 | 587412 | 587.412 | 60.69 | 19.31 | 729918 | 729.918 | 56.92 | 23.08 | 872424 | 872.424 | 53.15 | 26.85 | 1014930 | 1014.93 | 49.38 | 30.62 | 1157436 | 1157.436 | 45.61 | 34.39 | 1299942 | 1299.942 | 41.84 | 38.16 | 1442448 | 1442.448 | 38.07 | 41.93 | 1584954 | 1584.954 | 34.3 | 45.7 | 1727460 | 1727.46 | 35
1/26/20XX 3:00:00 PM | 0.625 | 5 | 34.7 | 52.7 | 34.7 |  | 34.7 | 68.27 | 11.73 | 443394 | 443.394 | 64.54 | 15.46 | 584388 | 584.388 | 60.81 | 19.19 | 725382 | 725.382 | 57.08 | 22.92 | 866376 | 866.376 | 53.35 | 26.65 | 1007370 | 1007.37 | 49.62 | 30.38 | 1148364 | 1148.364 | 45.89 | 34.11 | 1289358 | 1289.358 | 42.16 | 37.84 | 1430352 | 1430.352 | 38.43 | 41.57 | 1571346 | 1571.346 | 34.7 | 45.3 | 1712340 | 1712.34 | 35
1/26/20XX 4:00:00 PM | 0.66667 | 5 | 34.3 | 55.5 | 34.3 |  | 34.3 | 68.23 | 11.77 | 444906 | 444.906 | 64.46 | 15.54 | 587412 | 587.412 | 60.69 | 19.31 | 729918 | 729.918 | 56.92 | 23.08 | 872424 | 872.424 | 53.15 | 26.85 | 1014930 | 1014.93 | 49.38 | 30.62 | 1157436 | 1157.436 | 45.61 | 34.39 | 1299942 | 1299.942 | 41.84 | 38.16 | 1442448 | 1442.448 | 38.07 | 41.93 | 1584954 | 1584.954 | 34.3 | 45.7 | 1727460 | 1727.46 | 35
1/26/20XX 5:00:00 PM | 0.70833 | 5 | 33.9 | 57 | 33.9 |  | 33.9 | 68.19 | 11.81 | 446418 | 446.418 | 64.38 | 15.62 | 590436 | 590.436 | 60.57 | 19.43 | 734454 | 734.454 | 56.76 | 23.24 | 878472 | 878.472 | 52.95 | 27.05 | 1022490 | 1022.49 | 49.14 | 30.86 | 1166508 | 1166.508 | 45.33 | 34.67 | 1310526 | 1310.526 | 41.52 | 38.48 | 1454544 | 1454.544 | 37.71 | 42.29 | 1598562 | 1598.562 | 33.9 | 46.1 | 1742580 | 1742.58 | 35
1/26/20XX 6:00:00 PM | 0.75 | 5 | 33.5 | 58.1 | 33.5 |  | 33.5 | 68.15 | 11.85 | 447930 | 447.93 | 64.3 | 15.7 | 593460 | 593.46 | 60.45 | 19.55 | 738990 | 738.99 | 56.6 | 23.4 | 884520 | 884.52 | 52.75 | 27.25 | 1030050 | 1030.05 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.05 | 34.95 | 1321110 | 1321.11 | 41.2 | 38.8 | 1466640 | 1466.64 | 37.35 | 42.65 | 1612170 | 1612.17 | 33.5 | 46.5 | 1757700 | 1757.7 | 35
1/26/20XX 7:00:00 PM | 0.79167 | 5 | 33.6 | 58.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/26/20XX 8:00:00 PM | 0.83333 | 5 | 33.9 | 60.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/26/20XX 9:00:00 PM | 0.875 | 5 | 33.6 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/26/20XX 10:00:00 PM | 0.91667 | 5 | 33.6 | 61.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/26/20XX 11:00:00 PM | 0.95833 | 5 | 33.5 | 63.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/26/20XX 12:00:00 AM | 0 | 6 | 33.5 | 64 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/27/20XX 1:00:00 AM | 0.041667 | 6 | 33 | 65.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/27/20XX 2:00:00 AM | 0.083333 | 6 | 33 | 65.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/27/20XX 3:00:00 AM | 0.125 | 6 | 33.2 | 67.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/27/20XX 4:00:00 AM | 0.16667 | 6 | 33 | 69 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/27/20XX 5:00:00 AM | 0.20833 | 6 | 33.3 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/27/20XX 6:00:00 AM | 0.25 | 6 | 33.4 | 67.1 | 33.4 |  | 33.4 | 68.14 | 11.86 | 448308 | 448.308 | 64.28 | 15.72 | 594216 | 594.216 | 60.42 | 19.58 | 740124 | 740.124 | 56.56 | 23.44 | 886032 | 886.032 | 52.7 | 27.3 | 1031940 | 1031.94 | 48.84 | 31.16 | 1177848 | 1177.848 | 44.98 | 35.02 | 1323756 | 1323.756 | 41.12 | 38.88 | 1469664 | 1469.664 | 37.26 | 42.74 | 1615572 | 1615.572 | 33.4 | 46.6 | 1761480 | 1761.48 | 35
1/27/20XX 7:00:00 AM | 0.29167 | 6 | 33.6 | 66.3 | 33.6 |  | 33.6 | 68.16 | 11.84 | 447552 | 447.552 | 64.32 | 15.68 | 592704 | 592.704 | 60.48 | 19.52 | 737856 | 737.856 | 56.64 | 23.36 | 883008 | 883.008 | 52.8 | 27.2 | 1028160 | 1028.16 | 48.96 | 31.04 | 1173312 | 1173.312 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.28 | 38.72 | 1463616 | 1463.616 | 37.44 | 42.56 | 1608768 | 1608.768 | 33.6 | 46.4 | 1753920 | 1753.92 | 35
1/27/20XX 8:00:00 AM | 0.33333 | 6 | 34.5 | 63.3 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
1/27/20XX 9:00:00 AM | 0.375 | 6 | 35.1 | 63.6 | 35.1 |  | 35.1 | 68.31 | 11.69 | 441882 | 441.882 | 64.62 | 15.38 | 581364 | 581.364 | 60.93 | 19.07 | 720846 | 720.846 | 57.24 | 22.76 | 860328 | 860.328 | 53.55 | 26.45 | 999810 | 999.81 | 49.86 | 30.14 | 1139292 | 1139.292 | 46.17 | 33.83 | 1278774 | 1278.774 | 42.48 | 37.52 | 1418256 | 1418.256 | 38.79 | 41.21 | 1557738 | 1557.738 | 35.1 | 44.9 | 1697220 | 1697.22 | 35
1/27/20XX 10:00:00 AM | 0.41667 | 6 | 35.5 | 61.2 | 35.5 |  | 35.5 | 68.35 | 11.65 | 440370 | 440.37 | 64.7 | 15.3 | 578340 | 578.34 | 61.05 | 18.95 | 716310 | 716.31 | 57.4 | 22.6 | 854280 | 854.28 | 53.75 | 26.25 | 992250 | 992.25 | 50.1 | 29.9 | 1130220 | 1130.22 | 46.45 | 33.55 | 1268190 | 1268.19 | 42.8 | 37.2 | 1406160 | 1406.16 | 39.15 | 40.85 | 1544130 | 1544.13 | 35.5 | 44.5 | 1682100 | 1682.1 | 35
1/27/20XX 11:00:00 AM | 0.45833 | 6 | 36.9 | 58 | 36.9 |  | 36.9 | 68.49 | 11.51 | 435078 | 435.078 | 64.98 | 15.02 | 567756 | 567.756 | 61.47 | 18.53 | 700434 | 700.434 | 57.96 | 22.04 | 833112 | 833.112 | 54.45 | 25.55 | 965790 | 965.79 | 50.94 | 29.06 | 1098468 | 1098.468 | 47.43 | 32.57 | 1231146 | 1231.146 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.41 | 39.59 | 1496502 | 1496.502 | 36.9 | 43.1 | 1629180 | 1629.18 | 35
1/27/20XX 12:00:00 PM | 0.5 | 6 | 38.4 | 53.1 | 38.4 |  | 38.4 | 68.64 | 11.36 | 429408 | 429.408 | 65.28 | 14.72 | 556416 | 556.416 | 61.92 | 18.08 | 683424 | 683.424 | 58.56 | 21.44 | 810432 | 810.432 | 55.2 | 24.8 | 937440 | 937.44 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.76 | 38.24 | 1445472 | 1445.472 | 38.4 | 41.6 | 1572480 | 1572.48 | 40
1/27/20XX 1:00:00 PM | 0.54167 | 6 | 39.6 | 49.1 | 39.6 |  | 39.6 | 68.76 | 11.24 | 424872 | 424.872 | 65.52 | 14.48 | 547344 | 547.344 | 62.28 | 17.72 | 669816 | 669.816 | 59.04 | 20.96 | 792288 | 792.288 | 55.8 | 24.2 | 914760 | 914.76 | 52.56 | 27.44 | 1037232 | 1037.232 | 49.32 | 30.68 | 1159704 | 1159.704 | 46.08 | 33.92 | 1282176 | 1282.176 | 42.84 | 37.16 | 1404648 | 1404.648 | 39.6 | 40.4 | 1527120 | 1527.12 | 40
1/27/20XX 2:00:00 PM | 0.58333 | 6 | 39.9 | 48.8 | 39.9 |  | 39.9 | 68.79 | 11.21 | 423738 | 423.738 | 65.58 | 14.42 | 545076 | 545.076 | 62.37 | 17.63 | 666414 | 666.414 | 59.16 | 20.84 | 787752 | 787.752 | 55.95 | 24.05 | 909090 | 909.09 | 52.74 | 27.26 | 1030428 | 1030.428 | 49.53 | 30.47 | 1151766 | 1151.766 | 46.32 | 33.68 | 1273104 | 1273.104 | 43.11 | 36.89 | 1394442 | 1394.442 | 39.9 | 40.1 | 1515780 | 1515.78 | 40
1/27/20XX 3:00:00 PM | 0.625 | 6 | 39.7 | 48.8 | 39.7 |  | 39.7 | 68.77 | 11.23 | 424494 | 424.494 | 65.54 | 14.46 | 546588 | 546.588 | 62.31 | 17.69 | 668682 | 668.682 | 59.08 | 20.92 | 790776 | 790.776 | 55.85 | 24.15 | 912870 | 912.87 | 52.62 | 27.38 | 1034964 | 1034.964 | 49.39 | 30.61 | 1157058 | 1157.058 | 46.16 | 33.84 | 1279152 | 1279.152 | 42.93 | 37.07 | 1401246 | 1401.246 | 39.7 | 40.3 | 1523340 | 1523.34 | 40
1/27/20XX 4:00:00 PM | 0.66667 | 6 | 39.2 | 47.6 | 39.2 |  | 39.2 | 68.72 | 11.28 | 426384 | 426.384 | 65.44 | 14.56 | 550368 | 550.368 | 62.16 | 17.84 | 674352 | 674.352 | 58.88 | 21.12 | 798336 | 798.336 | 55.6 | 24.4 | 922320 | 922.32 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.04 | 30.96 | 1170288 | 1170.288 | 45.76 | 34.24 | 1294272 | 1294.272 | 42.48 | 37.52 | 1418256 | 1418.256 | 39.2 | 40.8 | 1542240 | 1542.24 | 40
1/27/20XX 5:00:00 PM | 0.70833 | 6 | 37.9 | 47.3 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
1/27/20XX 6:00:00 PM | 0.75 | 6 | 37.2 | 47.7 | 37.2 |  | 37.2 | 68.52 | 11.48 | 433944 | 433.944 | 65.04 | 14.96 | 565488 | 565.488 | 61.56 | 18.44 | 697032 | 697.032 | 58.08 | 21.92 | 828576 | 828.576 | 54.6 | 25.4 | 960120 | 960.12 | 51.12 | 28.88 | 1091664 | 1091.664 | 47.64 | 32.36 | 1223208 | 1223.208 | 44.16 | 35.84 | 1354752 | 1354.752 | 40.68 | 39.32 | 1486296 | 1486.296 | 37.2 | 42.8 | 1617840 | 1617.84 | 35
1/27/20XX 7:00:00 PM | 0.79167 | 6 | 36.9 | 46.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/27/20XX 8:00:00 PM | 0.83333 | 6 | 36.2 | 48.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/27/20XX 9:00:00 PM | 0.875 | 6 | 35.2 | 47.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/27/20XX 10:00:00 PM | 0.91667 | 6 | 34.5 | 49.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/27/20XX 11:00:00 PM | 0.95833 | 6 | 33.7 | 50.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/27/20XX 12:00:00 AM | 0 | 7 | 33.2 | 51.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/28/20XX 1:00:00 AM | 0.041667 | 7 | 32.6 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/28/20XX 2:00:00 AM | 0.083333 | 7 | 32.2 | 54.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/28/20XX 3:00:00 AM | 0.125 | 7 | 31.9 | 56.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/28/20XX 4:00:00 AM | 0.16667 | 7 | 31.2 | 57.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/28/20XX 5:00:00 AM | 0.20833 | 7 | 30.8 | 58.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/28/20XX 6:00:00 AM | 0.25 | 7 | 31 | 58.4 | 31 |  | 31 | 67.9 | 12.1 | 457380 | 457.38 | 63.8 | 16.2 | 612360 | 612.36 | 59.7 | 20.3 | 767340 | 767.34 | 55.6 | 24.4 | 922320 | 922.32 | 51.5 | 28.5 | 1077300 | 1077.3 | 47.4 | 32.6 | 1232280 | 1232.28 | 43.3 | 36.7 | 1387260 | 1387.26 | 39.2 | 40.8 | 1542240 | 1542.24 | 35.1 | 44.9 | 1697220 | 1697.22 | 31 | 49 | 1852200 | 1852.2 | 30
1/28/20XX 7:00:00 AM | 0.29167 | 7 | 30.6 | 62.1 | 30.6 |  | 30.6 | 67.86 | 12.14 | 458892 | 458.892 | 63.72 | 16.28 | 615384 | 615.384 | 59.58 | 20.42 | 771876 | 771.876 | 55.44 | 24.56 | 928368 | 928.368 | 51.3 | 28.7 | 1084860 | 1084.86 | 47.16 | 32.84 | 1241352 | 1241.352 | 43.02 | 36.98 | 1397844 | 1397.844 | 38.88 | 41.12 | 1554336 | 1554.336 | 34.74 | 45.26 | 1710828 | 1710.828 | 30.6 | 49.4 | 1867320 | 1867.32 | 30
1/28/20XX 8:00:00 AM | 0.33333 | 7 | 30.9 | 64 | 30.9 |  | 30.9 | 67.89 | 12.11 | 457758 | 457.758 | 63.78 | 16.22 | 613116 | 613.116 | 59.67 | 20.33 | 768474 | 768.474 | 55.56 | 24.44 | 923832 | 923.832 | 51.45 | 28.55 | 1079190 | 1079.19 | 47.34 | 32.66 | 1234548 | 1234.548 | 43.23 | 36.77 | 1389906 | 1389.906 | 39.12 | 40.88 | 1545264 | 1545.264 | 35.01 | 44.99 | 1700622 | 1700.622 | 30.9 | 49.1 | 1855980 | 1855.98 | 30
1/28/20XX 9:00:00 AM | 0.375 | 7 | 31.9 | 64.1 | 31.9 |  | 31.9 | 67.99 | 12.01 | 453978 | 453.978 | 63.98 | 16.02 | 605556 | 605.556 | 59.97 | 20.03 | 757134 | 757.134 | 55.96 | 24.04 | 908712 | 908.712 | 51.95 | 28.05 | 1060290 | 1060.29 | 47.94 | 32.06 | 1211868 | 1211.868 | 43.93 | 36.07 | 1363446 | 1363.446 | 39.92 | 40.08 | 1515024 | 1515.024 | 35.91 | 44.09 | 1666602 | 1666.602 | 31.9 | 48.1 | 1818180 | 1818.18 | 30
1/28/20XX 10:00:00 AM | 0.41667 | 7 | 32.2 | 67.8 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
1/28/20XX 11:00:00 AM | 0.45833 | 7 | 33.8 | 65.7 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
1/28/20XX 12:00:00 PM | 0.5 | 7 | 34.8 | 65.4 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
1/28/20XX 1:00:00 PM | 0.54167 | 7 | 36.1 | 60.5 | 36.1 |  | 36.1 | 68.41 | 11.59 | 438102 | 438.102 | 64.82 | 15.18 | 573804 | 573.804 | 61.23 | 18.77 | 709506 | 709.506 | 57.64 | 22.36 | 845208 | 845.208 | 54.05 | 25.95 | 980910 | 980.91 | 50.46 | 29.54 | 1116612 | 1116.612 | 46.87 | 33.13 | 1252314 | 1252.314 | 43.28 | 36.72 | 1388016 | 1388.016 | 39.69 | 40.31 | 1523718 | 1523.718 | 36.1 | 43.9 | 1659420 | 1659.42 | 35
1/28/20XX 2:00:00 PM | 0.58333 | 7 | 36.2 | 60.8 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
1/28/20XX 3:00:00 PM | 0.625 | 7 | 36.9 | 58.9 | 36.9 |  | 36.9 | 68.49 | 11.51 | 435078 | 435.078 | 64.98 | 15.02 | 567756 | 567.756 | 61.47 | 18.53 | 700434 | 700.434 | 57.96 | 22.04 | 833112 | 833.112 | 54.45 | 25.55 | 965790 | 965.79 | 50.94 | 29.06 | 1098468 | 1098.468 | 47.43 | 32.57 | 1231146 | 1231.146 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.41 | 39.59 | 1496502 | 1496.502 | 36.9 | 43.1 | 1629180 | 1629.18 | 35
1/28/20XX 4:00:00 PM | 0.66667 | 7 | 36.8 | 59.4 | 36.8 |  | 36.8 | 68.48 | 11.52 | 435456 | 435.456 | 64.96 | 15.04 | 568512 | 568.512 | 61.44 | 18.56 | 701568 | 701.568 | 57.92 | 22.08 | 834624 | 834.624 | 54.4 | 25.6 | 967680 | 967.68 | 50.88 | 29.12 | 1100736 | 1100.736 | 47.36 | 32.64 | 1233792 | 1233.792 | 43.84 | 36.16 | 1366848 | 1366.848 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.8 | 43.2 | 1632960 | 1632.96 | 35
1/28/20XX 5:00:00 PM | 0.70833 | 7 | 35.9 | 60.9 | 35.9 |  | 35.9 | 68.39 | 11.61 | 438858 | 438.858 | 64.78 | 15.22 | 575316 | 575.316 | 61.17 | 18.83 | 711774 | 711.774 | 57.56 | 22.44 | 848232 | 848.232 | 53.95 | 26.05 | 984690 | 984.69 | 50.34 | 29.66 | 1121148 | 1121.148 | 46.73 | 33.27 | 1257606 | 1257.606 | 43.12 | 36.88 | 1394064 | 1394.064 | 39.51 | 40.49 | 1530522 | 1530.522 | 35.9 | 44.1 | 1666980 | 1666.98 | 35
1/28/20XX 6:00:00 PM | 0.75 | 7 | 35.9 | 59.9 | 35.9 |  | 35.9 | 68.39 | 11.61 | 438858 | 438.858 | 64.78 | 15.22 | 575316 | 575.316 | 61.17 | 18.83 | 711774 | 711.774 | 57.56 | 22.44 | 848232 | 848.232 | 53.95 | 26.05 | 984690 | 984.69 | 50.34 | 29.66 | 1121148 | 1121.148 | 46.73 | 33.27 | 1257606 | 1257.606 | 43.12 | 36.88 | 1394064 | 1394.064 | 39.51 | 40.49 | 1530522 | 1530.522 | 35.9 | 44.1 | 1666980 | 1666.98 | 35
1/28/20XX 7:00:00 PM | 0.79167 | 7 | 35.5 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/28/20XX 8:00:00 PM | 0.83333 | 7 | 35.1 | 59.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/28/20XX 9:00:00 PM | 0.875 | 7 | 34.4 | 58.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/28/20XX 10:00:00 PM | 0.91667 | 7 | 34.2 | 56.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/28/20XX 11:00:00 PM | 0.95833 | 7 | 33.6 | 58.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/28/20XX 12:00:00 AM | 0 | 1 | 33.2 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/29/20XX 1:00:00 AM | 0.041667 | 1 | 32.7 | 60.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/29/20XX 2:00:00 AM | 0.083333 | 1 | 31.8 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/29/20XX 3:00:00 AM | 0.125 | 1 | 31.3 | 60.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/29/20XX 4:00:00 AM | 0.16667 | 1 | 30.4 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/29/20XX 5:00:00 AM | 0.20833 | 1 | 30.2 | 62.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/29/20XX 6:00:00 AM | 0.25 | 1 | 29.9 | 60.4 | 29.9 |  | 29.9 | 67.79 | 12.21 | 461538 | 461.538 | 63.58 | 16.42 | 620676 | 620.676 | 59.37 | 20.63 | 779814 | 779.814 | 55.16 | 24.84 | 938952 | 938.952 | 50.95 | 29.05 | 1098090 | 1098.09 | 46.74 | 33.26 | 1257228 | 1257.228 | 42.53 | 37.47 | 1416366 | 1416.366 | 38.32 | 41.68 | 1575504 | 1575.504 | 34.11 | 45.89 | 1734642 | 1734.642 | 29.9 | 50.1 | 1893780 | 1893.78 | 30
1/29/20XX 7:00:00 AM | 0.29167 | 1 | 29.9 | 58 | 29.9 |  | 29.9 | 67.79 | 12.21 | 461538 | 461.538 | 63.58 | 16.42 | 620676 | 620.676 | 59.37 | 20.63 | 779814 | 779.814 | 55.16 | 24.84 | 938952 | 938.952 | 50.95 | 29.05 | 1098090 | 1098.09 | 46.74 | 33.26 | 1257228 | 1257.228 | 42.53 | 37.47 | 1416366 | 1416.366 | 38.32 | 41.68 | 1575504 | 1575.504 | 34.11 | 45.89 | 1734642 | 1734.642 | 29.9 | 50.1 | 1893780 | 1893.78 | 30
1/29/20XX 8:00:00 AM | 0.33333 | 1 | 29.9 | 56.5 | 29.9 |  | 29.9 | 67.79 | 12.21 | 461538 | 461.538 | 63.58 | 16.42 | 620676 | 620.676 | 59.37 | 20.63 | 779814 | 779.814 | 55.16 | 24.84 | 938952 | 938.952 | 50.95 | 29.05 | 1098090 | 1098.09 | 46.74 | 33.26 | 1257228 | 1257.228 | 42.53 | 37.47 | 1416366 | 1416.366 | 38.32 | 41.68 | 1575504 | 1575.504 | 34.11 | 45.89 | 1734642 | 1734.642 | 29.9 | 50.1 | 1893780 | 1893.78 | 30
1/29/20XX 9:00:00 AM | 0.375 | 1 | 30.7 | 54.5 | 30.7 |  | 30.7 | 67.87 | 12.13 | 458514 | 458.514 | 63.74 | 16.26 | 614628 | 614.628 | 59.61 | 20.39 | 770742 | 770.742 | 55.48 | 24.52 | 926856 | 926.856 | 51.35 | 28.65 | 1082970 | 1082.97 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.09 | 36.91 | 1395198 | 1395.198 | 38.96 | 41.04 | 1551312 | 1551.312 | 34.83 | 45.17 | 1707426 | 1707.426 | 30.7 | 49.3 | 1863540 | 1863.54 | 30
1/29/20XX 10:00:00 AM | 0.41667 | 1 | 32.7 | 50.1 | 32.7 |  | 32.7 | 68.07 | 11.93 | 450954 | 450.954 | 64.14 | 15.86 | 599508 | 599.508 | 60.21 | 19.79 | 748062 | 748.062 | 56.28 | 23.72 | 896616 | 896.616 | 52.35 | 27.65 | 1045170 | 1045.17 | 48.42 | 31.58 | 1193724 | 1193.724 | 44.49 | 35.51 | 1342278 | 1342.278 | 40.56 | 39.44 | 1490832 | 1490.832 | 36.63 | 43.37 | 1639386 | 1639.386 | 32.7 | 47.3 | 1787940 | 1787.94 | 35
1/29/20XX 11:00:00 AM | 0.45833 | 1 | 33.2 | 48 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
1/29/20XX 12:00:00 PM | 0.5 | 1 | 34.4 | 46.5 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
1/29/20XX 1:00:00 PM | 0.54167 | 1 | 35.5 | 45.8 | 35.5 |  | 35.5 | 68.35 | 11.65 | 440370 | 440.37 | 64.7 | 15.3 | 578340 | 578.34 | 61.05 | 18.95 | 716310 | 716.31 | 57.4 | 22.6 | 854280 | 854.28 | 53.75 | 26.25 | 992250 | 992.25 | 50.1 | 29.9 | 1130220 | 1130.22 | 46.45 | 33.55 | 1268190 | 1268.19 | 42.8 | 37.2 | 1406160 | 1406.16 | 39.15 | 40.85 | 1544130 | 1544.13 | 35.5 | 44.5 | 1682100 | 1682.1 | 35
1/29/20XX 2:00:00 PM | 0.58333 | 1 | 35.5 | 45.2 | 35.5 |  | 35.5 | 68.35 | 11.65 | 440370 | 440.37 | 64.7 | 15.3 | 578340 | 578.34 | 61.05 | 18.95 | 716310 | 716.31 | 57.4 | 22.6 | 854280 | 854.28 | 53.75 | 26.25 | 992250 | 992.25 | 50.1 | 29.9 | 1130220 | 1130.22 | 46.45 | 33.55 | 1268190 | 1268.19 | 42.8 | 37.2 | 1406160 | 1406.16 | 39.15 | 40.85 | 1544130 | 1544.13 | 35.5 | 44.5 | 1682100 | 1682.1 | 35
1/29/20XX 3:00:00 PM | 0.625 | 1 | 35.2 | 46.9 | 35.2 |  | 35.2 | 68.32 | 11.68 | 441504 | 441.504 | 64.64 | 15.36 | 580608 | 580.608 | 60.96 | 19.04 | 719712 | 719.712 | 57.28 | 22.72 | 858816 | 858.816 | 53.6 | 26.4 | 997920 | 997.92 | 49.92 | 30.08 | 1137024 | 1137.024 | 46.24 | 33.76 | 1276128 | 1276.128 | 42.56 | 37.44 | 1415232 | 1415.232 | 38.88 | 41.12 | 1554336 | 1554.336 | 35.2 | 44.8 | 1693440 | 1693.44 | 35
1/29/20XX 4:00:00 PM | 0.66667 | 1 | 34.9 | 49 | 34.9 |  | 34.9 | 68.29 | 11.71 | 442638 | 442.638 | 64.58 | 15.42 | 582876 | 582.876 | 60.87 | 19.13 | 723114 | 723.114 | 57.16 | 22.84 | 863352 | 863.352 | 53.45 | 26.55 | 1003590 | 1003.59 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.03 | 33.97 | 1284066 | 1284.066 | 42.32 | 37.68 | 1424304 | 1424.304 | 38.61 | 41.39 | 1564542 | 1564.542 | 34.9 | 45.1 | 1704780 | 1704.78 | 35
1/29/20XX 5:00:00 PM | 0.70833 | 1 | 34.2 | 51.7 | 34.2 |  | 34.2 | 68.22 | 11.78 | 445284 | 445.284 | 64.44 | 15.56 | 588168 | 588.168 | 60.66 | 19.34 | 731052 | 731.052 | 56.88 | 23.12 | 873936 | 873.936 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.32 | 30.68 | 1159704 | 1159.704 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.98 | 42.02 | 1588356 | 1588.356 | 34.2 | 45.8 | 1731240 | 1731.24 | 35
1/29/20XX 6:00:00 PM | 0.75 | 1 | 33.4 | 54.6 | 33.4 |  | 33.4 | 68.14 | 11.86 | 448308 | 448.308 | 64.28 | 15.72 | 594216 | 594.216 | 60.42 | 19.58 | 740124 | 740.124 | 56.56 | 23.44 | 886032 | 886.032 | 52.7 | 27.3 | 1031940 | 1031.94 | 48.84 | 31.16 | 1177848 | 1177.848 | 44.98 | 35.02 | 1323756 | 1323.756 | 41.12 | 38.88 | 1469664 | 1469.664 | 37.26 | 42.74 | 1615572 | 1615.572 | 33.4 | 46.6 | 1761480 | 1761.48 | 35
1/29/20XX 7:00:00 PM | 0.79167 | 1 | 33 | 57.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/29/20XX 8:00:00 PM | 0.83333 | 1 | 32.8 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/29/20XX 9:00:00 PM | 0.875 | 1 | 32.6 | 59.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/29/20XX 10:00:00 PM | 0.91667 | 1 | 32.2 | 59.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/29/20XX 11:00:00 PM | 0.95833 | 1 | 31.4 | 60.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/29/20XX 12:00:00 AM | 0 | 2 | 30.8 | 63.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/30/20XX 1:00:00 AM | 0.041667 | 2 | 30.1 | 65.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/30/20XX 2:00:00 AM | 0.083333 | 2 | 30.1 | 64.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/30/20XX 3:00:00 AM | 0.125 | 2 | 29.9 | 66.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/30/20XX 4:00:00 AM | 0.16667 | 2 | 30.1 | 66.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/30/20XX 5:00:00 AM | 0.20833 | 2 | 29.7 | 69.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/30/20XX 6:00:00 AM | 0.25 | 2 | 29.3 | 69.4 | 29.3 |  | 29.3 | 67.73 | 12.27 | 463806 | 463.806 | 63.46 | 16.54 | 625212 | 625.212 | 59.19 | 20.81 | 786618 | 786.618 | 54.92 | 25.08 | 948024 | 948.024 | 50.65 | 29.35 | 1109430 | 1109.43 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.11 | 37.89 | 1432242 | 1432.242 | 37.84 | 42.16 | 1593648 | 1593.648 | 33.57 | 46.43 | 1755054 | 1755.054 | 29.3 | 50.7 | 1916460 | 1916.46 | 30
1/30/20XX 7:00:00 AM | 0.29167 | 2 | 29.3 | 67.9 | 29.3 |  | 29.3 | 67.73 | 12.27 | 463806 | 463.806 | 63.46 | 16.54 | 625212 | 625.212 | 59.19 | 20.81 | 786618 | 786.618 | 54.92 | 25.08 | 948024 | 948.024 | 50.65 | 29.35 | 1109430 | 1109.43 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.11 | 37.89 | 1432242 | 1432.242 | 37.84 | 42.16 | 1593648 | 1593.648 | 33.57 | 46.43 | 1755054 | 1755.054 | 29.3 | 50.7 | 1916460 | 1916.46 | 30
1/30/20XX 8:00:00 AM | 0.33333 | 2 | 29.8 | 65.6 | 29.8 |  | 29.8 | 67.78 | 12.22 | 461916 | 461.916 | 63.56 | 16.44 | 621432 | 621.432 | 59.34 | 20.66 | 780948 | 780.948 | 55.12 | 24.88 | 940464 | 940.464 | 50.9 | 29.1 | 1099980 | 1099.98 | 46.68 | 33.32 | 1259496 | 1259.496 | 42.46 | 37.54 | 1419012 | 1419.012 | 38.24 | 41.76 | 1578528 | 1578.528 | 34.02 | 45.98 | 1738044 | 1738.044 | 29.8 | 50.2 | 1897560 | 1897.56 | 30
1/30/20XX 9:00:00 AM | 0.375 | 2 | 30.5 | 64 | 30.5 |  | 30.5 | 67.85 | 12.15 | 459270 | 459.27 | 63.7 | 16.3 | 616140 | 616.14 | 59.55 | 20.45 | 773010 | 773.01 | 55.4 | 24.6 | 929880 | 929.88 | 51.25 | 28.75 | 1086750 | 1086.75 | 47.1 | 32.9 | 1243620 | 1243.62 | 42.95 | 37.05 | 1400490 | 1400.49 | 38.8 | 41.2 | 1557360 | 1557.36 | 34.65 | 45.35 | 1714230 | 1714.23 | 30.5 | 49.5 | 1871100 | 1871.1 | 30
1/30/20XX 10:00:00 AM | 0.41667 | 2 | 31.3 | 61.7 | 31.3 |  | 31.3 | 67.93 | 12.07 | 456246 | 456.246 | 63.86 | 16.14 | 610092 | 610.092 | 59.79 | 20.21 | 763938 | 763.938 | 55.72 | 24.28 | 917784 | 917.784 | 51.65 | 28.35 | 1071630 | 1071.63 | 47.58 | 32.42 | 1225476 | 1225.476 | 43.51 | 36.49 | 1379322 | 1379.322 | 39.44 | 40.56 | 1533168 | 1533.168 | 35.37 | 44.63 | 1687014 | 1687.014 | 31.3 | 48.7 | 1840860 | 1840.86 | 30
1/30/20XX 11:00:00 AM | 0.45833 | 2 | 33.1 | 58.7 | 33.1 |  | 33.1 | 68.11 | 11.89 | 449442 | 449.442 | 64.22 | 15.78 | 596484 | 596.484 | 60.33 | 19.67 | 743526 | 743.526 | 56.44 | 23.56 | 890568 | 890.568 | 52.55 | 27.45 | 1037610 | 1037.61 | 48.66 | 31.34 | 1184652 | 1184.652 | 44.77 | 35.23 | 1331694 | 1331.694 | 40.88 | 39.12 | 1478736 | 1478.736 | 36.99 | 43.01 | 1625778 | 1625.778 | 33.1 | 46.9 | 1772820 | 1772.82 | 35
1/30/20XX 12:00:00 PM | 0.5 | 2 | 34.5 | 54.4 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
1/30/20XX 1:00:00 PM | 0.54167 | 2 | 35.6 | 53.3 | 35.6 |  | 35.6 | 68.36 | 11.64 | 439992 | 439.992 | 64.72 | 15.28 | 577584 | 577.584 | 61.08 | 18.92 | 715176 | 715.176 | 57.44 | 22.56 | 852768 | 852.768 | 53.8 | 26.2 | 990360 | 990.36 | 50.16 | 29.84 | 1127952 | 1127.952 | 46.52 | 33.48 | 1265544 | 1265.544 | 42.88 | 37.12 | 1403136 | 1403.136 | 39.24 | 40.76 | 1540728 | 1540.728 | 35.6 | 44.4 | 1678320 | 1678.32 | 35
1/30/20XX 2:00:00 PM | 0.58333 | 2 | 35.8 | 51.7 | 35.8 |  | 35.8 | 68.38 | 11.62 | 439236 | 439.236 | 64.76 | 15.24 | 576072 | 576.072 | 61.14 | 18.86 | 712908 | 712.908 | 57.52 | 22.48 | 849744 | 849.744 | 53.9 | 26.1 | 986580 | 986.58 | 50.28 | 29.72 | 1123416 | 1123.416 | 46.66 | 33.34 | 1260252 | 1260.252 | 43.04 | 36.96 | 1397088 | 1397.088 | 39.42 | 40.58 | 1533924 | 1533.924 | 35.8 | 44.2 | 1670760 | 1670.76 | 35
1/30/20XX 3:00:00 PM | 0.625 | 2 | 36.1 | 50.2 | 36.1 |  | 36.1 | 68.41 | 11.59 | 438102 | 438.102 | 64.82 | 15.18 | 573804 | 573.804 | 61.23 | 18.77 | 709506 | 709.506 | 57.64 | 22.36 | 845208 | 845.208 | 54.05 | 25.95 | 980910 | 980.91 | 50.46 | 29.54 | 1116612 | 1116.612 | 46.87 | 33.13 | 1252314 | 1252.314 | 43.28 | 36.72 | 1388016 | 1388.016 | 39.69 | 40.31 | 1523718 | 1523.718 | 36.1 | 43.9 | 1659420 | 1659.42 | 35
1/30/20XX 4:00:00 PM | 0.66667 | 2 | 35.4 | 48.1 | 35.4 |  | 35.4 | 68.34 | 11.66 | 440748 | 440.748 | 64.68 | 15.32 | 579096 | 579.096 | 61.02 | 18.98 | 717444 | 717.444 | 57.36 | 22.64 | 855792 | 855.792 | 53.7 | 26.3 | 994140 | 994.14 | 50.04 | 29.96 | 1132488 | 1132.488 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.72 | 37.28 | 1409184 | 1409.184 | 39.06 | 40.94 | 1547532 | 1547.532 | 35.4 | 44.6 | 1685880 | 1685.88 | 35
1/30/20XX 5:00:00 PM | 0.70833 | 2 | 34.5 | 49.9 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
1/30/20XX 6:00:00 PM | 0.75 | 2 | 34.1 | 48.8 | 34.1 |  | 34.1 | 68.21 | 11.79 | 445662 | 445.662 | 64.42 | 15.58 | 588924 | 588.924 | 60.63 | 19.37 | 732186 | 732.186 | 56.84 | 23.16 | 875448 | 875.448 | 53.05 | 26.95 | 1018710 | 1018.71 | 49.26 | 30.74 | 1161972 | 1161.972 | 45.47 | 34.53 | 1305234 | 1305.234 | 41.68 | 38.32 | 1448496 | 1448.496 | 37.89 | 42.11 | 1591758 | 1591.758 | 34.1 | 45.9 | 1735020 | 1735.02 | 35
1/30/20XX 7:00:00 PM | 0.79167 | 2 | 33.1 | 50.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/30/20XX 8:00:00 PM | 0.83333 | 2 | 32.5 | 52.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/30/20XX 9:00:00 PM | 0.875 | 2 | 31.4 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/30/20XX 10:00:00 PM | 0.91667 | 2 | 30.9 | 52.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/30/20XX 11:00:00 PM | 0.95833 | 2 | 30.2 | 53 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/30/20XX 12:00:00 AM | 0 | 3 | 29.4 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/31/20XX 1:00:00 AM | 0.041667 | 3 | 29.5 | 54.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/31/20XX 2:00:00 AM | 0.083333 | 3 | 29.1 | 54.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/31/20XX 3:00:00 AM | 0.125 | 3 | 28.4 | 58 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/31/20XX 4:00:00 AM | 0.16667 | 3 | 28.1 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/31/20XX 5:00:00 AM | 0.20833 | 3 | 28.1 | 56.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/31/20XX 6:00:00 AM | 0.25 | 3 | 27.8 | 57.7 | 27.8 |  | 27.8 | 67.58 | 12.42 | 469476 | 469.476 | 63.16 | 16.84 | 636552 | 636.552 | 58.74 | 21.26 | 803628 | 803.628 | 54.32 | 25.68 | 970704 | 970.704 | 49.9 | 30.1 | 1137780 | 1137.78 | 45.48 | 34.52 | 1304856 | 1304.856 | 41.06 | 38.94 | 1471932 | 1471.932 | 36.64 | 43.36 | 1639008 | 1639.008 | 32.22 | 47.78 | 1806084 | 1806.084 | 27.8 | 52.2 | 1973160 | 1973.16 | 30
1/31/20XX 7:00:00 AM | 0.29167 | 3 | 27.1 | 59.6 | 27.1 |  | 27.1 | 67.51 | 12.49 | 472122 | 472.122 | 63.02 | 16.98 | 641844 | 641.844 | 58.53 | 21.47 | 811566 | 811.566 | 54.04 | 25.96 | 981288 | 981.288 | 49.55 | 30.45 | 1151010 | 1151.01 | 45.06 | 34.94 | 1320732 | 1320.732 | 40.57 | 39.43 | 1490454 | 1490.454 | 36.08 | 43.92 | 1660176 | 1660.176 | 31.59 | 48.41 | 1829898 | 1829.898 | 27.1 | 52.9 | 1999620 | 1999.62 | 25
1/31/20XX 8:00:00 AM | 0.33333 | 3 | 26.7 | 56.8 | 26.7 |  | 26.7 | 67.47 | 12.53 | 473634 | 473.634 | 62.94 | 17.06 | 644868 | 644.868 | 58.41 | 21.59 | 816102 | 816.102 | 53.88 | 26.12 | 987336 | 987.336 | 49.35 | 30.65 | 1158570 | 1158.57 | 44.82 | 35.18 | 1329804 | 1329.804 | 40.29 | 39.71 | 1501038 | 1501.038 | 35.76 | 44.24 | 1672272 | 1672.272 | 31.23 | 48.77 | 1843506 | 1843.506 | 26.7 | 53.3 | 2014740 | 2014.74 | 25
1/31/20XX 9:00:00 AM | 0.375 | 3 | 28.4 | 53.9 | 28.4 |  | 28.4 | 67.64 | 12.36 | 467208 | 467.208 | 63.28 | 16.72 | 632016 | 632.016 | 58.92 | 21.08 | 796824 | 796.824 | 54.56 | 25.44 | 961632 | 961.632 | 50.2 | 29.8 | 1126440 | 1126.44 | 45.84 | 34.16 | 1291248 | 1291.248 | 41.48 | 38.52 | 1456056 | 1456.056 | 37.12 | 42.88 | 1620864 | 1620.864 | 32.76 | 47.24 | 1785672 | 1785.672 | 28.4 | 51.6 | 1950480 | 1950.48 | 30
1/31/20XX 10:00:00 AM | 0.41667 | 3 | 29.5 | 50.4 | 29.5 |  | 29.5 | 67.75 | 12.25 | 463050 | 463.05 | 63.5 | 16.5 | 623700 | 623.7 | 59.25 | 20.75 | 784350 | 784.35 | 55 | 25 | 945000 | 945 | 50.75 | 29.25 | 1105650 | 1105.65 | 46.5 | 33.5 | 1266300 | 1266.3 | 42.25 | 37.75 | 1426950 | 1426.95 | 38 | 42 | 1587600 | 1587.6 | 33.75 | 46.25 | 1748250 | 1748.25 | 29.5 | 50.5 | 1908900 | 1908.9 | 30
1/31/20XX 11:00:00 AM | 0.45833 | 3 | 30.9 | 49.6 | 30.9 |  | 30.9 | 67.89 | 12.11 | 457758 | 457.758 | 63.78 | 16.22 | 613116 | 613.116 | 59.67 | 20.33 | 768474 | 768.474 | 55.56 | 24.44 | 923832 | 923.832 | 51.45 | 28.55 | 1079190 | 1079.19 | 47.34 | 32.66 | 1234548 | 1234.548 | 43.23 | 36.77 | 1389906 | 1389.906 | 39.12 | 40.88 | 1545264 | 1545.264 | 35.01 | 44.99 | 1700622 | 1700.622 | 30.9 | 49.1 | 1855980 | 1855.98 | 30
1/31/20XX 12:00:00 PM | 0.5 | 3 | 32.7 | 47.1 | 32.7 |  | 32.7 | 68.07 | 11.93 | 450954 | 450.954 | 64.14 | 15.86 | 599508 | 599.508 | 60.21 | 19.79 | 748062 | 748.062 | 56.28 | 23.72 | 896616 | 896.616 | 52.35 | 27.65 | 1045170 | 1045.17 | 48.42 | 31.58 | 1193724 | 1193.724 | 44.49 | 35.51 | 1342278 | 1342.278 | 40.56 | 39.44 | 1490832 | 1490.832 | 36.63 | 43.37 | 1639386 | 1639.386 | 32.7 | 47.3 | 1787940 | 1787.94 | 35
1/31/20XX 1:00:00 PM | 0.54167 | 3 | 34.7 | 45.1 | 34.7 |  | 34.7 | 68.27 | 11.73 | 443394 | 443.394 | 64.54 | 15.46 | 584388 | 584.388 | 60.81 | 19.19 | 725382 | 725.382 | 57.08 | 22.92 | 866376 | 866.376 | 53.35 | 26.65 | 1007370 | 1007.37 | 49.62 | 30.38 | 1148364 | 1148.364 | 45.89 | 34.11 | 1289358 | 1289.358 | 42.16 | 37.84 | 1430352 | 1430.352 | 38.43 | 41.57 | 1571346 | 1571.346 | 34.7 | 45.3 | 1712340 | 1712.34 | 35
1/31/20XX 2:00:00 PM | 0.58333 | 3 | 35.6 | 43.4 | 35.6 |  | 35.6 | 68.36 | 11.64 | 439992 | 439.992 | 64.72 | 15.28 | 577584 | 577.584 | 61.08 | 18.92 | 715176 | 715.176 | 57.44 | 22.56 | 852768 | 852.768 | 53.8 | 26.2 | 990360 | 990.36 | 50.16 | 29.84 | 1127952 | 1127.952 | 46.52 | 33.48 | 1265544 | 1265.544 | 42.88 | 37.12 | 1403136 | 1403.136 | 39.24 | 40.76 | 1540728 | 1540.728 | 35.6 | 44.4 | 1678320 | 1678.32 | 35
1/31/20XX 3:00:00 PM | 0.625 | 3 | 36.6 | 42.3 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
1/31/20XX 4:00:00 PM | 0.66667 | 3 | 36.7 | 43.4 | 36.7 |  | 36.7 | 68.47 | 11.53 | 435834 | 435.834 | 64.94 | 15.06 | 569268 | 569.268 | 61.41 | 18.59 | 702702 | 702.702 | 57.88 | 22.12 | 836136 | 836.136 | 54.35 | 25.65 | 969570 | 969.57 | 50.82 | 29.18 | 1103004 | 1103.004 | 47.29 | 32.71 | 1236438 | 1236.438 | 43.76 | 36.24 | 1369872 | 1369.872 | 40.23 | 39.77 | 1503306 | 1503.306 | 36.7 | 43.3 | 1636740 | 1636.74 | 35
1/31/20XX 5:00:00 PM | 0.70833 | 3 | 35.4 | 47.2 | 35.4 |  | 35.4 | 68.34 | 11.66 | 440748 | 440.748 | 64.68 | 15.32 | 579096 | 579.096 | 61.02 | 18.98 | 717444 | 717.444 | 57.36 | 22.64 | 855792 | 855.792 | 53.7 | 26.3 | 994140 | 994.14 | 50.04 | 29.96 | 1132488 | 1132.488 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.72 | 37.28 | 1409184 | 1409.184 | 39.06 | 40.94 | 1547532 | 1547.532 | 35.4 | 44.6 | 1685880 | 1685.88 | 35
1/31/20XX 6:00:00 PM | 0.75 | 3 | 34.6 | 44.1 | 34.6 |  | 34.6 | 68.26 | 11.74 | 443772 | 443.772 | 64.52 | 15.48 | 585144 | 585.144 | 60.78 | 19.22 | 726516 | 726.516 | 57.04 | 22.96 | 867888 | 867.888 | 53.3 | 26.7 | 1009260 | 1009.26 | 49.56 | 30.44 | 1150632 | 1150.632 | 45.82 | 34.18 | 1292004 | 1292.004 | 42.08 | 37.92 | 1433376 | 1433.376 | 38.34 | 41.66 | 1574748 | 1574.748 | 34.6 | 45.4 | 1716120 | 1716.12 | 35
1/31/20XX 7:00:00 PM | 0.79167 | 3 | 34 | 46.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/31/20XX 8:00:00 PM | 0.83333 | 3 | 34.1 | 45.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/31/20XX 9:00:00 PM | 0.875 | 3 | 34.1 | 47.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/31/20XX 10:00:00 PM | 0.91667 | 3 | 33.9 | 48.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/31/20XX 11:00:00 PM | 0.95833 | 3 | 33.6 | 48.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1/31/20XX 12:00:00 AM | 0 | 4 | 33.8 | 49.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/1/20XX 1:00:00 AM | 0.041667 | 4 | 33.6 | 52.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/1/20XX 2:00:00 AM | 0.083333 | 4 | 33.8 | 53 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/1/20XX 3:00:00 AM | 0.125 | 4 | 33.7 | 54 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/1/20XX 4:00:00 AM | 0.16667 | 4 | 34.2 | 54.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/1/20XX 5:00:00 AM | 0.20833 | 4 | 34.7 | 53.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/1/20XX 6:00:00 AM | 0.25 | 4 | 34.9 | 55.7 | 34.9 |  | 34.9 | 68.29 | 11.71 | 442638 | 442.638 | 64.58 | 15.42 | 582876 | 582.876 | 60.87 | 19.13 | 723114 | 723.114 | 57.16 | 22.84 | 863352 | 863.352 | 53.45 | 26.55 | 1003590 | 1003.59 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.03 | 33.97 | 1284066 | 1284.066 | 42.32 | 37.68 | 1424304 | 1424.304 | 38.61 | 41.39 | 1564542 | 1564.542 | 34.9 | 45.1 | 1704780 | 1704.78 | 35
2/1/20XX 7:00:00 AM | 0.29167 | 4 | 34.7 | 58.5 | 34.7 |  | 34.7 | 68.27 | 11.73 | 443394 | 443.394 | 64.54 | 15.46 | 584388 | 584.388 | 60.81 | 19.19 | 725382 | 725.382 | 57.08 | 22.92 | 866376 | 866.376 | 53.35 | 26.65 | 1007370 | 1007.37 | 49.62 | 30.38 | 1148364 | 1148.364 | 45.89 | 34.11 | 1289358 | 1289.358 | 42.16 | 37.84 | 1430352 | 1430.352 | 38.43 | 41.57 | 1571346 | 1571.346 | 34.7 | 45.3 | 1712340 | 1712.34 | 35
2/1/20XX 8:00:00 AM | 0.33333 | 4 | 35.2 | 58.5 | 35.2 |  | 35.2 | 68.32 | 11.68 | 441504 | 441.504 | 64.64 | 15.36 | 580608 | 580.608 | 60.96 | 19.04 | 719712 | 719.712 | 57.28 | 22.72 | 858816 | 858.816 | 53.6 | 26.4 | 997920 | 997.92 | 49.92 | 30.08 | 1137024 | 1137.024 | 46.24 | 33.76 | 1276128 | 1276.128 | 42.56 | 37.44 | 1415232 | 1415.232 | 38.88 | 41.12 | 1554336 | 1554.336 | 35.2 | 44.8 | 1693440 | 1693.44 | 35
2/1/20XX 9:00:00 AM | 0.375 | 4 | 36.2 | 57.6 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
2/1/20XX 10:00:00 AM | 0.41667 | 4 | 37.6 | 55.2 | 37.6 |  | 37.6 | 68.56 | 11.44 | 432432 | 432.432 | 65.12 | 14.88 | 562464 | 562.464 | 61.68 | 18.32 | 692496 | 692.496 | 58.24 | 21.76 | 822528 | 822.528 | 54.8 | 25.2 | 952560 | 952.56 | 51.36 | 28.64 | 1082592 | 1082.592 | 47.92 | 32.08 | 1212624 | 1212.624 | 44.48 | 35.52 | 1342656 | 1342.656 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.6 | 42.4 | 1602720 | 1602.72 | 40
2/1/20XX 11:00:00 AM | 0.45833 | 4 | 38.9 | 51.6 | 38.9 |  | 38.9 | 68.69 | 11.31 | 427518 | 427.518 | 65.38 | 14.62 | 552636 | 552.636 | 62.07 | 17.93 | 677754 | 677.754 | 58.76 | 21.24 | 802872 | 802.872 | 55.45 | 24.55 | 927990 | 927.99 | 52.14 | 27.86 | 1053108 | 1053.108 | 48.83 | 31.17 | 1178226 | 1178.226 | 45.52 | 34.48 | 1303344 | 1303.344 | 42.21 | 37.79 | 1428462 | 1428.462 | 38.9 | 41.1 | 1553580 | 1553.58 | 40
2/1/20XX 12:00:00 PM | 0.5 | 4 | 40.8 | 49.1 | 40.8 |  | 40.8 | 68.88 | 11.12 | 420336 | 420.336 | 65.76 | 14.24 | 538272 | 538.272 | 62.64 | 17.36 | 656208 | 656.208 | 59.52 | 20.48 | 774144 | 774.144 | 56.4 | 23.6 | 892080 | 892.08 | 53.28 | 26.72 | 1010016 | 1010.016 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.04 | 32.96 | 1245888 | 1245.888 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.8 | 39.2 | 1481760 | 1481.76 | 40
2/1/20XX 1:00:00 PM | 0.54167 | 4 | 42.5 | 46.9 | 42.5 |  | 42.5 | 69.05 | 10.95 | 413910 | 413.91 | 66.1 | 13.9 | 525420 | 525.42 | 63.15 | 16.85 | 636930 | 636.93 | 60.2 | 19.8 | 748440 | 748.44 | 57.25 | 22.75 | 859950 | 859.95 | 54.3 | 25.7 | 971460 | 971.46 | 51.35 | 28.65 | 1082970 | 1082.97 | 48.4 | 31.6 | 1194480 | 1194.48 | 45.45 | 34.55 | 1305990 | 1305.99 | 42.5 | 37.5 | 1417500 | 1417.5 | 40
2/1/20XX 2:00:00 PM | 0.58333 | 4 | 42.7 | 46.8 | 42.7 |  | 42.7 | 69.07 | 10.93 | 413154 | 413.154 | 66.14 | 13.86 | 523908 | 523.908 | 63.21 | 16.79 | 634662 | 634.662 | 60.28 | 19.72 | 745416 | 745.416 | 57.35 | 22.65 | 856170 | 856.17 | 54.42 | 25.58 | 966924 | 966.924 | 51.49 | 28.51 | 1077678 | 1077.678 | 48.56 | 31.44 | 1188432 | 1188.432 | 45.63 | 34.37 | 1299186 | 1299.186 | 42.7 | 37.3 | 1409940 | 1409.94 | 45
2/1/20XX 3:00:00 PM | 0.625 | 4 | 43 | 47.2 | 43 |  | 43 | 69.1 | 10.9 | 412020 | 412.02 | 66.2 | 13.8 | 521640 | 521.64 | 63.3 | 16.7 | 631260 | 631.26 | 60.4 | 19.6 | 740880 | 740.88 | 57.5 | 22.5 | 850500 | 850.5 | 54.6 | 25.4 | 960120 | 960.12 | 51.7 | 28.3 | 1069740 | 1069.74 | 48.8 | 31.2 | 1179360 | 1179.36 | 45.9 | 34.1 | 1288980 | 1288.98 | 43 | 37 | 1398600 | 1398.6 | 45
2/1/20XX 4:00:00 PM | 0.66667 | 4 | 42.4 | 47.9 | 42.4 |  | 42.4 | 69.04 | 10.96 | 414288 | 414.288 | 66.08 | 13.92 | 526176 | 526.176 | 63.12 | 16.88 | 638064 | 638.064 | 60.16 | 19.84 | 749952 | 749.952 | 57.2 | 22.8 | 861840 | 861.84 | 54.24 | 25.76 | 973728 | 973.728 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.32 | 31.68 | 1197504 | 1197.504 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.4 | 37.6 | 1421280 | 1421.28 | 40
2/1/20XX 5:00:00 PM | 0.70833 | 4 | 41.6 | 50.3 | 41.6 |  | 41.6 | 68.96 | 11.04 | 417312 | 417.312 | 65.92 | 14.08 | 532224 | 532.224 | 62.88 | 17.12 | 647136 | 647.136 | 59.84 | 20.16 | 762048 | 762.048 | 56.8 | 23.2 | 876960 | 876.96 | 53.76 | 26.24 | 991872 | 991.872 | 50.72 | 29.28 | 1106784 | 1106.784 | 47.68 | 32.32 | 1221696 | 1221.696 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.6 | 38.4 | 1451520 | 1451.52 | 40
2/1/20XX 6:00:00 PM | 0.75 | 4 | 41 | 53.2 | 41 |  | 41 | 68.9 | 11.1 | 419580 | 419.58 | 65.8 | 14.2 | 536760 | 536.76 | 62.7 | 17.3 | 653940 | 653.94 | 59.6 | 20.4 | 771120 | 771.12 | 56.5 | 23.5 | 888300 | 888.3 | 53.4 | 26.6 | 1005480 | 1005.48 | 50.3 | 29.7 | 1122660 | 1122.66 | 47.2 | 32.8 | 1239840 | 1239.84 | 44.1 | 35.9 | 1357020 | 1357.02 | 41 | 39 | 1474200 | 1474.2 | 40
2/1/20XX 7:00:00 PM | 0.79167 | 4 | 40.3 | 55.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/1/20XX 8:00:00 PM | 0.83333 | 4 | 40.1 | 55.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/1/20XX 9:00:00 PM | 0.875 | 4 | 39.7 | 55.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/1/20XX 10:00:00 PM | 0.91667 | 4 | 39.1 | 61.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/1/20XX 11:00:00 PM | 0.95833 | 4 | 38.5 | 63.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/1/20XX 12:00:00 AM | 0 | 5 | 37.9 | 64.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/2/20XX 1:00:00 AM | 0.041667 | 5 | 37 | 65.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/2/20XX 2:00:00 AM | 0.083333 | 5 | 36.2 | 66.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/2/20XX 3:00:00 AM | 0.125 | 5 | 35.6 | 66.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/2/20XX 4:00:00 AM | 0.16667 | 5 | 35.1 | 66.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/2/20XX 5:00:00 AM | 0.20833 | 5 | 34.2 | 67.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/2/20XX 6:00:00 AM | 0.25 | 5 | 34.1 | 67 | 34.1 |  | 34.1 | 68.21 | 11.79 | 445662 | 445.662 | 64.42 | 15.58 | 588924 | 588.924 | 60.63 | 19.37 | 732186 | 732.186 | 56.84 | 23.16 | 875448 | 875.448 | 53.05 | 26.95 | 1018710 | 1018.71 | 49.26 | 30.74 | 1161972 | 1161.972 | 45.47 | 34.53 | 1305234 | 1305.234 | 41.68 | 38.32 | 1448496 | 1448.496 | 37.89 | 42.11 | 1591758 | 1591.758 | 34.1 | 45.9 | 1735020 | 1735.02 | 35
2/2/20XX 7:00:00 AM | 0.29167 | 5 | 33.7 | 66.1 | 33.7 |  | 33.7 | 68.17 | 11.83 | 447174 | 447.174 | 64.34 | 15.66 | 591948 | 591.948 | 60.51 | 19.49 | 736722 | 736.722 | 56.68 | 23.32 | 881496 | 881.496 | 52.85 | 27.15 | 1026270 | 1026.27 | 49.02 | 30.98 | 1171044 | 1171.044 | 45.19 | 34.81 | 1315818 | 1315.818 | 41.36 | 38.64 | 1460592 | 1460.592 | 37.53 | 42.47 | 1605366 | 1605.366 | 33.7 | 46.3 | 1750140 | 1750.14 | 35
2/2/20XX 8:00:00 AM | 0.33333 | 5 | 33.8 | 65.6 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
2/2/20XX 9:00:00 AM | 0.375 | 5 | 34.6 | 62.5 | 34.6 |  | 34.6 | 68.26 | 11.74 | 443772 | 443.772 | 64.52 | 15.48 | 585144 | 585.144 | 60.78 | 19.22 | 726516 | 726.516 | 57.04 | 22.96 | 867888 | 867.888 | 53.3 | 26.7 | 1009260 | 1009.26 | 49.56 | 30.44 | 1150632 | 1150.632 | 45.82 | 34.18 | 1292004 | 1292.004 | 42.08 | 37.92 | 1433376 | 1433.376 | 38.34 | 41.66 | 1574748 | 1574.748 | 34.6 | 45.4 | 1716120 | 1716.12 | 35
2/2/20XX 10:00:00 AM | 0.41667 | 5 | 35.6 | 59.6 | 35.6 |  | 35.6 | 68.36 | 11.64 | 439992 | 439.992 | 64.72 | 15.28 | 577584 | 577.584 | 61.08 | 18.92 | 715176 | 715.176 | 57.44 | 22.56 | 852768 | 852.768 | 53.8 | 26.2 | 990360 | 990.36 | 50.16 | 29.84 | 1127952 | 1127.952 | 46.52 | 33.48 | 1265544 | 1265.544 | 42.88 | 37.12 | 1403136 | 1403.136 | 39.24 | 40.76 | 1540728 | 1540.728 | 35.6 | 44.4 | 1678320 | 1678.32 | 35
2/2/20XX 11:00:00 AM | 0.45833 | 5 | 36.8 | 56.1 | 36.8 |  | 36.8 | 68.48 | 11.52 | 435456 | 435.456 | 64.96 | 15.04 | 568512 | 568.512 | 61.44 | 18.56 | 701568 | 701.568 | 57.92 | 22.08 | 834624 | 834.624 | 54.4 | 25.6 | 967680 | 967.68 | 50.88 | 29.12 | 1100736 | 1100.736 | 47.36 | 32.64 | 1233792 | 1233.792 | 43.84 | 36.16 | 1366848 | 1366.848 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.8 | 43.2 | 1632960 | 1632.96 | 35
2/2/20XX 12:00:00 PM | 0.5 | 5 | 37.9 | 53.3 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
2/2/20XX 1:00:00 PM | 0.54167 | 5 | 38.6 | 49.7 | 38.6 |  | 38.6 | 68.66 | 11.34 | 428652 | 428.652 | 65.32 | 14.68 | 554904 | 554.904 | 61.98 | 18.02 | 681156 | 681.156 | 58.64 | 21.36 | 807408 | 807.408 | 55.3 | 24.7 | 933660 | 933.66 | 51.96 | 28.04 | 1059912 | 1059.912 | 48.62 | 31.38 | 1186164 | 1186.164 | 45.28 | 34.72 | 1312416 | 1312.416 | 41.94 | 38.06 | 1438668 | 1438.668 | 38.6 | 41.4 | 1564920 | 1564.92 | 40
2/2/20XX 2:00:00 PM | 0.58333 | 5 | 39.4 | 49.1 | 39.4 |  | 39.4 | 68.74 | 11.26 | 425628 | 425.628 | 65.48 | 14.52 | 548856 | 548.856 | 62.22 | 17.78 | 672084 | 672.084 | 58.96 | 21.04 | 795312 | 795.312 | 55.7 | 24.3 | 918540 | 918.54 | 52.44 | 27.56 | 1041768 | 1041.768 | 49.18 | 30.82 | 1164996 | 1164.996 | 45.92 | 34.08 | 1288224 | 1288.224 | 42.66 | 37.34 | 1411452 | 1411.452 | 39.4 | 40.6 | 1534680 | 1534.68 | 40
2/2/20XX 3:00:00 PM | 0.625 | 5 | 38.9 | 50.6 | 38.9 |  | 38.9 | 68.69 | 11.31 | 427518 | 427.518 | 65.38 | 14.62 | 552636 | 552.636 | 62.07 | 17.93 | 677754 | 677.754 | 58.76 | 21.24 | 802872 | 802.872 | 55.45 | 24.55 | 927990 | 927.99 | 52.14 | 27.86 | 1053108 | 1053.108 | 48.83 | 31.17 | 1178226 | 1178.226 | 45.52 | 34.48 | 1303344 | 1303.344 | 42.21 | 37.79 | 1428462 | 1428.462 | 38.9 | 41.1 | 1553580 | 1553.58 | 40
2/2/20XX 4:00:00 PM | 0.66667 | 5 | 38.5 | 50.1 | 38.5 |  | 38.5 | 68.65 | 11.35 | 429030 | 429.03 | 65.3 | 14.7 | 555660 | 555.66 | 61.95 | 18.05 | 682290 | 682.29 | 58.6 | 21.4 | 808920 | 808.92 | 55.25 | 24.75 | 935550 | 935.55 | 51.9 | 28.1 | 1062180 | 1062.18 | 48.55 | 31.45 | 1188810 | 1188.81 | 45.2 | 34.8 | 1315440 | 1315.44 | 41.85 | 38.15 | 1442070 | 1442.07 | 38.5 | 41.5 | 1568700 | 1568.7 | 40
2/2/20XX 5:00:00 PM | 0.70833 | 5 | 37.2 | 54.7 | 37.2 |  | 37.2 | 68.52 | 11.48 | 433944 | 433.944 | 65.04 | 14.96 | 565488 | 565.488 | 61.56 | 18.44 | 697032 | 697.032 | 58.08 | 21.92 | 828576 | 828.576 | 54.6 | 25.4 | 960120 | 960.12 | 51.12 | 28.88 | 1091664 | 1091.664 | 47.64 | 32.36 | 1223208 | 1223.208 | 44.16 | 35.84 | 1354752 | 1354.752 | 40.68 | 39.32 | 1486296 | 1486.296 | 37.2 | 42.8 | 1617840 | 1617.84 | 35
2/2/20XX 6:00:00 PM | 0.75 | 5 | 36.7 | 55.5 | 36.7 |  | 36.7 | 68.47 | 11.53 | 435834 | 435.834 | 64.94 | 15.06 | 569268 | 569.268 | 61.41 | 18.59 | 702702 | 702.702 | 57.88 | 22.12 | 836136 | 836.136 | 54.35 | 25.65 | 969570 | 969.57 | 50.82 | 29.18 | 1103004 | 1103.004 | 47.29 | 32.71 | 1236438 | 1236.438 | 43.76 | 36.24 | 1369872 | 1369.872 | 40.23 | 39.77 | 1503306 | 1503.306 | 36.7 | 43.3 | 1636740 | 1636.74 | 35
2/2/20XX 7:00:00 PM | 0.79167 | 5 | 35.4 | 57.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/2/20XX 8:00:00 PM | 0.83333 | 5 | 34.5 | 56 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/2/20XX 9:00:00 PM | 0.875 | 5 | 33 | 59.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/2/20XX 10:00:00 PM | 0.91667 | 5 | 31.7 | 62.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/2/20XX 11:00:00 PM | 0.95833 | 5 | 31 | 64 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/2/20XX 12:00:00 AM | 0 | 6 | 31 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/3/20XX 1:00:00 AM | 0.041667 | 6 | 30 | 66.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/3/20XX 2:00:00 AM | 0.083333 | 6 | 29.5 | 66.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/3/20XX 3:00:00 AM | 0.125 | 6 | 29.3 | 67.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/3/20XX 4:00:00 AM | 0.16667 | 6 | 28.8 | 68.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/3/20XX 5:00:00 AM | 0.20833 | 6 | 28.3 | 68.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/3/20XX 6:00:00 AM | 0.25 | 6 | 28.3 | 68.5 | 28.3 |  | 28.3 | 67.63 | 12.37 | 467586 | 467.586 | 63.26 | 16.74 | 632772 | 632.772 | 58.89 | 21.11 | 797958 | 797.958 | 54.52 | 25.48 | 963144 | 963.144 | 50.15 | 29.85 | 1128330 | 1128.33 | 45.78 | 34.22 | 1293516 | 1293.516 | 41.41 | 38.59 | 1458702 | 1458.702 | 37.04 | 42.96 | 1623888 | 1623.888 | 32.67 | 47.33 | 1789074 | 1789.074 | 28.3 | 51.7 | 1954260 | 1954.26 | 30
2/3/20XX 7:00:00 AM | 0.29167 | 6 | 28.3 | 67.9 | 28.3 |  | 28.3 | 67.63 | 12.37 | 467586 | 467.586 | 63.26 | 16.74 | 632772 | 632.772 | 58.89 | 21.11 | 797958 | 797.958 | 54.52 | 25.48 | 963144 | 963.144 | 50.15 | 29.85 | 1128330 | 1128.33 | 45.78 | 34.22 | 1293516 | 1293.516 | 41.41 | 38.59 | 1458702 | 1458.702 | 37.04 | 42.96 | 1623888 | 1623.888 | 32.67 | 47.33 | 1789074 | 1789.074 | 28.3 | 51.7 | 1954260 | 1954.26 | 30
2/3/20XX 8:00:00 AM | 0.33333 | 6 | 28.4 | 68.5 | 28.4 |  | 28.4 | 67.64 | 12.36 | 467208 | 467.208 | 63.28 | 16.72 | 632016 | 632.016 | 58.92 | 21.08 | 796824 | 796.824 | 54.56 | 25.44 | 961632 | 961.632 | 50.2 | 29.8 | 1126440 | 1126.44 | 45.84 | 34.16 | 1291248 | 1291.248 | 41.48 | 38.52 | 1456056 | 1456.056 | 37.12 | 42.88 | 1620864 | 1620.864 | 32.76 | 47.24 | 1785672 | 1785.672 | 28.4 | 51.6 | 1950480 | 1950.48 | 30
2/3/20XX 9:00:00 AM | 0.375 | 6 | 29.1 | 67.8 | 29.1 |  | 29.1 | 67.71 | 12.29 | 464562 | 464.562 | 63.42 | 16.58 | 626724 | 626.724 | 59.13 | 20.87 | 788886 | 788.886 | 54.84 | 25.16 | 951048 | 951.048 | 50.55 | 29.45 | 1113210 | 1113.21 | 46.26 | 33.74 | 1275372 | 1275.372 | 41.97 | 38.03 | 1437534 | 1437.534 | 37.68 | 42.32 | 1599696 | 1599.696 | 33.39 | 46.61 | 1761858 | 1761.858 | 29.1 | 50.9 | 1924020 | 1924.02 | 30
2/3/20XX 10:00:00 AM | 0.41667 | 6 | 29.8 | 66.4 | 29.8 |  | 29.8 | 67.78 | 12.22 | 461916 | 461.916 | 63.56 | 16.44 | 621432 | 621.432 | 59.34 | 20.66 | 780948 | 780.948 | 55.12 | 24.88 | 940464 | 940.464 | 50.9 | 29.1 | 1099980 | 1099.98 | 46.68 | 33.32 | 1259496 | 1259.496 | 42.46 | 37.54 | 1419012 | 1419.012 | 38.24 | 41.76 | 1578528 | 1578.528 | 34.02 | 45.98 | 1738044 | 1738.044 | 29.8 | 50.2 | 1897560 | 1897.56 | 30
2/3/20XX 11:00:00 AM | 0.45833 | 6 | 30.9 | 65 | 30.9 |  | 30.9 | 67.89 | 12.11 | 457758 | 457.758 | 63.78 | 16.22 | 613116 | 613.116 | 59.67 | 20.33 | 768474 | 768.474 | 55.56 | 24.44 | 923832 | 923.832 | 51.45 | 28.55 | 1079190 | 1079.19 | 47.34 | 32.66 | 1234548 | 1234.548 | 43.23 | 36.77 | 1389906 | 1389.906 | 39.12 | 40.88 | 1545264 | 1545.264 | 35.01 | 44.99 | 1700622 | 1700.622 | 30.9 | 49.1 | 1855980 | 1855.98 | 30
2/3/20XX 12:00:00 PM | 0.5 | 6 | 32.1 | 66.2 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
2/3/20XX 1:00:00 PM | 0.54167 | 6 | 33 | 63.4 | 33 |  | 33 | 68.1 | 11.9 | 449820 | 449.82 | 64.2 | 15.8 | 597240 | 597.24 | 60.3 | 19.7 | 744660 | 744.66 | 56.4 | 23.6 | 892080 | 892.08 | 52.5 | 27.5 | 1039500 | 1039.5 | 48.6 | 31.4 | 1186920 | 1186.92 | 44.7 | 35.3 | 1334340 | 1334.34 | 40.8 | 39.2 | 1481760 | 1481.76 | 36.9 | 43.1 | 1629180 | 1629.18 | 33 | 47 | 1776600 | 1776.6 | 35
2/3/20XX 2:00:00 PM | 0.58333 | 6 | 33.8 | 62.2 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
2/3/20XX 3:00:00 PM | 0.625 | 6 | 34.4 | 60.9 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
2/3/20XX 4:00:00 PM | 0.66667 | 6 | 34.8 | 58.8 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
2/3/20XX 5:00:00 PM | 0.70833 | 6 | 34.1 | 59.5 | 34.1 |  | 34.1 | 68.21 | 11.79 | 445662 | 445.662 | 64.42 | 15.58 | 588924 | 588.924 | 60.63 | 19.37 | 732186 | 732.186 | 56.84 | 23.16 | 875448 | 875.448 | 53.05 | 26.95 | 1018710 | 1018.71 | 49.26 | 30.74 | 1161972 | 1161.972 | 45.47 | 34.53 | 1305234 | 1305.234 | 41.68 | 38.32 | 1448496 | 1448.496 | 37.89 | 42.11 | 1591758 | 1591.758 | 34.1 | 45.9 | 1735020 | 1735.02 | 35
2/3/20XX 6:00:00 PM | 0.75 | 6 | 34 | 58.4 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
2/3/20XX 7:00:00 PM | 0.79167 | 6 | 33.5 | 59.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/3/20XX 8:00:00 PM | 0.83333 | 6 | 33 | 59.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/3/20XX 9:00:00 PM | 0.875 | 6 | 32.7 | 57.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/3/20XX 10:00:00 PM | 0.91667 | 6 | 32.4 | 58.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/3/20XX 11:00:00 PM | 0.95833 | 6 | 32.2 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/3/20XX 12:00:00 AM | 0 | 7 | 31.7 | 58.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/4/20XX 1:00:00 AM | 0.041667 | 7 | 31.6 | 57 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/4/20XX 2:00:00 AM | 0.083333 | 7 | 31.1 | 58.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/4/20XX 3:00:00 AM | 0.125 | 7 | 31 | 57.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/4/20XX 4:00:00 AM | 0.16667 | 7 | 30.7 | 56.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/4/20XX 5:00:00 AM | 0.20833 | 7 | 30.1 | 57.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/4/20XX 6:00:00 AM | 0.25 | 7 | 29.7 | 58.9 | 29.7 |  | 29.7 | 67.77 | 12.23 | 462294 | 462.294 | 63.54 | 16.46 | 622188 | 622.188 | 59.31 | 20.69 | 782082 | 782.082 | 55.08 | 24.92 | 941976 | 941.976 | 50.85 | 29.15 | 1101870 | 1101.87 | 46.62 | 33.38 | 1261764 | 1261.764 | 42.39 | 37.61 | 1421658 | 1421.658 | 38.16 | 41.84 | 1581552 | 1581.552 | 33.93 | 46.07 | 1741446 | 1741.446 | 29.7 | 50.3 | 1901340 | 1901.34 | 30
2/4/20XX 7:00:00 AM | 0.29167 | 7 | 29.6 | 58.3 | 29.6 |  | 29.6 | 67.76 | 12.24 | 462672 | 462.672 | 63.52 | 16.48 | 622944 | 622.944 | 59.28 | 20.72 | 783216 | 783.216 | 55.04 | 24.96 | 943488 | 943.488 | 50.8 | 29.2 | 1103760 | 1103.76 | 46.56 | 33.44 | 1264032 | 1264.032 | 42.32 | 37.68 | 1424304 | 1424.304 | 38.08 | 41.92 | 1584576 | 1584.576 | 33.84 | 46.16 | 1744848 | 1744.848 | 29.6 | 50.4 | 1905120 | 1905.12 | 30
2/4/20XX 8:00:00 AM | 0.33333 | 7 | 29.6 | 57.5 | 29.6 |  | 29.6 | 67.76 | 12.24 | 462672 | 462.672 | 63.52 | 16.48 | 622944 | 622.944 | 59.28 | 20.72 | 783216 | 783.216 | 55.04 | 24.96 | 943488 | 943.488 | 50.8 | 29.2 | 1103760 | 1103.76 | 46.56 | 33.44 | 1264032 | 1264.032 | 42.32 | 37.68 | 1424304 | 1424.304 | 38.08 | 41.92 | 1584576 | 1584.576 | 33.84 | 46.16 | 1744848 | 1744.848 | 29.6 | 50.4 | 1905120 | 1905.12 | 30
2/4/20XX 9:00:00 AM | 0.375 | 7 | 30.2 | 55 | 30.2 |  | 30.2 | 67.82 | 12.18 | 460404 | 460.404 | 63.64 | 16.36 | 618408 | 618.408 | 59.46 | 20.54 | 776412 | 776.412 | 55.28 | 24.72 | 934416 | 934.416 | 51.1 | 28.9 | 1092420 | 1092.42 | 46.92 | 33.08 | 1250424 | 1250.424 | 42.74 | 37.26 | 1408428 | 1408.428 | 38.56 | 41.44 | 1566432 | 1566.432 | 34.38 | 45.62 | 1724436 | 1724.436 | 30.2 | 49.8 | 1882440 | 1882.44 | 30
2/4/20XX 10:00:00 AM | 0.41667 | 7 | 31.5 | 51.5 | 31.5 |  | 31.5 | 67.95 | 12.05 | 455490 | 455.49 | 63.9 | 16.1 | 608580 | 608.58 | 59.85 | 20.15 | 761670 | 761.67 | 55.8 | 24.2 | 914760 | 914.76 | 51.75 | 28.25 | 1067850 | 1067.85 | 47.7 | 32.3 | 1220940 | 1220.94 | 43.65 | 36.35 | 1374030 | 1374.03 | 39.6 | 40.4 | 1527120 | 1527.12 | 35.55 | 44.45 | 1680210 | 1680.21 | 31.5 | 48.5 | 1833300 | 1833.3 | 30
2/4/20XX 11:00:00 AM | 0.45833 | 7 | 33.2 | 49.2 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
2/4/20XX 12:00:00 PM | 0.5 | 7 | 35.4 | 46.5 | 35.4 |  | 35.4 | 68.34 | 11.66 | 440748 | 440.748 | 64.68 | 15.32 | 579096 | 579.096 | 61.02 | 18.98 | 717444 | 717.444 | 57.36 | 22.64 | 855792 | 855.792 | 53.7 | 26.3 | 994140 | 994.14 | 50.04 | 29.96 | 1132488 | 1132.488 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.72 | 37.28 | 1409184 | 1409.184 | 39.06 | 40.94 | 1547532 | 1547.532 | 35.4 | 44.6 | 1685880 | 1685.88 | 35
2/4/20XX 1:00:00 PM | 0.54167 | 7 | 35.8 | 47.2 | 35.8 |  | 35.8 | 68.38 | 11.62 | 439236 | 439.236 | 64.76 | 15.24 | 576072 | 576.072 | 61.14 | 18.86 | 712908 | 712.908 | 57.52 | 22.48 | 849744 | 849.744 | 53.9 | 26.1 | 986580 | 986.58 | 50.28 | 29.72 | 1123416 | 1123.416 | 46.66 | 33.34 | 1260252 | 1260.252 | 43.04 | 36.96 | 1397088 | 1397.088 | 39.42 | 40.58 | 1533924 | 1533.924 | 35.8 | 44.2 | 1670760 | 1670.76 | 35
2/4/20XX 2:00:00 PM | 0.58333 | 7 | 36.3 | 46.5 | 36.3 |  | 36.3 | 68.43 | 11.57 | 437346 | 437.346 | 64.86 | 15.14 | 572292 | 572.292 | 61.29 | 18.71 | 707238 | 707.238 | 57.72 | 22.28 | 842184 | 842.184 | 54.15 | 25.85 | 977130 | 977.13 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.01 | 32.99 | 1247022 | 1247.022 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.87 | 40.13 | 1516914 | 1516.914 | 36.3 | 43.7 | 1651860 | 1651.86 | 35
2/4/20XX 3:00:00 PM | 0.625 | 7 | 36.8 | 45.8 | 36.8 |  | 36.8 | 68.48 | 11.52 | 435456 | 435.456 | 64.96 | 15.04 | 568512 | 568.512 | 61.44 | 18.56 | 701568 | 701.568 | 57.92 | 22.08 | 834624 | 834.624 | 54.4 | 25.6 | 967680 | 967.68 | 50.88 | 29.12 | 1100736 | 1100.736 | 47.36 | 32.64 | 1233792 | 1233.792 | 43.84 | 36.16 | 1366848 | 1366.848 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.8 | 43.2 | 1632960 | 1632.96 | 35
2/4/20XX 4:00:00 PM | 0.66667 | 7 | 37.1 | 45.2 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
2/4/20XX 5:00:00 PM | 0.70833 | 7 | 36.6 | 46.8 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
2/4/20XX 6:00:00 PM | 0.75 | 7 | 36.5 | 50 | 36.5 |  | 36.5 | 68.45 | 11.55 | 436590 | 436.59 | 64.9 | 15.1 | 570780 | 570.78 | 61.35 | 18.65 | 704970 | 704.97 | 57.8 | 22.2 | 839160 | 839.16 | 54.25 | 25.75 | 973350 | 973.35 | 50.7 | 29.3 | 1107540 | 1107.54 | 47.15 | 32.85 | 1241730 | 1241.73 | 43.6 | 36.4 | 1375920 | 1375.92 | 40.05 | 39.95 | 1510110 | 1510.11 | 36.5 | 43.5 | 1644300 | 1644.3 | 35
2/4/20XX 7:00:00 PM | 0.79167 | 7 | 36.6 | 49.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/4/20XX 8:00:00 PM | 0.83333 | 7 | 36.3 | 51.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/4/20XX 9:00:00 PM | 0.875 | 7 | 35.2 | 54.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/4/20XX 10:00:00 PM | 0.91667 | 7 | 35 | 54.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/4/20XX 11:00:00 PM | 0.95833 | 7 | 34.1 | 55 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/4/20XX 12:00:00 AM | 0 | 1 | 33.5 | 55.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/5/20XX 1:00:00 AM | 0.041667 | 1 | 32.6 | 58.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/5/20XX 2:00:00 AM | 0.083333 | 1 | 32.1 | 60.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/5/20XX 3:00:00 AM | 0.125 | 1 | 31.7 | 63.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/5/20XX 4:00:00 AM | 0.16667 | 1 | 31.4 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/5/20XX 5:00:00 AM | 0.20833 | 1 | 31 | 67.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/5/20XX 6:00:00 AM | 0.25 | 1 | 31.1 | 67.3 | 31.1 |  | 31.1 | 67.91 | 12.09 | 457002 | 457.002 | 63.82 | 16.18 | 611604 | 611.604 | 59.73 | 20.27 | 766206 | 766.206 | 55.64 | 24.36 | 920808 | 920.808 | 51.55 | 28.45 | 1075410 | 1075.41 | 47.46 | 32.54 | 1230012 | 1230.012 | 43.37 | 36.63 | 1384614 | 1384.614 | 39.28 | 40.72 | 1539216 | 1539.216 | 35.19 | 44.81 | 1693818 | 1693.818 | 31.1 | 48.9 | 1848420 | 1848.42 | 30
2/5/20XX 7:00:00 AM | 0.29167 | 1 | 30.5 | 68.9 | 30.5 |  | 30.5 | 67.85 | 12.15 | 459270 | 459.27 | 63.7 | 16.3 | 616140 | 616.14 | 59.55 | 20.45 | 773010 | 773.01 | 55.4 | 24.6 | 929880 | 929.88 | 51.25 | 28.75 | 1086750 | 1086.75 | 47.1 | 32.9 | 1243620 | 1243.62 | 42.95 | 37.05 | 1400490 | 1400.49 | 38.8 | 41.2 | 1557360 | 1557.36 | 34.65 | 45.35 | 1714230 | 1714.23 | 30.5 | 49.5 | 1871100 | 1871.1 | 30
2/5/20XX 8:00:00 AM | 0.33333 | 1 | 30.6 | 69.1 | 30.6 |  | 30.6 | 67.86 | 12.14 | 458892 | 458.892 | 63.72 | 16.28 | 615384 | 615.384 | 59.58 | 20.42 | 771876 | 771.876 | 55.44 | 24.56 | 928368 | 928.368 | 51.3 | 28.7 | 1084860 | 1084.86 | 47.16 | 32.84 | 1241352 | 1241.352 | 43.02 | 36.98 | 1397844 | 1397.844 | 38.88 | 41.12 | 1554336 | 1554.336 | 34.74 | 45.26 | 1710828 | 1710.828 | 30.6 | 49.4 | 1867320 | 1867.32 | 30
2/5/20XX 9:00:00 AM | 0.375 | 1 | 30.2 | 67.1 | 30.2 |  | 30.2 | 67.82 | 12.18 | 460404 | 460.404 | 63.64 | 16.36 | 618408 | 618.408 | 59.46 | 20.54 | 776412 | 776.412 | 55.28 | 24.72 | 934416 | 934.416 | 51.1 | 28.9 | 1092420 | 1092.42 | 46.92 | 33.08 | 1250424 | 1250.424 | 42.74 | 37.26 | 1408428 | 1408.428 | 38.56 | 41.44 | 1566432 | 1566.432 | 34.38 | 45.62 | 1724436 | 1724.436 | 30.2 | 49.8 | 1882440 | 1882.44 | 30
2/5/20XX 10:00:00 AM | 0.41667 | 1 | 30.2 | 64.7 | 30.2 |  | 30.2 | 67.82 | 12.18 | 460404 | 460.404 | 63.64 | 16.36 | 618408 | 618.408 | 59.46 | 20.54 | 776412 | 776.412 | 55.28 | 24.72 | 934416 | 934.416 | 51.1 | 28.9 | 1092420 | 1092.42 | 46.92 | 33.08 | 1250424 | 1250.424 | 42.74 | 37.26 | 1408428 | 1408.428 | 38.56 | 41.44 | 1566432 | 1566.432 | 34.38 | 45.62 | 1724436 | 1724.436 | 30.2 | 49.8 | 1882440 | 1882.44 | 30
2/5/20XX 11:00:00 AM | 0.45833 | 1 | 31.1 | 63.1 | 31.1 |  | 31.1 | 67.91 | 12.09 | 457002 | 457.002 | 63.82 | 16.18 | 611604 | 611.604 | 59.73 | 20.27 | 766206 | 766.206 | 55.64 | 24.36 | 920808 | 920.808 | 51.55 | 28.45 | 1075410 | 1075.41 | 47.46 | 32.54 | 1230012 | 1230.012 | 43.37 | 36.63 | 1384614 | 1384.614 | 39.28 | 40.72 | 1539216 | 1539.216 | 35.19 | 44.81 | 1693818 | 1693.818 | 31.1 | 48.9 | 1848420 | 1848.42 | 30
2/5/20XX 12:00:00 PM | 0.5 | 1 | 31.4 | 60.1 | 31.4 |  | 31.4 | 67.94 | 12.06 | 455868 | 455.868 | 63.88 | 16.12 | 609336 | 609.336 | 59.82 | 20.18 | 762804 | 762.804 | 55.76 | 24.24 | 916272 | 916.272 | 51.7 | 28.3 | 1069740 | 1069.74 | 47.64 | 32.36 | 1223208 | 1223.208 | 43.58 | 36.42 | 1376676 | 1376.676 | 39.52 | 40.48 | 1530144 | 1530.144 | 35.46 | 44.54 | 1683612 | 1683.612 | 31.4 | 48.6 | 1837080 | 1837.08 | 30
2/5/20XX 1:00:00 PM | 0.54167 | 1 | 31.9 | 59.4 | 31.9 |  | 31.9 | 67.99 | 12.01 | 453978 | 453.978 | 63.98 | 16.02 | 605556 | 605.556 | 59.97 | 20.03 | 757134 | 757.134 | 55.96 | 24.04 | 908712 | 908.712 | 51.95 | 28.05 | 1060290 | 1060.29 | 47.94 | 32.06 | 1211868 | 1211.868 | 43.93 | 36.07 | 1363446 | 1363.446 | 39.92 | 40.08 | 1515024 | 1515.024 | 35.91 | 44.09 | 1666602 | 1666.602 | 31.9 | 48.1 | 1818180 | 1818.18 | 30
2/5/20XX 2:00:00 PM | 0.58333 | 1 | 32.6 | 57 | 32.6 |  | 32.6 | 68.06 | 11.94 | 451332 | 451.332 | 64.12 | 15.88 | 600264 | 600.264 | 60.18 | 19.82 | 749196 | 749.196 | 56.24 | 23.76 | 898128 | 898.128 | 52.3 | 27.7 | 1047060 | 1047.06 | 48.36 | 31.64 | 1195992 | 1195.992 | 44.42 | 35.58 | 1344924 | 1344.924 | 40.48 | 39.52 | 1493856 | 1493.856 | 36.54 | 43.46 | 1642788 | 1642.788 | 32.6 | 47.4 | 1791720 | 1791.72 | 35
2/5/20XX 3:00:00 PM | 0.625 | 1 | 33.2 | 54.8 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
2/5/20XX 4:00:00 PM | 0.66667 | 1 | 33.1 | 53.4 | 33.1 |  | 33.1 | 68.11 | 11.89 | 449442 | 449.442 | 64.22 | 15.78 | 596484 | 596.484 | 60.33 | 19.67 | 743526 | 743.526 | 56.44 | 23.56 | 890568 | 890.568 | 52.55 | 27.45 | 1037610 | 1037.61 | 48.66 | 31.34 | 1184652 | 1184.652 | 44.77 | 35.23 | 1331694 | 1331.694 | 40.88 | 39.12 | 1478736 | 1478.736 | 36.99 | 43.01 | 1625778 | 1625.778 | 33.1 | 46.9 | 1772820 | 1772.82 | 35
2/5/20XX 5:00:00 PM | 0.70833 | 1 | 32.7 | 54.5 | 32.7 |  | 32.7 | 68.07 | 11.93 | 450954 | 450.954 | 64.14 | 15.86 | 599508 | 599.508 | 60.21 | 19.79 | 748062 | 748.062 | 56.28 | 23.72 | 896616 | 896.616 | 52.35 | 27.65 | 1045170 | 1045.17 | 48.42 | 31.58 | 1193724 | 1193.724 | 44.49 | 35.51 | 1342278 | 1342.278 | 40.56 | 39.44 | 1490832 | 1490.832 | 36.63 | 43.37 | 1639386 | 1639.386 | 32.7 | 47.3 | 1787940 | 1787.94 | 35
2/5/20XX 6:00:00 PM | 0.75 | 1 | 32.1 | 54.4 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
2/5/20XX 7:00:00 PM | 0.79167 | 1 | 31.8 | 56 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/5/20XX 8:00:00 PM | 0.83333 | 1 | 31.4 | 55.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/5/20XX 9:00:00 PM | 0.875 | 1 | 31.4 | 57.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/5/20XX 10:00:00 PM | 0.91667 | 1 | 30.5 | 57.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/5/20XX 11:00:00 PM | 0.95833 | 1 | 30.7 | 57.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/5/20XX 12:00:00 AM | 0 | 2 | 30 | 59.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/6/20XX 1:00:00 AM | 0.041667 | 2 | 29.7 | 58.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/6/20XX 2:00:00 AM | 0.083333 | 2 | 29.2 | 59.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/6/20XX 3:00:00 AM | 0.125 | 2 | 29.1 | 59.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/6/20XX 4:00:00 AM | 0.16667 | 2 | 29.1 | 59.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/6/20XX 5:00:00 AM | 0.20833 | 2 | 28.8 | 57.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/6/20XX 6:00:00 AM | 0.25 | 2 | 28.2 | 57.8 | 28.2 |  | 28.2 | 67.62 | 12.38 | 467964 | 467.964 | 63.24 | 16.76 | 633528 | 633.528 | 58.86 | 21.14 | 799092 | 799.092 | 54.48 | 25.52 | 964656 | 964.656 | 50.1 | 29.9 | 1130220 | 1130.22 | 45.72 | 34.28 | 1295784 | 1295.784 | 41.34 | 38.66 | 1461348 | 1461.348 | 36.96 | 43.04 | 1626912 | 1626.912 | 32.58 | 47.42 | 1792476 | 1792.476 | 28.2 | 51.8 | 1958040 | 1958.04 | 30
2/6/20XX 7:00:00 AM | 0.29167 | 2 | 27.9 | 59.2 | 27.9 |  | 27.9 | 67.59 | 12.41 | 469098 | 469.098 | 63.18 | 16.82 | 635796 | 635.796 | 58.77 | 21.23 | 802494 | 802.494 | 54.36 | 25.64 | 969192 | 969.192 | 49.95 | 30.05 | 1135890 | 1135.89 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.13 | 38.87 | 1469286 | 1469.286 | 36.72 | 43.28 | 1635984 | 1635.984 | 32.31 | 47.69 | 1802682 | 1802.682 | 27.9 | 52.1 | 1969380 | 1969.38 | 30
2/6/20XX 8:00:00 AM | 0.33333 | 2 | 27.9 | 57.1 | 27.9 |  | 27.9 | 67.59 | 12.41 | 469098 | 469.098 | 63.18 | 16.82 | 635796 | 635.796 | 58.77 | 21.23 | 802494 | 802.494 | 54.36 | 25.64 | 969192 | 969.192 | 49.95 | 30.05 | 1135890 | 1135.89 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.13 | 38.87 | 1469286 | 1469.286 | 36.72 | 43.28 | 1635984 | 1635.984 | 32.31 | 47.69 | 1802682 | 1802.682 | 27.9 | 52.1 | 1969380 | 1969.38 | 30
2/6/20XX 9:00:00 AM | 0.375 | 2 | 28.8 | 54.7 | 28.8 |  | 28.8 | 67.68 | 12.32 | 465696 | 465.696 | 63.36 | 16.64 | 628992 | 628.992 | 59.04 | 20.96 | 792288 | 792.288 | 54.72 | 25.28 | 955584 | 955.584 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.08 | 33.92 | 1282176 | 1282.176 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.44 | 42.56 | 1608768 | 1608.768 | 33.12 | 46.88 | 1772064 | 1772.064 | 28.8 | 51.2 | 1935360 | 1935.36 | 30
2/6/20XX 10:00:00 AM | 0.41667 | 2 | 30 | 52.8 | 30 |  | 30 | 67.8 | 12.2 | 461160 | 461.16 | 63.6 | 16.4 | 619920 | 619.92 | 59.4 | 20.6 | 778680 | 778.68 | 55.2 | 24.8 | 937440 | 937.44 | 51 | 29 | 1096200 | 1096.2 | 46.8 | 33.2 | 1254960 | 1254.96 | 42.6 | 37.4 | 1413720 | 1413.72 | 38.4 | 41.6 | 1572480 | 1572.48 | 34.2 | 45.8 | 1731240 | 1731.24 | 30 | 50 | 1890000 | 1890 | 30
2/6/20XX 11:00:00 AM | 0.45833 | 2 | 31.8 | 50.4 | 31.8 |  | 31.8 | 67.98 | 12.02 | 454356 | 454.356 | 63.96 | 16.04 | 606312 | 606.312 | 59.94 | 20.06 | 758268 | 758.268 | 55.92 | 24.08 | 910224 | 910.224 | 51.9 | 28.1 | 1062180 | 1062.18 | 47.88 | 32.12 | 1214136 | 1214.136 | 43.86 | 36.14 | 1366092 | 1366.092 | 39.84 | 40.16 | 1518048 | 1518.048 | 35.82 | 44.18 | 1670004 | 1670.004 | 31.8 | 48.2 | 1821960 | 1821.96 | 30
2/6/20XX 12:00:00 PM | 0.5 | 2 | 33.6 | 48.5 | 33.6 |  | 33.6 | 68.16 | 11.84 | 447552 | 447.552 | 64.32 | 15.68 | 592704 | 592.704 | 60.48 | 19.52 | 737856 | 737.856 | 56.64 | 23.36 | 883008 | 883.008 | 52.8 | 27.2 | 1028160 | 1028.16 | 48.96 | 31.04 | 1173312 | 1173.312 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.28 | 38.72 | 1463616 | 1463.616 | 37.44 | 42.56 | 1608768 | 1608.768 | 33.6 | 46.4 | 1753920 | 1753.92 | 35
2/6/20XX 1:00:00 PM | 0.54167 | 2 | 34.5 | 47.1 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
2/6/20XX 2:00:00 PM | 0.58333 | 2 | 35.6 | 44.5 | 35.6 |  | 35.6 | 68.36 | 11.64 | 439992 | 439.992 | 64.72 | 15.28 | 577584 | 577.584 | 61.08 | 18.92 | 715176 | 715.176 | 57.44 | 22.56 | 852768 | 852.768 | 53.8 | 26.2 | 990360 | 990.36 | 50.16 | 29.84 | 1127952 | 1127.952 | 46.52 | 33.48 | 1265544 | 1265.544 | 42.88 | 37.12 | 1403136 | 1403.136 | 39.24 | 40.76 | 1540728 | 1540.728 | 35.6 | 44.4 | 1678320 | 1678.32 | 35
2/6/20XX 3:00:00 PM | 0.625 | 2 | 37 | 41.8 | 37 |  | 37 | 68.5 | 11.5 | 434700 | 434.7 | 65 | 15 | 567000 | 567 | 61.5 | 18.5 | 699300 | 699.3 | 58 | 22 | 831600 | 831.6 | 54.5 | 25.5 | 963900 | 963.9 | 51 | 29 | 1096200 | 1096.2 | 47.5 | 32.5 | 1228500 | 1228.5 | 44 | 36 | 1360800 | 1360.8 | 40.5 | 39.5 | 1493100 | 1493.1 | 37 | 43 | 1625400 | 1625.4 | 35
2/6/20XX 4:00:00 PM | 0.66667 | 2 | 36.9 | 43.4 | 36.9 |  | 36.9 | 68.49 | 11.51 | 435078 | 435.078 | 64.98 | 15.02 | 567756 | 567.756 | 61.47 | 18.53 | 700434 | 700.434 | 57.96 | 22.04 | 833112 | 833.112 | 54.45 | 25.55 | 965790 | 965.79 | 50.94 | 29.06 | 1098468 | 1098.468 | 47.43 | 32.57 | 1231146 | 1231.146 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.41 | 39.59 | 1496502 | 1496.502 | 36.9 | 43.1 | 1629180 | 1629.18 | 35
2/6/20XX 5:00:00 PM | 0.70833 | 2 | 35.9 | 44.4 | 35.9 |  | 35.9 | 68.39 | 11.61 | 438858 | 438.858 | 64.78 | 15.22 | 575316 | 575.316 | 61.17 | 18.83 | 711774 | 711.774 | 57.56 | 22.44 | 848232 | 848.232 | 53.95 | 26.05 | 984690 | 984.69 | 50.34 | 29.66 | 1121148 | 1121.148 | 46.73 | 33.27 | 1257606 | 1257.606 | 43.12 | 36.88 | 1394064 | 1394.064 | 39.51 | 40.49 | 1530522 | 1530.522 | 35.9 | 44.1 | 1666980 | 1666.98 | 35
2/6/20XX 6:00:00 PM | 0.75 | 2 | 35.3 | 46.3 | 35.3 |  | 35.3 | 68.33 | 11.67 | 441126 | 441.126 | 64.66 | 15.34 | 579852 | 579.852 | 60.99 | 19.01 | 718578 | 718.578 | 57.32 | 22.68 | 857304 | 857.304 | 53.65 | 26.35 | 996030 | 996.03 | 49.98 | 30.02 | 1134756 | 1134.756 | 46.31 | 33.69 | 1273482 | 1273.482 | 42.64 | 37.36 | 1412208 | 1412.208 | 38.97 | 41.03 | 1550934 | 1550.934 | 35.3 | 44.7 | 1689660 | 1689.66 | 35
2/6/20XX 7:00:00 PM | 0.79167 | 2 | 34.8 | 47.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/6/20XX 8:00:00 PM | 0.83333 | 2 | 34.2 | 49.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/6/20XX 9:00:00 PM | 0.875 | 2 | 33.9 | 50.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/6/20XX 10:00:00 PM | 0.91667 | 2 | 33.7 | 49.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/6/20XX 11:00:00 PM | 0.95833 | 2 | 33.2 | 49.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/6/20XX 12:00:00 AM | 0 | 3 | 32.4 | 52.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/7/20XX 1:00:00 AM | 0.041667 | 3 | 31.9 | 54.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/7/20XX 2:00:00 AM | 0.083333 | 3 | 31.5 | 55.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/7/20XX 3:00:00 AM | 0.125 | 3 | 31 | 56.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/7/20XX 4:00:00 AM | 0.16667 | 3 | 30.9 | 57.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/7/20XX 5:00:00 AM | 0.20833 | 3 | 30.3 | 59.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/7/20XX 6:00:00 AM | 0.25 | 3 | 30.3 | 58.9 | 30.3 |  | 30.3 | 67.83 | 12.17 | 460026 | 460.026 | 63.66 | 16.34 | 617652 | 617.652 | 59.49 | 20.51 | 775278 | 775.278 | 55.32 | 24.68 | 932904 | 932.904 | 51.15 | 28.85 | 1090530 | 1090.53 | 46.98 | 33.02 | 1248156 | 1248.156 | 42.81 | 37.19 | 1405782 | 1405.782 | 38.64 | 41.36 | 1563408 | 1563.408 | 34.47 | 45.53 | 1721034 | 1721.034 | 30.3 | 49.7 | 1878660 | 1878.66 | 30
2/7/20XX 7:00:00 AM | 0.29167 | 3 | 30.6 | 59.3 | 30.6 |  | 30.6 | 67.86 | 12.14 | 458892 | 458.892 | 63.72 | 16.28 | 615384 | 615.384 | 59.58 | 20.42 | 771876 | 771.876 | 55.44 | 24.56 | 928368 | 928.368 | 51.3 | 28.7 | 1084860 | 1084.86 | 47.16 | 32.84 | 1241352 | 1241.352 | 43.02 | 36.98 | 1397844 | 1397.844 | 38.88 | 41.12 | 1554336 | 1554.336 | 34.74 | 45.26 | 1710828 | 1710.828 | 30.6 | 49.4 | 1867320 | 1867.32 | 30
2/7/20XX 8:00:00 AM | 0.33333 | 3 | 31 | 61.3 | 31 |  | 31 | 67.9 | 12.1 | 457380 | 457.38 | 63.8 | 16.2 | 612360 | 612.36 | 59.7 | 20.3 | 767340 | 767.34 | 55.6 | 24.4 | 922320 | 922.32 | 51.5 | 28.5 | 1077300 | 1077.3 | 47.4 | 32.6 | 1232280 | 1232.28 | 43.3 | 36.7 | 1387260 | 1387.26 | 39.2 | 40.8 | 1542240 | 1542.24 | 35.1 | 44.9 | 1697220 | 1697.22 | 31 | 49 | 1852200 | 1852.2 | 30
2/7/20XX 9:00:00 AM | 0.375 | 3 | 32.2 | 60 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
2/7/20XX 10:00:00 AM | 0.41667 | 3 | 33.6 | 58.2 | 33.6 |  | 33.6 | 68.16 | 11.84 | 447552 | 447.552 | 64.32 | 15.68 | 592704 | 592.704 | 60.48 | 19.52 | 737856 | 737.856 | 56.64 | 23.36 | 883008 | 883.008 | 52.8 | 27.2 | 1028160 | 1028.16 | 48.96 | 31.04 | 1173312 | 1173.312 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.28 | 38.72 | 1463616 | 1463.616 | 37.44 | 42.56 | 1608768 | 1608.768 | 33.6 | 46.4 | 1753920 | 1753.92 | 35
2/7/20XX 11:00:00 AM | 0.45833 | 3 | 35 | 57.2 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
2/7/20XX 12:00:00 PM | 0.5 | 3 | 35.9 | 57.5 | 35.9 |  | 35.9 | 68.39 | 11.61 | 438858 | 438.858 | 64.78 | 15.22 | 575316 | 575.316 | 61.17 | 18.83 | 711774 | 711.774 | 57.56 | 22.44 | 848232 | 848.232 | 53.95 | 26.05 | 984690 | 984.69 | 50.34 | 29.66 | 1121148 | 1121.148 | 46.73 | 33.27 | 1257606 | 1257.606 | 43.12 | 36.88 | 1394064 | 1394.064 | 39.51 | 40.49 | 1530522 | 1530.522 | 35.9 | 44.1 | 1666980 | 1666.98 | 35
2/7/20XX 1:00:00 PM | 0.54167 | 3 | 37.4 | 55.1 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
2/7/20XX 2:00:00 PM | 0.58333 | 3 | 38.2 | 53.9 | 38.2 |  | 38.2 | 68.62 | 11.38 | 430164 | 430.164 | 65.24 | 14.76 | 557928 | 557.928 | 61.86 | 18.14 | 685692 | 685.692 | 58.48 | 21.52 | 813456 | 813.456 | 55.1 | 24.9 | 941220 | 941.22 | 51.72 | 28.28 | 1068984 | 1068.984 | 48.34 | 31.66 | 1196748 | 1196.748 | 44.96 | 35.04 | 1324512 | 1324.512 | 41.58 | 38.42 | 1452276 | 1452.276 | 38.2 | 41.8 | 1580040 | 1580.04 | 40
2/7/20XX 3:00:00 PM | 0.625 | 3 | 38.3 | 55 | 38.3 |  | 38.3 | 68.63 | 11.37 | 429786 | 429.786 | 65.26 | 14.74 | 557172 | 557.172 | 61.89 | 18.11 | 684558 | 684.558 | 58.52 | 21.48 | 811944 | 811.944 | 55.15 | 24.85 | 939330 | 939.33 | 51.78 | 28.22 | 1066716 | 1066.716 | 48.41 | 31.59 | 1194102 | 1194.102 | 45.04 | 34.96 | 1321488 | 1321.488 | 41.67 | 38.33 | 1448874 | 1448.874 | 38.3 | 41.7 | 1576260 | 1576.26 | 40
2/7/20XX 4:00:00 PM | 0.66667 | 3 | 38 | 56 | 38 |  | 38 | 68.6 | 11.4 | 430920 | 430.92 | 65.2 | 14.8 | 559440 | 559.44 | 61.8 | 18.2 | 687960 | 687.96 | 58.4 | 21.6 | 816480 | 816.48 | 55 | 25 | 945000 | 945 | 51.6 | 28.4 | 1073520 | 1073.52 | 48.2 | 31.8 | 1202040 | 1202.04 | 44.8 | 35.2 | 1330560 | 1330.56 | 41.4 | 38.6 | 1459080 | 1459.08 | 38 | 42 | 1587600 | 1587.6 | 40
2/7/20XX 5:00:00 PM | 0.70833 | 3 | 38.2 | 56.8 | 38.2 |  | 38.2 | 68.62 | 11.38 | 430164 | 430.164 | 65.24 | 14.76 | 557928 | 557.928 | 61.86 | 18.14 | 685692 | 685.692 | 58.48 | 21.52 | 813456 | 813.456 | 55.1 | 24.9 | 941220 | 941.22 | 51.72 | 28.28 | 1068984 | 1068.984 | 48.34 | 31.66 | 1196748 | 1196.748 | 44.96 | 35.04 | 1324512 | 1324.512 | 41.58 | 38.42 | 1452276 | 1452.276 | 38.2 | 41.8 | 1580040 | 1580.04 | 40
2/7/20XX 6:00:00 PM | 0.75 | 3 | 37.7 | 61.3 | 37.7 |  | 37.7 | 68.57 | 11.43 | 432054 | 432.054 | 65.14 | 14.86 | 561708 | 561.708 | 61.71 | 18.29 | 691362 | 691.362 | 58.28 | 21.72 | 821016 | 821.016 | 54.85 | 25.15 | 950670 | 950.67 | 51.42 | 28.58 | 1080324 | 1080.324 | 47.99 | 32.01 | 1209978 | 1209.978 | 44.56 | 35.44 | 1339632 | 1339.632 | 41.13 | 38.87 | 1469286 | 1469.286 | 37.7 | 42.3 | 1598940 | 1598.94 | 40
2/7/20XX 7:00:00 PM | 0.79167 | 3 | 37.3 | 63.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/7/20XX 8:00:00 PM | 0.83333 | 3 | 36.7 | 63.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/7/20XX 9:00:00 PM | 0.875 | 3 | 36.5 | 66.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/7/20XX 10:00:00 PM | 0.91667 | 3 | 36.2 | 67.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/7/20XX 11:00:00 PM | 0.95833 | 3 | 36.2 | 65.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/7/20XX 12:00:00 AM | 0 | 4 | 35.5 | 65.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/8/20XX 1:00:00 AM | 0.041667 | 4 | 35.7 | 64.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/8/20XX 2:00:00 AM | 0.083333 | 4 | 34.7 | 65.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/8/20XX 3:00:00 AM | 0.125 | 4 | 34.5 | 66.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/8/20XX 4:00:00 AM | 0.16667 | 4 | 33.8 | 68 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/8/20XX 5:00:00 AM | 0.20833 | 4 | 34 | 68.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/8/20XX 6:00:00 AM | 0.25 | 4 | 33.8 | 69.1 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
2/8/20XX 7:00:00 AM | 0.29167 | 4 | 34.2 | 68.3 | 34.2 |  | 34.2 | 68.22 | 11.78 | 445284 | 445.284 | 64.44 | 15.56 | 588168 | 588.168 | 60.66 | 19.34 | 731052 | 731.052 | 56.88 | 23.12 | 873936 | 873.936 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.32 | 30.68 | 1159704 | 1159.704 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.98 | 42.02 | 1588356 | 1588.356 | 34.2 | 45.8 | 1731240 | 1731.24 | 35
2/8/20XX 8:00:00 AM | 0.33333 | 4 | 34.5 | 67.4 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
2/8/20XX 9:00:00 AM | 0.375 | 4 | 35.4 | 65.1 | 35.4 |  | 35.4 | 68.34 | 11.66 | 440748 | 440.748 | 64.68 | 15.32 | 579096 | 579.096 | 61.02 | 18.98 | 717444 | 717.444 | 57.36 | 22.64 | 855792 | 855.792 | 53.7 | 26.3 | 994140 | 994.14 | 50.04 | 29.96 | 1132488 | 1132.488 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.72 | 37.28 | 1409184 | 1409.184 | 39.06 | 40.94 | 1547532 | 1547.532 | 35.4 | 44.6 | 1685880 | 1685.88 | 35
2/8/20XX 10:00:00 AM | 0.41667 | 4 | 36.2 | 62.2 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
2/8/20XX 11:00:00 AM | 0.45833 | 4 | 36.7 | 59.8 | 36.7 |  | 36.7 | 68.47 | 11.53 | 435834 | 435.834 | 64.94 | 15.06 | 569268 | 569.268 | 61.41 | 18.59 | 702702 | 702.702 | 57.88 | 22.12 | 836136 | 836.136 | 54.35 | 25.65 | 969570 | 969.57 | 50.82 | 29.18 | 1103004 | 1103.004 | 47.29 | 32.71 | 1236438 | 1236.438 | 43.76 | 36.24 | 1369872 | 1369.872 | 40.23 | 39.77 | 1503306 | 1503.306 | 36.7 | 43.3 | 1636740 | 1636.74 | 35
2/8/20XX 12:00:00 PM | 0.5 | 4 | 37.3 | 58.7 | 37.3 |  | 37.3 | 68.53 | 11.47 | 433566 | 433.566 | 65.06 | 14.94 | 564732 | 564.732 | 61.59 | 18.41 | 695898 | 695.898 | 58.12 | 21.88 | 827064 | 827.064 | 54.65 | 25.35 | 958230 | 958.23 | 51.18 | 28.82 | 1089396 | 1089.396 | 47.71 | 32.29 | 1220562 | 1220.562 | 44.24 | 35.76 | 1351728 | 1351.728 | 40.77 | 39.23 | 1482894 | 1482.894 | 37.3 | 42.7 | 1614060 | 1614.06 | 35
2/8/20XX 1:00:00 PM | 0.54167 | 4 | 37.4 | 55.6 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
2/8/20XX 2:00:00 PM | 0.58333 | 4 | 37.4 | 53.1 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
2/8/20XX 3:00:00 PM | 0.625 | 4 | 37.2 | 53.5 | 37.2 |  | 37.2 | 68.52 | 11.48 | 433944 | 433.944 | 65.04 | 14.96 | 565488 | 565.488 | 61.56 | 18.44 | 697032 | 697.032 | 58.08 | 21.92 | 828576 | 828.576 | 54.6 | 25.4 | 960120 | 960.12 | 51.12 | 28.88 | 1091664 | 1091.664 | 47.64 | 32.36 | 1223208 | 1223.208 | 44.16 | 35.84 | 1354752 | 1354.752 | 40.68 | 39.32 | 1486296 | 1486.296 | 37.2 | 42.8 | 1617840 | 1617.84 | 35
2/8/20XX 4:00:00 PM | 0.66667 | 4 | 36.6 | 54.5 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
2/8/20XX 5:00:00 PM | 0.70833 | 4 | 35.6 | 57.4 | 35.6 |  | 35.6 | 68.36 | 11.64 | 439992 | 439.992 | 64.72 | 15.28 | 577584 | 577.584 | 61.08 | 18.92 | 715176 | 715.176 | 57.44 | 22.56 | 852768 | 852.768 | 53.8 | 26.2 | 990360 | 990.36 | 50.16 | 29.84 | 1127952 | 1127.952 | 46.52 | 33.48 | 1265544 | 1265.544 | 42.88 | 37.12 | 1403136 | 1403.136 | 39.24 | 40.76 | 1540728 | 1540.728 | 35.6 | 44.4 | 1678320 | 1678.32 | 35
2/8/20XX 6:00:00 PM | 0.75 | 4 | 34.8 | 58.5 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
2/8/20XX 7:00:00 PM | 0.79167 | 4 | 33.8 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/8/20XX 8:00:00 PM | 0.83333 | 4 | 32.9 | 60.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/8/20XX 9:00:00 PM | 0.875 | 4 | 32.2 | 60.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/8/20XX 10:00:00 PM | 0.91667 | 4 | 31.3 | 63.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/8/20XX 11:00:00 PM | 0.95833 | 4 | 30.9 | 62.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/8/20XX 12:00:00 AM | 0 | 5 | 29.5 | 64.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/9/20XX 1:00:00 AM | 0.041667 | 5 | 29.2 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/9/20XX 2:00:00 AM | 0.083333 | 5 | 28.7 | 65.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/9/20XX 3:00:00 AM | 0.125 | 5 | 28.5 | 66.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/9/20XX 4:00:00 AM | 0.16667 | 5 | 28.4 | 64.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/9/20XX 5:00:00 AM | 0.20833 | 5 | 27.2 | 67.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/9/20XX 6:00:00 AM | 0.25 | 5 | 27.1 | 67.3 | 27.1 |  | 27.1 | 67.51 | 12.49 | 472122 | 472.122 | 63.02 | 16.98 | 641844 | 641.844 | 58.53 | 21.47 | 811566 | 811.566 | 54.04 | 25.96 | 981288 | 981.288 | 49.55 | 30.45 | 1151010 | 1151.01 | 45.06 | 34.94 | 1320732 | 1320.732 | 40.57 | 39.43 | 1490454 | 1490.454 | 36.08 | 43.92 | 1660176 | 1660.176 | 31.59 | 48.41 | 1829898 | 1829.898 | 27.1 | 52.9 | 1999620 | 1999.62 | 25
2/9/20XX 7:00:00 AM | 0.29167 | 5 | 26.6 | 69.1 | 26.6 |  | 26.6 | 67.46 | 12.54 | 474012 | 474.012 | 62.92 | 17.08 | 645624 | 645.624 | 58.38 | 21.62 | 817236 | 817.236 | 53.84 | 26.16 | 988848 | 988.848 | 49.3 | 30.7 | 1160460 | 1160.46 | 44.76 | 35.24 | 1332072 | 1332.072 | 40.22 | 39.78 | 1503684 | 1503.684 | 35.68 | 44.32 | 1675296 | 1675.296 | 31.14 | 48.86 | 1846908 | 1846.908 | 26.6 | 53.4 | 2018520 | 2018.52 | 25
2/9/20XX 8:00:00 AM | 0.33333 | 5 | 27 | 67.3 | 27 |  | 27 | 67.5 | 12.5 | 472500 | 472.5 | 63 | 17 | 642600 | 642.6 | 58.5 | 21.5 | 812700 | 812.7 | 54 | 26 | 982800 | 982.8 | 49.5 | 30.5 | 1152900 | 1152.9 | 45 | 35 | 1323000 | 1323 | 40.5 | 39.5 | 1493100 | 1493.1 | 36 | 44 | 1663200 | 1663.2 | 31.5 | 48.5 | 1833300 | 1833.3 | 27 | 53 | 2003400 | 2003.4 | 25
2/9/20XX 9:00:00 AM | 0.375 | 5 | 27.6 | 65.8 | 27.6 |  | 27.6 | 67.56 | 12.44 | 470232 | 470.232 | 63.12 | 16.88 | 638064 | 638.064 | 58.68 | 21.32 | 805896 | 805.896 | 54.24 | 25.76 | 973728 | 973.728 | 49.8 | 30.2 | 1141560 | 1141.56 | 45.36 | 34.64 | 1309392 | 1309.392 | 40.92 | 39.08 | 1477224 | 1477.224 | 36.48 | 43.52 | 1645056 | 1645.056 | 32.04 | 47.96 | 1812888 | 1812.888 | 27.6 | 52.4 | 1980720 | 1980.72 | 30
2/9/20XX 10:00:00 AM | 0.41667 | 5 | 28.4 | 63 | 28.4 |  | 28.4 | 67.64 | 12.36 | 467208 | 467.208 | 63.28 | 16.72 | 632016 | 632.016 | 58.92 | 21.08 | 796824 | 796.824 | 54.56 | 25.44 | 961632 | 961.632 | 50.2 | 29.8 | 1126440 | 1126.44 | 45.84 | 34.16 | 1291248 | 1291.248 | 41.48 | 38.52 | 1456056 | 1456.056 | 37.12 | 42.88 | 1620864 | 1620.864 | 32.76 | 47.24 | 1785672 | 1785.672 | 28.4 | 51.6 | 1950480 | 1950.48 | 30
2/9/20XX 11:00:00 AM | 0.45833 | 5 | 30 | 59.2 | 30 |  | 30 | 67.8 | 12.2 | 461160 | 461.16 | 63.6 | 16.4 | 619920 | 619.92 | 59.4 | 20.6 | 778680 | 778.68 | 55.2 | 24.8 | 937440 | 937.44 | 51 | 29 | 1096200 | 1096.2 | 46.8 | 33.2 | 1254960 | 1254.96 | 42.6 | 37.4 | 1413720 | 1413.72 | 38.4 | 41.6 | 1572480 | 1572.48 | 34.2 | 45.8 | 1731240 | 1731.24 | 30 | 50 | 1890000 | 1890 | 30
2/9/20XX 12:00:00 PM | 0.5 | 5 | 31.8 | 55.6 | 31.8 |  | 31.8 | 67.98 | 12.02 | 454356 | 454.356 | 63.96 | 16.04 | 606312 | 606.312 | 59.94 | 20.06 | 758268 | 758.268 | 55.92 | 24.08 | 910224 | 910.224 | 51.9 | 28.1 | 1062180 | 1062.18 | 47.88 | 32.12 | 1214136 | 1214.136 | 43.86 | 36.14 | 1366092 | 1366.092 | 39.84 | 40.16 | 1518048 | 1518.048 | 35.82 | 44.18 | 1670004 | 1670.004 | 31.8 | 48.2 | 1821960 | 1821.96 | 30
2/9/20XX 1:00:00 PM | 0.54167 | 5 | 33.1 | 53.5 | 33.1 |  | 33.1 | 68.11 | 11.89 | 449442 | 449.442 | 64.22 | 15.78 | 596484 | 596.484 | 60.33 | 19.67 | 743526 | 743.526 | 56.44 | 23.56 | 890568 | 890.568 | 52.55 | 27.45 | 1037610 | 1037.61 | 48.66 | 31.34 | 1184652 | 1184.652 | 44.77 | 35.23 | 1331694 | 1331.694 | 40.88 | 39.12 | 1478736 | 1478.736 | 36.99 | 43.01 | 1625778 | 1625.778 | 33.1 | 46.9 | 1772820 | 1772.82 | 35
2/9/20XX 2:00:00 PM | 0.58333 | 5 | 33.7 | 50.4 | 33.7 |  | 33.7 | 68.17 | 11.83 | 447174 | 447.174 | 64.34 | 15.66 | 591948 | 591.948 | 60.51 | 19.49 | 736722 | 736.722 | 56.68 | 23.32 | 881496 | 881.496 | 52.85 | 27.15 | 1026270 | 1026.27 | 49.02 | 30.98 | 1171044 | 1171.044 | 45.19 | 34.81 | 1315818 | 1315.818 | 41.36 | 38.64 | 1460592 | 1460.592 | 37.53 | 42.47 | 1605366 | 1605.366 | 33.7 | 46.3 | 1750140 | 1750.14 | 35
2/9/20XX 3:00:00 PM | 0.625 | 5 | 34.1 | 49.9 | 34.1 |  | 34.1 | 68.21 | 11.79 | 445662 | 445.662 | 64.42 | 15.58 | 588924 | 588.924 | 60.63 | 19.37 | 732186 | 732.186 | 56.84 | 23.16 | 875448 | 875.448 | 53.05 | 26.95 | 1018710 | 1018.71 | 49.26 | 30.74 | 1161972 | 1161.972 | 45.47 | 34.53 | 1305234 | 1305.234 | 41.68 | 38.32 | 1448496 | 1448.496 | 37.89 | 42.11 | 1591758 | 1591.758 | 34.1 | 45.9 | 1735020 | 1735.02 | 35
2/9/20XX 4:00:00 PM | 0.66667 | 5 | 34.2 | 47.1 | 34.2 |  | 34.2 | 68.22 | 11.78 | 445284 | 445.284 | 64.44 | 15.56 | 588168 | 588.168 | 60.66 | 19.34 | 731052 | 731.052 | 56.88 | 23.12 | 873936 | 873.936 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.32 | 30.68 | 1159704 | 1159.704 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.98 | 42.02 | 1588356 | 1588.356 | 34.2 | 45.8 | 1731240 | 1731.24 | 35
2/9/20XX 5:00:00 PM | 0.70833 | 5 | 33.9 | 46.8 | 33.9 |  | 33.9 | 68.19 | 11.81 | 446418 | 446.418 | 64.38 | 15.62 | 590436 | 590.436 | 60.57 | 19.43 | 734454 | 734.454 | 56.76 | 23.24 | 878472 | 878.472 | 52.95 | 27.05 | 1022490 | 1022.49 | 49.14 | 30.86 | 1166508 | 1166.508 | 45.33 | 34.67 | 1310526 | 1310.526 | 41.52 | 38.48 | 1454544 | 1454.544 | 37.71 | 42.29 | 1598562 | 1598.562 | 33.9 | 46.1 | 1742580 | 1742.58 | 35
2/9/20XX 6:00:00 PM | 0.75 | 5 | 33 | 50.6 | 33 |  | 33 | 68.1 | 11.9 | 449820 | 449.82 | 64.2 | 15.8 | 597240 | 597.24 | 60.3 | 19.7 | 744660 | 744.66 | 56.4 | 23.6 | 892080 | 892.08 | 52.5 | 27.5 | 1039500 | 1039.5 | 48.6 | 31.4 | 1186920 | 1186.92 | 44.7 | 35.3 | 1334340 | 1334.34 | 40.8 | 39.2 | 1481760 | 1481.76 | 36.9 | 43.1 | 1629180 | 1629.18 | 33 | 47 | 1776600 | 1776.6 | 35
2/9/20XX 7:00:00 PM | 0.79167 | 5 | 32.7 | 53.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/9/20XX 8:00:00 PM | 0.83333 | 5 | 32.3 | 54.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/9/20XX 9:00:00 PM | 0.875 | 5 | 31.4 | 56.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/9/20XX 10:00:00 PM | 0.91667 | 5 | 31.2 | 58.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/9/20XX 11:00:00 PM | 0.95833 | 5 | 31 | 61 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/9/20XX 12:00:00 AM | 0 | 6 | 30.7 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/10/20XX 1:00:00 AM | 0.041667 | 6 | 30.6 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/10/20XX 2:00:00 AM | 0.083333 | 6 | 30.7 | 64.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/10/20XX 3:00:00 AM | 0.125 | 6 | 30.5 | 64.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/10/20XX 4:00:00 AM | 0.16667 | 6 | 29.8 | 67.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/10/20XX 5:00:00 AM | 0.20833 | 6 | 29.5 | 66.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/10/20XX 6:00:00 AM | 0.25 | 6 | 29 | 67.2 | 29 |  | 29 | 67.7 | 12.3 | 464940 | 464.94 | 63.4 | 16.6 | 627480 | 627.48 | 59.1 | 20.9 | 790020 | 790.02 | 54.8 | 25.2 | 952560 | 952.56 | 50.5 | 29.5 | 1115100 | 1115.1 | 46.2 | 33.8 | 1277640 | 1277.64 | 41.9 | 38.1 | 1440180 | 1440.18 | 37.6 | 42.4 | 1602720 | 1602.72 | 33.3 | 46.7 | 1765260 | 1765.26 | 29 | 51 | 1927800 | 1927.8 | 30
2/10/20XX 7:00:00 AM | 0.29167 | 6 | 28.5 | 67.4 | 28.5 |  | 28.5 | 67.65 | 12.35 | 466830 | 466.83 | 63.3 | 16.7 | 631260 | 631.26 | 58.95 | 21.05 | 795690 | 795.69 | 54.6 | 25.4 | 960120 | 960.12 | 50.25 | 29.75 | 1124550 | 1124.55 | 45.9 | 34.1 | 1288980 | 1288.98 | 41.55 | 38.45 | 1453410 | 1453.41 | 37.2 | 42.8 | 1617840 | 1617.84 | 32.85 | 47.15 | 1782270 | 1782.27 | 28.5 | 51.5 | 1946700 | 1946.7 | 30
2/10/20XX 8:00:00 AM | 0.33333 | 6 | 29.3 | 65.8 | 29.3 |  | 29.3 | 67.73 | 12.27 | 463806 | 463.806 | 63.46 | 16.54 | 625212 | 625.212 | 59.19 | 20.81 | 786618 | 786.618 | 54.92 | 25.08 | 948024 | 948.024 | 50.65 | 29.35 | 1109430 | 1109.43 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.11 | 37.89 | 1432242 | 1432.242 | 37.84 | 42.16 | 1593648 | 1593.648 | 33.57 | 46.43 | 1755054 | 1755.054 | 29.3 | 50.7 | 1916460 | 1916.46 | 30
2/10/20XX 9:00:00 AM | 0.375 | 6 | 30.2 | 64.3 | 30.2 |  | 30.2 | 67.82 | 12.18 | 460404 | 460.404 | 63.64 | 16.36 | 618408 | 618.408 | 59.46 | 20.54 | 776412 | 776.412 | 55.28 | 24.72 | 934416 | 934.416 | 51.1 | 28.9 | 1092420 | 1092.42 | 46.92 | 33.08 | 1250424 | 1250.424 | 42.74 | 37.26 | 1408428 | 1408.428 | 38.56 | 41.44 | 1566432 | 1566.432 | 34.38 | 45.62 | 1724436 | 1724.436 | 30.2 | 49.8 | 1882440 | 1882.44 | 30
2/10/20XX 10:00:00 AM | 0.41667 | 6 | 31.3 | 61.5 | 31.3 |  | 31.3 | 67.93 | 12.07 | 456246 | 456.246 | 63.86 | 16.14 | 610092 | 610.092 | 59.79 | 20.21 | 763938 | 763.938 | 55.72 | 24.28 | 917784 | 917.784 | 51.65 | 28.35 | 1071630 | 1071.63 | 47.58 | 32.42 | 1225476 | 1225.476 | 43.51 | 36.49 | 1379322 | 1379.322 | 39.44 | 40.56 | 1533168 | 1533.168 | 35.37 | 44.63 | 1687014 | 1687.014 | 31.3 | 48.7 | 1840860 | 1840.86 | 30
2/10/20XX 11:00:00 AM | 0.45833 | 6 | 33.1 | 59 | 33.1 |  | 33.1 | 68.11 | 11.89 | 449442 | 449.442 | 64.22 | 15.78 | 596484 | 596.484 | 60.33 | 19.67 | 743526 | 743.526 | 56.44 | 23.56 | 890568 | 890.568 | 52.55 | 27.45 | 1037610 | 1037.61 | 48.66 | 31.34 | 1184652 | 1184.652 | 44.77 | 35.23 | 1331694 | 1331.694 | 40.88 | 39.12 | 1478736 | 1478.736 | 36.99 | 43.01 | 1625778 | 1625.778 | 33.1 | 46.9 | 1772820 | 1772.82 | 35
2/10/20XX 12:00:00 PM | 0.5 | 6 | 34.6 | 55.7 | 34.6 |  | 34.6 | 68.26 | 11.74 | 443772 | 443.772 | 64.52 | 15.48 | 585144 | 585.144 | 60.78 | 19.22 | 726516 | 726.516 | 57.04 | 22.96 | 867888 | 867.888 | 53.3 | 26.7 | 1009260 | 1009.26 | 49.56 | 30.44 | 1150632 | 1150.632 | 45.82 | 34.18 | 1292004 | 1292.004 | 42.08 | 37.92 | 1433376 | 1433.376 | 38.34 | 41.66 | 1574748 | 1574.748 | 34.6 | 45.4 | 1716120 | 1716.12 | 35
2/10/20XX 1:00:00 PM | 0.54167 | 6 | 36.2 | 54.9 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
2/10/20XX 2:00:00 PM | 0.58333 | 6 | 36.6 | 53.8 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
2/10/20XX 3:00:00 PM | 0.625 | 6 | 36.9 | 54 | 36.9 |  | 36.9 | 68.49 | 11.51 | 435078 | 435.078 | 64.98 | 15.02 | 567756 | 567.756 | 61.47 | 18.53 | 700434 | 700.434 | 57.96 | 22.04 | 833112 | 833.112 | 54.45 | 25.55 | 965790 | 965.79 | 50.94 | 29.06 | 1098468 | 1098.468 | 47.43 | 32.57 | 1231146 | 1231.146 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.41 | 39.59 | 1496502 | 1496.502 | 36.9 | 43.1 | 1629180 | 1629.18 | 35
2/10/20XX 4:00:00 PM | 0.66667 | 6 | 36.6 | 53.8 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
2/10/20XX 5:00:00 PM | 0.70833 | 6 | 36.6 | 54.9 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
2/10/20XX 6:00:00 PM | 0.75 | 6 | 35 | 57.3 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
2/10/20XX 7:00:00 PM | 0.79167 | 6 | 34.7 | 57.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/10/20XX 8:00:00 PM | 0.83333 | 6 | 33.9 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/10/20XX 9:00:00 PM | 0.875 | 6 | 33.4 | 63 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/10/20XX 10:00:00 PM | 0.91667 | 6 | 32.9 | 66.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/10/20XX 11:00:00 PM | 0.95833 | 6 | 32.8 | 66.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/10/20XX 12:00:00 AM | 0 | 7 | 32.9 | 64.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/11/20XX 1:00:00 AM | 0.041667 | 7 | 32.9 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/11/20XX 2:00:00 AM | 0.083333 | 7 | 32.8 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/11/20XX 3:00:00 AM | 0.125 | 7 | 32.5 | 67.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/11/20XX 4:00:00 AM | 0.16667 | 7 | 31.7 | 66.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/11/20XX 5:00:00 AM | 0.20833 | 7 | 32 | 65.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/11/20XX 6:00:00 AM | 0.25 | 7 | 31.9 | 65.9 | 31.9 |  | 31.9 | 67.99 | 12.01 | 453978 | 453.978 | 63.98 | 16.02 | 605556 | 605.556 | 59.97 | 20.03 | 757134 | 757.134 | 55.96 | 24.04 | 908712 | 908.712 | 51.95 | 28.05 | 1060290 | 1060.29 | 47.94 | 32.06 | 1211868 | 1211.868 | 43.93 | 36.07 | 1363446 | 1363.446 | 39.92 | 40.08 | 1515024 | 1515.024 | 35.91 | 44.09 | 1666602 | 1666.602 | 31.9 | 48.1 | 1818180 | 1818.18 | 30
2/11/20XX 7:00:00 AM | 0.29167 | 7 | 31.7 | 66.6 | 31.7 |  | 31.7 | 67.97 | 12.03 | 454734 | 454.734 | 63.94 | 16.06 | 607068 | 607.068 | 59.91 | 20.09 | 759402 | 759.402 | 55.88 | 24.12 | 911736 | 911.736 | 51.85 | 28.15 | 1064070 | 1064.07 | 47.82 | 32.18 | 1216404 | 1216.404 | 43.79 | 36.21 | 1368738 | 1368.738 | 39.76 | 40.24 | 1521072 | 1521.072 | 35.73 | 44.27 | 1673406 | 1673.406 | 31.7 | 48.3 | 1825740 | 1825.74 | 30
2/11/20XX 8:00:00 AM | 0.33333 | 7 | 31.4 | 67.2 | 31.4 |  | 31.4 | 67.94 | 12.06 | 455868 | 455.868 | 63.88 | 16.12 | 609336 | 609.336 | 59.82 | 20.18 | 762804 | 762.804 | 55.76 | 24.24 | 916272 | 916.272 | 51.7 | 28.3 | 1069740 | 1069.74 | 47.64 | 32.36 | 1223208 | 1223.208 | 43.58 | 36.42 | 1376676 | 1376.676 | 39.52 | 40.48 | 1530144 | 1530.144 | 35.46 | 44.54 | 1683612 | 1683.612 | 31.4 | 48.6 | 1837080 | 1837.08 | 30
2/11/20XX 9:00:00 AM | 0.375 | 7 | 32.7 | 65.5 | 32.7 |  | 32.7 | 68.07 | 11.93 | 450954 | 450.954 | 64.14 | 15.86 | 599508 | 599.508 | 60.21 | 19.79 | 748062 | 748.062 | 56.28 | 23.72 | 896616 | 896.616 | 52.35 | 27.65 | 1045170 | 1045.17 | 48.42 | 31.58 | 1193724 | 1193.724 | 44.49 | 35.51 | 1342278 | 1342.278 | 40.56 | 39.44 | 1490832 | 1490.832 | 36.63 | 43.37 | 1639386 | 1639.386 | 32.7 | 47.3 | 1787940 | 1787.94 | 35
2/11/20XX 10:00:00 AM | 0.41667 | 7 | 34 | 62.9 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
2/11/20XX 11:00:00 AM | 0.45833 | 7 | 35.1 | 61.7 | 35.1 |  | 35.1 | 68.31 | 11.69 | 441882 | 441.882 | 64.62 | 15.38 | 581364 | 581.364 | 60.93 | 19.07 | 720846 | 720.846 | 57.24 | 22.76 | 860328 | 860.328 | 53.55 | 26.45 | 999810 | 999.81 | 49.86 | 30.14 | 1139292 | 1139.292 | 46.17 | 33.83 | 1278774 | 1278.774 | 42.48 | 37.52 | 1418256 | 1418.256 | 38.79 | 41.21 | 1557738 | 1557.738 | 35.1 | 44.9 | 1697220 | 1697.22 | 35
2/11/20XX 12:00:00 PM | 0.5 | 7 | 36.6 | 58.9 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
2/11/20XX 1:00:00 PM | 0.54167 | 7 | 38.1 | 56.7 | 38.1 |  | 38.1 | 68.61 | 11.39 | 430542 | 430.542 | 65.22 | 14.78 | 558684 | 558.684 | 61.83 | 18.17 | 686826 | 686.826 | 58.44 | 21.56 | 814968 | 814.968 | 55.05 | 24.95 | 943110 | 943.11 | 51.66 | 28.34 | 1071252 | 1071.252 | 48.27 | 31.73 | 1199394 | 1199.394 | 44.88 | 35.12 | 1327536 | 1327.536 | 41.49 | 38.51 | 1455678 | 1455.678 | 38.1 | 41.9 | 1583820 | 1583.82 | 40
2/11/20XX 2:00:00 PM | 0.58333 | 7 | 38.6 | 54.7 | 38.6 |  | 38.6 | 68.66 | 11.34 | 428652 | 428.652 | 65.32 | 14.68 | 554904 | 554.904 | 61.98 | 18.02 | 681156 | 681.156 | 58.64 | 21.36 | 807408 | 807.408 | 55.3 | 24.7 | 933660 | 933.66 | 51.96 | 28.04 | 1059912 | 1059.912 | 48.62 | 31.38 | 1186164 | 1186.164 | 45.28 | 34.72 | 1312416 | 1312.416 | 41.94 | 38.06 | 1438668 | 1438.668 | 38.6 | 41.4 | 1564920 | 1564.92 | 40
2/11/20XX 3:00:00 PM | 0.625 | 7 | 38.8 | 55.8 | 38.8 |  | 38.8 | 68.68 | 11.32 | 427896 | 427.896 | 65.36 | 14.64 | 553392 | 553.392 | 62.04 | 17.96 | 678888 | 678.888 | 58.72 | 21.28 | 804384 | 804.384 | 55.4 | 24.6 | 929880 | 929.88 | 52.08 | 27.92 | 1055376 | 1055.376 | 48.76 | 31.24 | 1180872 | 1180.872 | 45.44 | 34.56 | 1306368 | 1306.368 | 42.12 | 37.88 | 1431864 | 1431.864 | 38.8 | 41.2 | 1557360 | 1557.36 | 40
2/11/20XX 4:00:00 PM | 0.66667 | 7 | 39.7 | 54.4 | 39.7 |  | 39.7 | 68.77 | 11.23 | 424494 | 424.494 | 65.54 | 14.46 | 546588 | 546.588 | 62.31 | 17.69 | 668682 | 668.682 | 59.08 | 20.92 | 790776 | 790.776 | 55.85 | 24.15 | 912870 | 912.87 | 52.62 | 27.38 | 1034964 | 1034.964 | 49.39 | 30.61 | 1157058 | 1157.058 | 46.16 | 33.84 | 1279152 | 1279.152 | 42.93 | 37.07 | 1401246 | 1401.246 | 39.7 | 40.3 | 1523340 | 1523.34 | 40
2/11/20XX 5:00:00 PM | 0.70833 | 7 | 39.6 | 54.4 | 39.6 |  | 39.6 | 68.76 | 11.24 | 424872 | 424.872 | 65.52 | 14.48 | 547344 | 547.344 | 62.28 | 17.72 | 669816 | 669.816 | 59.04 | 20.96 | 792288 | 792.288 | 55.8 | 24.2 | 914760 | 914.76 | 52.56 | 27.44 | 1037232 | 1037.232 | 49.32 | 30.68 | 1159704 | 1159.704 | 46.08 | 33.92 | 1282176 | 1282.176 | 42.84 | 37.16 | 1404648 | 1404.648 | 39.6 | 40.4 | 1527120 | 1527.12 | 40
2/11/20XX 6:00:00 PM | 0.75 | 7 | 38.6 | 55.8 | 38.6 |  | 38.6 | 68.66 | 11.34 | 428652 | 428.652 | 65.32 | 14.68 | 554904 | 554.904 | 61.98 | 18.02 | 681156 | 681.156 | 58.64 | 21.36 | 807408 | 807.408 | 55.3 | 24.7 | 933660 | 933.66 | 51.96 | 28.04 | 1059912 | 1059.912 | 48.62 | 31.38 | 1186164 | 1186.164 | 45.28 | 34.72 | 1312416 | 1312.416 | 41.94 | 38.06 | 1438668 | 1438.668 | 38.6 | 41.4 | 1564920 | 1564.92 | 40
2/11/20XX 7:00:00 PM | 0.79167 | 7 | 37.8 | 56.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/11/20XX 8:00:00 PM | 0.83333 | 7 | 37 | 58.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/11/20XX 9:00:00 PM | 0.875 | 7 | 36.4 | 58.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/11/20XX 10:00:00 PM | 0.91667 | 7 | 35.8 | 60.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/11/20XX 11:00:00 PM | 0.95833 | 7 | 35.3 | 61.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/11/20XX 12:00:00 AM | 0 | 1 | 34.6 | 63.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/12/20XX 1:00:00 AM | 0.041667 | 1 | 34.8 | 64.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/12/20XX 2:00:00 AM | 0.083333 | 1 | 34.1 | 62 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/12/20XX 3:00:00 AM | 0.125 | 1 | 33.8 | 59.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/12/20XX 4:00:00 AM | 0.16667 | 1 | 33 | 58.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/12/20XX 5:00:00 AM | 0.20833 | 1 | 32.2 | 61.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/12/20XX 6:00:00 AM | 0.25 | 1 | 32 | 60.1 | 32 |  | 32 | 68 | 12 | 453600 | 453.6 | 64 | 16 | 604800 | 604.8 | 60 | 20 | 756000 | 756 | 56 | 24 | 907200 | 907.2 | 52 | 28 | 1058400 | 1058.4 | 48 | 32 | 1209600 | 1209.6 | 44 | 36 | 1360800 | 1360.8 | 40 | 40 | 1512000 | 1512 | 36 | 44 | 1663200 | 1663.2 | 32 | 48 | 1814400 | 1814.4 | 30
2/12/20XX 7:00:00 AM | 0.29167 | 1 | 31.2 | 59.6 | 31.2 |  | 31.2 | 67.92 | 12.08 | 456624 | 456.624 | 63.84 | 16.16 | 610848 | 610.848 | 59.76 | 20.24 | 765072 | 765.072 | 55.68 | 24.32 | 919296 | 919.296 | 51.6 | 28.4 | 1073520 | 1073.52 | 47.52 | 32.48 | 1227744 | 1227.744 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.36 | 40.64 | 1536192 | 1536.192 | 35.28 | 44.72 | 1690416 | 1690.416 | 31.2 | 48.8 | 1844640 | 1844.64 | 30
2/12/20XX 8:00:00 AM | 0.33333 | 1 | 30.6 | 59.7 | 30.6 |  | 30.6 | 67.86 | 12.14 | 458892 | 458.892 | 63.72 | 16.28 | 615384 | 615.384 | 59.58 | 20.42 | 771876 | 771.876 | 55.44 | 24.56 | 928368 | 928.368 | 51.3 | 28.7 | 1084860 | 1084.86 | 47.16 | 32.84 | 1241352 | 1241.352 | 43.02 | 36.98 | 1397844 | 1397.844 | 38.88 | 41.12 | 1554336 | 1554.336 | 34.74 | 45.26 | 1710828 | 1710.828 | 30.6 | 49.4 | 1867320 | 1867.32 | 30
2/12/20XX 9:00:00 AM | 0.375 | 1 | 31.5 | 57.8 | 31.5 |  | 31.5 | 67.95 | 12.05 | 455490 | 455.49 | 63.9 | 16.1 | 608580 | 608.58 | 59.85 | 20.15 | 761670 | 761.67 | 55.8 | 24.2 | 914760 | 914.76 | 51.75 | 28.25 | 1067850 | 1067.85 | 47.7 | 32.3 | 1220940 | 1220.94 | 43.65 | 36.35 | 1374030 | 1374.03 | 39.6 | 40.4 | 1527120 | 1527.12 | 35.55 | 44.45 | 1680210 | 1680.21 | 31.5 | 48.5 | 1833300 | 1833.3 | 30
2/12/20XX 10:00:00 AM | 0.41667 | 1 | 32.4 | 55.9 | 32.4 |  | 32.4 | 68.04 | 11.96 | 452088 | 452.088 | 64.08 | 15.92 | 601776 | 601.776 | 60.12 | 19.88 | 751464 | 751.464 | 56.16 | 23.84 | 901152 | 901.152 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.24 | 31.76 | 1200528 | 1200.528 | 44.28 | 35.72 | 1350216 | 1350.216 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.36 | 43.64 | 1649592 | 1649.592 | 32.4 | 47.6 | 1799280 | 1799.28 | 30
2/12/20XX 11:00:00 AM | 0.45833 | 1 | 33.8 | 51.5 | 33.8 |  | 33.8 | 68.18 | 11.82 | 446796 | 446.796 | 64.36 | 15.64 | 591192 | 591.192 | 60.54 | 19.46 | 735588 | 735.588 | 56.72 | 23.28 | 879984 | 879.984 | 52.9 | 27.1 | 1024380 | 1024.38 | 49.08 | 30.92 | 1168776 | 1168.776 | 45.26 | 34.74 | 1313172 | 1313.172 | 41.44 | 38.56 | 1457568 | 1457.568 | 37.62 | 42.38 | 1601964 | 1601.964 | 33.8 | 46.2 | 1746360 | 1746.36 | 35
2/12/20XX 12:00:00 PM | 0.5 | 1 | 34.8 | 50 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
2/12/20XX 1:00:00 PM | 0.54167 | 1 | 35 | 53.1 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
2/12/20XX 2:00:00 PM | 0.58333 | 1 | 35.5 | 50.7 | 35.5 |  | 35.5 | 68.35 | 11.65 | 440370 | 440.37 | 64.7 | 15.3 | 578340 | 578.34 | 61.05 | 18.95 | 716310 | 716.31 | 57.4 | 22.6 | 854280 | 854.28 | 53.75 | 26.25 | 992250 | 992.25 | 50.1 | 29.9 | 1130220 | 1130.22 | 46.45 | 33.55 | 1268190 | 1268.19 | 42.8 | 37.2 | 1406160 | 1406.16 | 39.15 | 40.85 | 1544130 | 1544.13 | 35.5 | 44.5 | 1682100 | 1682.1 | 35
2/12/20XX 3:00:00 PM | 0.625 | 1 | 36.2 | 48.5 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
2/12/20XX 4:00:00 PM | 0.66667 | 1 | 36.2 | 47.2 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
2/12/20XX 5:00:00 PM | 0.70833 | 1 | 36 | 47.7 | 36 |  | 36 | 68.4 | 11.6 | 438480 | 438.48 | 64.8 | 15.2 | 574560 | 574.56 | 61.2 | 18.8 | 710640 | 710.64 | 57.6 | 22.4 | 846720 | 846.72 | 54 | 26 | 982800 | 982.8 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.2 | 36.8 | 1391040 | 1391.04 | 39.6 | 40.4 | 1527120 | 1527.12 | 36 | 44 | 1663200 | 1663.2 | 35
2/12/20XX 6:00:00 PM | 0.75 | 1 | 34.4 | 54.7 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
2/12/20XX 7:00:00 PM | 0.79167 | 1 | 33.9 | 51.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/12/20XX 8:00:00 PM | 0.83333 | 1 | 32.8 | 52.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/12/20XX 9:00:00 PM | 0.875 | 1 | 31.9 | 51.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/12/20XX 10:00:00 PM | 0.91667 | 1 | 31.2 | 53.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/12/20XX 11:00:00 PM | 0.95833 | 1 | 30.6 | 53.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/12/20XX 12:00:00 AM | 0 | 2 | 30.1 | 54.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/13/20XX 1:00:00 AM | 0.041667 | 2 | 29.6 | 57.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/13/20XX 2:00:00 AM | 0.083333 | 2 | 28.7 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/13/20XX 3:00:00 AM | 0.125 | 2 | 28.5 | 60.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/13/20XX 4:00:00 AM | 0.16667 | 2 | 28.6 | 58.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/13/20XX 5:00:00 AM | 0.20833 | 2 | 28.2 | 59.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/13/20XX 6:00:00 AM | 0.25 | 2 | 27.9 | 59.3 | 27.9 |  | 27.9 | 67.59 | 12.41 | 469098 | 469.098 | 63.18 | 16.82 | 635796 | 635.796 | 58.77 | 21.23 | 802494 | 802.494 | 54.36 | 25.64 | 969192 | 969.192 | 49.95 | 30.05 | 1135890 | 1135.89 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.13 | 38.87 | 1469286 | 1469.286 | 36.72 | 43.28 | 1635984 | 1635.984 | 32.31 | 47.69 | 1802682 | 1802.682 | 27.9 | 52.1 | 1969380 | 1969.38 | 30
2/13/20XX 7:00:00 AM | 0.29167 | 2 | 27.7 | 58.2 | 27.7 |  | 27.7 | 67.57 | 12.43 | 469854 | 469.854 | 63.14 | 16.86 | 637308 | 637.308 | 58.71 | 21.29 | 804762 | 804.762 | 54.28 | 25.72 | 972216 | 972.216 | 49.85 | 30.15 | 1139670 | 1139.67 | 45.42 | 34.58 | 1307124 | 1307.124 | 40.99 | 39.01 | 1474578 | 1474.578 | 36.56 | 43.44 | 1642032 | 1642.032 | 32.13 | 47.87 | 1809486 | 1809.486 | 27.7 | 52.3 | 1976940 | 1976.94 | 30
2/13/20XX 8:00:00 AM | 0.33333 | 2 | 28 | 56.6 | 28 |  | 28 | 67.6 | 12.4 | 468720 | 468.72 | 63.2 | 16.8 | 635040 | 635.04 | 58.8 | 21.2 | 801360 | 801.36 | 54.4 | 25.6 | 967680 | 967.68 | 50 | 30 | 1134000 | 1134 | 45.6 | 34.4 | 1300320 | 1300.32 | 41.2 | 38.8 | 1466640 | 1466.64 | 36.8 | 43.2 | 1632960 | 1632.96 | 32.4 | 47.6 | 1799280 | 1799.28 | 28 | 52 | 1965600 | 1965.6 | 30
2/13/20XX 9:00:00 AM | 0.375 | 2 | 29.1 | 53.7 | 29.1 |  | 29.1 | 67.71 | 12.29 | 464562 | 464.562 | 63.42 | 16.58 | 626724 | 626.724 | 59.13 | 20.87 | 788886 | 788.886 | 54.84 | 25.16 | 951048 | 951.048 | 50.55 | 29.45 | 1113210 | 1113.21 | 46.26 | 33.74 | 1275372 | 1275.372 | 41.97 | 38.03 | 1437534 | 1437.534 | 37.68 | 42.32 | 1599696 | 1599.696 | 33.39 | 46.61 | 1761858 | 1761.858 | 29.1 | 50.9 | 1924020 | 1924.02 | 30
2/13/20XX 10:00:00 AM | 0.41667 | 2 | 30 | 49.8 | 30 |  | 30 | 67.8 | 12.2 | 461160 | 461.16 | 63.6 | 16.4 | 619920 | 619.92 | 59.4 | 20.6 | 778680 | 778.68 | 55.2 | 24.8 | 937440 | 937.44 | 51 | 29 | 1096200 | 1096.2 | 46.8 | 33.2 | 1254960 | 1254.96 | 42.6 | 37.4 | 1413720 | 1413.72 | 38.4 | 41.6 | 1572480 | 1572.48 | 34.2 | 45.8 | 1731240 | 1731.24 | 30 | 50 | 1890000 | 1890 | 30
2/13/20XX 11:00:00 AM | 0.45833 | 2 | 31.2 | 48.9 | 31.2 |  | 31.2 | 67.92 | 12.08 | 456624 | 456.624 | 63.84 | 16.16 | 610848 | 610.848 | 59.76 | 20.24 | 765072 | 765.072 | 55.68 | 24.32 | 919296 | 919.296 | 51.6 | 28.4 | 1073520 | 1073.52 | 47.52 | 32.48 | 1227744 | 1227.744 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.36 | 40.64 | 1536192 | 1536.192 | 35.28 | 44.72 | 1690416 | 1690.416 | 31.2 | 48.8 | 1844640 | 1844.64 | 30
2/13/20XX 12:00:00 PM | 0.5 | 2 | 32.6 | 45.2 | 32.6 |  | 32.6 | 68.06 | 11.94 | 451332 | 451.332 | 64.12 | 15.88 | 600264 | 600.264 | 60.18 | 19.82 | 749196 | 749.196 | 56.24 | 23.76 | 898128 | 898.128 | 52.3 | 27.7 | 1047060 | 1047.06 | 48.36 | 31.64 | 1195992 | 1195.992 | 44.42 | 35.58 | 1344924 | 1344.924 | 40.48 | 39.52 | 1493856 | 1493.856 | 36.54 | 43.46 | 1642788 | 1642.788 | 32.6 | 47.4 | 1791720 | 1791.72 | 35
2/13/20XX 1:00:00 PM | 0.54167 | 2 | 33.9 | 43 | 33.9 |  | 33.9 | 68.19 | 11.81 | 446418 | 446.418 | 64.38 | 15.62 | 590436 | 590.436 | 60.57 | 19.43 | 734454 | 734.454 | 56.76 | 23.24 | 878472 | 878.472 | 52.95 | 27.05 | 1022490 | 1022.49 | 49.14 | 30.86 | 1166508 | 1166.508 | 45.33 | 34.67 | 1310526 | 1310.526 | 41.52 | 38.48 | 1454544 | 1454.544 | 37.71 | 42.29 | 1598562 | 1598.562 | 33.9 | 46.1 | 1742580 | 1742.58 | 35
2/13/20XX 2:00:00 PM | 0.58333 | 2 | 34.6 | 41.7 | 34.6 |  | 34.6 | 68.26 | 11.74 | 443772 | 443.772 | 64.52 | 15.48 | 585144 | 585.144 | 60.78 | 19.22 | 726516 | 726.516 | 57.04 | 22.96 | 867888 | 867.888 | 53.3 | 26.7 | 1009260 | 1009.26 | 49.56 | 30.44 | 1150632 | 1150.632 | 45.82 | 34.18 | 1292004 | 1292.004 | 42.08 | 37.92 | 1433376 | 1433.376 | 38.34 | 41.66 | 1574748 | 1574.748 | 34.6 | 45.4 | 1716120 | 1716.12 | 35
2/13/20XX 3:00:00 PM | 0.625 | 2 | 35.2 | 40.4 | 35.2 |  | 35.2 | 68.32 | 11.68 | 441504 | 441.504 | 64.64 | 15.36 | 580608 | 580.608 | 60.96 | 19.04 | 719712 | 719.712 | 57.28 | 22.72 | 858816 | 858.816 | 53.6 | 26.4 | 997920 | 997.92 | 49.92 | 30.08 | 1137024 | 1137.024 | 46.24 | 33.76 | 1276128 | 1276.128 | 42.56 | 37.44 | 1415232 | 1415.232 | 38.88 | 41.12 | 1554336 | 1554.336 | 35.2 | 44.8 | 1693440 | 1693.44 | 35
2/13/20XX 4:00:00 PM | 0.66667 | 2 | 34.5 | 42.7 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
2/13/20XX 5:00:00 PM | 0.70833 | 2 | 33.4 | 43.9 | 33.4 |  | 33.4 | 68.14 | 11.86 | 448308 | 448.308 | 64.28 | 15.72 | 594216 | 594.216 | 60.42 | 19.58 | 740124 | 740.124 | 56.56 | 23.44 | 886032 | 886.032 | 52.7 | 27.3 | 1031940 | 1031.94 | 48.84 | 31.16 | 1177848 | 1177.848 | 44.98 | 35.02 | 1323756 | 1323.756 | 41.12 | 38.88 | 1469664 | 1469.664 | 37.26 | 42.74 | 1615572 | 1615.572 | 33.4 | 46.6 | 1761480 | 1761.48 | 35
2/13/20XX 6:00:00 PM | 0.75 | 2 | 32.5 | 46 | 32.5 |  | 32.5 | 68.05 | 11.95 | 451710 | 451.71 | 64.1 | 15.9 | 601020 | 601.02 | 60.15 | 19.85 | 750330 | 750.33 | 56.2 | 23.8 | 899640 | 899.64 | 52.25 | 27.75 | 1048950 | 1048.95 | 48.3 | 31.7 | 1198260 | 1198.26 | 44.35 | 35.65 | 1347570 | 1347.57 | 40.4 | 39.6 | 1496880 | 1496.88 | 36.45 | 43.55 | 1646190 | 1646.19 | 32.5 | 47.5 | 1795500 | 1795.5 | 30
2/13/20XX 7:00:00 PM | 0.79167 | 2 | 32 | 47.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/13/20XX 8:00:00 PM | 0.83333 | 2 | 31.5 | 49.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/13/20XX 9:00:00 PM | 0.875 | 2 | 30.8 | 51.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/13/20XX 10:00:00 PM | 0.91667 | 2 | 30.7 | 52.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/13/20XX 11:00:00 PM | 0.95833 | 2 | 30 | 55.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/13/20XX 12:00:00 AM | 0 | 3 | 29.8 | 56.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/14/20XX 1:00:00 AM | 0.041667 | 3 | 29.5 | 56.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/14/20XX 2:00:00 AM | 0.083333 | 3 | 29.4 | 57.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/14/20XX 3:00:00 AM | 0.125 | 3 | 29.3 | 58 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/14/20XX 4:00:00 AM | 0.16667 | 3 | 29.4 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/14/20XX 5:00:00 AM | 0.20833 | 3 | 29.3 | 58.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/14/20XX 6:00:00 AM | 0.25 | 3 | 29.1 | 57 | 29.1 |  | 29.1 | 67.71 | 12.29 | 464562 | 464.562 | 63.42 | 16.58 | 626724 | 626.724 | 59.13 | 20.87 | 788886 | 788.886 | 54.84 | 25.16 | 951048 | 951.048 | 50.55 | 29.45 | 1113210 | 1113.21 | 46.26 | 33.74 | 1275372 | 1275.372 | 41.97 | 38.03 | 1437534 | 1437.534 | 37.68 | 42.32 | 1599696 | 1599.696 | 33.39 | 46.61 | 1761858 | 1761.858 | 29.1 | 50.9 | 1924020 | 1924.02 | 30
2/14/20XX 7:00:00 AM | 0.29167 | 3 | 29.3 | 56.5 | 29.3 |  | 29.3 | 67.73 | 12.27 | 463806 | 463.806 | 63.46 | 16.54 | 625212 | 625.212 | 59.19 | 20.81 | 786618 | 786.618 | 54.92 | 25.08 | 948024 | 948.024 | 50.65 | 29.35 | 1109430 | 1109.43 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.11 | 37.89 | 1432242 | 1432.242 | 37.84 | 42.16 | 1593648 | 1593.648 | 33.57 | 46.43 | 1755054 | 1755.054 | 29.3 | 50.7 | 1916460 | 1916.46 | 30
2/14/20XX 8:00:00 AM | 0.33333 | 3 | 29.9 | 55.5 | 29.9 |  | 29.9 | 67.79 | 12.21 | 461538 | 461.538 | 63.58 | 16.42 | 620676 | 620.676 | 59.37 | 20.63 | 779814 | 779.814 | 55.16 | 24.84 | 938952 | 938.952 | 50.95 | 29.05 | 1098090 | 1098.09 | 46.74 | 33.26 | 1257228 | 1257.228 | 42.53 | 37.47 | 1416366 | 1416.366 | 38.32 | 41.68 | 1575504 | 1575.504 | 34.11 | 45.89 | 1734642 | 1734.642 | 29.9 | 50.1 | 1893780 | 1893.78 | 30
2/14/20XX 9:00:00 AM | 0.375 | 3 | 31.2 | 53.4 | 31.2 |  | 31.2 | 67.92 | 12.08 | 456624 | 456.624 | 63.84 | 16.16 | 610848 | 610.848 | 59.76 | 20.24 | 765072 | 765.072 | 55.68 | 24.32 | 919296 | 919.296 | 51.6 | 28.4 | 1073520 | 1073.52 | 47.52 | 32.48 | 1227744 | 1227.744 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.36 | 40.64 | 1536192 | 1536.192 | 35.28 | 44.72 | 1690416 | 1690.416 | 31.2 | 48.8 | 1844640 | 1844.64 | 30
2/14/20XX 10:00:00 AM | 0.41667 | 3 | 32.3 | 50.8 | 32.3 |  | 32.3 | 68.03 | 11.97 | 452466 | 452.466 | 64.06 | 15.94 | 602532 | 602.532 | 60.09 | 19.91 | 752598 | 752.598 | 56.12 | 23.88 | 902664 | 902.664 | 52.15 | 27.85 | 1052730 | 1052.73 | 48.18 | 31.82 | 1202796 | 1202.796 | 44.21 | 35.79 | 1352862 | 1352.862 | 40.24 | 39.76 | 1502928 | 1502.928 | 36.27 | 43.73 | 1652994 | 1652.994 | 32.3 | 47.7 | 1803060 | 1803.06 | 30
2/14/20XX 11:00:00 AM | 0.45833 | 3 | 34.4 | 48.7 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
2/14/20XX 12:00:00 PM | 0.5 | 3 | 36.4 | 45.2 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
2/14/20XX 1:00:00 PM | 0.54167 | 3 | 38.2 | 42.2 | 38.2 |  | 38.2 | 68.62 | 11.38 | 430164 | 430.164 | 65.24 | 14.76 | 557928 | 557.928 | 61.86 | 18.14 | 685692 | 685.692 | 58.48 | 21.52 | 813456 | 813.456 | 55.1 | 24.9 | 941220 | 941.22 | 51.72 | 28.28 | 1068984 | 1068.984 | 48.34 | 31.66 | 1196748 | 1196.748 | 44.96 | 35.04 | 1324512 | 1324.512 | 41.58 | 38.42 | 1452276 | 1452.276 | 38.2 | 41.8 | 1580040 | 1580.04 | 40
2/14/20XX 2:00:00 PM | 0.58333 | 3 | 39.3 | 39.9 | 39.3 |  | 39.3 | 68.73 | 11.27 | 426006 | 426.006 | 65.46 | 14.54 | 549612 | 549.612 | 62.19 | 17.81 | 673218 | 673.218 | 58.92 | 21.08 | 796824 | 796.824 | 55.65 | 24.35 | 920430 | 920.43 | 52.38 | 27.62 | 1044036 | 1044.036 | 49.11 | 30.89 | 1167642 | 1167.642 | 45.84 | 34.16 | 1291248 | 1291.248 | 42.57 | 37.43 | 1414854 | 1414.854 | 39.3 | 40.7 | 1538460 | 1538.46 | 40
2/14/20XX 3:00:00 PM | 0.625 | 3 | 39.6 | 42 | 39.6 |  | 39.6 | 68.76 | 11.24 | 424872 | 424.872 | 65.52 | 14.48 | 547344 | 547.344 | 62.28 | 17.72 | 669816 | 669.816 | 59.04 | 20.96 | 792288 | 792.288 | 55.8 | 24.2 | 914760 | 914.76 | 52.56 | 27.44 | 1037232 | 1037.232 | 49.32 | 30.68 | 1159704 | 1159.704 | 46.08 | 33.92 | 1282176 | 1282.176 | 42.84 | 37.16 | 1404648 | 1404.648 | 39.6 | 40.4 | 1527120 | 1527.12 | 40
2/14/20XX 4:00:00 PM | 0.66667 | 3 | 40.1 | 42.4 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
2/14/20XX 5:00:00 PM | 0.70833 | 3 | 39.2 | 46.8 | 39.2 |  | 39.2 | 68.72 | 11.28 | 426384 | 426.384 | 65.44 | 14.56 | 550368 | 550.368 | 62.16 | 17.84 | 674352 | 674.352 | 58.88 | 21.12 | 798336 | 798.336 | 55.6 | 24.4 | 922320 | 922.32 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.04 | 30.96 | 1170288 | 1170.288 | 45.76 | 34.24 | 1294272 | 1294.272 | 42.48 | 37.52 | 1418256 | 1418.256 | 39.2 | 40.8 | 1542240 | 1542.24 | 40
2/14/20XX 6:00:00 PM | 0.75 | 3 | 38.5 | 49 | 38.5 |  | 38.5 | 68.65 | 11.35 | 429030 | 429.03 | 65.3 | 14.7 | 555660 | 555.66 | 61.95 | 18.05 | 682290 | 682.29 | 58.6 | 21.4 | 808920 | 808.92 | 55.25 | 24.75 | 935550 | 935.55 | 51.9 | 28.1 | 1062180 | 1062.18 | 48.55 | 31.45 | 1188810 | 1188.81 | 45.2 | 34.8 | 1315440 | 1315.44 | 41.85 | 38.15 | 1442070 | 1442.07 | 38.5 | 41.5 | 1568700 | 1568.7 | 40
2/14/20XX 7:00:00 PM | 0.79167 | 3 | 37.9 | 53.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/14/20XX 8:00:00 PM | 0.83333 | 3 | 37.7 | 54.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/14/20XX 9:00:00 PM | 0.875 | 3 | 37.2 | 54.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/14/20XX 10:00:00 PM | 0.91667 | 3 | 36.2 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/14/20XX 11:00:00 PM | 0.95833 | 3 | 35.8 | 58.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/14/20XX 12:00:00 AM | 0 | 4 | 35.1 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/15/20XX 1:00:00 AM | 0.041667 | 4 | 34.3 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/15/20XX 2:00:00 AM | 0.083333 | 4 | 33.6 | 61.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/15/20XX 3:00:00 AM | 0.125 | 4 | 32.3 | 61.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/15/20XX 4:00:00 AM | 0.16667 | 4 | 31.8 | 61.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/15/20XX 5:00:00 AM | 0.20833 | 4 | 31.6 | 62.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/15/20XX 6:00:00 AM | 0.25 | 4 | 31.7 | 63 | 31.7 |  | 31.7 | 67.97 | 12.03 | 454734 | 454.734 | 63.94 | 16.06 | 607068 | 607.068 | 59.91 | 20.09 | 759402 | 759.402 | 55.88 | 24.12 | 911736 | 911.736 | 51.85 | 28.15 | 1064070 | 1064.07 | 47.82 | 32.18 | 1216404 | 1216.404 | 43.79 | 36.21 | 1368738 | 1368.738 | 39.76 | 40.24 | 1521072 | 1521.072 | 35.73 | 44.27 | 1673406 | 1673.406 | 31.7 | 48.3 | 1825740 | 1825.74 | 30
2/15/20XX 7:00:00 AM | 0.29167 | 4 | 31 | 65.3 | 31 |  | 31 | 67.9 | 12.1 | 457380 | 457.38 | 63.8 | 16.2 | 612360 | 612.36 | 59.7 | 20.3 | 767340 | 767.34 | 55.6 | 24.4 | 922320 | 922.32 | 51.5 | 28.5 | 1077300 | 1077.3 | 47.4 | 32.6 | 1232280 | 1232.28 | 43.3 | 36.7 | 1387260 | 1387.26 | 39.2 | 40.8 | 1542240 | 1542.24 | 35.1 | 44.9 | 1697220 | 1697.22 | 31 | 49 | 1852200 | 1852.2 | 30
2/15/20XX 8:00:00 AM | 0.33333 | 4 | 31.6 | 64.8 | 31.6 |  | 31.6 | 67.96 | 12.04 | 455112 | 455.112 | 63.92 | 16.08 | 607824 | 607.824 | 59.88 | 20.12 | 760536 | 760.536 | 55.84 | 24.16 | 913248 | 913.248 | 51.8 | 28.2 | 1065960 | 1065.96 | 47.76 | 32.24 | 1218672 | 1218.672 | 43.72 | 36.28 | 1371384 | 1371.384 | 39.68 | 40.32 | 1524096 | 1524.096 | 35.64 | 44.36 | 1676808 | 1676.808 | 31.6 | 48.4 | 1829520 | 1829.52 | 30
2/15/20XX 9:00:00 AM | 0.375 | 4 | 32.3 | 64.2 | 32.3 |  | 32.3 | 68.03 | 11.97 | 452466 | 452.466 | 64.06 | 15.94 | 602532 | 602.532 | 60.09 | 19.91 | 752598 | 752.598 | 56.12 | 23.88 | 902664 | 902.664 | 52.15 | 27.85 | 1052730 | 1052.73 | 48.18 | 31.82 | 1202796 | 1202.796 | 44.21 | 35.79 | 1352862 | 1352.862 | 40.24 | 39.76 | 1502928 | 1502.928 | 36.27 | 43.73 | 1652994 | 1652.994 | 32.3 | 47.7 | 1803060 | 1803.06 | 30
2/15/20XX 10:00:00 AM | 0.41667 | 4 | 33.9 | 60.7 | 33.9 |  | 33.9 | 68.19 | 11.81 | 446418 | 446.418 | 64.38 | 15.62 | 590436 | 590.436 | 60.57 | 19.43 | 734454 | 734.454 | 56.76 | 23.24 | 878472 | 878.472 | 52.95 | 27.05 | 1022490 | 1022.49 | 49.14 | 30.86 | 1166508 | 1166.508 | 45.33 | 34.67 | 1310526 | 1310.526 | 41.52 | 38.48 | 1454544 | 1454.544 | 37.71 | 42.29 | 1598562 | 1598.562 | 33.9 | 46.1 | 1742580 | 1742.58 | 35
2/15/20XX 11:00:00 AM | 0.45833 | 4 | 35 | 57.6 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
2/15/20XX 12:00:00 PM | 0.5 | 4 | 36.3 | 55.6 | 36.3 |  | 36.3 | 68.43 | 11.57 | 437346 | 437.346 | 64.86 | 15.14 | 572292 | 572.292 | 61.29 | 18.71 | 707238 | 707.238 | 57.72 | 22.28 | 842184 | 842.184 | 54.15 | 25.85 | 977130 | 977.13 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.01 | 32.99 | 1247022 | 1247.022 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.87 | 40.13 | 1516914 | 1516.914 | 36.3 | 43.7 | 1651860 | 1651.86 | 35
2/15/20XX 1:00:00 PM | 0.54167 | 4 | 37.8 | 53.4 | 37.8 |  | 37.8 | 68.58 | 11.42 | 431676 | 431.676 | 65.16 | 14.84 | 560952 | 560.952 | 61.74 | 18.26 | 690228 | 690.228 | 58.32 | 21.68 | 819504 | 819.504 | 54.9 | 25.1 | 948780 | 948.78 | 51.48 | 28.52 | 1078056 | 1078.056 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.22 | 38.78 | 1465884 | 1465.884 | 37.8 | 42.2 | 1595160 | 1595.16 | 40
2/15/20XX 2:00:00 PM | 0.58333 | 4 | 39 | 51.6 | 39 |  | 39 | 68.7 | 11.3 | 427140 | 427.14 | 65.4 | 14.6 | 551880 | 551.88 | 62.1 | 17.9 | 676620 | 676.62 | 58.8 | 21.2 | 801360 | 801.36 | 55.5 | 24.5 | 926100 | 926.1 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.6 | 34.4 | 1300320 | 1300.32 | 42.3 | 37.7 | 1425060 | 1425.06 | 39 | 41 | 1549800 | 1549.8 | 40
2/15/20XX 3:00:00 PM | 0.625 | 4 | 39.7 | 50.6 | 39.7 |  | 39.7 | 68.77 | 11.23 | 424494 | 424.494 | 65.54 | 14.46 | 546588 | 546.588 | 62.31 | 17.69 | 668682 | 668.682 | 59.08 | 20.92 | 790776 | 790.776 | 55.85 | 24.15 | 912870 | 912.87 | 52.62 | 27.38 | 1034964 | 1034.964 | 49.39 | 30.61 | 1157058 | 1157.058 | 46.16 | 33.84 | 1279152 | 1279.152 | 42.93 | 37.07 | 1401246 | 1401.246 | 39.7 | 40.3 | 1523340 | 1523.34 | 40
2/15/20XX 4:00:00 PM | 0.66667 | 4 | 39.1 | 53.8 | 39.1 |  | 39.1 | 68.71 | 11.29 | 426762 | 426.762 | 65.42 | 14.58 | 551124 | 551.124 | 62.13 | 17.87 | 675486 | 675.486 | 58.84 | 21.16 | 799848 | 799.848 | 55.55 | 24.45 | 924210 | 924.21 | 52.26 | 27.74 | 1048572 | 1048.572 | 48.97 | 31.03 | 1172934 | 1172.934 | 45.68 | 34.32 | 1297296 | 1297.296 | 42.39 | 37.61 | 1421658 | 1421.658 | 39.1 | 40.9 | 1546020 | 1546.02 | 40
2/15/20XX 5:00:00 PM | 0.70833 | 4 | 38.2 | 56.1 | 38.2 |  | 38.2 | 68.62 | 11.38 | 430164 | 430.164 | 65.24 | 14.76 | 557928 | 557.928 | 61.86 | 18.14 | 685692 | 685.692 | 58.48 | 21.52 | 813456 | 813.456 | 55.1 | 24.9 | 941220 | 941.22 | 51.72 | 28.28 | 1068984 | 1068.984 | 48.34 | 31.66 | 1196748 | 1196.748 | 44.96 | 35.04 | 1324512 | 1324.512 | 41.58 | 38.42 | 1452276 | 1452.276 | 38.2 | 41.8 | 1580040 | 1580.04 | 40
2/15/20XX 6:00:00 PM | 0.75 | 4 | 37.3 | 57.9 | 37.3 |  | 37.3 | 68.53 | 11.47 | 433566 | 433.566 | 65.06 | 14.94 | 564732 | 564.732 | 61.59 | 18.41 | 695898 | 695.898 | 58.12 | 21.88 | 827064 | 827.064 | 54.65 | 25.35 | 958230 | 958.23 | 51.18 | 28.82 | 1089396 | 1089.396 | 47.71 | 32.29 | 1220562 | 1220.562 | 44.24 | 35.76 | 1351728 | 1351.728 | 40.77 | 39.23 | 1482894 | 1482.894 | 37.3 | 42.7 | 1614060 | 1614.06 | 35
2/15/20XX 7:00:00 PM | 0.79167 | 4 | 36.4 | 61.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/15/20XX 8:00:00 PM | 0.83333 | 4 | 36.4 | 60.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/15/20XX 9:00:00 PM | 0.875 | 4 | 35.8 | 61.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/15/20XX 10:00:00 PM | 0.91667 | 4 | 34.9 | 62 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/15/20XX 11:00:00 PM | 0.95833 | 4 | 34.2 | 62.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/15/20XX 12:00:00 AM | 0 | 5 | 33.2 | 64.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/16/20XX 1:00:00 AM | 0.041667 | 5 | 32.7 | 66.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/16/20XX 2:00:00 AM | 0.083333 | 5 | 32.2 | 67.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/16/20XX 3:00:00 AM | 0.125 | 5 | 32.1 | 68.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/16/20XX 4:00:00 AM | 0.16667 | 5 | 32.4 | 67.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/16/20XX 5:00:00 AM | 0.20833 | 5 | 32.3 | 66.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/16/20XX 6:00:00 AM | 0.25 | 5 | 32.4 | 65.7 | 32.4 |  | 32.4 | 68.04 | 11.96 | 452088 | 452.088 | 64.08 | 15.92 | 601776 | 601.776 | 60.12 | 19.88 | 751464 | 751.464 | 56.16 | 23.84 | 901152 | 901.152 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.24 | 31.76 | 1200528 | 1200.528 | 44.28 | 35.72 | 1350216 | 1350.216 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.36 | 43.64 | 1649592 | 1649.592 | 32.4 | 47.6 | 1799280 | 1799.28 | 30
2/16/20XX 7:00:00 AM | 0.29167 | 5 | 32 | 67.2 | 32 |  | 32 | 68 | 12 | 453600 | 453.6 | 64 | 16 | 604800 | 604.8 | 60 | 20 | 756000 | 756 | 56 | 24 | 907200 | 907.2 | 52 | 28 | 1058400 | 1058.4 | 48 | 32 | 1209600 | 1209.6 | 44 | 36 | 1360800 | 1360.8 | 40 | 40 | 1512000 | 1512 | 36 | 44 | 1663200 | 1663.2 | 32 | 48 | 1814400 | 1814.4 | 30
2/16/20XX 8:00:00 AM | 0.33333 | 5 | 33 | 64.4 | 33 |  | 33 | 68.1 | 11.9 | 449820 | 449.82 | 64.2 | 15.8 | 597240 | 597.24 | 60.3 | 19.7 | 744660 | 744.66 | 56.4 | 23.6 | 892080 | 892.08 | 52.5 | 27.5 | 1039500 | 1039.5 | 48.6 | 31.4 | 1186920 | 1186.92 | 44.7 | 35.3 | 1334340 | 1334.34 | 40.8 | 39.2 | 1481760 | 1481.76 | 36.9 | 43.1 | 1629180 | 1629.18 | 33 | 47 | 1776600 | 1776.6 | 35
2/16/20XX 9:00:00 AM | 0.375 | 5 | 33.3 | 64.2 | 33.3 |  | 33.3 | 68.13 | 11.87 | 448686 | 448.686 | 64.26 | 15.74 | 594972 | 594.972 | 60.39 | 19.61 | 741258 | 741.258 | 56.52 | 23.48 | 887544 | 887.544 | 52.65 | 27.35 | 1033830 | 1033.83 | 48.78 | 31.22 | 1180116 | 1180.116 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.17 | 42.83 | 1618974 | 1618.974 | 33.3 | 46.7 | 1765260 | 1765.26 | 35
2/16/20XX 10:00:00 AM | 0.41667 | 5 | 34.4 | 61.4 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
2/16/20XX 11:00:00 AM | 0.45833 | 5 | 35.4 | 59.4 | 35.4 |  | 35.4 | 68.34 | 11.66 | 440748 | 440.748 | 64.68 | 15.32 | 579096 | 579.096 | 61.02 | 18.98 | 717444 | 717.444 | 57.36 | 22.64 | 855792 | 855.792 | 53.7 | 26.3 | 994140 | 994.14 | 50.04 | 29.96 | 1132488 | 1132.488 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.72 | 37.28 | 1409184 | 1409.184 | 39.06 | 40.94 | 1547532 | 1547.532 | 35.4 | 44.6 | 1685880 | 1685.88 | 35
2/16/20XX 12:00:00 PM | 0.5 | 5 | 37 | 57.2 | 37 |  | 37 | 68.5 | 11.5 | 434700 | 434.7 | 65 | 15 | 567000 | 567 | 61.5 | 18.5 | 699300 | 699.3 | 58 | 22 | 831600 | 831.6 | 54.5 | 25.5 | 963900 | 963.9 | 51 | 29 | 1096200 | 1096.2 | 47.5 | 32.5 | 1228500 | 1228.5 | 44 | 36 | 1360800 | 1360.8 | 40.5 | 39.5 | 1493100 | 1493.1 | 37 | 43 | 1625400 | 1625.4 | 35
2/16/20XX 1:00:00 PM | 0.54167 | 5 | 38 | 57.1 | 38 |  | 38 | 68.6 | 11.4 | 430920 | 430.92 | 65.2 | 14.8 | 559440 | 559.44 | 61.8 | 18.2 | 687960 | 687.96 | 58.4 | 21.6 | 816480 | 816.48 | 55 | 25 | 945000 | 945 | 51.6 | 28.4 | 1073520 | 1073.52 | 48.2 | 31.8 | 1202040 | 1202.04 | 44.8 | 35.2 | 1330560 | 1330.56 | 41.4 | 38.6 | 1459080 | 1459.08 | 38 | 42 | 1587600 | 1587.6 | 40
2/16/20XX 2:00:00 PM | 0.58333 | 5 | 38.6 | 56.9 | 38.6 |  | 38.6 | 68.66 | 11.34 | 428652 | 428.652 | 65.32 | 14.68 | 554904 | 554.904 | 61.98 | 18.02 | 681156 | 681.156 | 58.64 | 21.36 | 807408 | 807.408 | 55.3 | 24.7 | 933660 | 933.66 | 51.96 | 28.04 | 1059912 | 1059.912 | 48.62 | 31.38 | 1186164 | 1186.164 | 45.28 | 34.72 | 1312416 | 1312.416 | 41.94 | 38.06 | 1438668 | 1438.668 | 38.6 | 41.4 | 1564920 | 1564.92 | 40
2/16/20XX 3:00:00 PM | 0.625 | 5 | 38.4 | 58.3 | 38.4 |  | 38.4 | 68.64 | 11.36 | 429408 | 429.408 | 65.28 | 14.72 | 556416 | 556.416 | 61.92 | 18.08 | 683424 | 683.424 | 58.56 | 21.44 | 810432 | 810.432 | 55.2 | 24.8 | 937440 | 937.44 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.76 | 38.24 | 1445472 | 1445.472 | 38.4 | 41.6 | 1572480 | 1572.48 | 40
2/16/20XX 4:00:00 PM | 0.66667 | 5 | 38.3 | 58.3 | 38.3 |  | 38.3 | 68.63 | 11.37 | 429786 | 429.786 | 65.26 | 14.74 | 557172 | 557.172 | 61.89 | 18.11 | 684558 | 684.558 | 58.52 | 21.48 | 811944 | 811.944 | 55.15 | 24.85 | 939330 | 939.33 | 51.78 | 28.22 | 1066716 | 1066.716 | 48.41 | 31.59 | 1194102 | 1194.102 | 45.04 | 34.96 | 1321488 | 1321.488 | 41.67 | 38.33 | 1448874 | 1448.874 | 38.3 | 41.7 | 1576260 | 1576.26 | 40
2/16/20XX 5:00:00 PM | 0.70833 | 5 | 37.4 | 58.1 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
2/16/20XX 6:00:00 PM | 0.75 | 5 | 37.1 | 56.2 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
2/16/20XX 7:00:00 PM | 0.79167 | 5 | 35.9 | 57.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/16/20XX 8:00:00 PM | 0.83333 | 5 | 35.1 | 58 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/16/20XX 9:00:00 PM | 0.875 | 5 | 34.4 | 56.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/16/20XX 10:00:00 PM | 0.91667 | 5 | 33.7 | 55 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/16/20XX 11:00:00 PM | 0.95833 | 5 | 32.7 | 55.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/16/20XX 12:00:00 AM | 0 | 6 | 32.3 | 53.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/17/20XX 1:00:00 AM | 0.041667 | 6 | 32 | 54.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/17/20XX 2:00:00 AM | 0.083333 | 6 | 31.3 | 56.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/17/20XX 3:00:00 AM | 0.125 | 6 | 30.9 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/17/20XX 4:00:00 AM | 0.16667 | 6 | 30.4 | 61.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/17/20XX 5:00:00 AM | 0.20833 | 6 | 30.1 | 62.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/17/20XX 6:00:00 AM | 0.25 | 6 | 29.7 | 62.8 | 29.7 |  | 29.7 | 67.77 | 12.23 | 462294 | 462.294 | 63.54 | 16.46 | 622188 | 622.188 | 59.31 | 20.69 | 782082 | 782.082 | 55.08 | 24.92 | 941976 | 941.976 | 50.85 | 29.15 | 1101870 | 1101.87 | 46.62 | 33.38 | 1261764 | 1261.764 | 42.39 | 37.61 | 1421658 | 1421.658 | 38.16 | 41.84 | 1581552 | 1581.552 | 33.93 | 46.07 | 1741446 | 1741.446 | 29.7 | 50.3 | 1901340 | 1901.34 | 30
2/17/20XX 7:00:00 AM | 0.29167 | 6 | 29.3 | 62.7 | 29.3 |  | 29.3 | 67.73 | 12.27 | 463806 | 463.806 | 63.46 | 16.54 | 625212 | 625.212 | 59.19 | 20.81 | 786618 | 786.618 | 54.92 | 25.08 | 948024 | 948.024 | 50.65 | 29.35 | 1109430 | 1109.43 | 46.38 | 33.62 | 1270836 | 1270.836 | 42.11 | 37.89 | 1432242 | 1432.242 | 37.84 | 42.16 | 1593648 | 1593.648 | 33.57 | 46.43 | 1755054 | 1755.054 | 29.3 | 50.7 | 1916460 | 1916.46 | 30
2/17/20XX 8:00:00 AM | 0.33333 | 6 | 29.7 | 59.9 | 29.7 |  | 29.7 | 67.77 | 12.23 | 462294 | 462.294 | 63.54 | 16.46 | 622188 | 622.188 | 59.31 | 20.69 | 782082 | 782.082 | 55.08 | 24.92 | 941976 | 941.976 | 50.85 | 29.15 | 1101870 | 1101.87 | 46.62 | 33.38 | 1261764 | 1261.764 | 42.39 | 37.61 | 1421658 | 1421.658 | 38.16 | 41.84 | 1581552 | 1581.552 | 33.93 | 46.07 | 1741446 | 1741.446 | 29.7 | 50.3 | 1901340 | 1901.34 | 30
2/17/20XX 9:00:00 AM | 0.375 | 6 | 31 | 57.1 | 31 |  | 31 | 67.9 | 12.1 | 457380 | 457.38 | 63.8 | 16.2 | 612360 | 612.36 | 59.7 | 20.3 | 767340 | 767.34 | 55.6 | 24.4 | 922320 | 922.32 | 51.5 | 28.5 | 1077300 | 1077.3 | 47.4 | 32.6 | 1232280 | 1232.28 | 43.3 | 36.7 | 1387260 | 1387.26 | 39.2 | 40.8 | 1542240 | 1542.24 | 35.1 | 44.9 | 1697220 | 1697.22 | 31 | 49 | 1852200 | 1852.2 | 30
2/17/20XX 10:00:00 AM | 0.41667 | 6 | 32.2 | 54 | 32.2 |  | 32.2 | 68.02 | 11.98 | 452844 | 452.844 | 64.04 | 15.96 | 603288 | 603.288 | 60.06 | 19.94 | 753732 | 753.732 | 56.08 | 23.92 | 904176 | 904.176 | 52.1 | 27.9 | 1054620 | 1054.62 | 48.12 | 31.88 | 1205064 | 1205.064 | 44.14 | 35.86 | 1355508 | 1355.508 | 40.16 | 39.84 | 1505952 | 1505.952 | 36.18 | 43.82 | 1656396 | 1656.396 | 32.2 | 47.8 | 1806840 | 1806.84 | 30
2/17/20XX 11:00:00 AM | 0.45833 | 6 | 34 | 52.9 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
2/17/20XX 12:00:00 PM | 0.5 | 6 | 36.1 | 45.4 | 36.1 |  | 36.1 | 68.41 | 11.59 | 438102 | 438.102 | 64.82 | 15.18 | 573804 | 573.804 | 61.23 | 18.77 | 709506 | 709.506 | 57.64 | 22.36 | 845208 | 845.208 | 54.05 | 25.95 | 980910 | 980.91 | 50.46 | 29.54 | 1116612 | 1116.612 | 46.87 | 33.13 | 1252314 | 1252.314 | 43.28 | 36.72 | 1388016 | 1388.016 | 39.69 | 40.31 | 1523718 | 1523.718 | 36.1 | 43.9 | 1659420 | 1659.42 | 35
2/17/20XX 1:00:00 PM | 0.54167 | 6 | 37.5 | 42.5 | 37.5 |  | 37.5 | 68.55 | 11.45 | 432810 | 432.81 | 65.1 | 14.9 | 563220 | 563.22 | 61.65 | 18.35 | 693630 | 693.63 | 58.2 | 21.8 | 824040 | 824.04 | 54.75 | 25.25 | 954450 | 954.45 | 51.3 | 28.7 | 1084860 | 1084.86 | 47.85 | 32.15 | 1215270 | 1215.27 | 44.4 | 35.6 | 1345680 | 1345.68 | 40.95 | 39.05 | 1476090 | 1476.09 | 37.5 | 42.5 | 1606500 | 1606.5 | 35
2/17/20XX 2:00:00 PM | 0.58333 | 6 | 37.9 | 42.3 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
2/17/20XX 3:00:00 PM | 0.625 | 6 | 39 | 40.5 | 39 |  | 39 | 68.7 | 11.3 | 427140 | 427.14 | 65.4 | 14.6 | 551880 | 551.88 | 62.1 | 17.9 | 676620 | 676.62 | 58.8 | 21.2 | 801360 | 801.36 | 55.5 | 24.5 | 926100 | 926.1 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.6 | 34.4 | 1300320 | 1300.32 | 42.3 | 37.7 | 1425060 | 1425.06 | 39 | 41 | 1549800 | 1549.8 | 40
2/17/20XX 4:00:00 PM | 0.66667 | 6 | 38.5 | 40 | 38.5 |  | 38.5 | 68.65 | 11.35 | 429030 | 429.03 | 65.3 | 14.7 | 555660 | 555.66 | 61.95 | 18.05 | 682290 | 682.29 | 58.6 | 21.4 | 808920 | 808.92 | 55.25 | 24.75 | 935550 | 935.55 | 51.9 | 28.1 | 1062180 | 1062.18 | 48.55 | 31.45 | 1188810 | 1188.81 | 45.2 | 34.8 | 1315440 | 1315.44 | 41.85 | 38.15 | 1442070 | 1442.07 | 38.5 | 41.5 | 1568700 | 1568.7 | 40
2/17/20XX 5:00:00 PM | 0.70833 | 6 | 38.1 | 40.9 | 38.1 |  | 38.1 | 68.61 | 11.39 | 430542 | 430.542 | 65.22 | 14.78 | 558684 | 558.684 | 61.83 | 18.17 | 686826 | 686.826 | 58.44 | 21.56 | 814968 | 814.968 | 55.05 | 24.95 | 943110 | 943.11 | 51.66 | 28.34 | 1071252 | 1071.252 | 48.27 | 31.73 | 1199394 | 1199.394 | 44.88 | 35.12 | 1327536 | 1327.536 | 41.49 | 38.51 | 1455678 | 1455.678 | 38.1 | 41.9 | 1583820 | 1583.82 | 40
2/17/20XX 6:00:00 PM | 0.75 | 6 | 36.5 | 46.6 | 36.5 |  | 36.5 | 68.45 | 11.55 | 436590 | 436.59 | 64.9 | 15.1 | 570780 | 570.78 | 61.35 | 18.65 | 704970 | 704.97 | 57.8 | 22.2 | 839160 | 839.16 | 54.25 | 25.75 | 973350 | 973.35 | 50.7 | 29.3 | 1107540 | 1107.54 | 47.15 | 32.85 | 1241730 | 1241.73 | 43.6 | 36.4 | 1375920 | 1375.92 | 40.05 | 39.95 | 1510110 | 1510.11 | 36.5 | 43.5 | 1644300 | 1644.3 | 35
2/17/20XX 7:00:00 PM | 0.79167 | 6 | 36.1 | 47.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/17/20XX 8:00:00 PM | 0.83333 | 6 | 35 | 52.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/17/20XX 9:00:00 PM | 0.875 | 6 | 34.7 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/17/20XX 10:00:00 PM | 0.91667 | 6 | 34.9 | 53.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/17/20XX 11:00:00 PM | 0.95833 | 6 | 34.5 | 53.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/17/20XX 12:00:00 AM | 0 | 7 | 34.2 | 55.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/18/20XX 1:00:00 AM | 0.041667 | 7 | 33.5 | 56.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/18/20XX 2:00:00 AM | 0.083333 | 7 | 32.9 | 56.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/18/20XX 3:00:00 AM | 0.125 | 7 | 32.8 | 57.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/18/20XX 4:00:00 AM | 0.16667 | 7 | 32.2 | 57.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/18/20XX 5:00:00 AM | 0.20833 | 7 | 31.7 | 60.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/18/20XX 6:00:00 AM | 0.25 | 7 | 31.4 | 61.7 | 31.4 |  | 31.4 | 67.94 | 12.06 | 455868 | 455.868 | 63.88 | 16.12 | 609336 | 609.336 | 59.82 | 20.18 | 762804 | 762.804 | 55.76 | 24.24 | 916272 | 916.272 | 51.7 | 28.3 | 1069740 | 1069.74 | 47.64 | 32.36 | 1223208 | 1223.208 | 43.58 | 36.42 | 1376676 | 1376.676 | 39.52 | 40.48 | 1530144 | 1530.144 | 35.46 | 44.54 | 1683612 | 1683.612 | 31.4 | 48.6 | 1837080 | 1837.08 | 30
2/18/20XX 7:00:00 AM | 0.29167 | 7 | 32 | 62.4 | 32 |  | 32 | 68 | 12 | 453600 | 453.6 | 64 | 16 | 604800 | 604.8 | 60 | 20 | 756000 | 756 | 56 | 24 | 907200 | 907.2 | 52 | 28 | 1058400 | 1058.4 | 48 | 32 | 1209600 | 1209.6 | 44 | 36 | 1360800 | 1360.8 | 40 | 40 | 1512000 | 1512 | 36 | 44 | 1663200 | 1663.2 | 32 | 48 | 1814400 | 1814.4 | 30
2/18/20XX 8:00:00 AM | 0.33333 | 7 | 32.6 | 62.1 | 32.6 |  | 32.6 | 68.06 | 11.94 | 451332 | 451.332 | 64.12 | 15.88 | 600264 | 600.264 | 60.18 | 19.82 | 749196 | 749.196 | 56.24 | 23.76 | 898128 | 898.128 | 52.3 | 27.7 | 1047060 | 1047.06 | 48.36 | 31.64 | 1195992 | 1195.992 | 44.42 | 35.58 | 1344924 | 1344.924 | 40.48 | 39.52 | 1493856 | 1493.856 | 36.54 | 43.46 | 1642788 | 1642.788 | 32.6 | 47.4 | 1791720 | 1791.72 | 35
2/18/20XX 9:00:00 AM | 0.375 | 7 | 34.3 | 59.5 | 34.3 |  | 34.3 | 68.23 | 11.77 | 444906 | 444.906 | 64.46 | 15.54 | 587412 | 587.412 | 60.69 | 19.31 | 729918 | 729.918 | 56.92 | 23.08 | 872424 | 872.424 | 53.15 | 26.85 | 1014930 | 1014.93 | 49.38 | 30.62 | 1157436 | 1157.436 | 45.61 | 34.39 | 1299942 | 1299.942 | 41.84 | 38.16 | 1442448 | 1442.448 | 38.07 | 41.93 | 1584954 | 1584.954 | 34.3 | 45.7 | 1727460 | 1727.46 | 35
2/18/20XX 10:00:00 AM | 0.41667 | 7 | 35.8 | 56.1 | 35.8 |  | 35.8 | 68.38 | 11.62 | 439236 | 439.236 | 64.76 | 15.24 | 576072 | 576.072 | 61.14 | 18.86 | 712908 | 712.908 | 57.52 | 22.48 | 849744 | 849.744 | 53.9 | 26.1 | 986580 | 986.58 | 50.28 | 29.72 | 1123416 | 1123.416 | 46.66 | 33.34 | 1260252 | 1260.252 | 43.04 | 36.96 | 1397088 | 1397.088 | 39.42 | 40.58 | 1533924 | 1533.924 | 35.8 | 44.2 | 1670760 | 1670.76 | 35
2/18/20XX 11:00:00 AM | 0.45833 | 7 | 37.7 | 52.7 | 37.7 |  | 37.7 | 68.57 | 11.43 | 432054 | 432.054 | 65.14 | 14.86 | 561708 | 561.708 | 61.71 | 18.29 | 691362 | 691.362 | 58.28 | 21.72 | 821016 | 821.016 | 54.85 | 25.15 | 950670 | 950.67 | 51.42 | 28.58 | 1080324 | 1080.324 | 47.99 | 32.01 | 1209978 | 1209.978 | 44.56 | 35.44 | 1339632 | 1339.632 | 41.13 | 38.87 | 1469286 | 1469.286 | 37.7 | 42.3 | 1598940 | 1598.94 | 40
2/18/20XX 12:00:00 PM | 0.5 | 7 | 40 | 49.2 | 40 |  | 40 | 68.8 | 11.2 | 423360 | 423.36 | 65.6 | 14.4 | 544320 | 544.32 | 62.4 | 17.6 | 665280 | 665.28 | 59.2 | 20.8 | 786240 | 786.24 | 56 | 24 | 907200 | 907.2 | 52.8 | 27.2 | 1028160 | 1028.16 | 49.6 | 30.4 | 1149120 | 1149.12 | 46.4 | 33.6 | 1270080 | 1270.08 | 43.2 | 36.8 | 1391040 | 1391.04 | 40 | 40 | 1512000 | 1512 | 40
2/18/20XX 1:00:00 PM | 0.54167 | 7 | 41.3 | 48.1 | 41.3 |  | 41.3 | 68.93 | 11.07 | 418446 | 418.446 | 65.86 | 14.14 | 534492 | 534.492 | 62.79 | 17.21 | 650538 | 650.538 | 59.72 | 20.28 | 766584 | 766.584 | 56.65 | 23.35 | 882630 | 882.63 | 53.58 | 26.42 | 998676 | 998.676 | 50.51 | 29.49 | 1114722 | 1114.722 | 47.44 | 32.56 | 1230768 | 1230.768 | 44.37 | 35.63 | 1346814 | 1346.814 | 41.3 | 38.7 | 1462860 | 1462.86 | 40
2/18/20XX 2:00:00 PM | 0.58333 | 7 | 42.4 | 48.5 | 42.4 |  | 42.4 | 69.04 | 10.96 | 414288 | 414.288 | 66.08 | 13.92 | 526176 | 526.176 | 63.12 | 16.88 | 638064 | 638.064 | 60.16 | 19.84 | 749952 | 749.952 | 57.2 | 22.8 | 861840 | 861.84 | 54.24 | 25.76 | 973728 | 973.728 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.32 | 31.68 | 1197504 | 1197.504 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.4 | 37.6 | 1421280 | 1421.28 | 40
2/18/20XX 3:00:00 PM | 0.625 | 7 | 43.3 | 45.6 | 43.3 |  | 43.3 | 69.13 | 10.87 | 410886 | 410.886 | 66.26 | 13.74 | 519372 | 519.372 | 63.39 | 16.61 | 627858 | 627.858 | 60.52 | 19.48 | 736344 | 736.344 | 57.65 | 22.35 | 844830 | 844.83 | 54.78 | 25.22 | 953316 | 953.316 | 51.91 | 28.09 | 1061802 | 1061.802 | 49.04 | 30.96 | 1170288 | 1170.288 | 46.17 | 33.83 | 1278774 | 1278.774 | 43.3 | 36.7 | 1387260 | 1387.26 | 45
2/18/20XX 4:00:00 PM | 0.66667 | 7 | 43.3 | 46.9 | 43.3 |  | 43.3 | 69.13 | 10.87 | 410886 | 410.886 | 66.26 | 13.74 | 519372 | 519.372 | 63.39 | 16.61 | 627858 | 627.858 | 60.52 | 19.48 | 736344 | 736.344 | 57.65 | 22.35 | 844830 | 844.83 | 54.78 | 25.22 | 953316 | 953.316 | 51.91 | 28.09 | 1061802 | 1061.802 | 49.04 | 30.96 | 1170288 | 1170.288 | 46.17 | 33.83 | 1278774 | 1278.774 | 43.3 | 36.7 | 1387260 | 1387.26 | 45
2/18/20XX 5:00:00 PM | 0.70833 | 7 | 42.9 | 47.7 | 42.9 |  | 42.9 | 69.09 | 10.91 | 412398 | 412.398 | 66.18 | 13.82 | 522396 | 522.396 | 63.27 | 16.73 | 632394 | 632.394 | 60.36 | 19.64 | 742392 | 742.392 | 57.45 | 22.55 | 852390 | 852.39 | 54.54 | 25.46 | 962388 | 962.388 | 51.63 | 28.37 | 1072386 | 1072.386 | 48.72 | 31.28 | 1182384 | 1182.384 | 45.81 | 34.19 | 1292382 | 1292.382 | 42.9 | 37.1 | 1402380 | 1402.38 | 45
2/18/20XX 6:00:00 PM | 0.75 | 7 | 42.3 | 49.8 | 42.3 |  | 42.3 | 69.03 | 10.97 | 414666 | 414.666 | 66.06 | 13.94 | 526932 | 526.932 | 63.09 | 16.91 | 639198 | 639.198 | 60.12 | 19.88 | 751464 | 751.464 | 57.15 | 22.85 | 863730 | 863.73 | 54.18 | 25.82 | 975996 | 975.996 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.27 | 34.73 | 1312794 | 1312.794 | 42.3 | 37.7 | 1425060 | 1425.06 | 40
2/18/20XX 7:00:00 PM | 0.79167 | 7 | 41.6 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/18/20XX 8:00:00 PM | 0.83333 | 7 | 41.4 | 56.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/18/20XX 9:00:00 PM | 0.875 | 7 | 41.1 | 53.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/18/20XX 10:00:00 PM | 0.91667 | 7 | 40.5 | 49.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/18/20XX 11:00:00 PM | 0.95833 | 7 | 39.6 | 50.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/18/20XX 12:00:00 AM | 0 | 1 | 39.4 | 48.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/19/20XX 1:00:00 AM | 0.041667 | 1 | 38.8 | 50.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/19/20XX 2:00:00 AM | 0.083333 | 1 | 38.1 | 50.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/19/20XX 3:00:00 AM | 0.125 | 1 | 37.3 | 51.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/19/20XX 4:00:00 AM | 0.16667 | 1 | 37 | 54.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/19/20XX 5:00:00 AM | 0.20833 | 1 | 36.9 | 54.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/19/20XX 6:00:00 AM | 0.25 | 1 | 36.7 | 55.7 | 36.7 |  | 36.7 | 68.47 | 11.53 | 435834 | 435.834 | 64.94 | 15.06 | 569268 | 569.268 | 61.41 | 18.59 | 702702 | 702.702 | 57.88 | 22.12 | 836136 | 836.136 | 54.35 | 25.65 | 969570 | 969.57 | 50.82 | 29.18 | 1103004 | 1103.004 | 47.29 | 32.71 | 1236438 | 1236.438 | 43.76 | 36.24 | 1369872 | 1369.872 | 40.23 | 39.77 | 1503306 | 1503.306 | 36.7 | 43.3 | 1636740 | 1636.74 | 35
2/19/20XX 7:00:00 AM | 0.29167 | 1 | 36.3 | 56.5 | 36.3 |  | 36.3 | 68.43 | 11.57 | 437346 | 437.346 | 64.86 | 15.14 | 572292 | 572.292 | 61.29 | 18.71 | 707238 | 707.238 | 57.72 | 22.28 | 842184 | 842.184 | 54.15 | 25.85 | 977130 | 977.13 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.01 | 32.99 | 1247022 | 1247.022 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.87 | 40.13 | 1516914 | 1516.914 | 36.3 | 43.7 | 1651860 | 1651.86 | 35
2/19/20XX 8:00:00 AM | 0.33333 | 1 | 37.4 | 54.7 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
2/19/20XX 9:00:00 AM | 0.375 | 1 | 38.9 | 52.9 | 38.9 |  | 38.9 | 68.69 | 11.31 | 427518 | 427.518 | 65.38 | 14.62 | 552636 | 552.636 | 62.07 | 17.93 | 677754 | 677.754 | 58.76 | 21.24 | 802872 | 802.872 | 55.45 | 24.55 | 927990 | 927.99 | 52.14 | 27.86 | 1053108 | 1053.108 | 48.83 | 31.17 | 1178226 | 1178.226 | 45.52 | 34.48 | 1303344 | 1303.344 | 42.21 | 37.79 | 1428462 | 1428.462 | 38.9 | 41.1 | 1553580 | 1553.58 | 40
2/19/20XX 10:00:00 AM | 0.41667 | 1 | 40.4 | 52.1 | 40.4 |  | 40.4 | 68.84 | 11.16 | 421848 | 421.848 | 65.68 | 14.32 | 541296 | 541.296 | 62.52 | 17.48 | 660744 | 660.744 | 59.36 | 20.64 | 780192 | 780.192 | 56.2 | 23.8 | 899640 | 899.64 | 53.04 | 26.96 | 1019088 | 1019.088 | 49.88 | 30.12 | 1138536 | 1138.536 | 46.72 | 33.28 | 1257984 | 1257.984 | 43.56 | 36.44 | 1377432 | 1377.432 | 40.4 | 39.6 | 1496880 | 1496.88 | 40
2/19/20XX 11:00:00 AM | 0.45833 | 1 | 41.4 | 50.3 | 41.4 |  | 41.4 | 68.94 | 11.06 | 418068 | 418.068 | 65.88 | 14.12 | 533736 | 533.736 | 62.82 | 17.18 | 649404 | 649.404 | 59.76 | 20.24 | 765072 | 765.072 | 56.7 | 23.3 | 880740 | 880.74 | 53.64 | 26.36 | 996408 | 996.408 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.46 | 35.54 | 1343412 | 1343.412 | 41.4 | 38.6 | 1459080 | 1459.08 | 40
2/19/20XX 12:00:00 PM | 0.5 | 1 | 41.9 | 50.2 | 41.9 |  | 41.9 | 68.99 | 11.01 | 416178 | 416.178 | 65.98 | 14.02 | 529956 | 529.956 | 62.97 | 17.03 | 643734 | 643.734 | 59.96 | 20.04 | 757512 | 757.512 | 56.95 | 23.05 | 871290 | 871.29 | 53.94 | 26.06 | 985068 | 985.068 | 50.93 | 29.07 | 1098846 | 1098.846 | 47.92 | 32.08 | 1212624 | 1212.624 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.9 | 38.1 | 1440180 | 1440.18 | 40
2/19/20XX 1:00:00 PM | 0.54167 | 1 | 42.2 | 48.8 | 42.2 |  | 42.2 | 69.02 | 10.98 | 415044 | 415.044 | 66.04 | 13.96 | 527688 | 527.688 | 63.06 | 16.94 | 640332 | 640.332 | 60.08 | 19.92 | 752976 | 752.976 | 57.1 | 22.9 | 865620 | 865.62 | 54.12 | 25.88 | 978264 | 978.264 | 51.14 | 28.86 | 1090908 | 1090.908 | 48.16 | 31.84 | 1203552 | 1203.552 | 45.18 | 34.82 | 1316196 | 1316.196 | 42.2 | 37.8 | 1428840 | 1428.84 | 40
2/19/20XX 2:00:00 PM | 0.58333 | 1 | 42 | 50.5 | 42 |  | 42 | 69 | 11 | 415800 | 415.8 | 66 | 14 | 529200 | 529.2 | 63 | 17 | 642600 | 642.6 | 60 | 20 | 756000 | 756 | 57 | 23 | 869400 | 869.4 | 54 | 26 | 982800 | 982.8 | 51 | 29 | 1096200 | 1096.2 | 48 | 32 | 1209600 | 1209.6 | 45 | 35 | 1323000 | 1323 | 42 | 38 | 1436400 | 1436.4 | 40
2/19/20XX 3:00:00 PM | 0.625 | 1 | 42.1 | 46.8 | 42.1 |  | 42.1 | 69.01 | 10.99 | 415422 | 415.422 | 66.02 | 13.98 | 528444 | 528.444 | 63.03 | 16.97 | 641466 | 641.466 | 60.04 | 19.96 | 754488 | 754.488 | 57.05 | 22.95 | 867510 | 867.51 | 54.06 | 25.94 | 980532 | 980.532 | 51.07 | 28.93 | 1093554 | 1093.554 | 48.08 | 31.92 | 1206576 | 1206.576 | 45.09 | 34.91 | 1319598 | 1319.598 | 42.1 | 37.9 | 1432620 | 1432.62 | 40
2/19/20XX 4:00:00 PM | 0.66667 | 1 | 42.7 | 50 | 42.7 |  | 42.7 | 69.07 | 10.93 | 413154 | 413.154 | 66.14 | 13.86 | 523908 | 523.908 | 63.21 | 16.79 | 634662 | 634.662 | 60.28 | 19.72 | 745416 | 745.416 | 57.35 | 22.65 | 856170 | 856.17 | 54.42 | 25.58 | 966924 | 966.924 | 51.49 | 28.51 | 1077678 | 1077.678 | 48.56 | 31.44 | 1188432 | 1188.432 | 45.63 | 34.37 | 1299186 | 1299.186 | 42.7 | 37.3 | 1409940 | 1409.94 | 45
2/19/20XX 5:00:00 PM | 0.70833 | 1 | 41.4 | 53.6 | 41.4 |  | 41.4 | 68.94 | 11.06 | 418068 | 418.068 | 65.88 | 14.12 | 533736 | 533.736 | 62.82 | 17.18 | 649404 | 649.404 | 59.76 | 20.24 | 765072 | 765.072 | 56.7 | 23.3 | 880740 | 880.74 | 53.64 | 26.36 | 996408 | 996.408 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.46 | 35.54 | 1343412 | 1343.412 | 41.4 | 38.6 | 1459080 | 1459.08 | 40
2/19/20XX 6:00:00 PM | 0.75 | 1 | 40.3 | 57.7 | 40.3 |  | 40.3 | 68.83 | 11.17 | 422226 | 422.226 | 65.66 | 14.34 | 542052 | 542.052 | 62.49 | 17.51 | 661878 | 661.878 | 59.32 | 20.68 | 781704 | 781.704 | 56.15 | 23.85 | 901530 | 901.53 | 52.98 | 27.02 | 1021356 | 1021.356 | 49.81 | 30.19 | 1141182 | 1141.182 | 46.64 | 33.36 | 1261008 | 1261.008 | 43.47 | 36.53 | 1380834 | 1380.834 | 40.3 | 39.7 | 1500660 | 1500.66 | 40
2/19/20XX 7:00:00 PM | 0.79167 | 1 | 39.7 | 57.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/19/20XX 8:00:00 PM | 0.83333 | 1 | 38.9 | 56.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/19/20XX 9:00:00 PM | 0.875 | 1 | 38.1 | 57.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/19/20XX 10:00:00 PM | 0.91667 | 1 | 37 | 58.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/19/20XX 11:00:00 PM | 0.95833 | 1 | 36.3 | 57.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/19/20XX 12:00:00 AM | 0 | 2 | 35.3 | 57 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/20/20XX 1:00:00 AM | 0.041667 | 2 | 34.8 | 56 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/20/20XX 2:00:00 AM | 0.083333 | 2 | 34 | 56.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/20/20XX 3:00:00 AM | 0.125 | 2 | 33.7 | 56.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/20/20XX 4:00:00 AM | 0.16667 | 2 | 33.1 | 57.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/20/20XX 5:00:00 AM | 0.20833 | 2 | 32.7 | 55.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/20/20XX 6:00:00 AM | 0.25 | 2 | 32.1 | 58.2 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
2/20/20XX 7:00:00 AM | 0.29167 | 2 | 32.1 | 58.1 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
2/20/20XX 8:00:00 AM | 0.33333 | 2 | 32.4 | 56.9 | 32.4 |  | 32.4 | 68.04 | 11.96 | 452088 | 452.088 | 64.08 | 15.92 | 601776 | 601.776 | 60.12 | 19.88 | 751464 | 751.464 | 56.16 | 23.84 | 901152 | 901.152 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.24 | 31.76 | 1200528 | 1200.528 | 44.28 | 35.72 | 1350216 | 1350.216 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.36 | 43.64 | 1649592 | 1649.592 | 32.4 | 47.6 | 1799280 | 1799.28 | 30
2/20/20XX 9:00:00 AM | 0.375 | 2 | 33.5 | 53.2 | 33.5 |  | 33.5 | 68.15 | 11.85 | 447930 | 447.93 | 64.3 | 15.7 | 593460 | 593.46 | 60.45 | 19.55 | 738990 | 738.99 | 56.6 | 23.4 | 884520 | 884.52 | 52.75 | 27.25 | 1030050 | 1030.05 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.05 | 34.95 | 1321110 | 1321.11 | 41.2 | 38.8 | 1466640 | 1466.64 | 37.35 | 42.65 | 1612170 | 1612.17 | 33.5 | 46.5 | 1757700 | 1757.7 | 35
2/20/20XX 10:00:00 AM | 0.41667 | 2 | 35.3 | 51.3 | 35.3 |  | 35.3 | 68.33 | 11.67 | 441126 | 441.126 | 64.66 | 15.34 | 579852 | 579.852 | 60.99 | 19.01 | 718578 | 718.578 | 57.32 | 22.68 | 857304 | 857.304 | 53.65 | 26.35 | 996030 | 996.03 | 49.98 | 30.02 | 1134756 | 1134.756 | 46.31 | 33.69 | 1273482 | 1273.482 | 42.64 | 37.36 | 1412208 | 1412.208 | 38.97 | 41.03 | 1550934 | 1550.934 | 35.3 | 44.7 | 1689660 | 1689.66 | 35
2/20/20XX 11:00:00 AM | 0.45833 | 2 | 36.9 | 48.1 | 36.9 |  | 36.9 | 68.49 | 11.51 | 435078 | 435.078 | 64.98 | 15.02 | 567756 | 567.756 | 61.47 | 18.53 | 700434 | 700.434 | 57.96 | 22.04 | 833112 | 833.112 | 54.45 | 25.55 | 965790 | 965.79 | 50.94 | 29.06 | 1098468 | 1098.468 | 47.43 | 32.57 | 1231146 | 1231.146 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.41 | 39.59 | 1496502 | 1496.502 | 36.9 | 43.1 | 1629180 | 1629.18 | 35
2/20/20XX 12:00:00 PM | 0.5 | 2 | 39.2 | 45.1 | 39.2 |  | 39.2 | 68.72 | 11.28 | 426384 | 426.384 | 65.44 | 14.56 | 550368 | 550.368 | 62.16 | 17.84 | 674352 | 674.352 | 58.88 | 21.12 | 798336 | 798.336 | 55.6 | 24.4 | 922320 | 922.32 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.04 | 30.96 | 1170288 | 1170.288 | 45.76 | 34.24 | 1294272 | 1294.272 | 42.48 | 37.52 | 1418256 | 1418.256 | 39.2 | 40.8 | 1542240 | 1542.24 | 40
2/20/20XX 1:00:00 PM | 0.54167 | 2 | 41.1 | 42.1 | 41.1 |  | 41.1 | 68.91 | 11.09 | 419202 | 419.202 | 65.82 | 14.18 | 536004 | 536.004 | 62.73 | 17.27 | 652806 | 652.806 | 59.64 | 20.36 | 769608 | 769.608 | 56.55 | 23.45 | 886410 | 886.41 | 53.46 | 26.54 | 1003212 | 1003.212 | 50.37 | 29.63 | 1120014 | 1120.014 | 47.28 | 32.72 | 1236816 | 1236.816 | 44.19 | 35.81 | 1353618 | 1353.618 | 41.1 | 38.9 | 1470420 | 1470.42 | 40
2/20/20XX 2:00:00 PM | 0.58333 | 2 | 42.9 | 38.2 | 42.9 |  | 42.9 | 69.09 | 10.91 | 412398 | 412.398 | 66.18 | 13.82 | 522396 | 522.396 | 63.27 | 16.73 | 632394 | 632.394 | 60.36 | 19.64 | 742392 | 742.392 | 57.45 | 22.55 | 852390 | 852.39 | 54.54 | 25.46 | 962388 | 962.388 | 51.63 | 28.37 | 1072386 | 1072.386 | 48.72 | 31.28 | 1182384 | 1182.384 | 45.81 | 34.19 | 1292382 | 1292.382 | 42.9 | 37.1 | 1402380 | 1402.38 | 45
2/20/20XX 3:00:00 PM | 0.625 | 2 | 43.8 | 37.6 | 43.8 |  | 43.8 | 69.18 | 10.82 | 408996 | 408.996 | 66.36 | 13.64 | 515592 | 515.592 | 63.54 | 16.46 | 622188 | 622.188 | 60.72 | 19.28 | 728784 | 728.784 | 57.9 | 22.1 | 835380 | 835.38 | 55.08 | 24.92 | 941976 | 941.976 | 52.26 | 27.74 | 1048572 | 1048.572 | 49.44 | 30.56 | 1155168 | 1155.168 | 46.62 | 33.38 | 1261764 | 1261.764 | 43.8 | 36.2 | 1368360 | 1368.36 | 45
2/20/20XX 4:00:00 PM | 0.66667 | 2 | 43.8 | 36.9 | 43.8 |  | 43.8 | 69.18 | 10.82 | 408996 | 408.996 | 66.36 | 13.64 | 515592 | 515.592 | 63.54 | 16.46 | 622188 | 622.188 | 60.72 | 19.28 | 728784 | 728.784 | 57.9 | 22.1 | 835380 | 835.38 | 55.08 | 24.92 | 941976 | 941.976 | 52.26 | 27.74 | 1048572 | 1048.572 | 49.44 | 30.56 | 1155168 | 1155.168 | 46.62 | 33.38 | 1261764 | 1261.764 | 43.8 | 36.2 | 1368360 | 1368.36 | 45
2/20/20XX 5:00:00 PM | 0.70833 | 2 | 42.8 | 38.5 | 42.8 |  | 42.8 | 69.08 | 10.92 | 412776 | 412.776 | 66.16 | 13.84 | 523152 | 523.152 | 63.24 | 16.76 | 633528 | 633.528 | 60.32 | 19.68 | 743904 | 743.904 | 57.4 | 22.6 | 854280 | 854.28 | 54.48 | 25.52 | 964656 | 964.656 | 51.56 | 28.44 | 1075032 | 1075.032 | 48.64 | 31.36 | 1185408 | 1185.408 | 45.72 | 34.28 | 1295784 | 1295.784 | 42.8 | 37.2 | 1406160 | 1406.16 | 45
2/20/20XX 6:00:00 PM | 0.75 | 2 | 41.4 | 40 | 41.4 |  | 41.4 | 68.94 | 11.06 | 418068 | 418.068 | 65.88 | 14.12 | 533736 | 533.736 | 62.82 | 17.18 | 649404 | 649.404 | 59.76 | 20.24 | 765072 | 765.072 | 56.7 | 23.3 | 880740 | 880.74 | 53.64 | 26.36 | 996408 | 996.408 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.46 | 35.54 | 1343412 | 1343.412 | 41.4 | 38.6 | 1459080 | 1459.08 | 40
2/20/20XX 7:00:00 PM | 0.79167 | 2 | 40.7 | 42.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/20/20XX 8:00:00 PM | 0.83333 | 2 | 39.4 | 45.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/20/20XX 9:00:00 PM | 0.875 | 2 | 38.8 | 48.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/20/20XX 10:00:00 PM | 0.91667 | 2 | 38.7 | 49.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/20/20XX 11:00:00 PM | 0.95833 | 2 | 38.3 | 50.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/20/20XX 12:00:00 AM | 0 | 3 | 37.4 | 51.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/21/20XX 1:00:00 AM | 0.041667 | 3 | 36.9 | 53.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/21/20XX 2:00:00 AM | 0.083333 | 3 | 35.5 | 57.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/21/20XX 3:00:00 AM | 0.125 | 3 | 35.1 | 59.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/21/20XX 4:00:00 AM | 0.16667 | 3 | 34.8 | 60 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/21/20XX 5:00:00 AM | 0.20833 | 3 | 34.7 | 60.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/21/20XX 6:00:00 AM | 0.25 | 3 | 35 | 62.1 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
2/21/20XX 7:00:00 AM | 0.29167 | 3 | 35 | 63 | 35 |  | 35 | 68.3 | 11.7 | 442260 | 442.26 | 64.6 | 15.4 | 582120 | 582.12 | 60.9 | 19.1 | 721980 | 721.98 | 57.2 | 22.8 | 861840 | 861.84 | 53.5 | 26.5 | 1001700 | 1001.7 | 49.8 | 30.2 | 1141560 | 1141.56 | 46.1 | 33.9 | 1281420 | 1281.42 | 42.4 | 37.6 | 1421280 | 1421.28 | 38.7 | 41.3 | 1561140 | 1561.14 | 35 | 45 | 1701000 | 1701 | 35
2/21/20XX 8:00:00 AM | 0.33333 | 3 | 35.5 | 62.2 | 35.5 |  | 35.5 | 68.35 | 11.65 | 440370 | 440.37 | 64.7 | 15.3 | 578340 | 578.34 | 61.05 | 18.95 | 716310 | 716.31 | 57.4 | 22.6 | 854280 | 854.28 | 53.75 | 26.25 | 992250 | 992.25 | 50.1 | 29.9 | 1130220 | 1130.22 | 46.45 | 33.55 | 1268190 | 1268.19 | 42.8 | 37.2 | 1406160 | 1406.16 | 39.15 | 40.85 | 1544130 | 1544.13 | 35.5 | 44.5 | 1682100 | 1682.1 | 35
2/21/20XX 9:00:00 AM | 0.375 | 3 | 36.7 | 60 | 36.7 |  | 36.7 | 68.47 | 11.53 | 435834 | 435.834 | 64.94 | 15.06 | 569268 | 569.268 | 61.41 | 18.59 | 702702 | 702.702 | 57.88 | 22.12 | 836136 | 836.136 | 54.35 | 25.65 | 969570 | 969.57 | 50.82 | 29.18 | 1103004 | 1103.004 | 47.29 | 32.71 | 1236438 | 1236.438 | 43.76 | 36.24 | 1369872 | 1369.872 | 40.23 | 39.77 | 1503306 | 1503.306 | 36.7 | 43.3 | 1636740 | 1636.74 | 35
2/21/20XX 10:00:00 AM | 0.41667 | 3 | 37.9 | 59 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
2/21/20XX 11:00:00 AM | 0.45833 | 3 | 40.5 | 54.6 | 40.5 |  | 40.5 | 68.85 | 11.15 | 421470 | 421.47 | 65.7 | 14.3 | 540540 | 540.54 | 62.55 | 17.45 | 659610 | 659.61 | 59.4 | 20.6 | 778680 | 778.68 | 56.25 | 23.75 | 897750 | 897.75 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.95 | 30.05 | 1135890 | 1135.89 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.65 | 36.35 | 1374030 | 1374.03 | 40.5 | 39.5 | 1493100 | 1493.1 | 40
2/21/20XX 12:00:00 PM | 0.5 | 3 | 42 | 53.1 | 42 |  | 42 | 69 | 11 | 415800 | 415.8 | 66 | 14 | 529200 | 529.2 | 63 | 17 | 642600 | 642.6 | 60 | 20 | 756000 | 756 | 57 | 23 | 869400 | 869.4 | 54 | 26 | 982800 | 982.8 | 51 | 29 | 1096200 | 1096.2 | 48 | 32 | 1209600 | 1209.6 | 45 | 35 | 1323000 | 1323 | 42 | 38 | 1436400 | 1436.4 | 40
2/21/20XX 1:00:00 PM | 0.54167 | 3 | 43 | 51.3 | 43 |  | 43 | 69.1 | 10.9 | 412020 | 412.02 | 66.2 | 13.8 | 521640 | 521.64 | 63.3 | 16.7 | 631260 | 631.26 | 60.4 | 19.6 | 740880 | 740.88 | 57.5 | 22.5 | 850500 | 850.5 | 54.6 | 25.4 | 960120 | 960.12 | 51.7 | 28.3 | 1069740 | 1069.74 | 48.8 | 31.2 | 1179360 | 1179.36 | 45.9 | 34.1 | 1288980 | 1288.98 | 43 | 37 | 1398600 | 1398.6 | 45
2/21/20XX 2:00:00 PM | 0.58333 | 3 | 43.5 | 53 | 43.5 |  | 43.5 | 69.15 | 10.85 | 410130 | 410.13 | 66.3 | 13.7 | 517860 | 517.86 | 63.45 | 16.55 | 625590 | 625.59 | 60.6 | 19.4 | 733320 | 733.32 | 57.75 | 22.25 | 841050 | 841.05 | 54.9 | 25.1 | 948780 | 948.78 | 52.05 | 27.95 | 1056510 | 1056.51 | 49.2 | 30.8 | 1164240 | 1164.24 | 46.35 | 33.65 | 1271970 | 1271.97 | 43.5 | 36.5 | 1379700 | 1379.7 | 45
2/21/20XX 3:00:00 PM | 0.625 | 3 | 43.9 | 54.6 | 43.9 |  | 43.9 | 69.19 | 10.81 | 408618 | 408.618 | 66.38 | 13.62 | 514836 | 514.836 | 63.57 | 16.43 | 621054 | 621.054 | 60.76 | 19.24 | 727272 | 727.272 | 57.95 | 22.05 | 833490 | 833.49 | 55.14 | 24.86 | 939708 | 939.708 | 52.33 | 27.67 | 1045926 | 1045.926 | 49.52 | 30.48 | 1152144 | 1152.144 | 46.71 | 33.29 | 1258362 | 1258.362 | 43.9 | 36.1 | 1364580 | 1364.58 | 45
2/21/20XX 4:00:00 PM | 0.66667 | 3 | 44.2 | 54.8 | 44.2 |  | 44.2 | 69.22 | 10.78 | 407484 | 407.484 | 66.44 | 13.56 | 512568 | 512.568 | 63.66 | 16.34 | 617652 | 617.652 | 60.88 | 19.12 | 722736 | 722.736 | 58.1 | 21.9 | 827820 | 827.82 | 55.32 | 24.68 | 932904 | 932.904 | 52.54 | 27.46 | 1037988 | 1037.988 | 49.76 | 30.24 | 1143072 | 1143.072 | 46.98 | 33.02 | 1248156 | 1248.156 | 44.2 | 35.8 | 1353240 | 1353.24 | 45
2/21/20XX 5:00:00 PM | 0.70833 | 3 | 43.7 | 55.2 | 43.7 |  | 43.7 | 69.17 | 10.83 | 409374 | 409.374 | 66.34 | 13.66 | 516348 | 516.348 | 63.51 | 16.49 | 623322 | 623.322 | 60.68 | 19.32 | 730296 | 730.296 | 57.85 | 22.15 | 837270 | 837.27 | 55.02 | 24.98 | 944244 | 944.244 | 52.19 | 27.81 | 1051218 | 1051.218 | 49.36 | 30.64 | 1158192 | 1158.192 | 46.53 | 33.47 | 1265166 | 1265.166 | 43.7 | 36.3 | 1372140 | 1372.14 | 45
2/21/20XX 6:00:00 PM | 0.75 | 3 | 42.9 | 57.1 | 42.9 |  | 42.9 | 69.09 | 10.91 | 412398 | 412.398 | 66.18 | 13.82 | 522396 | 522.396 | 63.27 | 16.73 | 632394 | 632.394 | 60.36 | 19.64 | 742392 | 742.392 | 57.45 | 22.55 | 852390 | 852.39 | 54.54 | 25.46 | 962388 | 962.388 | 51.63 | 28.37 | 1072386 | 1072.386 | 48.72 | 31.28 | 1182384 | 1182.384 | 45.81 | 34.19 | 1292382 | 1292.382 | 42.9 | 37.1 | 1402380 | 1402.38 | 45
2/21/20XX 7:00:00 PM | 0.79167 | 3 | 42.5 | 58.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/21/20XX 8:00:00 PM | 0.83333 | 3 | 41.4 | 58.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/21/20XX 9:00:00 PM | 0.875 | 3 | 40.4 | 62.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/21/20XX 10:00:00 PM | 0.91667 | 3 | 39.5 | 62.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/21/20XX 11:00:00 PM | 0.95833 | 3 | 39.1 | 62.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/21/20XX 12:00:00 AM | 0 | 4 | 38.7 | 63.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/22/20XX 1:00:00 AM | 0.041667 | 4 | 38.4 | 64 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/22/20XX 2:00:00 AM | 0.083333 | 4 | 37.9 | 61.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/22/20XX 3:00:00 AM | 0.125 | 4 | 37.1 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/22/20XX 4:00:00 AM | 0.16667 | 4 | 36.6 | 65.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/22/20XX 5:00:00 AM | 0.20833 | 4 | 36.5 | 65.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/22/20XX 6:00:00 AM | 0.25 | 4 | 36 | 66.7 | 36 |  | 36 | 68.4 | 11.6 | 438480 | 438.48 | 64.8 | 15.2 | 574560 | 574.56 | 61.2 | 18.8 | 710640 | 710.64 | 57.6 | 22.4 | 846720 | 846.72 | 54 | 26 | 982800 | 982.8 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.2 | 36.8 | 1391040 | 1391.04 | 39.6 | 40.4 | 1527120 | 1527.12 | 36 | 44 | 1663200 | 1663.2 | 35
2/22/20XX 7:00:00 AM | 0.29167 | 4 | 35.9 | 66.9 | 35.9 |  | 35.9 | 68.39 | 11.61 | 438858 | 438.858 | 64.78 | 15.22 | 575316 | 575.316 | 61.17 | 18.83 | 711774 | 711.774 | 57.56 | 22.44 | 848232 | 848.232 | 53.95 | 26.05 | 984690 | 984.69 | 50.34 | 29.66 | 1121148 | 1121.148 | 46.73 | 33.27 | 1257606 | 1257.606 | 43.12 | 36.88 | 1394064 | 1394.064 | 39.51 | 40.49 | 1530522 | 1530.522 | 35.9 | 44.1 | 1666980 | 1666.98 | 35
2/22/20XX 8:00:00 AM | 0.33333 | 4 | 36.4 | 64.4 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
2/22/20XX 9:00:00 AM | 0.375 | 4 | 37.4 | 62.7 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
2/22/20XX 10:00:00 AM | 0.41667 | 4 | 39.2 | 58.5 | 39.2 |  | 39.2 | 68.72 | 11.28 | 426384 | 426.384 | 65.44 | 14.56 | 550368 | 550.368 | 62.16 | 17.84 | 674352 | 674.352 | 58.88 | 21.12 | 798336 | 798.336 | 55.6 | 24.4 | 922320 | 922.32 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.04 | 30.96 | 1170288 | 1170.288 | 45.76 | 34.24 | 1294272 | 1294.272 | 42.48 | 37.52 | 1418256 | 1418.256 | 39.2 | 40.8 | 1542240 | 1542.24 | 40
2/22/20XX 11:00:00 AM | 0.45833 | 4 | 40.6 | 56.2 | 40.6 |  | 40.6 | 68.86 | 11.14 | 421092 | 421.092 | 65.72 | 14.28 | 539784 | 539.784 | 62.58 | 17.42 | 658476 | 658.476 | 59.44 | 20.56 | 777168 | 777.168 | 56.3 | 23.7 | 895860 | 895.86 | 53.16 | 26.84 | 1014552 | 1014.552 | 50.02 | 29.98 | 1133244 | 1133.244 | 46.88 | 33.12 | 1251936 | 1251.936 | 43.74 | 36.26 | 1370628 | 1370.628 | 40.6 | 39.4 | 1489320 | 1489.32 | 40
2/22/20XX 12:00:00 PM | 0.5 | 4 | 42.6 | 53 | 42.6 |  | 42.6 | 69.06 | 10.94 | 413532 | 413.532 | 66.12 | 13.88 | 524664 | 524.664 | 63.18 | 16.82 | 635796 | 635.796 | 60.24 | 19.76 | 746928 | 746.928 | 57.3 | 22.7 | 858060 | 858.06 | 54.36 | 25.64 | 969192 | 969.192 | 51.42 | 28.58 | 1080324 | 1080.324 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.54 | 34.46 | 1302588 | 1302.588 | 42.6 | 37.4 | 1413720 | 1413.72 | 45
2/22/20XX 1:00:00 PM | 0.54167 | 4 | 43.7 | 51.1 | 43.7 |  | 43.7 | 69.17 | 10.83 | 409374 | 409.374 | 66.34 | 13.66 | 516348 | 516.348 | 63.51 | 16.49 | 623322 | 623.322 | 60.68 | 19.32 | 730296 | 730.296 | 57.85 | 22.15 | 837270 | 837.27 | 55.02 | 24.98 | 944244 | 944.244 | 52.19 | 27.81 | 1051218 | 1051.218 | 49.36 | 30.64 | 1158192 | 1158.192 | 46.53 | 33.47 | 1265166 | 1265.166 | 43.7 | 36.3 | 1372140 | 1372.14 | 45
2/22/20XX 2:00:00 PM | 0.58333 | 4 | 44.9 | 50.1 | 44.9 |  | 44.9 | 69.29 | 10.71 | 404838 | 404.838 | 66.58 | 13.42 | 507276 | 507.276 | 63.87 | 16.13 | 609714 | 609.714 | 61.16 | 18.84 | 712152 | 712.152 | 58.45 | 21.55 | 814590 | 814.59 | 55.74 | 24.26 | 917028 | 917.028 | 53.03 | 26.97 | 1019466 | 1019.466 | 50.32 | 29.68 | 1121904 | 1121.904 | 47.61 | 32.39 | 1224342 | 1224.342 | 44.9 | 35.1 | 1326780 | 1326.78 | 45
2/22/20XX 3:00:00 PM | 0.625 | 4 | 45.1 | 49.5 | 45.1 |  | 45.1 | 69.31 | 10.69 | 404082 | 404.082 | 66.62 | 13.38 | 505764 | 505.764 | 63.93 | 16.07 | 607446 | 607.446 | 61.24 | 18.76 | 709128 | 709.128 | 58.55 | 21.45 | 810810 | 810.81 | 55.86 | 24.14 | 912492 | 912.492 | 53.17 | 26.83 | 1014174 | 1014.174 | 50.48 | 29.52 | 1115856 | 1115.856 | 47.79 | 32.21 | 1217538 | 1217.538 | 45.1 | 34.9 | 1319220 | 1319.22 | 45
2/22/20XX 4:00:00 PM | 0.66667 | 4 | 45.4 | 49.3 | 45.4 |  | 45.4 | 69.34 | 10.66 | 402948 | 402.948 | 66.68 | 13.32 | 503496 | 503.496 | 64.02 | 15.98 | 604044 | 604.044 | 61.36 | 18.64 | 704592 | 704.592 | 58.7 | 21.3 | 805140 | 805.14 | 56.04 | 23.96 | 905688 | 905.688 | 53.38 | 26.62 | 1006236 | 1006.236 | 50.72 | 29.28 | 1106784 | 1106.784 | 48.06 | 31.94 | 1207332 | 1207.332 | 45.4 | 34.6 | 1307880 | 1307.88 | 45
2/22/20XX 5:00:00 PM | 0.70833 | 4 | 44.2 | 54.9 | 44.2 |  | 44.2 | 69.22 | 10.78 | 407484 | 407.484 | 66.44 | 13.56 | 512568 | 512.568 | 63.66 | 16.34 | 617652 | 617.652 | 60.88 | 19.12 | 722736 | 722.736 | 58.1 | 21.9 | 827820 | 827.82 | 55.32 | 24.68 | 932904 | 932.904 | 52.54 | 27.46 | 1037988 | 1037.988 | 49.76 | 30.24 | 1143072 | 1143.072 | 46.98 | 33.02 | 1248156 | 1248.156 | 44.2 | 35.8 | 1353240 | 1353.24 | 45
2/22/20XX 6:00:00 PM | 0.75 | 4 | 43.1 | 57.9 | 43.1 |  | 43.1 | 69.11 | 10.89 | 411642 | 411.642 | 66.22 | 13.78 | 520884 | 520.884 | 63.33 | 16.67 | 630126 | 630.126 | 60.44 | 19.56 | 739368 | 739.368 | 57.55 | 22.45 | 848610 | 848.61 | 54.66 | 25.34 | 957852 | 957.852 | 51.77 | 28.23 | 1067094 | 1067.094 | 48.88 | 31.12 | 1176336 | 1176.336 | 45.99 | 34.01 | 1285578 | 1285.578 | 43.1 | 36.9 | 1394820 | 1394.82 | 45
2/22/20XX 7:00:00 PM | 0.79167 | 4 | 42 | 61.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/22/20XX 8:00:00 PM | 0.83333 | 4 | 41.8 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/22/20XX 9:00:00 PM | 0.875 | 4 | 41.5 | 57 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/22/20XX 10:00:00 PM | 0.91667 | 4 | 40.5 | 59.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/22/20XX 11:00:00 PM | 0.95833 | 4 | 39.8 | 60.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/22/20XX 12:00:00 AM | 0 | 5 | 39.3 | 62.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/23/20XX 1:00:00 AM | 0.041667 | 5 | 38.9 | 63.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/23/20XX 2:00:00 AM | 0.083333 | 5 | 37.9 | 64.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/23/20XX 3:00:00 AM | 0.125 | 5 | 37.6 | 64.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/23/20XX 4:00:00 AM | 0.16667 | 5 | 37.4 | 66.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/23/20XX 5:00:00 AM | 0.20833 | 5 | 37 | 68.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/23/20XX 6:00:00 AM | 0.25 | 5 | 36.2 | 70.6 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
2/23/20XX 7:00:00 AM | 0.29167 | 5 | 36 | 70.7 | 36 |  | 36 | 68.4 | 11.6 | 438480 | 438.48 | 64.8 | 15.2 | 574560 | 574.56 | 61.2 | 18.8 | 710640 | 710.64 | 57.6 | 22.4 | 846720 | 846.72 | 54 | 26 | 982800 | 982.8 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.2 | 36.8 | 1391040 | 1391.04 | 39.6 | 40.4 | 1527120 | 1527.12 | 36 | 44 | 1663200 | 1663.2 | 35
2/23/20XX 8:00:00 AM | 0.33333 | 5 | 36.2 | 69.1 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
2/23/20XX 9:00:00 AM | 0.375 | 5 | 36.6 | 66.9 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
2/23/20XX 10:00:00 AM | 0.41667 | 5 | 37.9 | 64.6 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
2/23/20XX 11:00:00 AM | 0.45833 | 5 | 38.9 | 61.9 | 38.9 |  | 38.9 | 68.69 | 11.31 | 427518 | 427.518 | 65.38 | 14.62 | 552636 | 552.636 | 62.07 | 17.93 | 677754 | 677.754 | 58.76 | 21.24 | 802872 | 802.872 | 55.45 | 24.55 | 927990 | 927.99 | 52.14 | 27.86 | 1053108 | 1053.108 | 48.83 | 31.17 | 1178226 | 1178.226 | 45.52 | 34.48 | 1303344 | 1303.344 | 42.21 | 37.79 | 1428462 | 1428.462 | 38.9 | 41.1 | 1553580 | 1553.58 | 40
2/23/20XX 12:00:00 PM | 0.5 | 5 | 39.7 | 61.6 | 39.7 |  | 39.7 | 68.77 | 11.23 | 424494 | 424.494 | 65.54 | 14.46 | 546588 | 546.588 | 62.31 | 17.69 | 668682 | 668.682 | 59.08 | 20.92 | 790776 | 790.776 | 55.85 | 24.15 | 912870 | 912.87 | 52.62 | 27.38 | 1034964 | 1034.964 | 49.39 | 30.61 | 1157058 | 1157.058 | 46.16 | 33.84 | 1279152 | 1279.152 | 42.93 | 37.07 | 1401246 | 1401.246 | 39.7 | 40.3 | 1523340 | 1523.34 | 40
2/23/20XX 1:00:00 PM | 0.54167 | 5 | 40.6 | 60.5 | 40.6 |  | 40.6 | 68.86 | 11.14 | 421092 | 421.092 | 65.72 | 14.28 | 539784 | 539.784 | 62.58 | 17.42 | 658476 | 658.476 | 59.44 | 20.56 | 777168 | 777.168 | 56.3 | 23.7 | 895860 | 895.86 | 53.16 | 26.84 | 1014552 | 1014.552 | 50.02 | 29.98 | 1133244 | 1133.244 | 46.88 | 33.12 | 1251936 | 1251.936 | 43.74 | 36.26 | 1370628 | 1370.628 | 40.6 | 39.4 | 1489320 | 1489.32 | 40
2/23/20XX 2:00:00 PM | 0.58333 | 5 | 41.5 | 59.8 | 41.5 |  | 41.5 | 68.95 | 11.05 | 417690 | 417.69 | 65.9 | 14.1 | 532980 | 532.98 | 62.85 | 17.15 | 648270 | 648.27 | 59.8 | 20.2 | 763560 | 763.56 | 56.75 | 23.25 | 878850 | 878.85 | 53.7 | 26.3 | 994140 | 994.14 | 50.65 | 29.35 | 1109430 | 1109.43 | 47.6 | 32.4 | 1224720 | 1224.72 | 44.55 | 35.45 | 1340010 | 1340.01 | 41.5 | 38.5 | 1455300 | 1455.3 | 40
2/23/20XX 3:00:00 PM | 0.625 | 5 | 41.9 | 58.6 | 41.9 |  | 41.9 | 68.99 | 11.01 | 416178 | 416.178 | 65.98 | 14.02 | 529956 | 529.956 | 62.97 | 17.03 | 643734 | 643.734 | 59.96 | 20.04 | 757512 | 757.512 | 56.95 | 23.05 | 871290 | 871.29 | 53.94 | 26.06 | 985068 | 985.068 | 50.93 | 29.07 | 1098846 | 1098.846 | 47.92 | 32.08 | 1212624 | 1212.624 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.9 | 38.1 | 1440180 | 1440.18 | 40
2/23/20XX 4:00:00 PM | 0.66667 | 5 | 41.5 | 57.6 | 41.5 |  | 41.5 | 68.95 | 11.05 | 417690 | 417.69 | 65.9 | 14.1 | 532980 | 532.98 | 62.85 | 17.15 | 648270 | 648.27 | 59.8 | 20.2 | 763560 | 763.56 | 56.75 | 23.25 | 878850 | 878.85 | 53.7 | 26.3 | 994140 | 994.14 | 50.65 | 29.35 | 1109430 | 1109.43 | 47.6 | 32.4 | 1224720 | 1224.72 | 44.55 | 35.45 | 1340010 | 1340.01 | 41.5 | 38.5 | 1455300 | 1455.3 | 40
2/23/20XX 5:00:00 PM | 0.70833 | 5 | 40.5 | 60.3 | 40.5 |  | 40.5 | 68.85 | 11.15 | 421470 | 421.47 | 65.7 | 14.3 | 540540 | 540.54 | 62.55 | 17.45 | 659610 | 659.61 | 59.4 | 20.6 | 778680 | 778.68 | 56.25 | 23.75 | 897750 | 897.75 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.95 | 30.05 | 1135890 | 1135.89 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.65 | 36.35 | 1374030 | 1374.03 | 40.5 | 39.5 | 1493100 | 1493.1 | 40
2/23/20XX 6:00:00 PM | 0.75 | 5 | 39.7 | 61.7 | 39.7 |  | 39.7 | 68.77 | 11.23 | 424494 | 424.494 | 65.54 | 14.46 | 546588 | 546.588 | 62.31 | 17.69 | 668682 | 668.682 | 59.08 | 20.92 | 790776 | 790.776 | 55.85 | 24.15 | 912870 | 912.87 | 52.62 | 27.38 | 1034964 | 1034.964 | 49.39 | 30.61 | 1157058 | 1157.058 | 46.16 | 33.84 | 1279152 | 1279.152 | 42.93 | 37.07 | 1401246 | 1401.246 | 39.7 | 40.3 | 1523340 | 1523.34 | 40
2/23/20XX 7:00:00 PM | 0.79167 | 5 | 38.9 | 61.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/23/20XX 8:00:00 PM | 0.83333 | 5 | 38 | 63.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/23/20XX 9:00:00 PM | 0.875 | 5 | 37.2 | 64.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/23/20XX 10:00:00 PM | 0.91667 | 5 | 37.6 | 63.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/23/20XX 11:00:00 PM | 0.95833 | 5 | 37.3 | 63.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/23/20XX 12:00:00 AM | 0 | 6 | 37.1 | 65.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/24/20XX 1:00:00 AM | 0.041667 | 6 | 37.2 | 64.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/24/20XX 2:00:00 AM | 0.083333 | 6 | 36.6 | 66.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/24/20XX 3:00:00 AM | 0.125 | 6 | 36.1 | 68.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/24/20XX 4:00:00 AM | 0.16667 | 6 | 35.3 | 73.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/24/20XX 5:00:00 AM | 0.20833 | 6 | 35 | 72.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/24/20XX 6:00:00 AM | 0.25 | 6 | 34.4 | 73.5 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
2/24/20XX 7:00:00 AM | 0.29167 | 6 | 34.2 | 74.2 | 34.2 |  | 34.2 | 68.22 | 11.78 | 445284 | 445.284 | 64.44 | 15.56 | 588168 | 588.168 | 60.66 | 19.34 | 731052 | 731.052 | 56.88 | 23.12 | 873936 | 873.936 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.32 | 30.68 | 1159704 | 1159.704 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.76 | 38.24 | 1445472 | 1445.472 | 37.98 | 42.02 | 1588356 | 1588.356 | 34.2 | 45.8 | 1731240 | 1731.24 | 35
2/24/20XX 8:00:00 AM | 0.33333 | 6 | 35.1 | 71.3 | 35.1 |  | 35.1 | 68.31 | 11.69 | 441882 | 441.882 | 64.62 | 15.38 | 581364 | 581.364 | 60.93 | 19.07 | 720846 | 720.846 | 57.24 | 22.76 | 860328 | 860.328 | 53.55 | 26.45 | 999810 | 999.81 | 49.86 | 30.14 | 1139292 | 1139.292 | 46.17 | 33.83 | 1278774 | 1278.774 | 42.48 | 37.52 | 1418256 | 1418.256 | 38.79 | 41.21 | 1557738 | 1557.738 | 35.1 | 44.9 | 1697220 | 1697.22 | 35
2/24/20XX 9:00:00 AM | 0.375 | 6 | 36.4 | 67.9 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
2/24/20XX 10:00:00 AM | 0.41667 | 6 | 37.7 | 67 | 37.7 |  | 37.7 | 68.57 | 11.43 | 432054 | 432.054 | 65.14 | 14.86 | 561708 | 561.708 | 61.71 | 18.29 | 691362 | 691.362 | 58.28 | 21.72 | 821016 | 821.016 | 54.85 | 25.15 | 950670 | 950.67 | 51.42 | 28.58 | 1080324 | 1080.324 | 47.99 | 32.01 | 1209978 | 1209.978 | 44.56 | 35.44 | 1339632 | 1339.632 | 41.13 | 38.87 | 1469286 | 1469.286 | 37.7 | 42.3 | 1598940 | 1598.94 | 40
2/24/20XX 11:00:00 AM | 0.45833 | 6 | 39.4 | 63.3 | 39.4 |  | 39.4 | 68.74 | 11.26 | 425628 | 425.628 | 65.48 | 14.52 | 548856 | 548.856 | 62.22 | 17.78 | 672084 | 672.084 | 58.96 | 21.04 | 795312 | 795.312 | 55.7 | 24.3 | 918540 | 918.54 | 52.44 | 27.56 | 1041768 | 1041.768 | 49.18 | 30.82 | 1164996 | 1164.996 | 45.92 | 34.08 | 1288224 | 1288.224 | 42.66 | 37.34 | 1411452 | 1411.452 | 39.4 | 40.6 | 1534680 | 1534.68 | 40
2/24/20XX 12:00:00 PM | 0.5 | 6 | 41.6 | 59.8 | 41.6 |  | 41.6 | 68.96 | 11.04 | 417312 | 417.312 | 65.92 | 14.08 | 532224 | 532.224 | 62.88 | 17.12 | 647136 | 647.136 | 59.84 | 20.16 | 762048 | 762.048 | 56.8 | 23.2 | 876960 | 876.96 | 53.76 | 26.24 | 991872 | 991.872 | 50.72 | 29.28 | 1106784 | 1106.784 | 47.68 | 32.32 | 1221696 | 1221.696 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.6 | 38.4 | 1451520 | 1451.52 | 40
2/24/20XX 1:00:00 PM | 0.54167 | 6 | 42.1 | 59.3 | 42.1 |  | 42.1 | 69.01 | 10.99 | 415422 | 415.422 | 66.02 | 13.98 | 528444 | 528.444 | 63.03 | 16.97 | 641466 | 641.466 | 60.04 | 19.96 | 754488 | 754.488 | 57.05 | 22.95 | 867510 | 867.51 | 54.06 | 25.94 | 980532 | 980.532 | 51.07 | 28.93 | 1093554 | 1093.554 | 48.08 | 31.92 | 1206576 | 1206.576 | 45.09 | 34.91 | 1319598 | 1319.598 | 42.1 | 37.9 | 1432620 | 1432.62 | 40
2/24/20XX 2:00:00 PM | 0.58333 | 6 | 42.4 | 58.4 | 42.4 |  | 42.4 | 69.04 | 10.96 | 414288 | 414.288 | 66.08 | 13.92 | 526176 | 526.176 | 63.12 | 16.88 | 638064 | 638.064 | 60.16 | 19.84 | 749952 | 749.952 | 57.2 | 22.8 | 861840 | 861.84 | 54.24 | 25.76 | 973728 | 973.728 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.32 | 31.68 | 1197504 | 1197.504 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.4 | 37.6 | 1421280 | 1421.28 | 40
2/24/20XX 3:00:00 PM | 0.625 | 6 | 42.3 | 61.7 | 42.3 |  | 42.3 | 69.03 | 10.97 | 414666 | 414.666 | 66.06 | 13.94 | 526932 | 526.932 | 63.09 | 16.91 | 639198 | 639.198 | 60.12 | 19.88 | 751464 | 751.464 | 57.15 | 22.85 | 863730 | 863.73 | 54.18 | 25.82 | 975996 | 975.996 | 51.21 | 28.79 | 1088262 | 1088.262 | 48.24 | 31.76 | 1200528 | 1200.528 | 45.27 | 34.73 | 1312794 | 1312.794 | 42.3 | 37.7 | 1425060 | 1425.06 | 40
2/24/20XX 4:00:00 PM | 0.66667 | 6 | 43.2 | 63 | 43.2 |  | 43.2 | 69.12 | 10.88 | 411264 | 411.264 | 66.24 | 13.76 | 520128 | 520.128 | 63.36 | 16.64 | 628992 | 628.992 | 60.48 | 19.52 | 737856 | 737.856 | 57.6 | 22.4 | 846720 | 846.72 | 54.72 | 25.28 | 955584 | 955.584 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.08 | 33.92 | 1282176 | 1282.176 | 43.2 | 36.8 | 1391040 | 1391.04 | 45
2/24/20XX 5:00:00 PM | 0.70833 | 6 | 42.1 | 66.6 | 42.1 |  | 42.1 | 69.01 | 10.99 | 415422 | 415.422 | 66.02 | 13.98 | 528444 | 528.444 | 63.03 | 16.97 | 641466 | 641.466 | 60.04 | 19.96 | 754488 | 754.488 | 57.05 | 22.95 | 867510 | 867.51 | 54.06 | 25.94 | 980532 | 980.532 | 51.07 | 28.93 | 1093554 | 1093.554 | 48.08 | 31.92 | 1206576 | 1206.576 | 45.09 | 34.91 | 1319598 | 1319.598 | 42.1 | 37.9 | 1432620 | 1432.62 | 40
2/24/20XX 6:00:00 PM | 0.75 | 6 | 41.7 | 66.7 | 41.7 |  | 41.7 | 68.97 | 11.03 | 416934 | 416.934 | 65.94 | 14.06 | 531468 | 531.468 | 62.91 | 17.09 | 646002 | 646.002 | 59.88 | 20.12 | 760536 | 760.536 | 56.85 | 23.15 | 875070 | 875.07 | 53.82 | 26.18 | 989604 | 989.604 | 50.79 | 29.21 | 1104138 | 1104.138 | 47.76 | 32.24 | 1218672 | 1218.672 | 44.73 | 35.27 | 1333206 | 1333.206 | 41.7 | 38.3 | 1447740 | 1447.74 | 40
2/24/20XX 7:00:00 PM | 0.79167 | 6 | 41.6 | 67 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/24/20XX 8:00:00 PM | 0.83333 | 6 | 41.3 | 68.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/24/20XX 9:00:00 PM | 0.875 | 6 | 40.8 | 69.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/24/20XX 10:00:00 PM | 0.91667 | 6 | 40.3 | 69.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/24/20XX 11:00:00 PM | 0.95833 | 6 | 40.2 | 69.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/24/20XX 12:00:00 AM | 0 | 7 | 39.5 | 68.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/25/20XX 1:00:00 AM | 0.041667 | 7 | 39.2 | 68.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/25/20XX 2:00:00 AM | 0.083333 | 7 | 39 | 69.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/25/20XX 3:00:00 AM | 0.125 | 7 | 38.5 | 70.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/25/20XX 4:00:00 AM | 0.16667 | 7 | 37.3 | 71.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/25/20XX 5:00:00 AM | 0.20833 | 7 | 36.8 | 72.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/25/20XX 6:00:00 AM | 0.25 | 7 | 36.5 | 73.6 | 36.5 |  | 36.5 | 68.45 | 11.55 | 436590 | 436.59 | 64.9 | 15.1 | 570780 | 570.78 | 61.35 | 18.65 | 704970 | 704.97 | 57.8 | 22.2 | 839160 | 839.16 | 54.25 | 25.75 | 973350 | 973.35 | 50.7 | 29.3 | 1107540 | 1107.54 | 47.15 | 32.85 | 1241730 | 1241.73 | 43.6 | 36.4 | 1375920 | 1375.92 | 40.05 | 39.95 | 1510110 | 1510.11 | 36.5 | 43.5 | 1644300 | 1644.3 | 35
2/25/20XX 7:00:00 AM | 0.29167 | 7 | 36.4 | 73.6 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
2/25/20XX 8:00:00 AM | 0.33333 | 7 | 37 | 72.2 | 37 |  | 37 | 68.5 | 11.5 | 434700 | 434.7 | 65 | 15 | 567000 | 567 | 61.5 | 18.5 | 699300 | 699.3 | 58 | 22 | 831600 | 831.6 | 54.5 | 25.5 | 963900 | 963.9 | 51 | 29 | 1096200 | 1096.2 | 47.5 | 32.5 | 1228500 | 1228.5 | 44 | 36 | 1360800 | 1360.8 | 40.5 | 39.5 | 1493100 | 1493.1 | 37 | 43 | 1625400 | 1625.4 | 35
2/25/20XX 9:00:00 AM | 0.375 | 7 | 38.2 | 68.5 | 38.2 |  | 38.2 | 68.62 | 11.38 | 430164 | 430.164 | 65.24 | 14.76 | 557928 | 557.928 | 61.86 | 18.14 | 685692 | 685.692 | 58.48 | 21.52 | 813456 | 813.456 | 55.1 | 24.9 | 941220 | 941.22 | 51.72 | 28.28 | 1068984 | 1068.984 | 48.34 | 31.66 | 1196748 | 1196.748 | 44.96 | 35.04 | 1324512 | 1324.512 | 41.58 | 38.42 | 1452276 | 1452.276 | 38.2 | 41.8 | 1580040 | 1580.04 | 40
2/25/20XX 10:00:00 AM | 0.41667 | 7 | 39.9 | 66.7 | 39.9 |  | 39.9 | 68.79 | 11.21 | 423738 | 423.738 | 65.58 | 14.42 | 545076 | 545.076 | 62.37 | 17.63 | 666414 | 666.414 | 59.16 | 20.84 | 787752 | 787.752 | 55.95 | 24.05 | 909090 | 909.09 | 52.74 | 27.26 | 1030428 | 1030.428 | 49.53 | 30.47 | 1151766 | 1151.766 | 46.32 | 33.68 | 1273104 | 1273.104 | 43.11 | 36.89 | 1394442 | 1394.442 | 39.9 | 40.1 | 1515780 | 1515.78 | 40
2/25/20XX 11:00:00 AM | 0.45833 | 7 | 41.7 | 64.2 | 41.7 |  | 41.7 | 68.97 | 11.03 | 416934 | 416.934 | 65.94 | 14.06 | 531468 | 531.468 | 62.91 | 17.09 | 646002 | 646.002 | 59.88 | 20.12 | 760536 | 760.536 | 56.85 | 23.15 | 875070 | 875.07 | 53.82 | 26.18 | 989604 | 989.604 | 50.79 | 29.21 | 1104138 | 1104.138 | 47.76 | 32.24 | 1218672 | 1218.672 | 44.73 | 35.27 | 1333206 | 1333.206 | 41.7 | 38.3 | 1447740 | 1447.74 | 40
2/25/20XX 12:00:00 PM | 0.5 | 7 | 42.4 | 63.1 | 42.4 |  | 42.4 | 69.04 | 10.96 | 414288 | 414.288 | 66.08 | 13.92 | 526176 | 526.176 | 63.12 | 16.88 | 638064 | 638.064 | 60.16 | 19.84 | 749952 | 749.952 | 57.2 | 22.8 | 861840 | 861.84 | 54.24 | 25.76 | 973728 | 973.728 | 51.28 | 28.72 | 1085616 | 1085.616 | 48.32 | 31.68 | 1197504 | 1197.504 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.4 | 37.6 | 1421280 | 1421.28 | 40
2/25/20XX 1:00:00 PM | 0.54167 | 7 | 42.6 | 61.7 | 42.6 |  | 42.6 | 69.06 | 10.94 | 413532 | 413.532 | 66.12 | 13.88 | 524664 | 524.664 | 63.18 | 16.82 | 635796 | 635.796 | 60.24 | 19.76 | 746928 | 746.928 | 57.3 | 22.7 | 858060 | 858.06 | 54.36 | 25.64 | 969192 | 969.192 | 51.42 | 28.58 | 1080324 | 1080.324 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.54 | 34.46 | 1302588 | 1302.588 | 42.6 | 37.4 | 1413720 | 1413.72 | 45
2/25/20XX 2:00:00 PM | 0.58333 | 7 | 42.9 | 59.8 | 42.9 |  | 42.9 | 69.09 | 10.91 | 412398 | 412.398 | 66.18 | 13.82 | 522396 | 522.396 | 63.27 | 16.73 | 632394 | 632.394 | 60.36 | 19.64 | 742392 | 742.392 | 57.45 | 22.55 | 852390 | 852.39 | 54.54 | 25.46 | 962388 | 962.388 | 51.63 | 28.37 | 1072386 | 1072.386 | 48.72 | 31.28 | 1182384 | 1182.384 | 45.81 | 34.19 | 1292382 | 1292.382 | 42.9 | 37.1 | 1402380 | 1402.38 | 45
2/25/20XX 3:00:00 PM | 0.625 | 7 | 43 | 58.8 | 43 |  | 43 | 69.1 | 10.9 | 412020 | 412.02 | 66.2 | 13.8 | 521640 | 521.64 | 63.3 | 16.7 | 631260 | 631.26 | 60.4 | 19.6 | 740880 | 740.88 | 57.5 | 22.5 | 850500 | 850.5 | 54.6 | 25.4 | 960120 | 960.12 | 51.7 | 28.3 | 1069740 | 1069.74 | 48.8 | 31.2 | 1179360 | 1179.36 | 45.9 | 34.1 | 1288980 | 1288.98 | 43 | 37 | 1398600 | 1398.6 | 45
2/25/20XX 4:00:00 PM | 0.66667 | 7 | 42.1 | 60 | 42.1 |  | 42.1 | 69.01 | 10.99 | 415422 | 415.422 | 66.02 | 13.98 | 528444 | 528.444 | 63.03 | 16.97 | 641466 | 641.466 | 60.04 | 19.96 | 754488 | 754.488 | 57.05 | 22.95 | 867510 | 867.51 | 54.06 | 25.94 | 980532 | 980.532 | 51.07 | 28.93 | 1093554 | 1093.554 | 48.08 | 31.92 | 1206576 | 1206.576 | 45.09 | 34.91 | 1319598 | 1319.598 | 42.1 | 37.9 | 1432620 | 1432.62 | 40
2/25/20XX 5:00:00 PM | 0.70833 | 7 | 40.6 | 62.4 | 40.6 |  | 40.6 | 68.86 | 11.14 | 421092 | 421.092 | 65.72 | 14.28 | 539784 | 539.784 | 62.58 | 17.42 | 658476 | 658.476 | 59.44 | 20.56 | 777168 | 777.168 | 56.3 | 23.7 | 895860 | 895.86 | 53.16 | 26.84 | 1014552 | 1014.552 | 50.02 | 29.98 | 1133244 | 1133.244 | 46.88 | 33.12 | 1251936 | 1251.936 | 43.74 | 36.26 | 1370628 | 1370.628 | 40.6 | 39.4 | 1489320 | 1489.32 | 40
2/25/20XX 6:00:00 PM | 0.75 | 7 | 39.9 | 63.4 | 39.9 |  | 39.9 | 68.79 | 11.21 | 423738 | 423.738 | 65.58 | 14.42 | 545076 | 545.076 | 62.37 | 17.63 | 666414 | 666.414 | 59.16 | 20.84 | 787752 | 787.752 | 55.95 | 24.05 | 909090 | 909.09 | 52.74 | 27.26 | 1030428 | 1030.428 | 49.53 | 30.47 | 1151766 | 1151.766 | 46.32 | 33.68 | 1273104 | 1273.104 | 43.11 | 36.89 | 1394442 | 1394.442 | 39.9 | 40.1 | 1515780 | 1515.78 | 40
2/25/20XX 7:00:00 PM | 0.79167 | 7 | 39.2 | 65.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/25/20XX 8:00:00 PM | 0.83333 | 7 | 37.9 | 65.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/25/20XX 9:00:00 PM | 0.875 | 7 | 37.6 | 63.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/25/20XX 10:00:00 PM | 0.91667 | 7 | 36.8 | 63.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/25/20XX 11:00:00 PM | 0.95833 | 7 | 36.2 | 60.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/25/20XX 12:00:00 AM | 0 | 1 | 35.4 | 58.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/26/20XX 1:00:00 AM | 0.041667 | 1 | 34.8 | 57.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/26/20XX 2:00:00 AM | 0.083333 | 1 | 34.2 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/26/20XX 3:00:00 AM | 0.125 | 1 | 33.7 | 59.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/26/20XX 4:00:00 AM | 0.16667 | 1 | 33.2 | 58.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/26/20XX 5:00:00 AM | 0.20833 | 1 | 32.8 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/26/20XX 6:00:00 AM | 0.25 | 1 | 32.3 | 60.4 | 32.3 |  | 32.3 | 68.03 | 11.97 | 452466 | 452.466 | 64.06 | 15.94 | 602532 | 602.532 | 60.09 | 19.91 | 752598 | 752.598 | 56.12 | 23.88 | 902664 | 902.664 | 52.15 | 27.85 | 1052730 | 1052.73 | 48.18 | 31.82 | 1202796 | 1202.796 | 44.21 | 35.79 | 1352862 | 1352.862 | 40.24 | 39.76 | 1502928 | 1502.928 | 36.27 | 43.73 | 1652994 | 1652.994 | 32.3 | 47.7 | 1803060 | 1803.06 | 30
2/26/20XX 7:00:00 AM | 0.29167 | 1 | 32.1 | 61 | 32.1 |  | 32.1 | 68.01 | 11.99 | 453222 | 453.222 | 64.02 | 15.98 | 604044 | 604.044 | 60.03 | 19.97 | 754866 | 754.866 | 56.04 | 23.96 | 905688 | 905.688 | 52.05 | 27.95 | 1056510 | 1056.51 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.07 | 35.93 | 1358154 | 1358.154 | 40.08 | 39.92 | 1508976 | 1508.976 | 36.09 | 43.91 | 1659798 | 1659.798 | 32.1 | 47.9 | 1810620 | 1810.62 | 30
2/26/20XX 8:00:00 AM | 0.33333 | 1 | 32.3 | 60.2 | 32.3 |  | 32.3 | 68.03 | 11.97 | 452466 | 452.466 | 64.06 | 15.94 | 602532 | 602.532 | 60.09 | 19.91 | 752598 | 752.598 | 56.12 | 23.88 | 902664 | 902.664 | 52.15 | 27.85 | 1052730 | 1052.73 | 48.18 | 31.82 | 1202796 | 1202.796 | 44.21 | 35.79 | 1352862 | 1352.862 | 40.24 | 39.76 | 1502928 | 1502.928 | 36.27 | 43.73 | 1652994 | 1652.994 | 32.3 | 47.7 | 1803060 | 1803.06 | 30
2/26/20XX 9:00:00 AM | 0.375 | 1 | 33.2 | 59.4 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
2/26/20XX 10:00:00 AM | 0.41667 | 1 | 34 | 56 | 34 |  | 34 | 68.2 | 11.8 | 446040 | 446.04 | 64.4 | 15.6 | 589680 | 589.68 | 60.6 | 19.4 | 733320 | 733.32 | 56.8 | 23.2 | 876960 | 876.96 | 53 | 27 | 1020600 | 1020.6 | 49.2 | 30.8 | 1164240 | 1164.24 | 45.4 | 34.6 | 1307880 | 1307.88 | 41.6 | 38.4 | 1451520 | 1451.52 | 37.8 | 42.2 | 1595160 | 1595.16 | 34 | 46 | 1738800 | 1738.8 | 35
2/26/20XX 11:00:00 AM | 0.45833 | 1 | 34.9 | 54.2 | 34.9 |  | 34.9 | 68.29 | 11.71 | 442638 | 442.638 | 64.58 | 15.42 | 582876 | 582.876 | 60.87 | 19.13 | 723114 | 723.114 | 57.16 | 22.84 | 863352 | 863.352 | 53.45 | 26.55 | 1003590 | 1003.59 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.03 | 33.97 | 1284066 | 1284.066 | 42.32 | 37.68 | 1424304 | 1424.304 | 38.61 | 41.39 | 1564542 | 1564.542 | 34.9 | 45.1 | 1704780 | 1704.78 | 35
2/26/20XX 12:00:00 PM | 0.5 | 1 | 36.8 | 52 | 36.8 |  | 36.8 | 68.48 | 11.52 | 435456 | 435.456 | 64.96 | 15.04 | 568512 | 568.512 | 61.44 | 18.56 | 701568 | 701.568 | 57.92 | 22.08 | 834624 | 834.624 | 54.4 | 25.6 | 967680 | 967.68 | 50.88 | 29.12 | 1100736 | 1100.736 | 47.36 | 32.64 | 1233792 | 1233.792 | 43.84 | 36.16 | 1366848 | 1366.848 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.8 | 43.2 | 1632960 | 1632.96 | 35
2/26/20XX 1:00:00 PM | 0.54167 | 1 | 37.6 | 48.9 | 37.6 |  | 37.6 | 68.56 | 11.44 | 432432 | 432.432 | 65.12 | 14.88 | 562464 | 562.464 | 61.68 | 18.32 | 692496 | 692.496 | 58.24 | 21.76 | 822528 | 822.528 | 54.8 | 25.2 | 952560 | 952.56 | 51.36 | 28.64 | 1082592 | 1082.592 | 47.92 | 32.08 | 1212624 | 1212.624 | 44.48 | 35.52 | 1342656 | 1342.656 | 41.04 | 38.96 | 1472688 | 1472.688 | 37.6 | 42.4 | 1602720 | 1602.72 | 40
2/26/20XX 2:00:00 PM | 0.58333 | 1 | 38.2 | 48.4 | 38.2 |  | 38.2 | 68.62 | 11.38 | 430164 | 430.164 | 65.24 | 14.76 | 557928 | 557.928 | 61.86 | 18.14 | 685692 | 685.692 | 58.48 | 21.52 | 813456 | 813.456 | 55.1 | 24.9 | 941220 | 941.22 | 51.72 | 28.28 | 1068984 | 1068.984 | 48.34 | 31.66 | 1196748 | 1196.748 | 44.96 | 35.04 | 1324512 | 1324.512 | 41.58 | 38.42 | 1452276 | 1452.276 | 38.2 | 41.8 | 1580040 | 1580.04 | 40
2/26/20XX 3:00:00 PM | 0.625 | 1 | 39 | 44.6 | 39 |  | 39 | 68.7 | 11.3 | 427140 | 427.14 | 65.4 | 14.6 | 551880 | 551.88 | 62.1 | 17.9 | 676620 | 676.62 | 58.8 | 21.2 | 801360 | 801.36 | 55.5 | 24.5 | 926100 | 926.1 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.6 | 34.4 | 1300320 | 1300.32 | 42.3 | 37.7 | 1425060 | 1425.06 | 39 | 41 | 1549800 | 1549.8 | 40
2/26/20XX 4:00:00 PM | 0.66667 | 1 | 39.1 | 43.1 | 39.1 |  | 39.1 | 68.71 | 11.29 | 426762 | 426.762 | 65.42 | 14.58 | 551124 | 551.124 | 62.13 | 17.87 | 675486 | 675.486 | 58.84 | 21.16 | 799848 | 799.848 | 55.55 | 24.45 | 924210 | 924.21 | 52.26 | 27.74 | 1048572 | 1048.572 | 48.97 | 31.03 | 1172934 | 1172.934 | 45.68 | 34.32 | 1297296 | 1297.296 | 42.39 | 37.61 | 1421658 | 1421.658 | 39.1 | 40.9 | 1546020 | 1546.02 | 40
2/26/20XX 5:00:00 PM | 0.70833 | 1 | 38.6 | 43.8 | 38.6 |  | 38.6 | 68.66 | 11.34 | 428652 | 428.652 | 65.32 | 14.68 | 554904 | 554.904 | 61.98 | 18.02 | 681156 | 681.156 | 58.64 | 21.36 | 807408 | 807.408 | 55.3 | 24.7 | 933660 | 933.66 | 51.96 | 28.04 | 1059912 | 1059.912 | 48.62 | 31.38 | 1186164 | 1186.164 | 45.28 | 34.72 | 1312416 | 1312.416 | 41.94 | 38.06 | 1438668 | 1438.668 | 38.6 | 41.4 | 1564920 | 1564.92 | 40
2/26/20XX 6:00:00 PM | 0.75 | 1 | 37.3 | 47.2 | 37.3 |  | 37.3 | 68.53 | 11.47 | 433566 | 433.566 | 65.06 | 14.94 | 564732 | 564.732 | 61.59 | 18.41 | 695898 | 695.898 | 58.12 | 21.88 | 827064 | 827.064 | 54.65 | 25.35 | 958230 | 958.23 | 51.18 | 28.82 | 1089396 | 1089.396 | 47.71 | 32.29 | 1220562 | 1220.562 | 44.24 | 35.76 | 1351728 | 1351.728 | 40.77 | 39.23 | 1482894 | 1482.894 | 37.3 | 42.7 | 1614060 | 1614.06 | 35
2/26/20XX 7:00:00 PM | 0.79167 | 1 | 37 | 47.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/26/20XX 8:00:00 PM | 0.83333 | 1 | 35.9 | 49.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/26/20XX 9:00:00 PM | 0.875 | 1 | 35.1 | 53 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/26/20XX 10:00:00 PM | 0.91667 | 1 | 34.4 | 55.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/26/20XX 11:00:00 PM | 0.95833 | 1 | 33.7 | 57.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/26/20XX 12:00:00 AM | 0 | 2 | 33.7 | 55.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/20XX 1:00:00 AM | 0.041667 | 2 | 33.3 | 57.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/20XX 2:00:00 AM | 0.083333 | 2 | 33.4 | 59 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/20XX 3:00:00 AM | 0.125 | 2 | 33.2 | 61.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/20XX 4:00:00 AM | 0.16667 | 2 | 32.9 | 63.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/20XX 5:00:00 AM | 0.20833 | 2 | 33 | 64 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/20XX 6:00:00 AM | 0.25 | 2 | 33.2 | 63.9 | 33.2 |  | 33.2 | 68.12 | 11.88 | 449064 | 449.064 | 64.24 | 15.76 | 595728 | 595.728 | 60.36 | 19.64 | 742392 | 742.392 | 56.48 | 23.52 | 889056 | 889.056 | 52.6 | 27.4 | 1035720 | 1035.72 | 48.72 | 31.28 | 1182384 | 1182.384 | 44.84 | 35.16 | 1329048 | 1329.048 | 40.96 | 39.04 | 1475712 | 1475.712 | 37.08 | 42.92 | 1622376 | 1622.376 | 33.2 | 46.8 | 1769040 | 1769.04 | 35
2/27/20XX 7:00:00 AM | 0.29167 | 2 | 33.4 | 64.4 | 33.4 |  | 33.4 | 68.14 | 11.86 | 448308 | 448.308 | 64.28 | 15.72 | 594216 | 594.216 | 60.42 | 19.58 | 740124 | 740.124 | 56.56 | 23.44 | 886032 | 886.032 | 52.7 | 27.3 | 1031940 | 1031.94 | 48.84 | 31.16 | 1177848 | 1177.848 | 44.98 | 35.02 | 1323756 | 1323.756 | 41.12 | 38.88 | 1469664 | 1469.664 | 37.26 | 42.74 | 1615572 | 1615.572 | 33.4 | 46.6 | 1761480 | 1761.48 | 35
2/27/20XX 8:00:00 AM | 0.33333 | 2 | 34.4 | 63 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
2/27/20XX 9:00:00 AM | 0.375 | 2 | 36 | 60.1 | 36 |  | 36 | 68.4 | 11.6 | 438480 | 438.48 | 64.8 | 15.2 | 574560 | 574.56 | 61.2 | 18.8 | 710640 | 710.64 | 57.6 | 22.4 | 846720 | 846.72 | 54 | 26 | 982800 | 982.8 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.2 | 36.8 | 1391040 | 1391.04 | 39.6 | 40.4 | 1527120 | 1527.12 | 36 | 44 | 1663200 | 1663.2 | 35
2/27/20XX 10:00:00 AM | 0.41667 | 2 | 38.2 | 54.6 | 38.2 |  | 38.2 | 68.62 | 11.38 | 430164 | 430.164 | 65.24 | 14.76 | 557928 | 557.928 | 61.86 | 18.14 | 685692 | 685.692 | 58.48 | 21.52 | 813456 | 813.456 | 55.1 | 24.9 | 941220 | 941.22 | 51.72 | 28.28 | 1068984 | 1068.984 | 48.34 | 31.66 | 1196748 | 1196.748 | 44.96 | 35.04 | 1324512 | 1324.512 | 41.58 | 38.42 | 1452276 | 1452.276 | 38.2 | 41.8 | 1580040 | 1580.04 | 40
2/27/20XX 11:00:00 AM | 0.45833 | 2 | 39.8 | 54.2 | 39.8 |  | 39.8 | 68.78 | 11.22 | 424116 | 424.116 | 65.56 | 14.44 | 545832 | 545.832 | 62.34 | 17.66 | 667548 | 667.548 | 59.12 | 20.88 | 789264 | 789.264 | 55.9 | 24.1 | 910980 | 910.98 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.46 | 30.54 | 1154412 | 1154.412 | 46.24 | 33.76 | 1276128 | 1276.128 | 43.02 | 36.98 | 1397844 | 1397.844 | 39.8 | 40.2 | 1519560 | 1519.56 | 40
2/27/20XX 12:00:00 PM | 0.5 | 2 | 41.6 | 52 | 41.6 |  | 41.6 | 68.96 | 11.04 | 417312 | 417.312 | 65.92 | 14.08 | 532224 | 532.224 | 62.88 | 17.12 | 647136 | 647.136 | 59.84 | 20.16 | 762048 | 762.048 | 56.8 | 23.2 | 876960 | 876.96 | 53.76 | 26.24 | 991872 | 991.872 | 50.72 | 29.28 | 1106784 | 1106.784 | 47.68 | 32.32 | 1221696 | 1221.696 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.6 | 38.4 | 1451520 | 1451.52 | 40
2/27/20XX 1:00:00 PM | 0.54167 | 2 | 43.3 | 50.6 | 43.3 |  | 43.3 | 69.13 | 10.87 | 410886 | 410.886 | 66.26 | 13.74 | 519372 | 519.372 | 63.39 | 16.61 | 627858 | 627.858 | 60.52 | 19.48 | 736344 | 736.344 | 57.65 | 22.35 | 844830 | 844.83 | 54.78 | 25.22 | 953316 | 953.316 | 51.91 | 28.09 | 1061802 | 1061.802 | 49.04 | 30.96 | 1170288 | 1170.288 | 46.17 | 33.83 | 1278774 | 1278.774 | 43.3 | 36.7 | 1387260 | 1387.26 | 45
2/27/20XX 2:00:00 PM | 0.58333 | 2 | 44.4 | 44.6 | 44.4 |  | 44.4 | 69.24 | 10.76 | 406728 | 406.728 | 66.48 | 13.52 | 511056 | 511.056 | 63.72 | 16.28 | 615384 | 615.384 | 60.96 | 19.04 | 719712 | 719.712 | 58.2 | 21.8 | 824040 | 824.04 | 55.44 | 24.56 | 928368 | 928.368 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.92 | 30.08 | 1137024 | 1137.024 | 47.16 | 32.84 | 1241352 | 1241.352 | 44.4 | 35.6 | 1345680 | 1345.68 | 45
2/27/20XX 3:00:00 PM | 0.625 | 2 | 44.8 | 45.4 | 44.8 |  | 44.8 | 69.28 | 10.72 | 405216 | 405.216 | 66.56 | 13.44 | 508032 | 508.032 | 63.84 | 16.16 | 610848 | 610.848 | 61.12 | 18.88 | 713664 | 713.664 | 58.4 | 21.6 | 816480 | 816.48 | 55.68 | 24.32 | 919296 | 919.296 | 52.96 | 27.04 | 1022112 | 1022.112 | 50.24 | 29.76 | 1124928 | 1124.928 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.8 | 35.2 | 1330560 | 1330.56 | 45
2/27/20XX 4:00:00 PM | 0.66667 | 2 | 44.7 | 46.8 | 44.7 |  | 44.7 | 69.27 | 10.73 | 405594 | 405.594 | 66.54 | 13.46 | 508788 | 508.788 | 63.81 | 16.19 | 611982 | 611.982 | 61.08 | 18.92 | 715176 | 715.176 | 58.35 | 21.65 | 818370 | 818.37 | 55.62 | 24.38 | 921564 | 921.564 | 52.89 | 27.11 | 1024758 | 1024.758 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.43 | 32.57 | 1231146 | 1231.146 | 44.7 | 35.3 | 1334340 | 1334.34 | 45
2/27/20XX 5:00:00 PM | 0.70833 | 2 | 44.1 | 48.1 | 44.1 |  | 44.1 | 69.21 | 10.79 | 407862 | 407.862 | 66.42 | 13.58 | 513324 | 513.324 | 63.63 | 16.37 | 618786 | 618.786 | 60.84 | 19.16 | 724248 | 724.248 | 58.05 | 21.95 | 829710 | 829.71 | 55.26 | 24.74 | 935172 | 935.172 | 52.47 | 27.53 | 1040634 | 1040.634 | 49.68 | 30.32 | 1146096 | 1146.096 | 46.89 | 33.11 | 1251558 | 1251.558 | 44.1 | 35.9 | 1357020 | 1357.02 | 45
2/27/20XX 6:00:00 PM | 0.75 | 2 | 43.5 | 46.6 | 43.5 |  | 43.5 | 69.15 | 10.85 | 410130 | 410.13 | 66.3 | 13.7 | 517860 | 517.86 | 63.45 | 16.55 | 625590 | 625.59 | 60.6 | 19.4 | 733320 | 733.32 | 57.75 | 22.25 | 841050 | 841.05 | 54.9 | 25.1 | 948780 | 948.78 | 52.05 | 27.95 | 1056510 | 1056.51 | 49.2 | 30.8 | 1164240 | 1164.24 | 46.35 | 33.65 | 1271970 | 1271.97 | 43.5 | 36.5 | 1379700 | 1379.7 | 45
2/27/20XX 7:00:00 PM | 0.79167 | 2 | 42.3 | 51.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/20XX 8:00:00 PM | 0.83333 | 2 | 41.4 | 53.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/20XX 9:00:00 PM | 0.875 | 2 | 41.6 | 50.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/20XX 10:00:00 PM | 0.91667 | 2 | 40.9 | 52.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/20XX 11:00:00 PM | 0.95833 | 2 | 40 | 54.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/20XX 12:00:00 AM | 0 | 3 | 39.5 | 55.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/28/20XX 1:00:00 AM | 0.041667 | 3 | 38.8 | 55.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/28/20XX 2:00:00 AM | 0.083333 | 3 | 38.4 | 55.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/28/20XX 3:00:00 AM | 0.125 | 3 | 36.8 | 55.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/28/20XX 4:00:00 AM | 0.16667 | 3 | 35.7 | 56.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/28/20XX 5:00:00 AM | 0.20833 | 3 | 35.1 | 58.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/28/20XX 6:00:00 AM | 0.25 | 3 | 34.4 | 59.5 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
2/28/20XX 7:00:00 AM | 0.29167 | 3 | 34.5 | 60.3 | 34.5 |  | 34.5 | 68.25 | 11.75 | 444150 | 444.15 | 64.5 | 15.5 | 585900 | 585.9 | 60.75 | 19.25 | 727650 | 727.65 | 57 | 23 | 869400 | 869.4 | 53.25 | 26.75 | 1011150 | 1011.15 | 49.5 | 30.5 | 1152900 | 1152.9 | 45.75 | 34.25 | 1294650 | 1294.65 | 42 | 38 | 1436400 | 1436.4 | 38.25 | 41.75 | 1578150 | 1578.15 | 34.5 | 45.5 | 1719900 | 1719.9 | 35
2/28/20XX 8:00:00 AM | 0.33333 | 3 | 35.1 | 59.6 | 35.1 |  | 35.1 | 68.31 | 11.69 | 441882 | 441.882 | 64.62 | 15.38 | 581364 | 581.364 | 60.93 | 19.07 | 720846 | 720.846 | 57.24 | 22.76 | 860328 | 860.328 | 53.55 | 26.45 | 999810 | 999.81 | 49.86 | 30.14 | 1139292 | 1139.292 | 46.17 | 33.83 | 1278774 | 1278.774 | 42.48 | 37.52 | 1418256 | 1418.256 | 38.79 | 41.21 | 1557738 | 1557.738 | 35.1 | 44.9 | 1697220 | 1697.22 | 35
2/28/20XX 9:00:00 AM | 0.375 | 3 | 36.3 | 59.1 | 36.3 |  | 36.3 | 68.43 | 11.57 | 437346 | 437.346 | 64.86 | 15.14 | 572292 | 572.292 | 61.29 | 18.71 | 707238 | 707.238 | 57.72 | 22.28 | 842184 | 842.184 | 54.15 | 25.85 | 977130 | 977.13 | 50.58 | 29.42 | 1112076 | 1112.076 | 47.01 | 32.99 | 1247022 | 1247.022 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.87 | 40.13 | 1516914 | 1516.914 | 36.3 | 43.7 | 1651860 | 1651.86 | 35
2/28/20XX 10:00:00 AM | 0.41667 | 3 | 37.9 | 55.7 | 37.9 |  | 37.9 | 68.59 | 11.41 | 431298 | 431.298 | 65.18 | 14.82 | 560196 | 560.196 | 61.77 | 18.23 | 689094 | 689.094 | 58.36 | 21.64 | 817992 | 817.992 | 54.95 | 25.05 | 946890 | 946.89 | 51.54 | 28.46 | 1075788 | 1075.788 | 48.13 | 31.87 | 1204686 | 1204.686 | 44.72 | 35.28 | 1333584 | 1333.584 | 41.31 | 38.69 | 1462482 | 1462.482 | 37.9 | 42.1 | 1591380 | 1591.38 | 40
2/28/20XX 11:00:00 AM | 0.45833 | 3 | 40.2 | 52.5 | 40.2 |  | 40.2 | 68.82 | 11.18 | 422604 | 422.604 | 65.64 | 14.36 | 542808 | 542.808 | 62.46 | 17.54 | 663012 | 663.012 | 59.28 | 20.72 | 783216 | 783.216 | 56.1 | 23.9 | 903420 | 903.42 | 52.92 | 27.08 | 1023624 | 1023.624 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.56 | 33.44 | 1264032 | 1264.032 | 43.38 | 36.62 | 1384236 | 1384.236 | 40.2 | 39.8 | 1504440 | 1504.44 | 40
2/28/20XX 12:00:00 PM | 0.5 | 3 | 42.5 | 49 | 42.5 |  | 42.5 | 69.05 | 10.95 | 413910 | 413.91 | 66.1 | 13.9 | 525420 | 525.42 | 63.15 | 16.85 | 636930 | 636.93 | 60.2 | 19.8 | 748440 | 748.44 | 57.25 | 22.75 | 859950 | 859.95 | 54.3 | 25.7 | 971460 | 971.46 | 51.35 | 28.65 | 1082970 | 1082.97 | 48.4 | 31.6 | 1194480 | 1194.48 | 45.45 | 34.55 | 1305990 | 1305.99 | 42.5 | 37.5 | 1417500 | 1417.5 | 40
2/28/20XX 1:00:00 PM | 0.54167 | 3 | 44.1 | 46.2 | 44.1 |  | 44.1 | 69.21 | 10.79 | 407862 | 407.862 | 66.42 | 13.58 | 513324 | 513.324 | 63.63 | 16.37 | 618786 | 618.786 | 60.84 | 19.16 | 724248 | 724.248 | 58.05 | 21.95 | 829710 | 829.71 | 55.26 | 24.74 | 935172 | 935.172 | 52.47 | 27.53 | 1040634 | 1040.634 | 49.68 | 30.32 | 1146096 | 1146.096 | 46.89 | 33.11 | 1251558 | 1251.558 | 44.1 | 35.9 | 1357020 | 1357.02 | 45
2/28/20XX 2:00:00 PM | 0.58333 | 3 | 44.8 | 45.7 | 44.8 |  | 44.8 | 69.28 | 10.72 | 405216 | 405.216 | 66.56 | 13.44 | 508032 | 508.032 | 63.84 | 16.16 | 610848 | 610.848 | 61.12 | 18.88 | 713664 | 713.664 | 58.4 | 21.6 | 816480 | 816.48 | 55.68 | 24.32 | 919296 | 919.296 | 52.96 | 27.04 | 1022112 | 1022.112 | 50.24 | 29.76 | 1124928 | 1124.928 | 47.52 | 32.48 | 1227744 | 1227.744 | 44.8 | 35.2 | 1330560 | 1330.56 | 45
2/28/20XX 3:00:00 PM | 0.625 | 3 | 45.8 | 45.6 | 45.8 |  | 45.8 | 69.38 | 10.62 | 401436 | 401.436 | 66.76 | 13.24 | 500472 | 500.472 | 64.14 | 15.86 | 599508 | 599.508 | 61.52 | 18.48 | 698544 | 698.544 | 58.9 | 21.1 | 797580 | 797.58 | 56.28 | 23.72 | 896616 | 896.616 | 53.66 | 26.34 | 995652 | 995.652 | 51.04 | 28.96 | 1094688 | 1094.688 | 48.42 | 31.58 | 1193724 | 1193.724 | 45.8 | 34.2 | 1292760 | 1292.76 | 45
2/28/20XX 4:00:00 PM | 0.66667 | 3 | 45.8 | 45.2 | 45.8 |  | 45.8 | 69.38 | 10.62 | 401436 | 401.436 | 66.76 | 13.24 | 500472 | 500.472 | 64.14 | 15.86 | 599508 | 599.508 | 61.52 | 18.48 | 698544 | 698.544 | 58.9 | 21.1 | 797580 | 797.58 | 56.28 | 23.72 | 896616 | 896.616 | 53.66 | 26.34 | 995652 | 995.652 | 51.04 | 28.96 | 1094688 | 1094.688 | 48.42 | 31.58 | 1193724 | 1193.724 | 45.8 | 34.2 | 1292760 | 1292.76 | 45
2/28/20XX 5:00:00 PM | 0.70833 | 3 | 44.9 | 47 | 44.9 |  | 44.9 | 69.29 | 10.71 | 404838 | 404.838 | 66.58 | 13.42 | 507276 | 507.276 | 63.87 | 16.13 | 609714 | 609.714 | 61.16 | 18.84 | 712152 | 712.152 | 58.45 | 21.55 | 814590 | 814.59 | 55.74 | 24.26 | 917028 | 917.028 | 53.03 | 26.97 | 1019466 | 1019.466 | 50.32 | 29.68 | 1121904 | 1121.904 | 47.61 | 32.39 | 1224342 | 1224.342 | 44.9 | 35.1 | 1326780 | 1326.78 | 45
2/28/20XX 6:00:00 PM | 0.75 | 3 | 44 | 47.5 | 44 |  | 44 | 69.2 | 10.8 | 408240 | 408.24 | 66.4 | 13.6 | 514080 | 514.08 | 63.6 | 16.4 | 619920 | 619.92 | 60.8 | 19.2 | 725760 | 725.76 | 58 | 22 | 831600 | 831.6 | 55.2 | 24.8 | 937440 | 937.44 | 52.4 | 27.6 | 1043280 | 1043.28 | 49.6 | 30.4 | 1149120 | 1149.12 | 46.8 | 33.2 | 1254960 | 1254.96 | 44 | 36 | 1360800 | 1360.8 | 45
2/28/20XX 7:00:00 PM | 0.79167 | 3 | 43.4 | 49.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/28/20XX 8:00:00 PM | 0.83333 | 3 | 42 | 49.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/28/20XX 9:00:00 PM | 0.875 | 3 | 41.1 | 52 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/28/20XX 10:00:00 PM | 0.91667 | 3 | 40.6 | 52.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/28/20XX 11:00:00 PM | 0.95833 | 3 | 39.9 | 53.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/28/20XX 12:00:00 AM | 0 | 4 | 39.9 | 52.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/1/20XX 1:00:00 AM | 0.041667 | 4 | 38.9 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/1/20XX 2:00:00 AM | 0.083333 | 4 | 38.3 | 58.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/1/20XX 3:00:00 AM | 0.125 | 4 | 38.1 | 59.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/1/20XX 4:00:00 AM | 0.16667 | 4 | 37.7 | 61.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/1/20XX 5:00:00 AM | 0.20833 | 4 | 36.9 | 63.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/1/20XX 6:00:00 AM | 0.25 | 4 | 37.1 | 63.3 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
3/1/20XX 7:00:00 AM | 0.29167 | 4 | 37.2 | 63.5 | 37.2 |  | 37.2 | 68.52 | 11.48 | 433944 | 433.944 | 65.04 | 14.96 | 565488 | 565.488 | 61.56 | 18.44 | 697032 | 697.032 | 58.08 | 21.92 | 828576 | 828.576 | 54.6 | 25.4 | 960120 | 960.12 | 51.12 | 28.88 | 1091664 | 1091.664 | 47.64 | 32.36 | 1223208 | 1223.208 | 44.16 | 35.84 | 1354752 | 1354.752 | 40.68 | 39.32 | 1486296 | 1486.296 | 37.2 | 42.8 | 1617840 | 1617.84 | 35
3/1/20XX 8:00:00 AM | 0.33333 | 4 | 37.8 | 62.6 | 37.8 |  | 37.8 | 68.58 | 11.42 | 431676 | 431.676 | 65.16 | 14.84 | 560952 | 560.952 | 61.74 | 18.26 | 690228 | 690.228 | 58.32 | 21.68 | 819504 | 819.504 | 54.9 | 25.1 | 948780 | 948.78 | 51.48 | 28.52 | 1078056 | 1078.056 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.22 | 38.78 | 1465884 | 1465.884 | 37.8 | 42.2 | 1595160 | 1595.16 | 40
3/1/20XX 9:00:00 AM | 0.375 | 4 | 39.2 | 59.8 | 39.2 |  | 39.2 | 68.72 | 11.28 | 426384 | 426.384 | 65.44 | 14.56 | 550368 | 550.368 | 62.16 | 17.84 | 674352 | 674.352 | 58.88 | 21.12 | 798336 | 798.336 | 55.6 | 24.4 | 922320 | 922.32 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.04 | 30.96 | 1170288 | 1170.288 | 45.76 | 34.24 | 1294272 | 1294.272 | 42.48 | 37.52 | 1418256 | 1418.256 | 39.2 | 40.8 | 1542240 | 1542.24 | 40
3/1/20XX 10:00:00 AM | 0.41667 | 4 | 40.7 | 57.5 | 40.7 |  | 40.7 | 68.87 | 11.13 | 420714 | 420.714 | 65.74 | 14.26 | 539028 | 539.028 | 62.61 | 17.39 | 657342 | 657.342 | 59.48 | 20.52 | 775656 | 775.656 | 56.35 | 23.65 | 893970 | 893.97 | 53.22 | 26.78 | 1012284 | 1012.284 | 50.09 | 29.91 | 1130598 | 1130.598 | 46.96 | 33.04 | 1248912 | 1248.912 | 43.83 | 36.17 | 1367226 | 1367.226 | 40.7 | 39.3 | 1485540 | 1485.54 | 40
3/1/20XX 11:00:00 AM | 0.45833 | 4 | 41.6 | 53.9 | 41.6 |  | 41.6 | 68.96 | 11.04 | 417312 | 417.312 | 65.92 | 14.08 | 532224 | 532.224 | 62.88 | 17.12 | 647136 | 647.136 | 59.84 | 20.16 | 762048 | 762.048 | 56.8 | 23.2 | 876960 | 876.96 | 53.76 | 26.24 | 991872 | 991.872 | 50.72 | 29.28 | 1106784 | 1106.784 | 47.68 | 32.32 | 1221696 | 1221.696 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.6 | 38.4 | 1451520 | 1451.52 | 40
3/1/20XX 12:00:00 PM | 0.5 | 4 | 43 | 52.8 | 43 |  | 43 | 69.1 | 10.9 | 412020 | 412.02 | 66.2 | 13.8 | 521640 | 521.64 | 63.3 | 16.7 | 631260 | 631.26 | 60.4 | 19.6 | 740880 | 740.88 | 57.5 | 22.5 | 850500 | 850.5 | 54.6 | 25.4 | 960120 | 960.12 | 51.7 | 28.3 | 1069740 | 1069.74 | 48.8 | 31.2 | 1179360 | 1179.36 | 45.9 | 34.1 | 1288980 | 1288.98 | 43 | 37 | 1398600 | 1398.6 | 45
3/1/20XX 1:00:00 PM | 0.54167 | 4 | 43.6 | 55.3 | 43.6 |  | 43.6 | 69.16 | 10.84 | 409752 | 409.752 | 66.32 | 13.68 | 517104 | 517.104 | 63.48 | 16.52 | 624456 | 624.456 | 60.64 | 19.36 | 731808 | 731.808 | 57.8 | 22.2 | 839160 | 839.16 | 54.96 | 25.04 | 946512 | 946.512 | 52.12 | 27.88 | 1053864 | 1053.864 | 49.28 | 30.72 | 1161216 | 1161.216 | 46.44 | 33.56 | 1268568 | 1268.568 | 43.6 | 36.4 | 1375920 | 1375.92 | 45
3/1/20XX 2:00:00 PM | 0.58333 | 4 | 44.5 | 54.9 | 44.5 |  | 44.5 | 69.25 | 10.75 | 406350 | 406.35 | 66.5 | 13.5 | 510300 | 510.3 | 63.75 | 16.25 | 614250 | 614.25 | 61 | 19 | 718200 | 718.2 | 58.25 | 21.75 | 822150 | 822.15 | 55.5 | 24.5 | 926100 | 926.1 | 52.75 | 27.25 | 1030050 | 1030.05 | 50 | 30 | 1134000 | 1134 | 47.25 | 32.75 | 1237950 | 1237.95 | 44.5 | 35.5 | 1341900 | 1341.9 | 45
3/1/20XX 3:00:00 PM | 0.625 | 4 | 44.4 | 55.5 | 44.4 |  | 44.4 | 69.24 | 10.76 | 406728 | 406.728 | 66.48 | 13.52 | 511056 | 511.056 | 63.72 | 16.28 | 615384 | 615.384 | 60.96 | 19.04 | 719712 | 719.712 | 58.2 | 21.8 | 824040 | 824.04 | 55.44 | 24.56 | 928368 | 928.368 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.92 | 30.08 | 1137024 | 1137.024 | 47.16 | 32.84 | 1241352 | 1241.352 | 44.4 | 35.6 | 1345680 | 1345.68 | 45
3/1/20XX 4:00:00 PM | 0.66667 | 4 | 43.9 | 56.3 | 43.9 |  | 43.9 | 69.19 | 10.81 | 408618 | 408.618 | 66.38 | 13.62 | 514836 | 514.836 | 63.57 | 16.43 | 621054 | 621.054 | 60.76 | 19.24 | 727272 | 727.272 | 57.95 | 22.05 | 833490 | 833.49 | 55.14 | 24.86 | 939708 | 939.708 | 52.33 | 27.67 | 1045926 | 1045.926 | 49.52 | 30.48 | 1152144 | 1152.144 | 46.71 | 33.29 | 1258362 | 1258.362 | 43.9 | 36.1 | 1364580 | 1364.58 | 45
3/1/20XX 5:00:00 PM | 0.70833 | 4 | 44.1 | 55.5 | 44.1 |  | 44.1 | 69.21 | 10.79 | 407862 | 407.862 | 66.42 | 13.58 | 513324 | 513.324 | 63.63 | 16.37 | 618786 | 618.786 | 60.84 | 19.16 | 724248 | 724.248 | 58.05 | 21.95 | 829710 | 829.71 | 55.26 | 24.74 | 935172 | 935.172 | 52.47 | 27.53 | 1040634 | 1040.634 | 49.68 | 30.32 | 1146096 | 1146.096 | 46.89 | 33.11 | 1251558 | 1251.558 | 44.1 | 35.9 | 1357020 | 1357.02 | 45
3/1/20XX 6:00:00 PM | 0.75 | 4 | 43.5 | 57.5 | 43.5 |  | 43.5 | 69.15 | 10.85 | 410130 | 410.13 | 66.3 | 13.7 | 517860 | 517.86 | 63.45 | 16.55 | 625590 | 625.59 | 60.6 | 19.4 | 733320 | 733.32 | 57.75 | 22.25 | 841050 | 841.05 | 54.9 | 25.1 | 948780 | 948.78 | 52.05 | 27.95 | 1056510 | 1056.51 | 49.2 | 30.8 | 1164240 | 1164.24 | 46.35 | 33.65 | 1271970 | 1271.97 | 43.5 | 36.5 | 1379700 | 1379.7 | 45
3/1/20XX 7:00:00 PM | 0.79167 | 4 | 42.7 | 57.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/1/20XX 8:00:00 PM | 0.83333 | 4 | 42.5 | 58.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/1/20XX 9:00:00 PM | 0.875 | 4 | 42.2 | 61.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/1/20XX 10:00:00 PM | 0.91667 | 4 | 41 | 70.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/1/20XX 11:00:00 PM | 0.95833 | 4 | 40.7 | 69.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/1/20XX 12:00:00 AM | 0 | 5 | 40.3 | 69 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/2/20XX 1:00:00 AM | 0.041667 | 5 | 39.8 | 69.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/2/20XX 2:00:00 AM | 0.083333 | 5 | 39.4 | 68.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/2/20XX 3:00:00 AM | 0.125 | 5 | 38.9 | 68.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/2/20XX 4:00:00 AM | 0.16667 | 5 | 38.3 | 68.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/2/20XX 5:00:00 AM | 0.20833 | 5 | 37.6 | 67.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/2/20XX 6:00:00 AM | 0.25 | 5 | 36.6 | 67.6 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
3/2/20XX 7:00:00 AM | 0.29167 | 5 | 36.5 | 68.7 | 36.5 |  | 36.5 | 68.45 | 11.55 | 436590 | 436.59 | 64.9 | 15.1 | 570780 | 570.78 | 61.35 | 18.65 | 704970 | 704.97 | 57.8 | 22.2 | 839160 | 839.16 | 54.25 | 25.75 | 973350 | 973.35 | 50.7 | 29.3 | 1107540 | 1107.54 | 47.15 | 32.85 | 1241730 | 1241.73 | 43.6 | 36.4 | 1375920 | 1375.92 | 40.05 | 39.95 | 1510110 | 1510.11 | 36.5 | 43.5 | 1644300 | 1644.3 | 35
3/2/20XX 8:00:00 AM | 0.33333 | 5 | 36.2 | 64.6 | 36.2 |  | 36.2 | 68.42 | 11.58 | 437724 | 437.724 | 64.84 | 15.16 | 573048 | 573.048 | 61.26 | 18.74 | 708372 | 708.372 | 57.68 | 22.32 | 843696 | 843.696 | 54.1 | 25.9 | 979020 | 979.02 | 50.52 | 29.48 | 1114344 | 1114.344 | 46.94 | 33.06 | 1249668 | 1249.668 | 43.36 | 36.64 | 1384992 | 1384.992 | 39.78 | 40.22 | 1520316 | 1520.316 | 36.2 | 43.8 | 1655640 | 1655.64 | 35
3/2/20XX 9:00:00 AM | 0.375 | 5 | 36.6 | 62.2 | 36.6 |  | 36.6 | 68.46 | 11.54 | 436212 | 436.212 | 64.92 | 15.08 | 570024 | 570.024 | 61.38 | 18.62 | 703836 | 703.836 | 57.84 | 22.16 | 837648 | 837.648 | 54.3 | 25.7 | 971460 | 971.46 | 50.76 | 29.24 | 1105272 | 1105.272 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.68 | 36.32 | 1372896 | 1372.896 | 40.14 | 39.86 | 1506708 | 1506.708 | 36.6 | 43.4 | 1640520 | 1640.52 | 35
3/2/20XX 10:00:00 AM | 0.41667 | 5 | 37.4 | 59.4 | 37.4 |  | 37.4 | 68.54 | 11.46 | 433188 | 433.188 | 65.08 | 14.92 | 563976 | 563.976 | 61.62 | 18.38 | 694764 | 694.764 | 58.16 | 21.84 | 825552 | 825.552 | 54.7 | 25.3 | 956340 | 956.34 | 51.24 | 28.76 | 1087128 | 1087.128 | 47.78 | 32.22 | 1217916 | 1217.916 | 44.32 | 35.68 | 1348704 | 1348.704 | 40.86 | 39.14 | 1479492 | 1479.492 | 37.4 | 42.6 | 1610280 | 1610.28 | 35
3/2/20XX 11:00:00 AM | 0.45833 | 5 | 38.3 | 56.2 | 38.3 |  | 38.3 | 68.63 | 11.37 | 429786 | 429.786 | 65.26 | 14.74 | 557172 | 557.172 | 61.89 | 18.11 | 684558 | 684.558 | 58.52 | 21.48 | 811944 | 811.944 | 55.15 | 24.85 | 939330 | 939.33 | 51.78 | 28.22 | 1066716 | 1066.716 | 48.41 | 31.59 | 1194102 | 1194.102 | 45.04 | 34.96 | 1321488 | 1321.488 | 41.67 | 38.33 | 1448874 | 1448.874 | 38.3 | 41.7 | 1576260 | 1576.26 | 40
3/2/20XX 12:00:00 PM | 0.5 | 5 | 38.7 | 52.4 | 38.7 |  | 38.7 | 68.67 | 11.33 | 428274 | 428.274 | 65.34 | 14.66 | 554148 | 554.148 | 62.01 | 17.99 | 680022 | 680.022 | 58.68 | 21.32 | 805896 | 805.896 | 55.35 | 24.65 | 931770 | 931.77 | 52.02 | 27.98 | 1057644 | 1057.644 | 48.69 | 31.31 | 1183518 | 1183.518 | 45.36 | 34.64 | 1309392 | 1309.392 | 42.03 | 37.97 | 1435266 | 1435.266 | 38.7 | 41.3 | 1561140 | 1561.14 | 40
3/2/20XX 1:00:00 PM | 0.54167 | 5 | 39.5 | 50.9 | 39.5 |  | 39.5 | 68.75 | 11.25 | 425250 | 425.25 | 65.5 | 14.5 | 548100 | 548.1 | 62.25 | 17.75 | 670950 | 670.95 | 59 | 21 | 793800 | 793.8 | 55.75 | 24.25 | 916650 | 916.65 | 52.5 | 27.5 | 1039500 | 1039.5 | 49.25 | 30.75 | 1162350 | 1162.35 | 46 | 34 | 1285200 | 1285.2 | 42.75 | 37.25 | 1408050 | 1408.05 | 39.5 | 40.5 | 1530900 | 1530.9 | 40
3/2/20XX 2:00:00 PM | 0.58333 | 5 | 39.9 | 51.9 | 39.9 |  | 39.9 | 68.79 | 11.21 | 423738 | 423.738 | 65.58 | 14.42 | 545076 | 545.076 | 62.37 | 17.63 | 666414 | 666.414 | 59.16 | 20.84 | 787752 | 787.752 | 55.95 | 24.05 | 909090 | 909.09 | 52.74 | 27.26 | 1030428 | 1030.428 | 49.53 | 30.47 | 1151766 | 1151.766 | 46.32 | 33.68 | 1273104 | 1273.104 | 43.11 | 36.89 | 1394442 | 1394.442 | 39.9 | 40.1 | 1515780 | 1515.78 | 40
3/2/20XX 3:00:00 PM | 0.625 | 5 | 39.7 | 51.2 | 39.7 |  | 39.7 | 68.77 | 11.23 | 424494 | 424.494 | 65.54 | 14.46 | 546588 | 546.588 | 62.31 | 17.69 | 668682 | 668.682 | 59.08 | 20.92 | 790776 | 790.776 | 55.85 | 24.15 | 912870 | 912.87 | 52.62 | 27.38 | 1034964 | 1034.964 | 49.39 | 30.61 | 1157058 | 1157.058 | 46.16 | 33.84 | 1279152 | 1279.152 | 42.93 | 37.07 | 1401246 | 1401.246 | 39.7 | 40.3 | 1523340 | 1523.34 | 40
3/2/20XX 4:00:00 PM | 0.66667 | 5 | 39.2 | 52.7 | 39.2 |  | 39.2 | 68.72 | 11.28 | 426384 | 426.384 | 65.44 | 14.56 | 550368 | 550.368 | 62.16 | 17.84 | 674352 | 674.352 | 58.88 | 21.12 | 798336 | 798.336 | 55.6 | 24.4 | 922320 | 922.32 | 52.32 | 27.68 | 1046304 | 1046.304 | 49.04 | 30.96 | 1170288 | 1170.288 | 45.76 | 34.24 | 1294272 | 1294.272 | 42.48 | 37.52 | 1418256 | 1418.256 | 39.2 | 40.8 | 1542240 | 1542.24 | 40
3/2/20XX 5:00:00 PM | 0.70833 | 5 | 38.1 | 53.8 | 38.1 |  | 38.1 | 68.61 | 11.39 | 430542 | 430.542 | 65.22 | 14.78 | 558684 | 558.684 | 61.83 | 18.17 | 686826 | 686.826 | 58.44 | 21.56 | 814968 | 814.968 | 55.05 | 24.95 | 943110 | 943.11 | 51.66 | 28.34 | 1071252 | 1071.252 | 48.27 | 31.73 | 1199394 | 1199.394 | 44.88 | 35.12 | 1327536 | 1327.536 | 41.49 | 38.51 | 1455678 | 1455.678 | 38.1 | 41.9 | 1583820 | 1583.82 | 40
3/2/20XX 6:00:00 PM | 0.75 | 5 | 37.1 | 52.8 | 37.1 |  | 37.1 | 68.51 | 11.49 | 434322 | 434.322 | 65.02 | 14.98 | 566244 | 566.244 | 61.53 | 18.47 | 698166 | 698.166 | 58.04 | 21.96 | 830088 | 830.088 | 54.55 | 25.45 | 962010 | 962.01 | 51.06 | 28.94 | 1093932 | 1093.932 | 47.57 | 32.43 | 1225854 | 1225.854 | 44.08 | 35.92 | 1357776 | 1357.776 | 40.59 | 39.41 | 1489698 | 1489.698 | 37.1 | 42.9 | 1621620 | 1621.62 | 35
3/2/20XX 7:00:00 PM | 0.79167 | 5 | 36.1 | 54.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/2/20XX 8:00:00 PM | 0.83333 | 5 | 35.2 | 52.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/2/20XX 9:00:00 PM | 0.875 | 5 | 34.1 | 54.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/2/20XX 10:00:00 PM | 0.91667 | 5 | 32.7 | 56.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/2/20XX 11:00:00 PM | 0.95833 | 5 | 32.2 | 57 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/2/20XX 12:00:00 AM | 0 | 6 | 31.3 | 56.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/3/20XX 1:00:00 AM | 0.041667 | 6 | 30.8 | 57.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/3/20XX 2:00:00 AM | 0.083333 | 6 | 30.2 | 59.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/3/20XX 3:00:00 AM | 0.125 | 6 | 29.2 | 61.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/3/20XX 4:00:00 AM | 0.16667 | 6 | 28.7 | 62.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/3/20XX 5:00:00 AM | 0.20833 | 6 | 28.5 | 62 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/3/20XX 6:00:00 AM | 0.25 | 6 | 27.9 | 60.8 | 27.9 |  | 27.9 | 67.59 | 12.41 | 469098 | 469.098 | 63.18 | 16.82 | 635796 | 635.796 | 58.77 | 21.23 | 802494 | 802.494 | 54.36 | 25.64 | 969192 | 969.192 | 49.95 | 30.05 | 1135890 | 1135.89 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.13 | 38.87 | 1469286 | 1469.286 | 36.72 | 43.28 | 1635984 | 1635.984 | 32.31 | 47.69 | 1802682 | 1802.682 | 27.9 | 52.1 | 1969380 | 1969.38 | 30
3/3/20XX 7:00:00 AM | 0.29167 | 6 | 27.9 | 58.9 | 27.9 |  | 27.9 | 67.59 | 12.41 | 469098 | 469.098 | 63.18 | 16.82 | 635796 | 635.796 | 58.77 | 21.23 | 802494 | 802.494 | 54.36 | 25.64 | 969192 | 969.192 | 49.95 | 30.05 | 1135890 | 1135.89 | 45.54 | 34.46 | 1302588 | 1302.588 | 41.13 | 38.87 | 1469286 | 1469.286 | 36.72 | 43.28 | 1635984 | 1635.984 | 32.31 | 47.69 | 1802682 | 1802.682 | 27.9 | 52.1 | 1969380 | 1969.38 | 30
3/3/20XX 8:00:00 AM | 0.33333 | 6 | 28.2 | 57.7 | 28.2 |  | 28.2 | 67.62 | 12.38 | 467964 | 467.964 | 63.24 | 16.76 | 633528 | 633.528 | 58.86 | 21.14 | 799092 | 799.092 | 54.48 | 25.52 | 964656 | 964.656 | 50.1 | 29.9 | 1130220 | 1130.22 | 45.72 | 34.28 | 1295784 | 1295.784 | 41.34 | 38.66 | 1461348 | 1461.348 | 36.96 | 43.04 | 1626912 | 1626.912 | 32.58 | 47.42 | 1792476 | 1792.476 | 28.2 | 51.8 | 1958040 | 1958.04 | 30
3/3/20XX 9:00:00 AM | 0.375 | 6 | 29 | 56.5 | 29 |  | 29 | 67.7 | 12.3 | 464940 | 464.94 | 63.4 | 16.6 | 627480 | 627.48 | 59.1 | 20.9 | 790020 | 790.02 | 54.8 | 25.2 | 952560 | 952.56 | 50.5 | 29.5 | 1115100 | 1115.1 | 46.2 | 33.8 | 1277640 | 1277.64 | 41.9 | 38.1 | 1440180 | 1440.18 | 37.6 | 42.4 | 1602720 | 1602.72 | 33.3 | 46.7 | 1765260 | 1765.26 | 29 | 51 | 1927800 | 1927.8 | 30
3/3/20XX 10:00:00 AM | 0.41667 | 6 | 30.3 | 54.2 | 30.3 |  | 30.3 | 67.83 | 12.17 | 460026 | 460.026 | 63.66 | 16.34 | 617652 | 617.652 | 59.49 | 20.51 | 775278 | 775.278 | 55.32 | 24.68 | 932904 | 932.904 | 51.15 | 28.85 | 1090530 | 1090.53 | 46.98 | 33.02 | 1248156 | 1248.156 | 42.81 | 37.19 | 1405782 | 1405.782 | 38.64 | 41.36 | 1563408 | 1563.408 | 34.47 | 45.53 | 1721034 | 1721.034 | 30.3 | 49.7 | 1878660 | 1878.66 | 30
3/3/20XX 11:00:00 AM | 0.45833 | 6 | 32 | 51 | 32 |  | 32 | 68 | 12 | 453600 | 453.6 | 64 | 16 | 604800 | 604.8 | 60 | 20 | 756000 | 756 | 56 | 24 | 907200 | 907.2 | 52 | 28 | 1058400 | 1058.4 | 48 | 32 | 1209600 | 1209.6 | 44 | 36 | 1360800 | 1360.8 | 40 | 40 | 1512000 | 1512 | 36 | 44 | 1663200 | 1663.2 | 32 | 48 | 1814400 | 1814.4 | 30
3/3/20XX 12:00:00 PM | 0.5 | 6 | 33.5 | 47.2 | 33.5 |  | 33.5 | 68.15 | 11.85 | 447930 | 447.93 | 64.3 | 15.7 | 593460 | 593.46 | 60.45 | 19.55 | 738990 | 738.99 | 56.6 | 23.4 | 884520 | 884.52 | 52.75 | 27.25 | 1030050 | 1030.05 | 48.9 | 31.1 | 1175580 | 1175.58 | 45.05 | 34.95 | 1321110 | 1321.11 | 41.2 | 38.8 | 1466640 | 1466.64 | 37.35 | 42.65 | 1612170 | 1612.17 | 33.5 | 46.5 | 1757700 | 1757.7 | 35
3/3/20XX 1:00:00 PM | 0.54167 | 6 | 34.8 | 44.2 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
3/3/20XX 2:00:00 PM | 0.58333 | 6 | 35.2 | 43.1 | 35.2 |  | 35.2 | 68.32 | 11.68 | 441504 | 441.504 | 64.64 | 15.36 | 580608 | 580.608 | 60.96 | 19.04 | 719712 | 719.712 | 57.28 | 22.72 | 858816 | 858.816 | 53.6 | 26.4 | 997920 | 997.92 | 49.92 | 30.08 | 1137024 | 1137.024 | 46.24 | 33.76 | 1276128 | 1276.128 | 42.56 | 37.44 | 1415232 | 1415.232 | 38.88 | 41.12 | 1554336 | 1554.336 | 35.2 | 44.8 | 1693440 | 1693.44 | 35
3/3/20XX 3:00:00 PM | 0.625 | 6 | 35.9 | 41 | 35.9 |  | 35.9 | 68.39 | 11.61 | 438858 | 438.858 | 64.78 | 15.22 | 575316 | 575.316 | 61.17 | 18.83 | 711774 | 711.774 | 57.56 | 22.44 | 848232 | 848.232 | 53.95 | 26.05 | 984690 | 984.69 | 50.34 | 29.66 | 1121148 | 1121.148 | 46.73 | 33.27 | 1257606 | 1257.606 | 43.12 | 36.88 | 1394064 | 1394.064 | 39.51 | 40.49 | 1530522 | 1530.522 | 35.9 | 44.1 | 1666980 | 1666.98 | 35
3/3/20XX 4:00:00 PM | 0.66667 | 6 | 36.4 | 42.3 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
3/3/20XX 5:00:00 PM | 0.70833 | 6 | 35.6 | 43.6 | 35.6 |  | 35.6 | 68.36 | 11.64 | 439992 | 439.992 | 64.72 | 15.28 | 577584 | 577.584 | 61.08 | 18.92 | 715176 | 715.176 | 57.44 | 22.56 | 852768 | 852.768 | 53.8 | 26.2 | 990360 | 990.36 | 50.16 | 29.84 | 1127952 | 1127.952 | 46.52 | 33.48 | 1265544 | 1265.544 | 42.88 | 37.12 | 1403136 | 1403.136 | 39.24 | 40.76 | 1540728 | 1540.728 | 35.6 | 44.4 | 1678320 | 1678.32 | 35
3/3/20XX 6:00:00 PM | 0.75 | 6 | 34.9 | 45.2 | 34.9 |  | 34.9 | 68.29 | 11.71 | 442638 | 442.638 | 64.58 | 15.42 | 582876 | 582.876 | 60.87 | 19.13 | 723114 | 723.114 | 57.16 | 22.84 | 863352 | 863.352 | 53.45 | 26.55 | 1003590 | 1003.59 | 49.74 | 30.26 | 1143828 | 1143.828 | 46.03 | 33.97 | 1284066 | 1284.066 | 42.32 | 37.68 | 1424304 | 1424.304 | 38.61 | 41.39 | 1564542 | 1564.542 | 34.9 | 45.1 | 1704780 | 1704.78 | 35
3/3/20XX 7:00:00 PM | 0.79167 | 6 | 34.7 | 46.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/3/20XX 8:00:00 PM | 0.83333 | 6 | 34.2 | 47 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/3/20XX 9:00:00 PM | 0.875 | 6 | 33.3 | 48.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/3/20XX 10:00:00 PM | 0.91667 | 6 | 32.6 | 48.4 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/3/20XX 11:00:00 PM | 0.95833 | 6 | 32.1 | 48.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/3/20XX 12:00:00 AM | 0 | 7 | 31.4 | 48.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/4/20XX 1:00:00 AM | 0.041667 | 7 | 30.8 | 51.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/4/20XX 2:00:00 AM | 0.083333 | 7 | 30.2 | 54.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/4/20XX 3:00:00 AM | 0.125 | 7 | 29.6 | 56.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/4/20XX 4:00:00 AM | 0.16667 | 7 | 29.6 | 56.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/4/20XX 5:00:00 AM | 0.20833 | 7 | 29.3 | 58.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/4/20XX 6:00:00 AM | 0.25 | 7 | 29 | 60.2 | 29 |  | 29 | 67.7 | 12.3 | 464940 | 464.94 | 63.4 | 16.6 | 627480 | 627.48 | 59.1 | 20.9 | 790020 | 790.02 | 54.8 | 25.2 | 952560 | 952.56 | 50.5 | 29.5 | 1115100 | 1115.1 | 46.2 | 33.8 | 1277640 | 1277.64 | 41.9 | 38.1 | 1440180 | 1440.18 | 37.6 | 42.4 | 1602720 | 1602.72 | 33.3 | 46.7 | 1765260 | 1765.26 | 29 | 51 | 1927800 | 1927.8 | 30
3/4/20XX 7:00:00 AM | 0.29167 | 7 | 29 | 60 | 29 |  | 29 | 67.7 | 12.3 | 464940 | 464.94 | 63.4 | 16.6 | 627480 | 627.48 | 59.1 | 20.9 | 790020 | 790.02 | 54.8 | 25.2 | 952560 | 952.56 | 50.5 | 29.5 | 1115100 | 1115.1 | 46.2 | 33.8 | 1277640 | 1277.64 | 41.9 | 38.1 | 1440180 | 1440.18 | 37.6 | 42.4 | 1602720 | 1602.72 | 33.3 | 46.7 | 1765260 | 1765.26 | 29 | 51 | 1927800 | 1927.8 | 30
3/4/20XX 8:00:00 AM | 0.33333 | 7 | 29.7 | 59.4 | 29.7 |  | 29.7 | 67.77 | 12.23 | 462294 | 462.294 | 63.54 | 16.46 | 622188 | 622.188 | 59.31 | 20.69 | 782082 | 782.082 | 55.08 | 24.92 | 941976 | 941.976 | 50.85 | 29.15 | 1101870 | 1101.87 | 46.62 | 33.38 | 1261764 | 1261.764 | 42.39 | 37.61 | 1421658 | 1421.658 | 38.16 | 41.84 | 1581552 | 1581.552 | 33.93 | 46.07 | 1741446 | 1741.446 | 29.7 | 50.3 | 1901340 | 1901.34 | 30
3/4/20XX 9:00:00 AM | 0.375 | 7 | 31.3 | 57.3 | 31.3 |  | 31.3 | 67.93 | 12.07 | 456246 | 456.246 | 63.86 | 16.14 | 610092 | 610.092 | 59.79 | 20.21 | 763938 | 763.938 | 55.72 | 24.28 | 917784 | 917.784 | 51.65 | 28.35 | 1071630 | 1071.63 | 47.58 | 32.42 | 1225476 | 1225.476 | 43.51 | 36.49 | 1379322 | 1379.322 | 39.44 | 40.56 | 1533168 | 1533.168 | 35.37 | 44.63 | 1687014 | 1687.014 | 31.3 | 48.7 | 1840860 | 1840.86 | 30
3/4/20XX 10:00:00 AM | 0.41667 | 7 | 32.8 | 55.2 | 32.8 |  | 32.8 | 68.08 | 11.92 | 450576 | 450.576 | 64.16 | 15.84 | 598752 | 598.752 | 60.24 | 19.76 | 746928 | 746.928 | 56.32 | 23.68 | 895104 | 895.104 | 52.4 | 27.6 | 1043280 | 1043.28 | 48.48 | 31.52 | 1191456 | 1191.456 | 44.56 | 35.44 | 1339632 | 1339.632 | 40.64 | 39.36 | 1487808 | 1487.808 | 36.72 | 43.28 | 1635984 | 1635.984 | 32.8 | 47.2 | 1784160 | 1784.16 | 35
3/4/20XX 11:00:00 AM | 0.45833 | 7 | 34.4 | 51.8 | 34.4 |  | 34.4 | 68.24 | 11.76 | 444528 | 444.528 | 64.48 | 15.52 | 586656 | 586.656 | 60.72 | 19.28 | 728784 | 728.784 | 56.96 | 23.04 | 870912 | 870.912 | 53.2 | 26.8 | 1013040 | 1013.04 | 49.44 | 30.56 | 1155168 | 1155.168 | 45.68 | 34.32 | 1297296 | 1297.296 | 41.92 | 38.08 | 1439424 | 1439.424 | 38.16 | 41.84 | 1581552 | 1581.552 | 34.4 | 45.6 | 1723680 | 1723.68 | 35
3/4/20XX 12:00:00 PM | 0.5 | 7 | 35.6 | 48.7 | 35.6 |  | 35.6 | 68.36 | 11.64 | 439992 | 439.992 | 64.72 | 15.28 | 577584 | 577.584 | 61.08 | 18.92 | 715176 | 715.176 | 57.44 | 22.56 | 852768 | 852.768 | 53.8 | 26.2 | 990360 | 990.36 | 50.16 | 29.84 | 1127952 | 1127.952 | 46.52 | 33.48 | 1265544 | 1265.544 | 42.88 | 37.12 | 1403136 | 1403.136 | 39.24 | 40.76 | 1540728 | 1540.728 | 35.6 | 44.4 | 1678320 | 1678.32 | 35
3/4/20XX 1:00:00 PM | 0.54167 | 7 | 36.8 | 47.4 | 36.8 |  | 36.8 | 68.48 | 11.52 | 435456 | 435.456 | 64.96 | 15.04 | 568512 | 568.512 | 61.44 | 18.56 | 701568 | 701.568 | 57.92 | 22.08 | 834624 | 834.624 | 54.4 | 25.6 | 967680 | 967.68 | 50.88 | 29.12 | 1100736 | 1100.736 | 47.36 | 32.64 | 1233792 | 1233.792 | 43.84 | 36.16 | 1366848 | 1366.848 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.8 | 43.2 | 1632960 | 1632.96 | 35
3/4/20XX 2:00:00 PM | 0.58333 | 7 | 38.1 | 45.8 | 38.1 |  | 38.1 | 68.61 | 11.39 | 430542 | 430.542 | 65.22 | 14.78 | 558684 | 558.684 | 61.83 | 18.17 | 686826 | 686.826 | 58.44 | 21.56 | 814968 | 814.968 | 55.05 | 24.95 | 943110 | 943.11 | 51.66 | 28.34 | 1071252 | 1071.252 | 48.27 | 31.73 | 1199394 | 1199.394 | 44.88 | 35.12 | 1327536 | 1327.536 | 41.49 | 38.51 | 1455678 | 1455.678 | 38.1 | 41.9 | 1583820 | 1583.82 | 40
3/4/20XX 3:00:00 PM | 0.625 | 7 | 37.8 | 44.1 | 37.8 |  | 37.8 | 68.58 | 11.42 | 431676 | 431.676 | 65.16 | 14.84 | 560952 | 560.952 | 61.74 | 18.26 | 690228 | 690.228 | 58.32 | 21.68 | 819504 | 819.504 | 54.9 | 25.1 | 948780 | 948.78 | 51.48 | 28.52 | 1078056 | 1078.056 | 48.06 | 31.94 | 1207332 | 1207.332 | 44.64 | 35.36 | 1336608 | 1336.608 | 41.22 | 38.78 | 1465884 | 1465.884 | 37.8 | 42.2 | 1595160 | 1595.16 | 40
3/4/20XX 4:00:00 PM | 0.66667 | 7 | 38.4 | 43.1 | 38.4 |  | 38.4 | 68.64 | 11.36 | 429408 | 429.408 | 65.28 | 14.72 | 556416 | 556.416 | 61.92 | 18.08 | 683424 | 683.424 | 58.56 | 21.44 | 810432 | 810.432 | 55.2 | 24.8 | 937440 | 937.44 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.76 | 38.24 | 1445472 | 1445.472 | 38.4 | 41.6 | 1572480 | 1572.48 | 40
3/4/20XX 5:00:00 PM | 0.70833 | 7 | 37.5 | 43.7 | 37.5 |  | 37.5 | 68.55 | 11.45 | 432810 | 432.81 | 65.1 | 14.9 | 563220 | 563.22 | 61.65 | 18.35 | 693630 | 693.63 | 58.2 | 21.8 | 824040 | 824.04 | 54.75 | 25.25 | 954450 | 954.45 | 51.3 | 28.7 | 1084860 | 1084.86 | 47.85 | 32.15 | 1215270 | 1215.27 | 44.4 | 35.6 | 1345680 | 1345.68 | 40.95 | 39.05 | 1476090 | 1476.09 | 37.5 | 42.5 | 1606500 | 1606.5 | 35
3/4/20XX 6:00:00 PM | 0.75 | 7 | 36.4 | 44.5 | 36.4 |  | 36.4 | 68.44 | 11.56 | 436968 | 436.968 | 64.88 | 15.12 | 571536 | 571.536 | 61.32 | 18.68 | 706104 | 706.104 | 57.76 | 22.24 | 840672 | 840.672 | 54.2 | 25.8 | 975240 | 975.24 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.08 | 32.92 | 1244376 | 1244.376 | 43.52 | 36.48 | 1378944 | 1378.944 | 39.96 | 40.04 | 1513512 | 1513.512 | 36.4 | 43.6 | 1648080 | 1648.08 | 35
3/4/20XX 7:00:00 PM | 0.79167 | 7 | 35.9 | 46.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/4/20XX 8:00:00 PM | 0.83333 | 7 | 35 | 48.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/4/20XX 9:00:00 PM | 0.875 | 7 | 34.7 | 51.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/4/20XX 10:00:00 PM | 0.91667 | 7 | 33.7 | 53.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/4/20XX 11:00:00 PM | 0.95833 | 7 | 33.1 | 54.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/4/20XX 12:00:00 AM | 0 | 1 | 32.9 | 55.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/5/20XX 1:00:00 AM | 0.041667 | 1 | 32.5 | 56.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/5/20XX 2:00:00 AM | 0.083333 | 1 | 32.1 | 56.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/5/20XX 3:00:00 AM | 0.125 | 1 | 31.7 | 55.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/5/20XX 4:00:00 AM | 0.16667 | 1 | 31.2 | 56.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/5/20XX 5:00:00 AM | 0.20833 | 1 | 31.1 | 56.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/5/20XX 6:00:00 AM | 0.25 | 1 | 30.8 | 57.8 | 30.8 |  | 30.8 | 67.88 | 12.12 | 458136 | 458.136 | 63.76 | 16.24 | 613872 | 613.872 | 59.64 | 20.36 | 769608 | 769.608 | 55.52 | 24.48 | 925344 | 925.344 | 51.4 | 28.6 | 1081080 | 1081.08 | 47.28 | 32.72 | 1236816 | 1236.816 | 43.16 | 36.84 | 1392552 | 1392.552 | 39.04 | 40.96 | 1548288 | 1548.288 | 34.92 | 45.08 | 1704024 | 1704.024 | 30.8 | 49.2 | 1859760 | 1859.76 | 30
3/5/20XX 7:00:00 AM | 0.29167 | 1 | 30.7 | 58.3 | 30.7 |  | 30.7 | 67.87 | 12.13 | 458514 | 458.514 | 63.74 | 16.26 | 614628 | 614.628 | 59.61 | 20.39 | 770742 | 770.742 | 55.48 | 24.52 | 926856 | 926.856 | 51.35 | 28.65 | 1082970 | 1082.97 | 47.22 | 32.78 | 1239084 | 1239.084 | 43.09 | 36.91 | 1395198 | 1395.198 | 38.96 | 41.04 | 1551312 | 1551.312 | 34.83 | 45.17 | 1707426 | 1707.426 | 30.7 | 49.3 | 1863540 | 1863.54 | 30
3/5/20XX 8:00:00 AM | 0.33333 | 1 | 31.4 | 58 | 31.4 |  | 31.4 | 67.94 | 12.06 | 455868 | 455.868 | 63.88 | 16.12 | 609336 | 609.336 | 59.82 | 20.18 | 762804 | 762.804 | 55.76 | 24.24 | 916272 | 916.272 | 51.7 | 28.3 | 1069740 | 1069.74 | 47.64 | 32.36 | 1223208 | 1223.208 | 43.58 | 36.42 | 1376676 | 1376.676 | 39.52 | 40.48 | 1530144 | 1530.144 | 35.46 | 44.54 | 1683612 | 1683.612 | 31.4 | 48.6 | 1837080 | 1837.08 | 30
3/5/20XX 9:00:00 AM | 0.375 | 1 | 32.9 | 53.6 | 32.9 |  | 32.9 | 68.09 | 11.91 | 450198 | 450.198 | 64.18 | 15.82 | 597996 | 597.996 | 60.27 | 19.73 | 745794 | 745.794 | 56.36 | 23.64 | 893592 | 893.592 | 52.45 | 27.55 | 1041390 | 1041.39 | 48.54 | 31.46 | 1189188 | 1189.188 | 44.63 | 35.37 | 1336986 | 1336.986 | 40.72 | 39.28 | 1484784 | 1484.784 | 36.81 | 43.19 | 1632582 | 1632.582 | 32.9 | 47.1 | 1780380 | 1780.38 | 35
3/5/20XX 10:00:00 AM | 0.41667 | 1 | 34.8 | 49.7 | 34.8 |  | 34.8 | 68.28 | 11.72 | 443016 | 443.016 | 64.56 | 15.44 | 583632 | 583.632 | 60.84 | 19.16 | 724248 | 724.248 | 57.12 | 22.88 | 864864 | 864.864 | 53.4 | 26.6 | 1005480 | 1005.48 | 49.68 | 30.32 | 1146096 | 1146.096 | 45.96 | 34.04 | 1286712 | 1286.712 | 42.24 | 37.76 | 1427328 | 1427.328 | 38.52 | 41.48 | 1567944 | 1567.944 | 34.8 | 45.2 | 1708560 | 1708.56 | 35
3/5/20XX 11:00:00 AM | 0.45833 | 1 | 37.7 | 45.5 | 37.7 |  | 37.7 | 68.57 | 11.43 | 432054 | 432.054 | 65.14 | 14.86 | 561708 | 561.708 | 61.71 | 18.29 | 691362 | 691.362 | 58.28 | 21.72 | 821016 | 821.016 | 54.85 | 25.15 | 950670 | 950.67 | 51.42 | 28.58 | 1080324 | 1080.324 | 47.99 | 32.01 | 1209978 | 1209.978 | 44.56 | 35.44 | 1339632 | 1339.632 | 41.13 | 38.87 | 1469286 | 1469.286 | 37.7 | 42.3 | 1598940 | 1598.94 | 40
3/5/20XX 12:00:00 PM | 0.5 | 1 | 39.5 | 42.3 | 39.5 |  | 39.5 | 68.75 | 11.25 | 425250 | 425.25 | 65.5 | 14.5 | 548100 | 548.1 | 62.25 | 17.75 | 670950 | 670.95 | 59 | 21 | 793800 | 793.8 | 55.75 | 24.25 | 916650 | 916.65 | 52.5 | 27.5 | 1039500 | 1039.5 | 49.25 | 30.75 | 1162350 | 1162.35 | 46 | 34 | 1285200 | 1285.2 | 42.75 | 37.25 | 1408050 | 1408.05 | 39.5 | 40.5 | 1530900 | 1530.9 | 40
3/5/20XX 1:00:00 PM | 0.54167 | 1 | 40.1 | 40.3 | 40.1 |  | 40.1 | 68.81 | 11.19 | 422982 | 422.982 | 65.62 | 14.38 | 543564 | 543.564 | 62.43 | 17.57 | 664146 | 664.146 | 59.24 | 20.76 | 784728 | 784.728 | 56.05 | 23.95 | 905310 | 905.31 | 52.86 | 27.14 | 1025892 | 1025.892 | 49.67 | 30.33 | 1146474 | 1146.474 | 46.48 | 33.52 | 1267056 | 1267.056 | 43.29 | 36.71 | 1387638 | 1387.638 | 40.1 | 39.9 | 1508220 | 1508.22 | 40
3/5/20XX 2:00:00 PM | 0.58333 | 1 | 40.6 | 39.4 | 40.6 |  | 40.6 | 68.86 | 11.14 | 421092 | 421.092 | 65.72 | 14.28 | 539784 | 539.784 | 62.58 | 17.42 | 658476 | 658.476 | 59.44 | 20.56 | 777168 | 777.168 | 56.3 | 23.7 | 895860 | 895.86 | 53.16 | 26.84 | 1014552 | 1014.552 | 50.02 | 29.98 | 1133244 | 1133.244 | 46.88 | 33.12 | 1251936 | 1251.936 | 43.74 | 36.26 | 1370628 | 1370.628 | 40.6 | 39.4 | 1489320 | 1489.32 | 40
3/5/20XX 3:00:00 PM | 0.625 | 1 | 41.1 | 39.7 | 41.1 |  | 41.1 | 68.91 | 11.09 | 419202 | 419.202 | 65.82 | 14.18 | 536004 | 536.004 | 62.73 | 17.27 | 652806 | 652.806 | 59.64 | 20.36 | 769608 | 769.608 | 56.55 | 23.45 | 886410 | 886.41 | 53.46 | 26.54 | 1003212 | 1003.212 | 50.37 | 29.63 | 1120014 | 1120.014 | 47.28 | 32.72 | 1236816 | 1236.816 | 44.19 | 35.81 | 1353618 | 1353.618 | 41.1 | 38.9 | 1470420 | 1470.42 | 40
3/5/20XX 4:00:00 PM | 0.66667 | 1 | 40.8 | 39.9 | 40.8 |  | 40.8 | 68.88 | 11.12 | 420336 | 420.336 | 65.76 | 14.24 | 538272 | 538.272 | 62.64 | 17.36 | 656208 | 656.208 | 59.52 | 20.48 | 774144 | 774.144 | 56.4 | 23.6 | 892080 | 892.08 | 53.28 | 26.72 | 1010016 | 1010.016 | 50.16 | 29.84 | 1127952 | 1127.952 | 47.04 | 32.96 | 1245888 | 1245.888 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.8 | 39.2 | 1481760 | 1481.76 | 40
3/5/20XX 5:00:00 PM | 0.70833 | 1 | 39.8 | 42.9 | 39.8 |  | 39.8 | 68.78 | 11.22 | 424116 | 424.116 | 65.56 | 14.44 | 545832 | 545.832 | 62.34 | 17.66 | 667548 | 667.548 | 59.12 | 20.88 | 789264 | 789.264 | 55.9 | 24.1 | 910980 | 910.98 | 52.68 | 27.32 | 1032696 | 1032.696 | 49.46 | 30.54 | 1154412 | 1154.412 | 46.24 | 33.76 | 1276128 | 1276.128 | 43.02 | 36.98 | 1397844 | 1397.844 | 39.8 | 40.2 | 1519560 | 1519.56 | 40
3/5/20XX 6:00:00 PM | 0.75 | 1 | 38.4 | 47.1 | 38.4 |  | 38.4 | 68.64 | 11.36 | 429408 | 429.408 | 65.28 | 14.72 | 556416 | 556.416 | 61.92 | 18.08 | 683424 | 683.424 | 58.56 | 21.44 | 810432 | 810.432 | 55.2 | 24.8 | 937440 | 937.44 | 51.84 | 28.16 | 1064448 | 1064.448 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.12 | 34.88 | 1318464 | 1318.464 | 41.76 | 38.24 | 1445472 | 1445.472 | 38.4 | 41.6 | 1572480 | 1572.48 | 40
3/5/20XX 7:00:00 PM | 0.79167 | 1 | 37.6 | 48 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/5/20XX 8:00:00 PM | 0.83333 | 1 | 36.8 | 47.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/5/20XX 9:00:00 PM | 0.875 | 1 | 35.7 | 48.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/5/20XX 10:00:00 PM | 0.91667 | 1 | 35.4 | 47.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/5/20XX 11:00:00 PM | 0.95833 | 1 | 34.7 | 50 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/5/20XX 12:00:00 AM | 0 | 2 | 33.8 | 51.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/6/20XX 1:00:00 AM | 0.041667 | 2 | 33.3 | 52.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/6/20XX 2:00:00 AM | 0.083333 | 2 | 32.6 | 53.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/6/20XX 3:00:00 AM | 0.125 | 2 | 32.2 | 53.7 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/6/20XX 4:00:00 AM | 0.16667 | 2 | 31.6 | 54.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/6/20XX 5:00:00 AM | 0.20833 | 2 | 31.5 | 55.1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/6/20XX 6:00:00 AM | 0.25 | 2 | 31.2 | 55 | 31.2 |  | 31.2 | 67.92 | 12.08 | 456624 | 456.624 | 63.84 | 16.16 | 610848 | 610.848 | 59.76 | 20.24 | 765072 | 765.072 | 55.68 | 24.32 | 919296 | 919.296 | 51.6 | 28.4 | 1073520 | 1073.52 | 47.52 | 32.48 | 1227744 | 1227.744 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.36 | 40.64 | 1536192 | 1536.192 | 35.28 | 44.72 | 1690416 | 1690.416 | 31.2 | 48.8 | 1844640 | 1844.64 | 30
3/6/20XX 7:00:00 AM | 0.29167 | 2 | 31.2 | 55.4 | 31.2 |  | 31.2 | 67.92 | 12.08 | 456624 | 456.624 | 63.84 | 16.16 | 610848 | 610.848 | 59.76 | 20.24 | 765072 | 765.072 | 55.68 | 24.32 | 919296 | 919.296 | 51.6 | 28.4 | 1073520 | 1073.52 | 47.52 | 32.48 | 1227744 | 1227.744 | 43.44 | 36.56 | 1381968 | 1381.968 | 39.36 | 40.64 | 1536192 | 1536.192 | 35.28 | 44.72 | 1690416 | 1690.416 | 31.2 | 48.8 | 1844640 | 1844.64 | 30
3/6/20XX 8:00:00 AM | 0.33333 | 2 | 32.4 | 54.2 | 32.4 |  | 32.4 | 68.04 | 11.96 | 452088 | 452.088 | 64.08 | 15.92 | 601776 | 601.776 | 60.12 | 19.88 | 751464 | 751.464 | 56.16 | 23.84 | 901152 | 901.152 | 52.2 | 27.8 | 1050840 | 1050.84 | 48.24 | 31.76 | 1200528 | 1200.528 | 44.28 | 35.72 | 1350216 | 1350.216 | 40.32 | 39.68 | 1499904 | 1499.904 | 36.36 | 43.64 | 1649592 | 1649.592 | 32.4 | 47.6 | 1799280 | 1799.28 | 30
3/6/20XX 9:00:00 AM | 0.375 | 2 | 34.1 | 51.7 | 34.1 |  | 34.1 | 68.21 | 11.79 | 445662 | 445.662 | 64.42 | 15.58 | 588924 | 588.924 | 60.63 | 19.37 | 732186 | 732.186 | 56.84 | 23.16 | 875448 | 875.448 | 53.05 | 26.95 | 1018710 | 1018.71 | 49.26 | 30.74 | 1161972 | 1161.972 | 45.47 | 34.53 | 1305234 | 1305.234 | 41.68 | 38.32 | 1448496 | 1448.496 | 37.89 | 42.11 | 1591758 | 1591.758 | 34.1 | 45.9 | 1735020 | 1735.02 | 35
3/6/20XX 10:00:00 AM | 0.41667 | 2 | 35.6 | 49.6 | 35.6 |  | 35.6 | 68.36 | 11.64 | 439992 | 439.992 | 64.72 | 15.28 | 577584 | 577.584 | 61.08 | 18.92 | 715176 | 715.176 | 57.44 | 22.56 | 852768 | 852.768 | 53.8 | 26.2 | 990360 | 990.36 | 50.16 | 29.84 | 1127952 | 1127.952 | 46.52 | 33.48 | 1265544 | 1265.544 | 42.88 | 37.12 | 1403136 | 1403.136 | 39.24 | 40.76 | 1540728 | 1540.728 | 35.6 | 44.4 | 1678320 | 1678.32 | 35
3/6/20XX 11:00:00 AM | 0.45833 | 2 | 38 | 46.5 | 38 |  | 38 | 68.6 | 11.4 | 430920 | 430.92 | 65.2 | 14.8 | 559440 | 559.44 | 61.8 | 18.2 | 687960 | 687.96 | 58.4 | 21.6 | 816480 | 816.48 | 55 | 25 | 945000 | 945 | 51.6 | 28.4 | 1073520 | 1073.52 | 48.2 | 31.8 | 1202040 | 1202.04 | 44.8 | 35.2 | 1330560 | 1330.56 | 41.4 | 38.6 | 1459080 | 1459.08 | 38 | 42 | 1587600 | 1587.6 | 40
3/6/20XX 12:00:00 PM | 0.5 | 2 | 40.5 | 44.1 | 40.5 |  | 40.5 | 68.85 | 11.15 | 421470 | 421.47 | 65.7 | 14.3 | 540540 | 540.54 | 62.55 | 17.45 | 659610 | 659.61 | 59.4 | 20.6 | 778680 | 778.68 | 56.25 | 23.75 | 897750 | 897.75 | 53.1 | 26.9 | 1016820 | 1016.82 | 49.95 | 30.05 | 1135890 | 1135.89 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.65 | 36.35 | 1374030 | 1374.03 | 40.5 | 39.5 | 1493100 | 1493.1 | 40
3/6/20XX 1:00:00 PM | 0.54167 | 2 | 41.3 | 42.8 | 41.3 |  | 41.3 | 68.93 | 11.07 | 418446 | 418.446 | 65.86 | 14.14 | 534492 | 534.492 | 62.79 | 17.21 | 650538 | 650.538 | 59.72 | 20.28 | 766584 | 766.584 | 56.65 | 23.35 | 882630 | 882.63 | 53.58 | 26.42 | 998676 | 998.676 | 50.51 | 29.49 | 1114722 | 1114.722 | 47.44 | 32.56 | 1230768 | 1230.768 | 44.37 | 35.63 | 1346814 | 1346.814 | 41.3 | 38.7 | 1462860 | 1462.86 | 40
3/6/20XX 2:00:00 PM | 0.58333 | 2 | 42.5 | 42.1 | 42.5 |  | 42.5 | 69.05 | 10.95 | 413910 | 413.91 | 66.1 | 13.9 | 525420 | 525.42 | 63.15 | 16.85 | 636930 | 636.93 | 60.2 | 19.8 | 748440 | 748.44 | 57.25 | 22.75 | 859950 | 859.95 | 54.3 | 25.7 | 971460 | 971.46 | 51.35 | 28.65 | 1082970 | 1082.97 | 48.4 | 31.6 | 1194480 | 1194.48 | 45.45 | 34.55 | 1305990 | 1305.99 | 42.5 | 37.5 | 1417500 | 1417.5 | 40
3/6/20XX 3:00:00 PM | 0.625 | 2 | 43 | 41.6 | 43 |  | 43 | 69.1 | 10.9 | 412020 | 412.02 | 66.2 | 13.8 | 521640 | 521.64 | 63.3 | 16.7 | 631260 | 631.26 | 60.4 | 19.6 | 740880 | 740.88 | 57.5 | 22.5 | 850500 | 850.5 | 54.6 | 25.4 | 960120 | 960.12 | 51.7 | 28.3 | 1069740 | 1069.74 | 48.8 | 31.2 | 1179360 | 1179.36 | 45.9 | 34.1 | 1288980 | 1288.98 | 43 | 37 | 1398600 | 1398.6 | 45
3/6/20XX 4:00:00 PM | 0.66667 | 2 | 42.6 | 43.1 | 42.6 |  | 42.6 | 69.06 | 10.94 | 413532 | 413.532 | 66.12 | 13.88 | 524664 | 524.664 | 63.18 | 16.82 | 635796 | 635.796 | 60.24 | 19.76 | 746928 | 746.928 | 57.3 | 22.7 | 858060 | 858.06 | 54.36 | 25.64 | 969192 | 969.192 | 51.42 | 28.58 | 1080324 | 1080.324 | 48.48 | 31.52 | 1191456 | 1191.456 | 45.54 | 34.46 | 1302588 | 1302.588 | 42.6 | 37.4 | 1413720 | 1413.72 | 45
3/6/20XX 5:00:00 PM | 0.70833 | 2 | 41.9 | 45.8 | 41.9 |  | 41.9 | 68.99 | 11.01 | 416178 | 416.178 | 65.98 | 14.02 | 529956 | 529.956 | 62.97 | 17.03 | 643734 | 643.734 | 59.96 | 20.04 | 757512 | 757.512 | 56.95 | 23.05 | 871290 | 871.29 | 53.94 | 26.06 | 985068 | 985.068 | 50.93 | 29.07 | 1098846 | 1098.846 | 47.92 | 32.08 | 1212624 | 1212.624 | 44.91 | 35.09 | 1326402 | 1326.402 | 41.9 | 38.1 | 1440180 | 1440.18 | 40
3/6/20XX 6:00:00 PM | 0.75 | 2 | 40.9 | 49.2 | 40.9 |  | 40.9 | 68.89 | 11.11 | 419958 | 419.958 | 65.78 | 14.22 | 537516 | 537.516 | 62.67 | 17.33 | 655074 | 655.074 | 59.56 | 20.44 | 772632 | 772.632 | 56.45 | 23.55 | 890190 | 890.19 | 53.34 | 26.66 | 1007748 | 1007.748 | 50.23 | 29.77 | 1125306 | 1125.306 | 47.12 | 32.88 | 1242864 | 1242.864 | 44.01 | 35.99 | 1360422 | 1360.422 | 40.9 | 39.1 | 1477980 | 1477.98 | 40
3/6/20XX 7:00:00 PM | 0.79167 | 2 | 41 | 50.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/6/20XX 8:00:00 PM | 0.83333 | 2 | 40.5 | 52.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/6/20XX 9:00:00 PM | 0.875 | 2 | 40.4 | 52 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/6/20XX 10:00:00 PM | 0.91667 | 2 | 39.9 | 53.3 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/6/20XX 11:00:00 PM | 0.95833 | 2 | 39.8 | 53.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/6/20XX 12:00:00 AM | 0 | 3 | 39.2 | 55.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/7/20XX 1:00:00 AM | 0.041667 | 3 | 38.4 | 60.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/7/20XX 2:00:00 AM | 0.083333 | 3 | 38.1 | 63.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/7/20XX 3:00:00 AM | 0.125 | 3 | 37.9 | 65.8 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/7/20XX 4:00:00 AM | 0.16667 | 3 | 36.5 | 66.9 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/7/20XX 5:00:00 AM | 0.20833 | 3 | 36.5 | 67.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3/7/20XX 6:00:00 AM | 0.25 | 3 | 36 | 69.4 | 36 |  | 36 | 68.4 | 11.6 | 438480 | 438.48 | 64.8 | 15.2 | 574560 | 574.56 | 61.2 | 18.8 | 710640 | 710.64 | 57.6 | 22.4 | 846720 | 846.72 | 54 | 26 | 982800 | 982.8 | 50.4 | 29.6 | 1118880 | 1118.88 | 46.8 | 33.2 | 1254960 | 1254.96 | 43.2 | 36.8 | 1391040 | 1391.04 | 39.6 | 40.4 | 1527120 | 1527.12 | 36 | 44 | 1663200 | 1663.2 | 35
3/7/20XX 7:00:00 AM | 0.29167 | 3 | 36.5 | 67.3 | 36.5 |  | 36.5 | 68.45 | 11.55 | 436590 | 436.59 | 64.9 | 15.1 | 570780 | 570.78 | 61.35 | 18.65 | 704970 | 704.97 | 57.8 | 22.2 | 839160 | 839.16 | 54.25 | 25.75 | 973350 | 973.35 | 50.7 | 29.3 | 1107540 | 1107.54 | 47.15 | 32.85 | 1241730 | 1241.73 | 43.6 | 36.4 | 1375920 | 1375.92 | 40.05 | 39.95 | 1510110 | 1510.11 | 36.5 | 43.5 | 1644300 | 1644.3 | 35
3/7/20XX 8:00:00 AM | 0.33333 | 3 | 36.9 | 68.1 | 36.9 |  | 36.9 | 68.49 | 11.51 | 435078 | 435.078 | 64.98 | 15.02 | 567756 | 567.756 | 61.47 | 18.53 | 700434 | 700.434 | 57.96 | 22.04 | 833112 | 833.112 | 54.45 | 25.55 | 965790 | 965.79 | 50.94 | 29.06 | 1098468 | 1098.468 | 47.43 | 32.57 | 1231146 | 1231.146 | 43.92 | 36.08 | 1363824 | 1363.824 | 40.41 | 39.59 | 1496502 | 1496.502 | 36.9 | 43.1 | 1629180 | 1629.18 | 35
3/7/20XX 9:00:00 AM | 0.375 | 3 | 38.3 | 66.7 | 38.3 |  | 38.3 | 68.63 | 11.37 | 429786 | 429.786 | 65.26 | 14.74 | 557172 | 557.172 | 61.89 | 18.11 | 684558 | 684.558 | 58.52 | 21.48 | 811944 | 811.944 | 55.15 | 24.85 | 939330 | 939.33 | 51.78 | 28.22 | 1066716 | 1066.716 | 48.41 | 31.59 | 1194102 | 1194.102 | 45.04 | 34.96 | 1321488 | 1321.488 | 41.67 | 38.33 | 1448874 | 1448.874 | 38.3 | 41.7 | 1576260 | 1576.26 | 40
3/7/20XX 10:00:00 AM | 0.41667 | 3 | 39.9 | 65.2 | 39.9 |  | 39.9 | 68.79 | 11.21 | 423738 | 423.738 | 65.58 | 14.42 | 545076 | 545.076 | 62.37 | 17.63 | 666414 | 666.414 | 59.16 | 20.84 | 787752 | 787.752 | 55.95 | 24.05 | 909090 | 909.09 | 52.74 | 27.26 | 1030428 | 1030.428 | 49.53 | 30.47 | 1151766 | 1151.766 | 46.32 | 33.68 | 1273104 | 1273.104 | 43.11 | 36.89 | 1394442 | 1394.442 | 39.9 | 40.1 | 1515780 | 1515.78 | 40
3/7/20XX 11:00:00 AM | 0.45833 | 3 | 42.2 | 60.3 | 42.2 |  | 42.2 | 69.02 | 10.98 | 415044 | 415.044 | 66.04 | 13.96 | 527688 | 527.688 | 63.06 | 16.94 | 640332 | 640.332 | 60.08 | 19.92 | 752976 | 752.976 | 57.1 | 22.9 | 865620 | 865.62 | 54.12 | 25.88 | 978264 | 978.264 | 51.14 | 28.86 | 1090908 | 1090.908 | 48.16 | 31.84 | 1203552 | 1203.552 | 45.18 | 34.82 | 1316196 | 1316.196 | 42.2 | 37.8 | 1428840 | 1428.84 | 40
3/7/20XX 12:00:00 PM | 0.5 | 3 | 44.2 | 58.4 | 44.2 |  | 44.2 | 69.22 | 10.78 | 407484 | 407.484 | 66.44 | 13.56 | 512568 | 512.568 | 63.66 | 16.34 | 617652 | 617.652 | 60.88 | 19.12 | 722736 | 722.736 | 58.1 | 21.9 | 827820 | 827.82 | 55.32 | 24.68 | 932904 | 932.904 | 52.54 | 27.46 | 1037988 | 1037.988 | 49.76 | 30.24 | 1143072 | 1143.072 | 46.98 | 33.02 | 1248156 | 1248.156 | 44.2 | 35.8 | 1353240 | 1353.24 | 45
3/7/20XX 1:00:00 PM | 0.54167 | 3 | 45.3 | 57.4 | 45.3 |  | 45.3 | 69.33 | 10.67 | 403326 | 403.326 | 66.66 | 13.34 | 504252 | 504.252 | 63.99 | 16.01 | 605178 | 605.178 | 61.32 | 18.68 | 706104 | 706.104 | 58.65 | 21.35 | 807030 | 807.03 | 55.98 | 24.02 | 907956 | 907.956 | 53.31 | 26.69 | 1008882 | 1008.882 | 50.64 | 29.36 | 1109808 | 1109.808 | 47.97 | 32.03 | 1210734 | 1210.734 | 45.3 | 34.7 | 1311660 | 1311.66 | 45
3/7/20XX 2:00:00 PM | 0.58333 | 3 | 47.6 | 54.5 | 47.6 |  | 47.6 | 69.56 | 10.44 | 394632 | 394.632 | 67.12 | 12.88 | 486864 | 486.864 | 64.68 | 15.32 | 579096 | 579.096 | 62.24 | 17.76 | 671328 | 671.328 | 59.8 | 20.2 | 763560 | 763.56 | 57.36 | 22.64 | 855792 | 855.792 | 54.92 | 25.08 | 948024 | 948.024 | 52.48 | 27.52 | 1040256 | 1040.256 | 50.04 | 29.96 | 1132488 | 1132.488 | 47.6 | 32.4 | 1224720 | 1224.72 | 50
3/7/20XX 3:00:00 PM | 0.625 | 3 | 48.4 | 53.2 | 48.4 |  | 48.4 | 69.64 | 10.36 | 391608 | 391.608 | 67.28 | 12.72 | 480816 | 480.816 | 64.92 | 15.08 | 570024 | 570.024 | 62.56 | 17.44 | 659232 | 659.232 | 60.2 | 19.8 | 748440 | 748.44 | 57.84 | 22.16 | 837648 | 837.648 | 55.48 | 24.52 | 926856 | 926.856 | 53.12 | 26.88 | 1016064 | 1016.064 | 50.76 | 29.24 | 1105272 | 1105.272 | 48.4 | 31.6 | 1194480 | 1194.48 | 50
3/7/20XX 4:00:00 PM | 0.66667 | 3 | 47.8 | 55.8 | 47.8 |  | 47.8 | 69.58 | 10.42 | 393876 | 393.876 | 67.16 | 12.84 | 485352 | 485.352 | 64.74 | 15.26 | 576828 | 576.828 | 62.32 | 17.68 | 668304 | 668.304 | 59.9 | 20.1 | 759780 | 759.78 | 57.48 | 22.52 | 851256 | 851.256 | 55.06 | 24.94 | 942732 | 942.732 | 52.64 | 27.36 | 1034208 | 1034.208 | 50.22 | 29.78 | 1125684 | 1125.684 | 47.8 | 32.2 | 1217160 | 1217.16 | 50
3/7/20XX 5:00:00 PM | 0.70833 | 3 | 47.3 | 56 | 47.3 |  | 47.3 | 69.53 | 10.47 | 395766 | 395.766 | 67.06 | 12.94 | 489132 | 489.132 | 64.59 | 15.41 | 582498 | 582.498 | 62.12 | 17.88 | 675864 | 675.864 | 59.65 | 20.35 | 769230 | 769.23 | 57.18 | 22.82 | 862596 | 862.596 | 54.71 | 25.29 | 955962 | 955.962 | 52.24 | 27.76 | 1049328 | 1049.328 | 49.77 | 30.23 | 1142694 | 1142.694 | 47.3 | 32.7 | 1236060 | 1236.06 | 45
3/7/20XX 6:00:00 PM | 0.75 | 3 | 46.4 | 58.5 | 46.4 |  | 46.4 | 69.44 | 10.56 | 399168 | 399.168 | 66.88 | 13.12 | 495936 | 495.936 | 64.32 | 15.68 | 592704 | 592.704 | 61.76 | 18.24 | 689472 | 689.472 | 59.2 | 20.8 | 786240 | 786.24 | 56.64 | 23.36 | 883008 | 883.008 | 54.08 | 25.92 | 979776 | 979.776 | 51.52 | 28.48 | 1076544 | 1076.544 | 48.96 | 31.04 | 1173312 | 1173.312 | 46.4 | 33.6 | 1270080 | 1270.08 | 45
3/7/20XX 7:00:00 PM | 0.79167 | 3 | 45.8 | 59.6 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0